| NOGRR Number | 106 | NOGRR Title | Delegation of Firm Load Shedding Responsibility |
| --- | --- | --- | --- |

| Date | November 12, 2012 |
| --- | --- |

| Submitter’s Information |
| --- |
| Name | Gary Miller |
| E-mail Address | gmiller@btutilities.com |
| Company | Bryan Texas Utilities |
| Phone Number | (979) 821-5621 |
| Cell Number | (979) 820-0487 |
| Market Segment | Municipal |

Comments

Further revisions are needed to Section 4.5.3.4, Load Shed Obligation, to assure proper calculation of firm Load shed share given delegation of responsibility.

Revised Cover Page Language

| NOGRR Number | 106 | NOGRR Title | Delegation of Firm Load Shedding Responsibility |
| --- | --- | --- | --- |

| Nodal Operating Guide Section(s) Requiring Revision | 2.6.1, Automatic Firm Load Shedding 4.5.3, Implementation 4.5.3.4, Load Shed Obligation |
| --- | --- |

Revised Proposed Guide Language

### 2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.  The under-frequency relays shall be set to provide Load relief as follows:

| Frequency Threshold | Load Relief |
| --- | --- |
| 59.3 Hz | 5% of the ERCOT System Load (Total 5%) |
| 58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%) |
| 58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%) |

(2)	With the assistance of applicable Transmission Operators (TO), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC).  For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times.  It is not permitted to use rounding to meet the minimum.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another Entity and the Entity’s associated TO.  ERCOT will be notified in writing and provided with the details of any such arrangement prior to implementation.

(3)	ERCOT will direct a review of the automatic firm Load shedding program whenever warranted by conditions.  At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm Load shedding conducted at five-year intervals beginning in the Summer of 2001.

(4)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay.

(5)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay of no more than 30 cycles.  Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(6)	If a loss of Load occurs due to the operation of under-frequency relays, a TO designated by a DSP to shed Load may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased by a TO without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  TOs, in coordination with DSPs, shall exercise extreme caution in restoring Load so that the capability limits of Generation Resources and Transmission Facilities are not exceeded.

(7)	Whenever possible, TOs and DSPs shall not manually drop Load connected to under-frequency relays during the implementation of Level 3 of an Energy Emergency Alert (EEA).

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EEA levels below, notifying all Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs), and coordinating the implementation of the EEA conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EEA level.

(2)	During the EEA, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using Direct Current Tie(s) (DC Tie(s)) or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with North American Electric Reliability Corporation (NERC) scheduling guidelines.

(3) 	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all levels in sequence.  ERCOT may immediately implement Level 3 of the EEA any time the steady-state system frequency is below 59.8 Hz and shall immediately implement Level 3 any time the steady-state frequency is below 59.5 Hz.

(5)	Percentages for Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EEA levels to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that level (and all above if not previously accomplished) and if ordered by the ERCOT shift supervisor or his designate, shall report back to the ERCOT System Operator when the requested level has been completed.

(7)	During EEA Level 3, ERCOT must be capable of shedding sufficient firm Load to arrest frequency decay and to prevent generator tripping.  The amount of firm Load to be shed may vary depending on ERCOT Transmission Grid conditions during the event.  Each TSP will be capable of shedding its allocation of firm Load, without delay.  The maximum time for the TSP to interrupt firm Load will depend on how much Load is to be shed and whether the Load is to be interrupted by Supervisory Control and Data Acquisition (SCADA) or by the dispatch of personnel to substations.  Since the need for firm Load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm Load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed 30 minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed Load will be implemented within a time period not to exceed one hour;

(c)	The initial clock on the firm Load shed shall apply only to Load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first Load shed instruction, ERCOT determines that an additional amount of firm Load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

(8)	A DSP may by mutual agreement arrange to have all or part of its EEA Load shedding requirement performed by another Entity and the Entity’s associated TO.  ERCOT will be notified in writing and provided with the details of any such arrangement prior to implementation.

(9)	Each TSP, or its designated agent, will provide ERCOT a status report of Load shed progress within 30 minutes of the time of ERCOT’s instruction or upon ERCOT’s request.

4.5.3.4	Load Shed Obligation

Obligation for Load shed is by DSP.  Load shedding obligations need to be represented by a qualified TO with sufficient control over load serving breakers to meet the obligation.  Percentages for Level 3 Load shedding will be based on the previous year’s peak Loads as calculated to determine transmission cost of service and aggregated to the appropriate TO by ERCOT according to Load shed obligation as described in Section 4.5.3, Implementation.  This obligation will be reviewed by ERCOT and modified annually.

ERCOT Load Shed Table

| Transmission Operator | 2011 Total Transmission Operator Load (MW) |
| --- | --- |
| American Electric Power Service Corp. | 8.63 |
| Brazos Electric Power Cooperative Inc. | 4.85 |
| Brownsville Public Utilities Board | 0.40 |
| Bryan Texas Utilities | 0.79 |
| CenterPoint Energy Houston Electric LLC | 24.42 |
| City of Austin DBA Austin Energy | 3.93 |
| City of Garland | 0.76 |
| CPS Energy (San Antonio) | 7.09 |
| Denton Municipal Electric | 0.52 |
| GEUS (Greenville) | 0.17 |
| LCRA Transmission Services Corporation | 5.42 |
| Oncor Electric Delivery Company LLC | 37.59 |
| Rayburn Country Electric Cooperative Inc. DBA Rayburn Electric | 1.17 |
| South Texas Electric Cooperative Inc. | 1.84 |
| Texas-New Mexico Power Company | 2.42 |
| ERCOT Total | 100.00 |