## Sheet1
Requirement |  | Resource Registration Glossary | [10 empty] | Data Validation Rules
Groups that use data element | Purpose of data element | RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | RARF DATA FIELD | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS)
|  | Static Var Compensator Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke |  | N | N
|  | Static Var Compensator Data | X | X | X |  | All Caps | SVC Name | Static Var Compensator name as provided in the ERCOT model, which must be 14 characters or less and contain no special characters other than an underscore "_" meet the character limitation of the system. |  |  | R | SVC Name | 1) This field is required 2) May not be > than 14 characters..Warning! SVC Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke |  | N | N
|  | Static Var Compensator Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R | ERCOT Station Name (Station Code or Station Mnemonic) | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B/DVE | Joel Koepke |  | N | N
|  | Static Var Compensator Data | X | X | X |  | Automatic | SVC Code | Concatenated code automatically provided |  |  | A | SVC CODE | Concantenate (Site Code_Substation Code_SVC Name) | [5 empty] | N | N
|  | Static Var Compensator Data | X | X | X |  | kV | SVC Base Voltage Level | Enter base voltage for this SVC device (i.e. voltage that the SVC is modeled at) |  | R | R | SVC Base Voltage Level | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | MVAr | Fixed MVAr (var injections at Nominal Voltage) | Enter fixed MVAr for this SVC device at nominal voltage |  | R | R | Fixed Mvar (var injection At Nominal Voltage) | 1) This field is required 2. Value must be numeric | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | p.u. | Minimum Admittance Limits (100 MVA base) | Minimum Admittance Limits (100 MVA base) |  | R | R | Minimum Admittance Limits (1 MVA Base) | 1) This field is required 2) Value must be <= Maximum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | p.u. | Maximum Admittance Limits (100 MVA base) | Maximum Admittance Limits (100 MVA base) |  | R | R | Maximum Admittance Limits (1 MVA Base) | 1) This field is required 2) Value must be >= Minimum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | MVAr | Minimum Steady State Reactive power Limits (100 MVA base) | Minimum Steady State Reactive power Limits (100 MVA base) |  | R | R | Minimum Steady State Reactive Power Limits | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | MVAr | Maximum Steady State Reactive power Limits (100 MVA base) | Maximum Steady State Reactive power Limits (100 MVA base) |  | R | R | Maximum Steady State Reactive Power Limits | 1) This field is required 2) Value must be >= Minimum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | MVAr | Minimum Threshold (post contingency) Reactive Power Limits | Minimum Threshold (post contingency) Reactive Power Limits |  | R | R | Minimum Threshold (post Contingency) Reactive Power Limits | 1) This field is required 2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | MVAr | Maximum Threshold (post contingency) Reactive Power Limits | Maximum Threshold (post contingency) Reactive Power Limits |  | R | R | Maximum Threshold (post Contingency) Reactive Power Limits | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | kV | Minimum Voltage Threshold | Minimum Voltage Threshold |  | R | R | Minimum Voltage Threshold | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | kV | Maximum Voltage Threshold | Maximum Voltage Threshold |  | R | R | Maximum Voltage Threshold | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  | N | Y
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this SVC (can provide up to 10) |  |  | R | Device Name(s) - that this reactive device is directly connected to | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke |  | N | N
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this SVC (can provide up to 10) |  |  | C
|  | Static Var Compensator Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O | COMMENTS | [6 empty] | N | N
|  | Static Var Compensator Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R | EFFECTIVE DATE: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie |  | N | N
|  | Series Device Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | All Caps | Series Device Name | Series Device name as provided in the ERCOT model, which must be 14 characters or less and contain no special characters other than an underscore "_" meet the character limitation of the system. |  |  | R | Series Device Name | 1) This field is required 2) No special characters except and underscore 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Series Device Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R | Ercot Station Code Mnemonic | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | Automatic | SD Code | Concatenated code automatically provided |  |  | A | SD Code | Concantenate (Site Code_Substation Code_SD Name) | [5 empty] | N | N
|  | Series Device Data | X | X | X |  | kV | Voltage Level | Enter voltage for this Series device |  | R | R | Voltage Level | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | p.u. | Resistance | Enter resistance for this series device (100 MVA base) |  | R | R | Resistance | 1) This value is required 2) Value must be > 0 | T | Float | B | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | p.u. | Reactance | Enter reactance for this series device (100 MVA base) |  | R | R | Reactance | 1) This value is required 2) Value may be negative. Allow negative Reactance (to represent Series Capacitors) 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | T | Float | B | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | MVA | Continuous Rating | Rating that device can operate at indefinitely without damage, or violation fo NESC clearances. |  | R | R | Continuous Rating | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | MVA | 2-hr Emergency Rating | Rating that device can operate at this rating for two hours without violation of NESC clearances or equipment failure |  | R | R | 2-hr Emergency Rating | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <=15-min Rating | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | MVA | 15-min Rating | Rating that device can operate at this rating for fifteen minutes without violation of NESC clearances or equipment failure |  | R | R | 15-min Rating | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | T | Float | B/DVE | Joel Koepke |  | N | Y
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | R | Side 1 - Connected Switching Device Name(s) | 1) This field is required 2) May not have duplicates within the TO or FROM Station. Warning Only 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to side 1 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Bus number for Side 1 of this Series Device |  |  | O | Side 1 - Bus Number (PTI Bus Number) | 1) This field is optional 2) This field must be between 1 - 999,999 | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 1 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | R | Side 2 - Connected Switching Device Name(s) | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 2 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 3 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 4 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 5 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 6 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 7 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 8 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 9 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | All Caps | Connected Device 10 | Enter device connected to side 2 of this Series Device (can provide up to 10) |  |  | C
|  | Series Device Data | X | X | X |  | Number | Bus Number (PTI Bus Number) | Bus number for Side 2 of this Series Device |  |  | O | Side 2 - Bus Number (PTI Bus Number) | 1) This field is optional 2) This field must be between 1 - 999,999 | T | Integer | B/DVE | Joel Koepke |  | N | N
|  | Series Device Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O | COMMENTS | [6 empty] | N | N
|  | Series Device Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R | EFFECTIVE DATE: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie |  | N | N
|  | Load Data | X | X | X |  | List | Description of Change | Select: description of change from drop down list: Add, Change or Delete |  |  | C | DESCRIPTION OF CHANGE
|  | Load Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Code Mnemonic that the breaker or switch is located, as listed in the model |  |  | R | Ercot Station Code Mnemonic | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | L | Alpha | B
|  | Load Data | X | X | X |  | All Caps | Load Name | Load name as provided in the ERCOT model, which must be 14 characters or less and contain no special characters other than an underscore "_" meet the character limitation of the system. |  |  | R | Load Name | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 2) Warn if >= 14 characters. First 14 characters must be unique. 3)Warning! ERCOT Load Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Load Name can not be duplicated in a Station | L | Alpha | B
|  | Load Data | X | X | X |  | Automatic | Load Code | Concatenated code automatically provided |  |  | A | Load Code | Concantenate (Site Code_Substation Code_Lode Name
|  | Load Data | X | X | X |  | kV | Load Voltage Level | Enter voltage for this Load device |  |  | R | Load Voltage Level | 1) This field is required 2) Value must be >= 0 3) If the value >= 69kv it must be 69,138, or 345 | T | Float | B
|  | Load Data | X | X | X |  | Number | PTI Bus Number | Enter bus number for this Load device |  |  | O | PTI Bus Number | 1) This field is optional 2) This field must be between 1 - 999,999 | T | Integer | B
|  | Load Data | X | X | X |  | MW | Average Load Under Normal Operations | Enter average amount of MW Load under normal operations |  |  | R | Average Load Under Normal Operations | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float | B
|  | Load Data | X | X | X |  | MVAr | Average MVAr Under Normal Operations | Enter average MVAr amount for this Load under normal operations |  |  | R | Average Mvar Under Normal Operations | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float | B
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 1 | Enter device connected to this Load (can provide up to 10) |  |  | R | Device Name(s) - that this load is physically connected to | 1) This field is required 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. First 17 characters must be unique. Warning! ERCOT Device Name() should not be >=17 characters long or the name will be truncated in the model which requires uniqueness. 4) 'Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Produce an Error when connected device is missing in the Breaker_switch Tab. 'Error! Unique controlling device must also exist in the 'BREAKER_SWITCH Tab' | T | Alpha | B
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 2 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 3 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 4 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 5 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 6 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 7 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 8 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 9 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  | All Caps | Directly Connected Device 10 | Enter device connected to this Load (can provide up to 10) |  |  | C
|  | Load Data | X | X | X |  |  | Comments | Enter any comments regarding this breaker-switch data |  |  | O | Comments
|  | Load Data | X | X | X |  | mm/dd/yyyy | Effective Date | Date this breaker or switch was added, removed or updated in the model |  |  | R | Effective Date: | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
|  | PUN Load Data | X | X | X |  | All Caps | ERCOT Station Name (Station Code or Station Mnemonic) | Enter Station Code for this PUN Load |  |  | C | Station Code | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null 3) All caps | [5 empty] | N | N
|  | PUN Load Data | X | X | X |  | List | Load Name | Select Load Name from drop down list (as provided from the Load Data tab) |  |  | C | Load Name | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model 3) Not Null | L | Alpha | B |  |  | N | N
|  | PUN Load Data | X | X | X |  | Automatic | Load Code | Concatenated code automatically provided |  |  | A | Load Code | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null | [5 empty] | N | N
|  | PUN Load Data | X | X | X |  | Automatic | Hour Ending | Ending Hour of the day that the MW amount is provided |  |  | A | Hour Ending | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null | [5 empty] | N | N
|  | PUN Load Data | X | X | X |  | Automatic | Day of the Week | Day of the week for each Ending Hour of the Day that the MW amount is provided |  |  | A | Day of Week | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Not Null | [5 empty] | N | N
|  | PUN Load Data | X | X | X |  | MW | MW | MW Amount for each ending hour of each day of the week for this Load (168 hour period) |  |  | C | MW | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null. Must be numeric. 3) Value must be >= 0 (for zero load, place a 0 in that space) | [5 empty] | N | N
|  | One Line | [5 empty] | Embed a PDF or CAD One Line Diagram below: | Include a PDF or CAD One Line Diagram
|  | Transformer Test Data | [5 empty] | Transformer Test Data | Include the Transformer Test Data Diagram
|  | Unit Info - TRAIN |  |  | X |  | List | Train Name | Select Train name from drop-down list. assigned by ERCOT | R | R | R
|  | Unit Info - TRAIN |  |  | X |  | Automatic | Train Code | A sitecode and train name code concatenation |  |  | A
|  | Unit Info - TRAIN |  |  | X |  | Date | Train Unit Commercial Date | Train Unit Commercial Operations Date. The date at which the Resource Entity anticipates or declares the resource (first generator in train) released for commercial operations. It is the date on which Generator declares that the construction of the plant has been substantially completed, trial operation of the plant has been completed, and commercial operations has been declared. Format is MM/DD/YYYY | R | R | R
|  | Unit Info - TRAIN |  |  | X |  | Date | Train Unit Retirement Date | Train Unit Retirement Date in MM/DD/YYYY format. Leave blank if unknown. |  |  | O
|  | Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Duct Burner(s)? | Indicate whether Duct Burner(s) augmentation is available for use for increased capacity |  |  | R
|  | Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Evap Cooler(s)? | Indicate whether Evap Cooler(s) augmentation is available for use for increased capacity |  |  | R
|  | Unit Info - TRAIN |  |  | X |  | Y/N | Is train augmented with Chiller(s)? | Indicate whether Chiller(s) augmentation is available for use for increased capacity |  |  | R
|  | Unit Info - TRAIN |  |  | X |  | Y/N | Other augmentation? | Indicate whether other augmentation is available for use for increased capacity |  |  | R
|  | CC Configurations |  |  | X |  | List | Train Code | Train Code as provided on the Unit Information Train tab. Select from drop-down list. |  |  | R
|  | CC Configurations |  |  | X |  | Automatic | Site Code | Site Code as provided on the General and Site Information tab. |  |  | A
|  | CC Configurations |  |  | X |  | List | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name as provided on the Unit Info tab. Select from drop-down list. |  |  | R
|  | CC Configurations |  |  | X |  | Number | Configuration # | Number of this configuration,. The configuration numbers should increase based on increasing capability, not necessarily by increasing number of components. This is a sequential numbering of all possible operational configurations. |  |  | R
|  | CC Configurations |  |  | X |  | Automatic | Configuration Code | Concatenated code of the Train Code and the Configuration Number |  |  | A
|  | CC Configurations |  |  | X |  | List | Configuration Type | Register all operationally unique configurations. Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper. |  |  | R
|  | CC Transistions Configurations |  |  | X |  | List | Site Code | Site Code as provided on the General and Site Information tab. |  |  | R
|  | CC Transistions Configurations |  |  | X |  | List | Train Code | A sitecode and train code concatenation |  |  | R
|  | CC Transistions Configurations |  |  | X |  | List | Configuration Code From | Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper within the Procedure for Identifying Resource Nodes |  |  | C
|  | CC Transistions Configurations |  |  | X |  | List | Configuration Code To | Additional background to assist with this step can be obtained from the Combined Cycle Whitepaper |  |  | C
|  | Unit Info - Wind | X |  |  |  | meters | Average Height above ground of Turbine Hub | Used for Wind Generation Forecasting |  |  | R
|  | Unit Info - Wind | X |  |  |  | decimal degrees (N) | Latitude of Meteorological Tower | Used for Wind Generation Forecasting. For multiple meteorological towers, select one location that best represents the conditions for the site. |  |  | R
|  | Unit Info - Wind | X |  |  |  | decimal degrees (W) | Longitude of Meteorological Tower | Used for Wind Generation Forecasting. For multiple meteorological towers, select one location that best represents the conditions for the site. |  |  | R
|  | Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Wind speed | Used for Wind Generation Forecasting |  |  | R
|  | Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Wind direction | Used for Wind Generation Forecasting |  |  | R
|  | Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Barometric pressure | Used for Wind Generation Forecasting |  |  | R
|  | Unit Info - Wind | X |  |  |  | meters | Height of Meteorological Instrumentation - Temperature | Used for Wind Generation Forecasting |  |  | R
|  | Turbine Details | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
|  | Turbine Details | X |  |  |  | Number | WGR Group | WGR Group # 1,2,3… only if grouping two or more WGRs. Leave blank if not grouping. Refer to definition of Wind-powered Generation Resource Group in Protocol Section 2. |  |  | O
|  | Turbine Details | X |  |  |  | Automatic | Site_Group | Automatic field |  |  | A
|  | Turbine Details | X |  |  |  | Number | Total Number of Turbines | Count total of wind turbines | R | R | R
|  | Turbine Details | X |  |  |  | All Caps | Turbine Manufacturer and Model | From name-plate or manufacturer data sheet | R | R | R
|  | Turbine Details | X |  |  |  | MW | MW Rating for this model of Turbine | From name-plate or manufacturer data sheet | R | R | R
|  | Turbine Details | X |  |  |  | Number | Number of Turbine Manufacturer/Model | Count of wind turbines in this group | R | R | R
|  | Turbine Details | X |  |  |  | Number | Turbine Type | Indicate the electrical type of Turbine (eg. Type 1, 2, 3, 4) |  |  | R
|  | Turbine Details | X |  |  |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances. |  | R | R
|  | Turbine Details | X |  |  |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated) | Enter the instantaneous subtransient reactance (unsaturated) for the fault. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) | Enter the transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  | R | R
|  | Turbine Details | X |  |  |  | R in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | X in p.u. | Negative Sequence Z (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | R in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | X in p.u. | Zero Sequence Z (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated | Enter the instantaneous subtransient reactance (saturated) for the fault. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) | Enter the transient reactance (saturated) for the first 2-3 cycles of the fault. |  | R | R
|  | Turbine Details | X |  |  |  | R in p.u. | Positive Sequence Resistance (saturated) | Enter the positive sequence resistance (saturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | X in p.u. | Synchronous Reactance X (After 4 cycles of the fault) (saturated) | Enter the synchronous reactance (saturated) after 4 cycles of the fault. |  | R | R
|  | Turbine Details | X |  |  |  | R in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence resistance (saturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | X in p.u. | Negative Sequence Z (saturated) | Enter the negative sequence reactance (saturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | R in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence resistance (saturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | X in p.u. | Zero Sequence Z (saturated) | Enter the zero sequence reactance (saturated) for system models. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Grounding Resistance For An Impedance Grounded Generator In p.u. (100 MVA Base) | Zero sequence resistance value of the generator grounding impedance is required. The value must be specified on a 100 MVA base. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Grounding Reactance For An Impedance Grounded Generator In p.u. (100 MVA Base) | Zero sequence reactance value of the generator grounding impedance is required. The value must be specified on a 100 MVA base. |  | R | R
|  | Turbine Details | X |  |  |  | p.u. | Instantaneous Controlled Fault Current Magnitude (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine instantaneous fault current magnitude for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
|  | Turbine Details | X |  |  |  | p.u. | Controlled Fault Current Magnitude At 2 to 3 cycles after fault (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine fault current magnitude at 2 – 3 cycles after a fault for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
|  | Turbine Details | X |  |  |  | p.u. | Controlled Fault Current Magnitude At 4 plus cycles after fault (Multiple of full Load current) for Turbine Types 3 & 4 | Wind turbine fault current magnitude at 4+ cycles after a fault for Type 4 and Type 3, if the controls operate (no crowbar operation) as a percent of full Load current, expressed in per unit. |  |  | C
|  | Turbine Details | X |  |  |  | kV | High Side Voltage Level (nominal) | Enter the voltage level (in kV) on the high-voltage side of the wind generator pad-mount transformer. |  |  | R
|  | Turbine Details | X |  |  |  | kV | Low Side Voltage Level (nominal) | Enter the voltage level (in kV) on the low-voltage side of the wind generator pad-mount transformer. |  |  | R
|  | Turbine Details | X |  |  |  | List | High Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the high-voltage side of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  | List | Low Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the low-voltage side of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  | p.u. | Impedance Z | Enter the impedance of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  |  | X/R Ratio | Enter the ratio of the reactance to the resistance of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  | p.u. | Zero Sequence Z | Enter the zero sequence impedance of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  |  | Zero Sequence X/R Ratio | Enter the ratio of the zero sequence reactance to the zero sequence resistance of the transformer. |  |  | R
|  | Turbine Details | X |  |  |  | MVA | Base MVA for Transformer Data | Enter the base MVA upon which the per unit transformer data is provided. |  |  | R
|  | Collector System - WIND | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
|  | Collector System - WIND | X |  |  |  |  | Cable Type | Enter the type(s) of conductor(s) used in the collector system. |  | R | R
|  | Collector System - WIND | X |  |  |  | kV | Voltage Level kV | Enter the voltage level (in kV) of the collector system. Used when calculating Positive and Zero Sequence resistance and reactance. |  | R | R
|  | Collector System - WIND | X |  |  |  | p.u. | Positive Sequence R/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence resistance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
|  | Collector System - WIND | X |  |  |  | p.u. | Positive Sequence X/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
|  | Collector System - WIND | X |  |  |  | p.u. | Positive Charging Bc/kft (p.u. on 100 MVA base) | Enter in per unit, the positive sequence line charging reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
|  | Collector System - WIND | X |  |  |  | p.u. | Zero Sequence R0/kft (p.u. on 100 MVA base) | Enter in per unit, the zero sequence resistance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
|  | Collector System - WIND | X |  |  |  | p.u. | Zero Sequence X0/kft (p.u. on 100 MVA base) | Enter in per unit, the zero sequence reactance per kilo-foot of the collector system calculated on a 100 MVA base. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A
|  | Collector System - Wind Segment Data | X |  |  |  | List | Cable Type | Cable Type as provided on the Collector System - Wind tab |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | Integer | From | Enter the bus number for the sending end or "from" bus of the cable segment. Consistent with .raw file if available. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | Integer | To | Enter the bus number for the receiving end or "to" bus of the cable segment. Consistent with .raw file if available. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | Integer | Circuit Number | Enter the circuit number for the cable segment. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | kV | Voltage Level | Enter the voltage level of the cable segment in kV. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | kft | Cable Segment Length | Enter the length of the cable segment in kilo-feet. |  | R | R
|  | Collector System - Wind Segment Data | X |  |  |  | Integer | Number of Turbines On Cable Segment | Enter the number of turbines connected to which have power flowing through the cable segment. |  | R | R