## Current_2016_RRS
RRS Requirement in Plexos
| Assumed Load Participation in Plexos |  |  |  |  | Using only participation factor |  |  |  | Using the Buffer
| Equivalency Ratio | RRS Req. (no Load participation), MW | Min Gen RRS, based on BAL-003 IFRO, MW | Max Load RRS, 50% of total Req., MW | Total RRS Req., MW | 2014 Avg. Participation for Month&Hour (as % of participation limit) | Expected available Load Resources | Gen RRS need based on expected Load participaiton | Total RRS Req. | Gen RRS Buffer needed to meet needs 95% of time (given the distribution of load participation across ~30 data points for each month&hour) | Expected incremental LoadRRS per MW of increased RRS requirement | Expected incremental GenRRS per MW of increased RRS requirement | Average equivalency ratio of incremental resources | Buffer needed, assuming load responds to increased requirements at usual participation rate | Total RRS Req. | Max avail. FFR | Will be provided from Gen RRS
2016-01-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.58% | 1220.8093 | 1512.9479 | 2733.7572 | 96.9341 | 0.45288 | 0.54712 | 1.1359 | 85.3395 | 2819.0967 | 1259.4579 | 1559.6388
2016-01-01 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.86% | 1224.5775 | 1508.0493 | 2732.6268 | 108.3641 | 0.45428 | 0.54572 | 1.1363 | 95.3671 | 2827.9939 | 1267.9007 | 1560.0932
2016-01-01 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.88% | 1224.8826 | 1507.6526 | 2732.5352 | 108.8321 | 0.45439 | 0.54561 | 1.1363 | 95.7761 | 2828.3113 | 1268.4025 | 1559.9088
2016-01-01 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.79% | 1223.6835 | 1509.2114 | 2732.8949 | 108.2911 | 0.45395 | 0.54605 | 1.1362 | 95.3112 | 2828.2062 | 1266.9498 | 1561.2564
2016-01-01 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.21% | 1215.8484 | 1519.3971 | 2735.2455 | 107.7527 | 0.45104 | 0.54896 | 1.1353 | 94.9102 | 2830.1556 | 1258.6567 | 1571.4989
2016-01-01 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.3% | 1217.1146 | 1517.751 | 2734.8656 | 87.8263 | 0.45151 | 0.54849 | 1.1355 | 77.3491 | 2812.2147 | 1252.0385 | 1560.1762
2016-01-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-01 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-01 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-01 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-01 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-01 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-01 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-01 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.23% | 1256.5876 | 1466.4361 | 2723.0237 | 53.6935 | 0.46615 | 0.53385 | 1.1398 | 47.1059 | 2770.1296 | 1278.5462 | 1491.5834
2016-01-01 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.02% | 1253.7099 | 1470.1771 | 2723.887 | 49.895 | 0.46509 | 0.53491 | 1.1395 | 43.7857 | 2767.6728 | 1274.074 | 1493.5987
2016-01-01 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.88% | 1251.9222 | 1472.5011 | 2724.4233 | 50.4149 | 0.46442 | 0.53558 | 1.1393 | 44.2497 | 2768.6731 | 1272.4728 | 1496.2002
2016-01-01 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.07% | 1254.3992 | 1469.281 | 2723.6802 | 50.5664 | 0.46534 | 0.53466 | 1.1396 | 44.3719 | 2768.0521 | 1275.0473 | 1493.0048
2016-01-01 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.313 | 1469.3931 | 2723.7061 | 47.9999 | 0.46531 | 0.53469 | 1.1396 | 42.1203 | 2765.8264 | 1273.912 | 1491.9144
2016-01-01 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-01 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-01 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-01 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-01 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.32% | 1233.7907 | 1497.7616 | 2731.5523 | 56.2373 | 0.45658 | 0.54342 | 1.1141 | 50.4757 | 2782.028 | 1256.8371 | 1525.1909
2016-01-02 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-02 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-02 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-02 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-02 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-02 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-02 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.56% | 1223.5703 | 1510.5371 | 2734.1074 | 75.6734 | 0.4528 | 0.5472 | 1.1132 | 67.9782 | 2802.0856 | 1254.3509 | 1547.7347
2016-01-02 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.02% | 1189.3114 | 1553.3608 | 2742.6722 | 76.7324 | 0.44012 | 0.55988 | 1.11 | 69.1264 | 2811.7985 | 1219.7355 | 1592.063
2016-01-02 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.59% | 1196.9296 | 1543.8381 | 2740.7676 | 78.679 | 0.44294 | 0.55706 | 1.1107 | 70.835 | 2811.6027 | 1228.3054 | 1583.2972
2016-01-02 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-02 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-02 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-02 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-02 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-02 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.23% | 1256.5876 | 1466.4361 | 2723.0237 | 53.6935 | 0.46615 | 0.53385 | 1.1398 | 47.1059 | 2770.1296 | 1278.5462 | 1491.5834
2016-01-02 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.02% | 1253.7099 | 1470.1771 | 2723.887 | 49.895 | 0.46509 | 0.53491 | 1.1395 | 43.7857 | 2767.6728 | 1274.074 | 1493.5987
2016-01-02 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.88% | 1251.9222 | 1472.5011 | 2724.4233 | 50.4149 | 0.46442 | 0.53558 | 1.1393 | 44.2497 | 2768.6731 | 1272.4728 | 1496.2002
2016-01-02 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.07% | 1254.3992 | 1469.281 | 2723.6802 | 50.5664 | 0.46534 | 0.53466 | 1.1396 | 44.3719 | 2768.0521 | 1275.0473 | 1493.0048
2016-01-02 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.313 | 1469.3931 | 2723.7061 | 47.9999 | 0.46531 | 0.53469 | 1.1396 | 42.1203 | 2765.8264 | 1273.912 | 1491.9144
2016-01-02 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.42% | 1245.6933 | 1480.5987 | 2726.292 | 84.6397 | 0.46211 | 0.53789 | 1.1386 | 74.3345 | 2800.6265 | 1280.0442 | 1520.5823
2016-01-02 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.91% | 1238.8056 | 1489.5527 | 2728.3583 | 54.9249 | 0.45956 | 0.54044 | 1.1379 | 48.27 | 2776.6283 | 1260.9885 | 1515.6399
2016-01-02 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.36% | 1231.3273 | 1499.2745 | 2730.6018 | 50.7985 | 0.45678 | 0.54322 | 1.137 | 44.6763 | 2775.2781 | 1251.7347 | 1523.5434
2016-01-02 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.19% | 1215.6515 | 1519.6531 | 2735.3046 | 61.9632 | 0.45097 | 0.54903 | 1.1353 | 54.5792 | 2789.8837 | 1240.2649 | 1549.6188
2016-01-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.32% | 1230.791 | 1499.9717 | 2730.7627 | 67.4847 | 0.45658 | 0.54342 | 1.137 | 59.3546 | 2790.1173 | 1257.8913 | 1532.226
2016-01-03 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.58% | 1220.8093 | 1512.9479 | 2733.7572 | 96.9341 | 0.45288 | 0.54712 | 1.1359 | 85.3395 | 2819.0967 | 1259.4579 | 1559.6388
2016-01-03 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.86% | 1224.5775 | 1508.0493 | 2732.6268 | 108.3641 | 0.45428 | 0.54572 | 1.1363 | 95.3671 | 2827.9939 | 1267.9007 | 1560.0932
2016-01-03 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.88% | 1224.8826 | 1507.6526 | 2732.5352 | 108.8321 | 0.45439 | 0.54561 | 1.1363 | 95.7761 | 2828.3113 | 1268.4025 | 1559.9088
2016-01-03 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.79% | 1223.6835 | 1509.2114 | 2732.8949 | 108.2911 | 0.45395 | 0.54605 | 1.1362 | 95.3112 | 2828.2062 | 1266.9498 | 1561.2564
2016-01-03 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.21% | 1215.8484 | 1519.3971 | 2735.2455 | 107.7527 | 0.45104 | 0.54896 | 1.1353 | 94.9102 | 2830.1556 | 1258.6567 | 1571.4989
2016-01-03 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.3% | 1217.1146 | 1517.751 | 2734.8656 | 87.8263 | 0.45151 | 0.54849 | 1.1355 | 77.3491 | 2812.2147 | 1252.0385 | 1560.1762
2016-01-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-03 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.02% | 1189.3114 | 1553.3608 | 2742.6722 | 76.7324 | 0.44012 | 0.55988 | 1.11 | 69.1264 | 2811.7985 | 1219.7355 | 1592.063
2016-01-03 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.59% | 1196.9296 | 1543.8381 | 2740.7676 | 78.679 | 0.44294 | 0.55706 | 1.1107 | 70.835 | 2811.6027 | 1228.3054 | 1583.2972
2016-01-03 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-03 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-03 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-03 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-03 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-03 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-03 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-03 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.88% | 1151.7685 | 1339.7016 | 2491.4701 | 21.8465 | 0.46442 | 0.53558 | 1.0604 | 20.6026 | 2512.0727 | 1161.3368 | 1350.7359
2016-01-03 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.07% | 1154.0473 | 1337.1266 | 2491.1739 | 21.9121 | 0.46534 | 0.53466 | 1.0605 | 20.6621 | 2511.836 | 1163.6623 | 1348.1737
2016-01-03 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.968 | 1337.2162 | 2491.1842 | 20.8 | 0.46531 | 0.53469 | 1.0605 | 19.6135 | 2510.7977 | 1163.0943 | 1347.7034
2016-01-03 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-03 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-03 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-03 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.19% | 1118.3993 | 1377.4087 | 2495.8081 | 26.8507 | 0.45097 | 0.54903 | 1.0586 | 25.3637 | 2521.1718 | 1129.8376 | 1391.3343
2016-01-03 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.32% | 1132.3277 | 1361.6697 | 2493.9974 | 29.2434 | 0.45658 | 0.54342 | 1.0594 | 27.6049 | 2521.6023 | 1144.9316 | 1376.6706
2016-01-04 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-04 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-04 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-04 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-04 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-04 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-04 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-04 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.02% | 1117.2365 | 1433.3846 | 2550.6211 | 24.5544 | 0.44012 | 0.55988 | 1.0352 | 23.7192 | 2574.3403 | 1127.6759 | 1446.6644
2016-01-04 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.59% | 1124.393 | 1425.6556 | 2550.0486 | 25.1773 | 0.44294 | 0.55706 | 1.0354 | 24.3156 | 2574.3642 | 1135.1634 | 1439.2008
2016-01-04 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.93% | 1115.9898 | 1434.731 | 2550.7208 | 22.7865 | 0.43963 | 0.56037 | 1.0352 | 22.0123 | 2572.7331 | 1125.6671 | 1447.066
2016-01-04 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.67% | 1125.4266 | 1424.5392 | 2549.9659 | 29.4362 | 0.44335 | 0.55665 | 1.0355 | 28.4279 | 2578.3938 | 1138.0302 | 1440.3636
2016-01-04 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 90.5% | 1148.6149 | 1399.4959 | 2548.1108 | 26.6421 | 0.45248 | 0.54752 | 1.0362 | 25.7113 | 2573.8222 | 1160.2489 | 1413.5733
2016-01-04 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 92.72% | 1176.8213 | 1369.033 | 2545.8543 | 14.23 | 0.4636 | 0.5364 | 1.0371 | 13.7211 | 2559.5754 | 1183.1823 | 1376.3931
2016-01-04 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.06% | 1181.1822 | 1364.3232 | 2545.5054 | 15.0298 | 0.46531 | 0.53469 | 1.0372 | 14.4904 | 2559.9959 | 1187.9248 | 1372.0711
2016-01-04 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.23% | 1183.3127 | 1362.0223 | 2545.335 | 14.3183 | 0.46615 | 0.53385 | 1.0373 | 13.8035 | 2559.1385 | 1189.7472 | 1369.3913
2016-01-04 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.02% | 1180.6027 | 1364.949 | 2545.5518 | 13.3053 | 0.46509 | 0.53491 | 1.0372 | 12.828 | 2558.3798 | 1186.5689 | 1371.8109
2016-01-04 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 92.88% | 1178.9193 | 1366.7671 | 2545.6865 | 13.444 | 0.46442 | 0.53558 | 1.0372 | 12.9624 | 2558.6488 | 1184.9394 | 1373.7095
2016-01-04 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.07% | 1181.2519 | 1364.248 | 2545.4998 | 13.4844 | 0.46534 | 0.53466 | 1.0372 | 13.0004 | 2558.5002 | 1187.3015 | 1371.1987
2016-01-04 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.06% | 1181.1707 | 1364.3357 | 2545.5063 | 12.8 | 0.46531 | 0.53469 | 1.0372 | 12.3406 | 2557.847 | 1186.9129 | 1370.9341
2016-01-04 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 92.42% | 1173.0536 | 1373.1021 | 2546.1557 | 22.5706 | 0.46211 | 0.53789 | 1.037 | 21.7659 | 2567.9216 | 1183.1119 | 1384.8097
2016-01-04 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 91.91% | 1166.5676 | 1380.107 | 2546.6746 | 14.6466 | 0.45956 | 0.54044 | 1.0368 | 14.1272 | 2560.8018 | 1173.0599 | 1387.742
2016-01-04 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-04 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-04 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.32% | 1233.7907 | 1497.7616 | 2731.5523 | 56.2373 | 0.45658 | 0.54342 | 1.1141 | 50.4757 | 2782.028 | 1256.8371 | 1525.1909
2016-01-05 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-05 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-05 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-05 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-05 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-05 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-05 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-05 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-05 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-05 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-05 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-05 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-05 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-05 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-05 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-05 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-05 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-05 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-05 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-05 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-05 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-05 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.36% | 1231.3273 | 1499.2745 | 2730.6018 | 50.7985 | 0.45678 | 0.54322 | 1.137 | 44.6763 | 2775.2781 | 1251.7347 | 1523.5434
2016-01-05 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.19% | 1215.6515 | 1519.6531 | 2735.3046 | 61.9632 | 0.45097 | 0.54903 | 1.1353 | 54.5792 | 2789.8837 | 1240.2649 | 1549.6188
2016-01-05 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.32% | 1230.791 | 1499.9717 | 2730.7627 | 67.4847 | 0.45658 | 0.54342 | 1.137 | 59.3546 | 2790.1173 | 1257.8913 | 1532.226
2016-01-06 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.58% | 1271.8405 | 1589.4234 | 2861.2638 | 129.2454 | 0.45288 | 0.54712 | 1.1812 | 109.4232 | 2970.687 | 1321.3961 | 1649.2909
2016-01-06 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.86% | 1275.7661 | 1583.9274 | 2859.6936 | 144.4855 | 0.45428 | 0.54572 | 1.1817 | 122.268 | 2981.9615 | 1331.3099 | 1650.6517
2016-01-06 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.88% | 1276.0841 | 1583.4823 | 2859.5664 | 145.1095 | 0.45439 | 0.54561 | 1.1818 | 122.7913 | 2982.3577 | 1331.8794 | 1650.4783
2016-01-06 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.79% | 1274.8348 | 1585.2312 | 2860.0661 | 144.3881 | 0.45395 | 0.54605 | 1.1816 | 122.1993 | 2982.2654 | 1330.3068 | 1651.9585
2016-01-06 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.21% | 1266.6722 | 1596.659 | 2863.3311 | 143.6702 | 0.45104 | 0.54896 | 1.1804 | 121.7115 | 2985.0426 | 1321.569 | 1663.4736
2016-01-06 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.3% | 1267.9913 | 1594.8122 | 2862.8035 | 117.1017 | 0.45151 | 0.54849 | 1.1806 | 99.1879 | 2961.9914 | 1312.7757 | 1649.2157
2016-01-06 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-06 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-06 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.59% | 1196.9296 | 1543.8381 | 2740.7676 | 78.679 | 0.44294 | 0.55706 | 1.1107 | 70.835 | 2811.6027 | 1228.3054 | 1583.2972
2016-01-06 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-06 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-06 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-06 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-06 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-06 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-06 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-06 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-06 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-06 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-06 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.42% | 1245.6933 | 1480.5987 | 2726.292 | 84.6397 | 0.46211 | 0.53789 | 1.1386 | 74.3345 | 2800.6265 | 1280.0442 | 1520.5823
2016-01-06 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.91% | 1238.8056 | 1489.5527 | 2728.3583 | 54.9249 | 0.45956 | 0.54044 | 1.1379 | 48.27 | 2776.6283 | 1260.9885 | 1515.6399
2016-01-06 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.36% | 1282.7981 | 1574.0826 | 2856.8807 | 67.7314 | 0.45678 | 0.54322 | 1.1827 | 57.2678 | 2914.1486 | 1308.9571 | 1605.1915
2016-01-06 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.19% | 1352.9024 | 1720.6463 | 3073.5488 | 103.272 | 0.45097 | 0.54903 | 1.2255 | 84.2704 | 3157.8191 | 1390.9056 | 1766.9135
2016-01-06 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-07 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-07 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-07 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-07 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-07 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.3% | 1354.5308 | 1718.2038 | 3072.7346 | 146.3771 | 0.45151 | 0.54849 | 1.2258 | 119.4179 | 3192.1525 | 1408.4492 | 1783.7033
2016-01-07 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.56% | 1271.6176 | 1589.7354 | 2861.353 | 121.0774 | 0.4528 | 0.5472 | 1.1811 | 102.5106 | 2963.8636 | 1318.0345 | 1645.8291
2016-01-07 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-07 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-07 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-07 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-07 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-07 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-07 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-07 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.23% | 1256.5876 | 1466.4361 | 2723.0237 | 53.6935 | 0.46615 | 0.53385 | 1.1398 | 47.1059 | 2770.1296 | 1278.5462 | 1491.5834
2016-01-07 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.02% | 1253.7099 | 1470.1771 | 2723.887 | 49.895 | 0.46509 | 0.53491 | 1.1395 | 43.7857 | 2767.6728 | 1274.074 | 1493.5987
2016-01-07 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.88% | 1251.9222 | 1472.5011 | 2724.4233 | 50.4149 | 0.46442 | 0.53558 | 1.1393 | 44.2497 | 2768.6731 | 1272.4728 | 1496.2002
2016-01-07 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-07 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-07 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-07 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-07 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-07 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.19% | 1118.3993 | 1377.4087 | 2495.8081 | 26.8507 | 0.45097 | 0.54903 | 1.0586 | 25.3637 | 2521.1718 | 1129.8376 | 1391.3343
2016-01-07 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.32% | 1132.3277 | 1361.6697 | 2493.9974 | 29.2434 | 0.45658 | 0.54342 | 1.0594 | 27.6049 | 2521.6023 | 1144.9316 | 1376.6706
2016-01-08 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.58% | 1123.1446 | 1372.0466 | 2495.1912 | 42.0048 | 0.45288 | 0.54712 | 1.0589 | 39.6693 | 2534.8605 | 1141.11 | 1393.7504
2016-01-08 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.86% | 1126.6113 | 1368.1293 | 2494.7405 | 46.9578 | 0.45428 | 0.54572 | 1.0591 | 44.3393 | 2539.0798 | 1146.7536 | 1392.3262
2016-01-08 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.88% | 1126.892 | 1367.812 | 2494.704 | 47.1606 | 0.45439 | 0.54561 | 1.0591 | 44.5301 | 2539.2342 | 1147.1262 | 1392.108
2016-01-08 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.79% | 1125.7889 | 1369.0586 | 2494.8474 | 46.9261 | 0.45395 | 0.54605 | 1.059 | 44.3112 | 2539.1586 | 1145.9038 | 1393.2549
2016-01-08 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.21% | 1118.5805 | 1377.204 | 2495.7845 | 46.6928 | 0.45104 | 0.54896 | 1.0586 | 44.1066 | 2539.8911 | 1138.4744 | 1401.4167
2016-01-08 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.3% | 1119.7454 | 1375.8877 | 2495.6331 | 38.058 | 0.45151 | 0.54849 | 1.0587 | 35.948 | 2531.5811 | 1135.9763 | 1395.6048
2016-01-08 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-08 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-08 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.59% | 1124.393 | 1425.6556 | 2550.0486 | 25.1773 | 0.44294 | 0.55706 | 1.0354 | 24.3156 | 2574.3642 | 1135.1634 | 1439.2008
2016-01-08 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.93% | 1115.9898 | 1434.731 | 2550.7208 | 22.7865 | 0.43963 | 0.56037 | 1.0352 | 22.0123 | 2572.7331 | 1125.6671 | 1447.066
2016-01-08 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.67% | 1125.4266 | 1424.5392 | 2549.9659 | 29.4362 | 0.44335 | 0.55665 | 1.0355 | 28.4279 | 2578.3938 | 1138.0302 | 1440.3636
2016-01-08 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.5% | 1122.1619 | 1373.157 | 2495.3189 | 43.2934 | 0.45248 | 0.54752 | 1.0588 | 40.8882 | 2536.2071 | 1140.6632 | 1395.5439
2016-01-08 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.72% | 1149.7187 | 1342.0179 | 2491.7366 | 23.1237 | 0.4636 | 0.5364 | 1.0603 | 21.8093 | 2513.5459 | 1159.8294 | 1353.7164
2016-01-08 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.9792 | 1337.2035 | 2491.1827 | 24.4235 | 0.46531 | 0.53469 | 1.0605 | 23.0304 | 2514.2131 | 1164.6956 | 1349.5175
2016-01-08 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.23% | 1156.0606 | 1334.8515 | 2490.9121 | 23.2672 | 0.46615 | 0.53385 | 1.0606 | 21.9378 | 2512.8499 | 1166.287 | 1346.5629
2016-01-08 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.02% | 1153.4131 | 1337.8432 | 2491.2563 | 21.6212 | 0.46509 | 0.53491 | 1.0605 | 20.3884 | 2511.6447 | 1162.8955 | 1348.7493
2016-01-08 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.88% | 1151.7685 | 1339.7016 | 2491.4701 | 21.8465 | 0.46442 | 0.53558 | 1.0604 | 20.6026 | 2512.0727 | 1161.3368 | 1350.7359
2016-01-08 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.07% | 1154.0473 | 1337.1266 | 2491.1739 | 21.9121 | 0.46534 | 0.53466 | 1.0605 | 20.6621 | 2511.836 | 1163.6623 | 1348.1737
2016-01-08 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.968 | 1337.2162 | 2491.1842 | 20.8 | 0.46531 | 0.53469 | 1.0605 | 19.6135 | 2510.7977 | 1163.0943 | 1347.7034
2016-01-08 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-08 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-08 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-08 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.19% | 1118.3993 | 1377.4087 | 2495.8081 | 26.8507 | 0.45097 | 0.54903 | 1.0586 | 25.3637 | 2521.1718 | 1129.8376 | 1391.3343
2016-01-08 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.32% | 1132.3277 | 1361.6697 | 2493.9974 | 29.2434 | 0.45658 | 0.54342 | 1.0594 | 27.6049 | 2521.6023 | 1144.9316 | 1376.6706
2016-01-09 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.58% | 1123.1446 | 1372.0466 | 2495.1912 | 42.0048 | 0.45288 | 0.54712 | 1.0589 | 39.6693 | 2534.8605 | 1141.11 | 1393.7504
2016-01-09 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.86% | 1126.6113 | 1368.1293 | 2494.7405 | 46.9578 | 0.45428 | 0.54572 | 1.0591 | 44.3393 | 2539.0798 | 1146.7536 | 1392.3262
2016-01-09 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.88% | 1126.892 | 1367.812 | 2494.704 | 47.1606 | 0.45439 | 0.54561 | 1.0591 | 44.5301 | 2539.2342 | 1147.1262 | 1392.108
2016-01-09 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.79% | 1125.7889 | 1369.0586 | 2494.8474 | 46.9261 | 0.45395 | 0.54605 | 1.059 | 44.3112 | 2539.1586 | 1145.9038 | 1393.2549
2016-01-09 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.21% | 1118.5805 | 1377.204 | 2495.7845 | 46.6928 | 0.45104 | 0.54896 | 1.0586 | 44.1066 | 2539.8911 | 1138.4744 | 1401.4167
2016-01-09 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.3% | 1119.7454 | 1375.8877 | 2495.6331 | 38.058 | 0.45151 | 0.54849 | 1.0587 | 35.948 | 2531.5811 | 1135.9763 | 1395.6048
2016-01-09 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-09 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-09 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-09 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.93% | 1090.2882 | 1409.1743 | 2499.4625 | 37.028 | 0.43963 | 0.56037 | 1.0572 | 35.0262 | 2534.4887 | 1105.6868 | 1428.8019
2016-01-09 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.67% | 1099.5077 | 1398.7563 | 2498.264 | 47.8338 | 0.44335 | 0.55665 | 1.0576 | 45.2272 | 2543.4912 | 1119.5592 | 1423.932
2016-01-09 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.5% | 1122.1619 | 1373.157 | 2495.3189 | 43.2934 | 0.45248 | 0.54752 | 1.0588 | 40.8882 | 2536.2071 | 1140.6632 | 1395.5439
2016-01-09 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.72% | 1149.7187 | 1342.0179 | 2491.7366 | 23.1237 | 0.4636 | 0.5364 | 1.0603 | 21.8093 | 2513.5459 | 1159.8294 | 1353.7164
2016-01-09 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.9792 | 1337.2035 | 2491.1827 | 24.4235 | 0.46531 | 0.53469 | 1.0605 | 23.0304 | 2514.2131 | 1164.6956 | 1349.5175
2016-01-09 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.23% | 1156.0606 | 1334.8515 | 2490.9121 | 23.2672 | 0.46615 | 0.53385 | 1.0606 | 21.9378 | 2512.8499 | 1166.287 | 1346.5629
2016-01-09 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.02% | 1153.4131 | 1337.8432 | 2491.2563 | 21.6212 | 0.46509 | 0.53491 | 1.0605 | 20.3884 | 2511.6447 | 1162.8955 | 1348.7493
2016-01-09 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.88% | 1151.7685 | 1339.7016 | 2491.4701 | 21.8465 | 0.46442 | 0.53558 | 1.0604 | 20.6026 | 2512.0727 | 1161.3368 | 1350.7359
2016-01-09 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.07% | 1154.0473 | 1337.1266 | 2491.1739 | 21.9121 | 0.46534 | 0.53466 | 1.0605 | 20.6621 | 2511.836 | 1163.6623 | 1348.1737
2016-01-09 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.968 | 1337.2162 | 2491.1842 | 20.8 | 0.46531 | 0.53469 | 1.0605 | 19.6135 | 2510.7977 | 1163.0943 | 1347.7034
2016-01-09 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-09 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-09 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-09 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.19% | 1118.3993 | 1377.4087 | 2495.8081 | 26.8507 | 0.45097 | 0.54903 | 1.0586 | 25.3637 | 2521.1718 | 1129.8376 | 1391.3343
2016-01-09 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.32% | 1132.3277 | 1361.6697 | 2493.9974 | 29.2434 | 0.45658 | 0.54342 | 1.0594 | 27.6049 | 2521.6023 | 1144.9316 | 1376.6706
2016-01-10 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.58% | 1123.1446 | 1372.0466 | 2495.1912 | 42.0048 | 0.45288 | 0.54712 | 1.0589 | 39.6693 | 2534.8605 | 1141.11 | 1393.7504
2016-01-10 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.86% | 1126.6113 | 1368.1293 | 2494.7405 | 46.9578 | 0.45428 | 0.54572 | 1.0591 | 44.3393 | 2539.0798 | 1146.7536 | 1392.3262
2016-01-10 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.88% | 1126.892 | 1367.812 | 2494.704 | 47.1606 | 0.45439 | 0.54561 | 1.0591 | 44.5301 | 2539.2342 | 1147.1262 | 1392.108
2016-01-10 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.79% | 1125.7889 | 1369.0586 | 2494.8474 | 46.9261 | 0.45395 | 0.54605 | 1.059 | 44.3112 | 2539.1586 | 1145.9038 | 1393.2549
2016-01-10 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.21% | 1118.5805 | 1377.204 | 2495.7845 | 46.6928 | 0.45104 | 0.54896 | 1.0586 | 44.1066 | 2539.8911 | 1138.4744 | 1401.4167
2016-01-10 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.3% | 1119.7454 | 1375.8877 | 2495.6331 | 38.058 | 0.45151 | 0.54849 | 1.0587 | 35.948 | 2531.5811 | 1135.9763 | 1395.6048
2016-01-10 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-10 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-10 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-10 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-10 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-10 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-10 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-10 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-10 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-10 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-10 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-10 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-10 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-10 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-10 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-10 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-10 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-10 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.32% | 1233.7907 | 1497.7616 | 2731.5523 | 56.2373 | 0.45658 | 0.54342 | 1.1141 | 50.4757 | 2782.028 | 1256.8371 | 1525.1909
2016-01-11 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-11 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-11 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-11 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-11 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-11 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-11 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.56% | 1122.9477 | 1372.2691 | 2495.2168 | 39.3502 | 0.4528 | 0.5472 | 1.0589 | 37.1626 | 2532.3794 | 1139.775 | 1392.6044
2016-01-11 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-11 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-11 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.93% | 1090.2882 | 1409.1743 | 2499.4625 | 37.028 | 0.43963 | 0.56037 | 1.0572 | 35.0262 | 2534.4887 | 1105.6868 | 1428.8019
2016-01-11 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.67% | 1099.5077 | 1398.7563 | 2498.264 | 47.8338 | 0.44335 | 0.55665 | 1.0576 | 45.2272 | 2543.4912 | 1119.5592 | 1423.932
2016-01-11 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.5% | 1122.1619 | 1373.157 | 2495.3189 | 43.2934 | 0.45248 | 0.54752 | 1.0588 | 40.8882 | 2536.2071 | 1140.6632 | 1395.5439
2016-01-11 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-11 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-11 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-11 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-11 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-11 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-11 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-11 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-11 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-11 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-11 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.19% | 1118.3993 | 1377.4087 | 2495.8081 | 26.8507 | 0.45097 | 0.54903 | 1.0586 | 25.3637 | 2521.1718 | 1129.8376 | 1391.3343
2016-01-11 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.32% | 1132.3277 | 1361.6697 | 2493.9974 | 29.2434 | 0.45658 | 0.54342 | 1.0594 | 27.6049 | 2521.6023 | 1144.9316 | 1376.6706
2016-01-12 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.58% | 1123.1446 | 1372.0466 | 2495.1912 | 42.0048 | 0.45288 | 0.54712 | 1.0589 | 39.6693 | 2534.8605 | 1141.11 | 1393.7504
2016-01-12 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.86% | 1126.6113 | 1368.1293 | 2494.7405 | 46.9578 | 0.45428 | 0.54572 | 1.0591 | 44.3393 | 2539.0798 | 1146.7536 | 1392.3262
2016-01-12 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.88% | 1126.892 | 1367.812 | 2494.704 | 47.1606 | 0.45439 | 0.54561 | 1.0591 | 44.5301 | 2539.2342 | 1147.1262 | 1392.108
2016-01-12 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.79% | 1125.7889 | 1369.0586 | 2494.8474 | 46.9261 | 0.45395 | 0.54605 | 1.059 | 44.3112 | 2539.1586 | 1145.9038 | 1393.2549
2016-01-12 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.21% | 1118.5805 | 1377.204 | 2495.7845 | 46.6928 | 0.45104 | 0.54896 | 1.0586 | 44.1066 | 2539.8911 | 1138.4744 | 1401.4167
2016-01-12 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.3% | 1119.7454 | 1375.8877 | 2495.6331 | 38.058 | 0.45151 | 0.54849 | 1.0587 | 35.948 | 2531.5811 | 1135.9763 | 1395.6048
2016-01-12 06:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 90.56% | 1149.4192 | 1398.6273 | 2548.0465 | 24.2155 | 0.4528 | 0.5472 | 1.0362 | 23.369 | 2571.4154 | 1160.0007 | 1411.4147
2016-01-12 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.02% | 1117.2365 | 1433.3846 | 2550.6211 | 24.5544 | 0.44012 | 0.55988 | 1.0352 | 23.7192 | 2574.3403 | 1127.6759 | 1446.6644
2016-01-12 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 88.59% | 1124.393 | 1425.6556 | 2550.0486 | 25.1773 | 0.44294 | 0.55706 | 1.0354 | 24.3156 | 2574.3642 | 1135.1634 | 1439.2008
2016-01-12 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.93% | 1090.2882 | 1409.1743 | 2499.4625 | 37.028 | 0.43963 | 0.56037 | 1.0572 | 35.0262 | 2534.4887 | 1105.6868 | 1428.8019
2016-01-12 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.67% | 1099.5077 | 1398.7563 | 2498.264 | 47.8338 | 0.44335 | 0.55665 | 1.0576 | 45.2272 | 2543.4912 | 1119.5592 | 1423.932
2016-01-12 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-12 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-12 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-12 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-12 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-12 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-12 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-12 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.313 | 1469.3931 | 2723.7061 | 47.9999 | 0.46531 | 0.53469 | 1.1396 | 42.1203 | 2765.8264 | 1273.912 | 1491.9144
2016-01-12 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.42% | 1245.6933 | 1480.5987 | 2726.292 | 84.6397 | 0.46211 | 0.53789 | 1.1386 | 74.3345 | 2800.6265 | 1280.0442 | 1520.5823
2016-01-12 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.91% | 1238.8056 | 1489.5527 | 2728.3583 | 54.9249 | 0.45956 | 0.54044 | 1.1379 | 48.27 | 2776.6283 | 1260.9885 | 1515.6399
2016-01-12 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.36% | 1231.3273 | 1499.2745 | 2730.6018 | 50.7985 | 0.45678 | 0.54322 | 1.137 | 44.6763 | 2775.2781 | 1251.7347 | 1523.5434
2016-01-12 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.19% | 1266.467 | 1596.9462 | 2863.4132 | 82.6176 | 0.45097 | 0.54903 | 1.1804 | 69.9919 | 2933.4051 | 1298.0311 | 1635.374
2016-01-12 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.32% | 1282.2394 | 1574.8649 | 2857.1043 | 89.9796 | 0.45658 | 0.54342 | 1.1826 | 76.0841 | 2933.1884 | 1316.9781 | 1616.2103
2016-01-13 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.58% | 1271.8405 | 1589.4234 | 2861.2638 | 129.2454 | 0.45288 | 0.54712 | 1.1812 | 109.4232 | 2970.687 | 1321.3961 | 1649.2909
2016-01-13 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.86% | 1275.7661 | 1583.9274 | 2859.6936 | 144.4855 | 0.45428 | 0.54572 | 1.1817 | 122.268 | 2981.9615 | 1331.3099 | 1650.6517
2016-01-13 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.88% | 1276.0841 | 1583.4823 | 2859.5664 | 145.1095 | 0.45439 | 0.54561 | 1.1818 | 122.7913 | 2982.3577 | 1331.8794 | 1650.4783
2016-01-13 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.79% | 1274.8348 | 1585.2312 | 2860.0661 | 144.3881 | 0.45395 | 0.54605 | 1.1816 | 122.1993 | 2982.2654 | 1330.3068 | 1651.9585
2016-01-13 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.21% | 1266.6722 | 1596.659 | 2863.3311 | 143.6702 | 0.45104 | 0.54896 | 1.1804 | 121.7115 | 2985.0426 | 1321.569 | 1663.4736
2016-01-13 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.3% | 1267.9913 | 1594.8122 | 2862.8035 | 117.1017 | 0.45151 | 0.54849 | 1.1806 | 99.1879 | 2961.9914 | 1312.7757 | 1649.2157
2016-01-13 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-13 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-13 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-13 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-13 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.67% | 1245.0743 | 1626.896 | 2871.9703 | 147.1811 | 0.44335 | 0.55665 | 1.1773 | 125.0115 | 2996.9818 | 1300.4981 | 1696.4837
2016-01-13 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.5% | 1270.7277 | 1590.9812 | 2861.7089 | 133.2103 | 0.45248 | 0.54752 | 1.181 | 112.7951 | 2974.504 | 1321.7658 | 1652.7382
2016-01-13 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.72% | 1301.9328 | 1547.2941 | 2849.2269 | 71.1499 | 0.4636 | 0.5364 | 1.1854 | 60.0199 | 2909.2467 | 1329.7578 | 1579.4889
2016-01-13 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.9426 | 1656.0861 | 3052.0287 | 93.9365 | 0.46531 | 0.53469 | 1.2327 | 76.2065 | 3128.2352 | 1431.4026 | 1696.8326
2016-01-13 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.23% | 1398.4604 | 1652.3094 | 3050.7698 | 89.4892 | 0.46615 | 0.53385 | 1.2331 | 72.5739 | 3123.3437 | 1432.291 | 1691.0527
2016-01-13 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.02% | 1395.2578 | 1657.1133 | 3052.3711 | 83.1583 | 0.46509 | 0.53491 | 1.2325 | 67.4689 | 3119.84 | 1426.6366 | 1693.2034
2016-01-13 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.88% | 1393.2683 | 1660.0975 | 3053.3658 | 84.0248 | 0.46442 | 0.53558 | 1.2322 | 68.1903 | 3121.5561 | 1424.9374 | 1696.6187
2016-01-13 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.07% | 1396.025 | 1655.9626 | 3051.9875 | 84.2773 | 0.46534 | 0.53466 | 1.2327 | 68.3696 | 3120.3572 | 1427.8402 | 1692.517
2016-01-13 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.929 | 1656.1065 | 3052.0355 | 79.9999 | 0.46531 | 0.53469 | 1.2327 | 64.9005 | 3116.936 | 1426.1278 | 1690.8082
2016-01-13 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.42% | 1386.3361 | 1670.4958 | 3056.8319 | 141.0662 | 0.46211 | 0.53789 | 1.2311 | 114.5896 | 3171.4216 | 1439.2893 | 1732.1322
2016-01-13 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-13 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-13 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.19% | 1352.9024 | 1720.6463 | 3073.5488 | 103.272 | 0.45097 | 0.54903 | 1.2255 | 84.2704 | 3157.8191 | 1390.9056 | 1766.9135
2016-01-13 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.32% | 1369.7512 | 1695.3731 | 3065.1244 | 112.4745 | 0.45658 | 0.54342 | 1.2283 | 91.5699 | 3156.6943 | 1411.5606 | 1745.1337
2016-01-14 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.58% | 1358.6426 | 1712.0361 | 3070.6787 | 161.5568 | 0.45288 | 0.54712 | 1.2264 | 131.7282 | 3202.4069 | 1418.2998 | 1784.1071
2016-01-14 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.86% | 1362.8362 | 1705.7457 | 3068.5819 | 180.6069 | 0.45428 | 0.54572 | 1.2271 | 147.1771 | 3215.759 | 1429.6956 | 1786.0634
2016-01-14 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.88% | 1363.1758 | 1705.2362 | 3068.4121 | 181.3868 | 0.45439 | 0.54561 | 1.2272 | 147.8059 | 3216.218 | 1430.3377 | 1785.8803
2016-01-14 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.79% | 1361.8414 | 1707.238 | 3069.0793 | 180.4851 | 0.45395 | 0.54605 | 1.227 | 147.0978 | 3216.1771 | 1428.616 | 1787.5612
2016-01-14 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.21% | 1353.1216 | 1720.3176 | 3073.4392 | 179.5878 | 0.45104 | 0.54896 | 1.2255 | 146.54 | 3219.9792 | 1419.2171 | 1800.7621
2016-01-14 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.3% | 1354.5308 | 1718.2038 | 3072.7346 | 146.3771 | 0.45151 | 0.54849 | 1.2258 | 119.4179 | 3192.1525 | 1408.4492 | 1783.7033
2016-01-14 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.56% | 1271.6176 | 1589.7354 | 2861.353 | 121.0774 | 0.4528 | 0.5472 | 1.1811 | 102.5106 | 2963.8636 | 1318.0345 | 1645.8291
2016-01-14 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.02% | 1236.0134 | 1639.5813 | 2875.5946 | 122.7718 | 0.44012 | 0.55988 | 1.176 | 104.3934 | 2979.9881 | 1281.9594 | 1698.0287
2016-01-14 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.59% | 1243.9307 | 1628.497 | 2872.4277 | 125.8864 | 0.44294 | 0.55706 | 1.1772 | 106.9392 | 2979.367 | 1291.2986 | 1688.0683
2016-01-14 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-14 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.67% | 1245.0743 | 1626.896 | 2871.9703 | 147.1811 | 0.44335 | 0.55665 | 1.1773 | 125.0115 | 2996.9818 | 1300.4981 | 1696.4837
2016-01-14 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.5% | 1270.7277 | 1590.9812 | 2861.7089 | 133.2103 | 0.45248 | 0.54752 | 1.181 | 112.7951 | 2974.504 | 1321.7658 | 1652.7382
2016-01-14 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.72% | 1301.9328 | 1547.2941 | 2849.2269 | 71.1499 | 0.4636 | 0.5364 | 1.1854 | 60.0199 | 2909.2467 | 1329.7578 | 1579.4889
2016-01-14 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-14 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-14 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-14 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-14 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.07% | 1306.8345 | 1540.4317 | 2847.2662 | 67.4218 | 0.46534 | 0.53466 | 1.1861 | 56.8415 | 2904.1077 | 1333.2852 | 1570.8225
2016-01-14 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-14 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.42% | 1245.6933 | 1480.5987 | 2726.292 | 84.6397 | 0.46211 | 0.53789 | 1.1386 | 74.3345 | 2800.6265 | 1280.0442 | 1520.5823
2016-01-14 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.91% | 1238.8056 | 1489.5527 | 2728.3583 | 54.9249 | 0.45956 | 0.54044 | 1.1379 | 48.27 | 2776.6283 | 1260.9885 | 1515.6399
2016-01-14 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.36% | 1282.7981 | 1574.0826 | 2856.8807 | 67.7314 | 0.45678 | 0.54322 | 1.1827 | 57.2678 | 2914.1486 | 1308.9571 | 1605.1915
2016-01-14 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.19% | 1266.467 | 1596.9462 | 2863.4132 | 82.6176 | 0.45097 | 0.54903 | 1.1804 | 69.9919 | 2933.4051 | 1298.0311 | 1635.374
2016-01-14 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.32% | 1282.2394 | 1574.8649 | 2857.1043 | 89.9796 | 0.45658 | 0.54342 | 1.1826 | 76.0841 | 2933.1884 | 1316.9781 | 1616.2103
2016-01-15 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.58% | 1271.8405 | 1589.4234 | 2861.2638 | 129.2454 | 0.45288 | 0.54712 | 1.1812 | 109.4232 | 2970.687 | 1321.3961 | 1649.2909
2016-01-15 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.86% | 1275.7661 | 1583.9274 | 2859.6936 | 144.4855 | 0.45428 | 0.54572 | 1.1817 | 122.268 | 2981.9615 | 1331.3099 | 1650.6517
2016-01-15 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.88% | 1276.0841 | 1583.4823 | 2859.5664 | 145.1095 | 0.45439 | 0.54561 | 1.1818 | 122.7913 | 2982.3577 | 1331.8794 | 1650.4783
2016-01-15 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.79% | 1274.8348 | 1585.2312 | 2860.0661 | 144.3881 | 0.45395 | 0.54605 | 1.1816 | 122.1993 | 2982.2654 | 1330.3068 | 1651.9585
2016-01-15 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.21% | 1266.6722 | 1596.659 | 2863.3311 | 143.6702 | 0.45104 | 0.54896 | 1.1804 | 121.7115 | 2985.0426 | 1321.569 | 1663.4736
2016-01-15 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.3% | 1267.9913 | 1594.8122 | 2862.8035 | 117.1017 | 0.45151 | 0.54849 | 1.1806 | 99.1879 | 2961.9914 | 1312.7757 | 1649.2157
2016-01-15 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-15 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-15 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-15 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-15 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-15 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-15 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-15 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-15 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.23% | 1256.5876 | 1466.4361 | 2723.0237 | 53.6935 | 0.46615 | 0.53385 | 1.1398 | 47.1059 | 2770.1296 | 1278.5462 | 1491.5834
2016-01-15 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.02% | 1253.7099 | 1470.1771 | 2723.887 | 49.895 | 0.46509 | 0.53491 | 1.1395 | 43.7857 | 2767.6728 | 1274.074 | 1493.5987
2016-01-15 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.88% | 1251.9222 | 1472.5011 | 2724.4233 | 50.4149 | 0.46442 | 0.53558 | 1.1393 | 44.2497 | 2768.6731 | 1272.4728 | 1496.2002
2016-01-15 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.07% | 1254.3992 | 1469.281 | 2723.6802 | 50.5664 | 0.46534 | 0.53466 | 1.1396 | 44.3719 | 2768.0521 | 1275.0473 | 1493.0048
2016-01-15 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.313 | 1469.3931 | 2723.7061 | 47.9999 | 0.46531 | 0.53469 | 1.1396 | 42.1203 | 2765.8264 | 1273.912 | 1491.9144
2016-01-15 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.42% | 1245.6933 | 1480.5987 | 2726.292 | 84.6397 | 0.46211 | 0.53789 | 1.1386 | 74.3345 | 2800.6265 | 1280.0442 | 1520.5823
2016-01-15 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.91% | 1238.8056 | 1489.5527 | 2728.3583 | 54.9249 | 0.45956 | 0.54044 | 1.1379 | 48.27 | 2776.6283 | 1260.9885 | 1515.6399
2016-01-15 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.36% | 1231.3273 | 1499.2745 | 2730.6018 | 50.7985 | 0.45678 | 0.54322 | 1.137 | 44.6763 | 2775.2781 | 1251.7347 | 1523.5434
2016-01-15 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.19% | 1266.467 | 1596.9462 | 2863.4132 | 82.6176 | 0.45097 | 0.54903 | 1.1804 | 69.9919 | 2933.4051 | 1298.0311 | 1635.374
2016-01-15 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.32% | 1282.2394 | 1574.8649 | 2857.1043 | 89.9796 | 0.45658 | 0.54342 | 1.1826 | 76.0841 | 2933.1884 | 1316.9781 | 1616.2103
2016-01-16 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.58% | 1271.8405 | 1589.4234 | 2861.2638 | 129.2454 | 0.45288 | 0.54712 | 1.1812 | 109.4232 | 2970.687 | 1321.3961 | 1649.2909
2016-01-16 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.86% | 1275.7661 | 1583.9274 | 2859.6936 | 144.4855 | 0.45428 | 0.54572 | 1.1817 | 122.268 | 2981.9615 | 1331.3099 | 1650.6517
2016-01-16 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.88% | 1276.0841 | 1583.4823 | 2859.5664 | 145.1095 | 0.45439 | 0.54561 | 1.1818 | 122.7913 | 2982.3577 | 1331.8794 | 1650.4783
2016-01-16 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.79% | 1274.8348 | 1585.2312 | 2860.0661 | 144.3881 | 0.45395 | 0.54605 | 1.1816 | 122.1993 | 2982.2654 | 1330.3068 | 1651.9585
2016-01-16 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.21% | 1266.6722 | 1596.659 | 2863.3311 | 143.6702 | 0.45104 | 0.54896 | 1.1804 | 121.7115 | 2985.0426 | 1321.569 | 1663.4736
2016-01-16 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.3% | 1267.9913 | 1594.8122 | 2862.8035 | 117.1017 | 0.45151 | 0.54849 | 1.1806 | 99.1879 | 2961.9914 | 1312.7757 | 1649.2157
2016-01-16 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.56% | 1271.6176 | 1589.7354 | 2861.353 | 121.0774 | 0.4528 | 0.5472 | 1.1811 | 102.5106 | 2963.8636 | 1318.0345 | 1645.8291
2016-01-16 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-16 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-16 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-16 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-16 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-16 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-16 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-16 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-16 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-16 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-16 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-16 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-16 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-16 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-16 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-16 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-16 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.32% | 1230.791 | 1499.9717 | 2730.7627 | 67.4847 | 0.45658 | 0.54342 | 1.137 | 59.3546 | 2790.1173 | 1257.8913 | 1532.226
2016-01-17 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.58% | 1220.8093 | 1512.9479 | 2733.7572 | 96.9341 | 0.45288 | 0.54712 | 1.1359 | 85.3395 | 2819.0967 | 1259.4579 | 1559.6388
2016-01-17 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.86% | 1224.5775 | 1508.0493 | 2732.6268 | 108.3641 | 0.45428 | 0.54572 | 1.1363 | 95.3671 | 2827.9939 | 1267.9007 | 1560.0932
2016-01-17 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.88% | 1224.8826 | 1507.6526 | 2732.5352 | 108.8321 | 0.45439 | 0.54561 | 1.1363 | 95.7761 | 2828.3113 | 1268.4025 | 1559.9088
2016-01-17 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.79% | 1223.6835 | 1509.2114 | 2732.8949 | 108.2911 | 0.45395 | 0.54605 | 1.1362 | 95.3112 | 2828.2062 | 1266.9498 | 1561.2564
2016-01-17 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.21% | 1215.8484 | 1519.3971 | 2735.2455 | 107.7527 | 0.45104 | 0.54896 | 1.1353 | 94.9102 | 2830.1556 | 1258.6567 | 1571.4989
2016-01-17 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.3% | 1217.1146 | 1517.751 | 2734.8656 | 87.8263 | 0.45151 | 0.54849 | 1.1355 | 77.3491 | 2812.2147 | 1252.0385 | 1560.1762
2016-01-17 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.56% | 1220.5954 | 1513.226 | 2733.8214 | 90.8081 | 0.4528 | 0.5472 | 1.1358 | 79.9479 | 2813.7693 | 1256.7959 | 1556.9734
2016-01-17 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-17 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-17 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-17 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-17 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-17 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-17 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-17 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-17 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-17 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-17 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.07% | 1306.8345 | 1540.4317 | 2847.2662 | 67.4218 | 0.46534 | 0.53466 | 1.1861 | 56.8415 | 2904.1077 | 1333.2852 | 1570.8225
2016-01-17 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-17 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-17 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.91% | 1290.5891 | 1563.1753 | 2853.7644 | 73.2331 | 0.45956 | 0.54044 | 1.1838 | 61.8616 | 2915.6259 | 1319.018 | 1596.608
2016-01-17 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-17 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-17 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-18 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-18 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-18 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-18 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-18 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-18 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-18 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.56% | 1358.4045 | 1712.3932 | 3070.7977 | 151.3468 | 0.4528 | 0.5472 | 1.2264 | 123.4073 | 3194.205 | 1414.2835 | 1779.9215
2016-01-18 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.02% | 1236.0134 | 1639.5813 | 2875.5946 | 122.7718 | 0.44012 | 0.55988 | 1.176 | 104.3934 | 2979.9881 | 1281.9594 | 1698.0287
2016-01-18 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.59% | 1243.9307 | 1628.497 | 2872.4277 | 125.8864 | 0.44294 | 0.55706 | 1.1772 | 106.9392 | 2979.367 | 1291.2986 | 1688.0683
2016-01-18 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-18 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.67% | 1245.0743 | 1626.896 | 2871.9703 | 147.1811 | 0.44335 | 0.55665 | 1.1773 | 125.0115 | 2996.9818 | 1300.4981 | 1696.4837
2016-01-18 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-18 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-18 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-18 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-18 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-18 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-18 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.07% | 1254.3992 | 1469.281 | 2723.6802 | 50.5664 | 0.46534 | 0.53466 | 1.1396 | 44.3719 | 2768.0521 | 1275.0473 | 1493.0048
2016-01-18 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-18 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-18 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.91% | 1290.5891 | 1563.1753 | 2853.7644 | 73.2331 | 0.45956 | 0.54044 | 1.1838 | 61.8616 | 2915.6259 | 1319.018 | 1596.608
2016-01-18 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.36% | 1282.7981 | 1574.0826 | 2856.8807 | 67.7314 | 0.45678 | 0.54322 | 1.1827 | 57.2678 | 2914.1486 | 1308.9571 | 1605.1915
2016-01-18 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.19% | 1352.9024 | 1720.6463 | 3073.5488 | 103.272 | 0.45097 | 0.54903 | 1.2255 | 84.2704 | 3157.8191 | 1390.9056 | 1766.9135
2016-01-18 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-19 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-19 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-19 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-19 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-19 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-19 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-19 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.56% | 1358.4045 | 1712.3932 | 3070.7977 | 151.3468 | 0.4528 | 0.5472 | 1.2264 | 123.4073 | 3194.205 | 1414.2835 | 1779.9215
2016-01-19 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.02% | 1236.0134 | 1639.5813 | 2875.5946 | 122.7718 | 0.44012 | 0.55988 | 1.176 | 104.3934 | 2979.9881 | 1281.9594 | 1698.0287
2016-01-19 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.59% | 1243.9307 | 1628.497 | 2872.4277 | 125.8864 | 0.44294 | 0.55706 | 1.1772 | 106.9392 | 2979.367 | 1291.2986 | 1688.0683
2016-01-19 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-19 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.67% | 1245.0743 | 1626.896 | 2871.9703 | 147.1811 | 0.44335 | 0.55665 | 1.1773 | 125.0115 | 2996.9818 | 1300.4981 | 1696.4837
2016-01-19 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.5% | 1270.7277 | 1590.9812 | 2861.7089 | 133.2103 | 0.45248 | 0.54752 | 1.181 | 112.7951 | 2974.504 | 1321.7658 | 1652.7382
2016-01-19 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.72% | 1301.9328 | 1547.2941 | 2849.2269 | 71.1499 | 0.4636 | 0.5364 | 1.1854 | 60.0199 | 2909.2467 | 1329.7578 | 1579.4889
2016-01-19 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-19 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-19 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.02% | 1395.2578 | 1657.1133 | 3052.3711 | 83.1583 | 0.46509 | 0.53491 | 1.2325 | 67.4689 | 3119.84 | 1426.6366 | 1693.2034
2016-01-19 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.88% | 1393.2683 | 1660.0975 | 3053.3658 | 84.0248 | 0.46442 | 0.53558 | 1.2322 | 68.1903 | 3121.5561 | 1424.9374 | 1696.6187
2016-01-19 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.07% | 1396.025 | 1655.9626 | 3051.9875 | 84.2773 | 0.46534 | 0.53466 | 1.2327 | 68.3696 | 3120.3572 | 1427.8402 | 1692.517
2016-01-19 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.929 | 1656.1065 | 3052.0355 | 79.9999 | 0.46531 | 0.53469 | 1.2327 | 64.9005 | 3116.936 | 1426.1278 | 1690.8082
2016-01-19 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.42% | 1386.3361 | 1670.4958 | 3056.8319 | 141.0662 | 0.46211 | 0.53789 | 1.2311 | 114.5896 | 3171.4216 | 1439.2893 | 1732.1322
2016-01-19 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-19 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.36% | 1431.2525 | 1837.495 | 3268.7475 | 169.3285 | 0.45678 | 0.54322 | 1.4568 | 116.2345 | 3384.982 | 1484.3465 | 1900.6356
2016-01-19 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-19 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-20 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-20 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-20 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-20 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-20 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-20 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-20 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.56% | 1271.6176 | 1589.7354 | 2861.353 | 121.0774 | 0.4528 | 0.5472 | 1.1811 | 102.5106 | 2963.8636 | 1318.0345 | 1645.8291
2016-01-20 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.02% | 1236.0134 | 1639.5813 | 2875.5946 | 122.7718 | 0.44012 | 0.55988 | 1.176 | 104.3934 | 2979.9881 | 1281.9594 | 1698.0287
2016-01-20 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.59% | 1243.9307 | 1628.497 | 2872.4277 | 125.8864 | 0.44294 | 0.55706 | 1.1772 | 106.9392 | 2979.367 | 1291.2986 | 1688.0683
2016-01-20 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-20 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.67% | 1245.0743 | 1626.896 | 2871.9703 | 147.1811 | 0.44335 | 0.55665 | 1.1773 | 125.0115 | 2996.9818 | 1300.4981 | 1696.4837
2016-01-20 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.5% | 1270.7277 | 1590.9812 | 2861.7089 | 133.2103 | 0.45248 | 0.54752 | 1.181 | 112.7951 | 2974.504 | 1321.7658 | 1652.7382
2016-01-20 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.72% | 1301.9328 | 1547.2941 | 2849.2269 | 71.1499 | 0.4636 | 0.5364 | 1.1854 | 60.0199 | 2909.2467 | 1329.7578 | 1579.4889
2016-01-20 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-20 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.23% | 1398.4604 | 1652.3094 | 3050.7698 | 89.4892 | 0.46615 | 0.53385 | 1.2331 | 72.5739 | 3123.3437 | 1432.291 | 1691.0527
2016-01-20 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.02% | 1395.2578 | 1657.1133 | 3052.3711 | 83.1583 | 0.46509 | 0.53491 | 1.2325 | 67.4689 | 3119.84 | 1426.6366 | 1693.2034
2016-01-20 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.88% | 1393.2683 | 1660.0975 | 3053.3658 | 84.0248 | 0.46442 | 0.53558 | 1.2322 | 68.1903 | 3121.5561 | 1424.9374 | 1696.6187
2016-01-20 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.07% | 1396.025 | 1655.9626 | 3051.9875 | 84.2773 | 0.46534 | 0.53466 | 1.2327 | 68.3696 | 3120.3572 | 1427.8402 | 1692.517
2016-01-20 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.929 | 1656.1065 | 3052.0355 | 79.9999 | 0.46531 | 0.53469 | 1.2327 | 64.9005 | 3116.936 | 1426.1278 | 1690.8082
2016-01-20 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.42% | 1447.951 | 1804.0979 | 3252.049 | 282.1325 | 0.46211 | 0.53789 | 1.4621 | 192.9623 | 3445.0112 | 1537.1212 | 1907.89
2016-01-20 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.91% | 1439.9451 | 1820.1099 | 3260.0549 | 183.0828 | 0.45956 | 0.54044 | 1.4596 | 125.4373 | 3385.4922 | 1497.5906 | 1887.9016
2016-01-20 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.36% | 1431.2525 | 1837.495 | 3268.7475 | 169.3285 | 0.45678 | 0.54322 | 1.4568 | 116.2345 | 3384.982 | 1484.3465 | 1900.6356
2016-01-20 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-20 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-21 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-21 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-21 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-21 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-21 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-21 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-21 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.56% | 1418.7781 | 1862.4439 | 3281.2219 | 302.6935 | 0.4528 | 0.5472 | 1.4528 | 208.3516 | 3489.5735 | 1513.12 | 1976.4536
2016-01-21 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.02% | 1320.3704 | 1769.4444 | 3089.8148 | 153.4648 | 0.44012 | 0.55988 | 1.2201 | 125.7845 | 3215.5993 | 1375.7311 | 1839.8682
2016-01-21 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.59% | 1328.828 | 1756.7579 | 3085.586 | 157.358 | 0.44294 | 0.55706 | 1.2215 | 128.8266 | 3214.4126 | 1385.8908 | 1828.5217
2016-01-21 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.93% | 1318.897 | 1771.6545 | 3090.5515 | 142.4153 | 0.43963 | 0.56037 | 1.2198 | 116.7515 | 3207.3029 | 1370.2247 | 1837.0782
2016-01-21 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.67% | 1330.0497 | 1754.9255 | 3084.9752 | 183.9763 | 0.44335 | 0.55665 | 1.2217 | 150.5935 | 3235.5687 | 1396.8153 | 1838.7534
2016-01-21 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.5% | 1270.7277 | 1590.9812 | 2861.7089 | 133.2103 | 0.45248 | 0.54752 | 1.181 | 112.7951 | 2974.504 | 1321.7658 | 1652.7382
2016-01-21 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.72% | 1301.9328 | 1547.2941 | 2849.2269 | 71.1499 | 0.4636 | 0.5364 | 1.1854 | 60.0199 | 2909.2467 | 1329.7578 | 1579.4889
2016-01-21 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7574 | 1540.5397 | 2847.297 | 75.1492 | 0.46531 | 0.53469 | 1.1861 | 63.3569 | 2910.6539 | 1336.2382 | 1574.4157
2016-01-21 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-21 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-21 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-21 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.07% | 1306.8345 | 1540.4317 | 2847.2662 | 67.4218 | 0.46534 | 0.53466 | 1.1861 | 56.8415 | 2904.1077 | 1333.2852 | 1570.8225
2016-01-21 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-21 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-21 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-21 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-21 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-21 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-22 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-22 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-22 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-22 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-22 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-22 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-22 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.56% | 1358.4045 | 1712.3932 | 3070.7977 | 151.3468 | 0.4528 | 0.5472 | 1.2264 | 123.4073 | 3194.205 | 1414.2835 | 1779.9215
2016-01-22 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.02% | 1320.3704 | 1769.4444 | 3089.8148 | 153.4648 | 0.44012 | 0.55988 | 1.2201 | 125.7845 | 3215.5993 | 1375.7311 | 1839.8682
2016-01-22 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.59% | 1387.8871 | 1924.2259 | 3312.1129 | 314.716 | 0.44294 | 0.55706 | 1.4429 | 218.1071 | 3530.22 | 1484.496 | 2045.724
2016-01-22 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.93% | 1377.5147 | 1944.9707 | 3322.4853 | 284.8306 | 0.43963 | 0.56037 | 1.4396 | 197.8496 | 3520.3349 | 1464.4957 | 2055.8392
2016-01-22 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.67% | 1389.163 | 1921.674 | 3310.837 | 367.9527 | 0.44335 | 0.55665 | 1.4433 | 254.9297 | 3565.7667 | 1502.186 | 2063.5806
2016-01-22 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.5% | 1417.7852 | 1864.4295 | 3282.2148 | 333.0258 | 0.45248 | 0.54752 | 1.4525 | 229.2801 | 3511.4948 | 1521.531 | 1989.9639
2016-01-22 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.72% | 1452.6016 | 1794.7968 | 3247.3984 | 177.8747 | 0.4636 | 0.5364 | 1.4636 | 121.5326 | 3368.931 | 1508.9437 | 1859.9873
2016-01-22 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.06% | 1457.9845 | 1784.031 | 3242.0155 | 187.873 | 0.46531 | 0.53469 | 1.4653 | 128.2134 | 3370.2289 | 1517.644 | 1852.5849
2016-01-22 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.23% | 1460.6142 | 1778.7716 | 3239.3858 | 178.9783 | 0.46615 | 0.53385 | 1.4662 | 122.0734 | 3361.4592 | 1517.5191 | 1843.94
2016-01-22 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.02% | 1457.2692 | 1785.4615 | 3242.7308 | 166.3165 | 0.46509 | 0.53491 | 1.4651 | 113.52 | 3356.2508 | 1510.0658 | 1846.185
2016-01-22 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.88% | 1455.1913 | 1789.6173 | 3244.8087 | 168.0497 | 0.46442 | 0.53558 | 1.4644 | 114.7549 | 3359.5636 | 1508.4861 | 1851.0774
2016-01-22 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.07% | 1458.0705 | 1783.859 | 3241.9295 | 168.5545 | 0.46534 | 0.53466 | 1.4653 | 115.0274 | 3356.9569 | 1511.5976 | 1845.3594
2016-01-22 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.06% | 1457.9703 | 1784.0595 | 3242.0297 | 159.9998 | 0.46531 | 0.53469 | 1.4653 | 109.1918 | 3351.2215 | 1508.7783 | 1842.4433
2016-01-22 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.42% | 1447.951 | 1804.0979 | 3252.049 | 282.1325 | 0.46211 | 0.53789 | 1.4621 | 192.9623 | 3445.0112 | 1537.1212 | 1907.89
2016-01-22 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.91% | 1439.9451 | 1820.1099 | 3260.0549 | 183.0828 | 0.45956 | 0.54044 | 1.4596 | 125.4373 | 3385.4922 | 1497.5906 | 1887.9016
2016-01-22 21:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 91.36% | 1484.5438 | 1934.0036 | 3418.5474 | 203.1942 | 0.45678 | 0.54322 | 1.5481 | 131.2506 | 3549.798 | 1544.4968 | 2005.3011
2016-01-22 22:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 90.19% | 1465.6443 | 1975.5825 | 3441.2268 | 247.8527 | 0.45097 | 0.54903 | 1.5412 | 160.8221 | 3602.0489 | 1538.1698 | 2063.8791
2016-01-22 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 91.32% | 1483.8972 | 1935.4262 | 3419.3234 | 269.9389 | 0.45658 | 0.54342 | 1.5479 | 174.3903 | 3593.7137 | 1563.521 | 2030.1928
2016-01-23 | 2.2 | 5200 | 1240 | 1625 | 3250 | 90.58% | 1471.8628 | 1961.9018 | 3433.7646 | 387.7363 | 0.45288 | 0.54712 | 1.5435 | 251.2129 | 3684.9775 | 1585.6323 | 2099.3451
2016-01-23 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 90.86% | 1476.4059 | 1951.9071 | 3428.3129 | 433.4564 | 0.45428 | 0.54572 | 1.5451 | 280.5299 | 3708.8429 | 1603.8447 | 2104.9982
2016-01-23 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 90.88% | 1476.7738 | 1951.0976 | 3427.8714 | 435.3284 | 0.45439 | 0.54561 | 1.5453 | 281.7167 | 3709.5881 | 1604.7836 | 2104.8045
2016-01-23 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-23 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-23 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-23 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.56% | 1418.7781 | 1862.4439 | 3281.2219 | 302.6935 | 0.4528 | 0.5472 | 1.4528 | 208.3516 | 3489.5735 | 1513.12 | 1976.4536
2016-01-23 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.02% | 1320.3704 | 1769.4444 | 3089.8148 | 153.4648 | 0.44012 | 0.55988 | 1.2201 | 125.7845 | 3215.5993 | 1375.7311 | 1839.8682
2016-01-23 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.59% | 1328.828 | 1756.7579 | 3085.586 | 157.358 | 0.44294 | 0.55706 | 1.2215 | 128.8266 | 3214.4126 | 1385.8908 | 1828.5217
2016-01-23 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.93% | 1318.897 | 1771.6545 | 3090.5515 | 142.4153 | 0.43963 | 0.56037 | 1.2198 | 116.7515 | 3207.3029 | 1370.2247 | 1837.0782
2016-01-23 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.67% | 1330.0497 | 1754.9255 | 3084.9752 | 183.9763 | 0.44335 | 0.55665 | 1.2217 | 150.5935 | 3235.5687 | 1396.8153 | 1838.7534
2016-01-23 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.5% | 1357.454 | 1713.8191 | 3071.273 | 166.5129 | 0.45248 | 0.54752 | 1.2262 | 135.7912 | 3207.0642 | 1418.8974 | 1788.1668
2016-01-23 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.72% | 1390.7888 | 1663.8168 | 3054.6056 | 88.9373 | 0.4636 | 0.5364 | 1.2318 | 72.2012 | 3126.8068 | 1424.261 | 1702.5459
2016-01-23 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.9426 | 1656.0861 | 3052.0287 | 93.9365 | 0.46531 | 0.53469 | 1.2327 | 76.2065 | 3128.2352 | 1431.4026 | 1696.8326
2016-01-23 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.23% | 1398.4604 | 1652.3094 | 3050.7698 | 89.4892 | 0.46615 | 0.53385 | 1.2331 | 72.5739 | 3123.3437 | 1432.291 | 1691.0527
2016-01-23 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.02% | 1395.2578 | 1657.1133 | 3052.3711 | 83.1583 | 0.46509 | 0.53491 | 1.2325 | 67.4689 | 3119.84 | 1426.6366 | 1693.2034
2016-01-23 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.88% | 1393.2683 | 1660.0975 | 3053.3658 | 84.0248 | 0.46442 | 0.53558 | 1.2322 | 68.1903 | 3121.5561 | 1424.9374 | 1696.6187
2016-01-23 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.07% | 1396.025 | 1655.9626 | 3051.9875 | 84.2773 | 0.46534 | 0.53466 | 1.2327 | 68.3696 | 3120.3572 | 1427.8402 | 1692.517
2016-01-23 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.929 | 1656.1065 | 3052.0355 | 79.9999 | 0.46531 | 0.53469 | 1.2327 | 64.9005 | 3116.936 | 1426.1278 | 1690.8082
2016-01-23 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.42% | 1386.3361 | 1670.4958 | 3056.8319 | 141.0662 | 0.46211 | 0.53789 | 1.2311 | 114.5896 | 3171.4216 | 1439.2893 | 1732.1322
2016-01-23 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-23 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-23 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-23 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-24 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-24 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-24 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-24 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-24 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-24 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-24 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.56% | 1418.7781 | 1862.4439 | 3281.2219 | 302.6935 | 0.4528 | 0.5472 | 1.4528 | 208.3516 | 3489.5735 | 1513.12 | 1976.4536
2016-01-24 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.02% | 1379.0535 | 1941.893 | 3320.9465 | 306.9296 | 0.44012 | 0.55988 | 1.4401 | 213.1273 | 3534.0738 | 1472.8558 | 2061.218
2016-01-24 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.59% | 1387.8871 | 1924.2259 | 3312.1129 | 314.716 | 0.44294 | 0.55706 | 1.4429 | 218.1071 | 3530.22 | 1484.496 | 2045.724
2016-01-24 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.93% | 1318.897 | 1771.6545 | 3090.5515 | 142.4153 | 0.43963 | 0.56037 | 1.2198 | 116.7515 | 3207.3029 | 1370.2247 | 1837.0782
2016-01-24 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.67% | 1330.0497 | 1754.9255 | 3084.9752 | 183.9763 | 0.44335 | 0.55665 | 1.2217 | 150.5935 | 3235.5687 | 1396.8153 | 1838.7534
2016-01-24 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.5% | 1357.454 | 1713.8191 | 3071.273 | 166.5129 | 0.45248 | 0.54752 | 1.2262 | 135.7912 | 3207.0642 | 1418.8974 | 1788.1668
2016-01-24 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.72% | 1452.6016 | 1794.7968 | 3247.3984 | 177.8747 | 0.4636 | 0.5364 | 1.4636 | 121.5326 | 3368.931 | 1508.9437 | 1859.9873
2016-01-24 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.9426 | 1656.0861 | 3052.0287 | 93.9365 | 0.46531 | 0.53469 | 1.2327 | 76.2065 | 3128.2352 | 1431.4026 | 1696.8326
2016-01-24 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.23% | 1398.4604 | 1652.3094 | 3050.7698 | 89.4892 | 0.46615 | 0.53385 | 1.2331 | 72.5739 | 3123.3437 | 1432.291 | 1691.0527
2016-01-24 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.02% | 1395.2578 | 1657.1133 | 3052.3711 | 83.1583 | 0.46509 | 0.53491 | 1.2325 | 67.4689 | 3119.84 | 1426.6366 | 1693.2034
2016-01-24 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.88% | 1393.2683 | 1660.0975 | 3053.3658 | 84.0248 | 0.46442 | 0.53558 | 1.2322 | 68.1903 | 3121.5561 | 1424.9374 | 1696.6187
2016-01-24 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.07% | 1396.025 | 1655.9626 | 3051.9875 | 84.2773 | 0.46534 | 0.53466 | 1.2327 | 68.3696 | 3120.3572 | 1427.8402 | 1692.517
2016-01-24 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.929 | 1656.1065 | 3052.0355 | 79.9999 | 0.46531 | 0.53469 | 1.2327 | 64.9005 | 3116.936 | 1426.1278 | 1690.8082
2016-01-24 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-24 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.91% | 1290.5891 | 1563.1753 | 2853.7644 | 73.2331 | 0.45956 | 0.54044 | 1.1838 | 61.8616 | 2915.6259 | 1319.018 | 1596.608
2016-01-24 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.36% | 1282.7981 | 1574.0826 | 2856.8807 | 67.7314 | 0.45678 | 0.54322 | 1.1827 | 57.2678 | 2914.1486 | 1308.9571 | 1605.1915
2016-01-24 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.19% | 1266.467 | 1596.9462 | 2863.4132 | 82.6176 | 0.45097 | 0.54903 | 1.1804 | 69.9919 | 2933.4051 | 1298.0311 | 1635.374
2016-01-24 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.32% | 1282.2394 | 1574.8649 | 2857.1043 | 89.9796 | 0.45658 | 0.54342 | 1.1826 | 76.0841 | 2933.1884 | 1316.9781 | 1616.2103
2016-01-25 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.58% | 1271.8405 | 1589.4234 | 2861.2638 | 129.2454 | 0.45288 | 0.54712 | 1.1812 | 109.4232 | 2970.687 | 1321.3961 | 1649.2909
2016-01-25 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.86% | 1275.7661 | 1583.9274 | 2859.6936 | 144.4855 | 0.45428 | 0.54572 | 1.1817 | 122.268 | 2981.9615 | 1331.3099 | 1650.6517
2016-01-25 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.88% | 1276.0841 | 1583.4823 | 2859.5664 | 145.1095 | 0.45439 | 0.54561 | 1.1818 | 122.7913 | 2982.3577 | 1331.8794 | 1650.4783
2016-01-25 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.79% | 1274.8348 | 1585.2312 | 2860.0661 | 144.3881 | 0.45395 | 0.54605 | 1.1816 | 122.1993 | 2982.2654 | 1330.3068 | 1651.9585
2016-01-25 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.21% | 1266.6722 | 1596.659 | 2863.3311 | 143.6702 | 0.45104 | 0.54896 | 1.1804 | 121.7115 | 2985.0426 | 1321.569 | 1663.4736
2016-01-25 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.3% | 1217.1146 | 1517.751 | 2734.8656 | 87.8263 | 0.45151 | 0.54849 | 1.1355 | 77.3491 | 2812.2147 | 1252.0385 | 1560.1762
2016-01-25 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.56% | 1223.5703 | 1510.5371 | 2734.1074 | 75.6734 | 0.4528 | 0.5472 | 1.1132 | 67.9782 | 2802.0856 | 1254.3509 | 1547.7347
2016-01-25 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.02% | 1189.3114 | 1553.3608 | 2742.6722 | 76.7324 | 0.44012 | 0.55988 | 1.11 | 69.1264 | 2811.7985 | 1219.7355 | 1592.063
2016-01-25 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.59% | 1196.9296 | 1543.8381 | 2740.7676 | 78.679 | 0.44294 | 0.55706 | 1.1107 | 70.835 | 2811.6027 | 1228.3054 | 1583.2972
2016-01-25 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.93% | 1187.9843 | 1555.0196 | 2743.0039 | 71.2077 | 0.43963 | 0.56037 | 1.1099 | 64.1564 | 2807.1603 | 1216.1895 | 1590.9708
2016-01-25 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.67% | 1198.0299 | 1542.4626 | 2740.4925 | 91.9882 | 0.44335 | 0.55665 | 1.1108 | 82.8097 | 2823.3023 | 1234.7436 | 1588.5586
2016-01-25 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.5% | 1222.7141 | 1511.6074 | 2734.3215 | 83.2565 | 0.45248 | 0.54752 | 1.1131 | 74.7955 | 2809.117 | 1256.5579 | 1552.5591
2016-01-25 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.72% | 1252.7401 | 1474.0749 | 2726.815 | 44.4687 | 0.4636 | 0.5364 | 1.1159 | 39.8501 | 2766.6651 | 1271.2145 | 1495.4506
2016-01-25 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3824 | 1468.272 | 2725.6544 | 46.9682 | 0.46531 | 0.53469 | 1.1163 | 42.0739 | 2767.7283 | 1276.9599 | 1490.7683
2016-01-25 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-25 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-25 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-25 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-25 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-25 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-25 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-25 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-25 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.19% | 1215.6515 | 1519.6531 | 2735.3046 | 61.9632 | 0.45097 | 0.54903 | 1.1353 | 54.5792 | 2789.8837 | 1240.2649 | 1549.6188
2016-01-25 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.32% | 1230.791 | 1499.9717 | 2730.7627 | 67.4847 | 0.45658 | 0.54342 | 1.137 | 59.3546 | 2790.1173 | 1257.8913 | 1532.226
2016-01-26 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.58% | 1220.8093 | 1512.9479 | 2733.7572 | 96.9341 | 0.45288 | 0.54712 | 1.1359 | 85.3395 | 2819.0967 | 1259.4579 | 1559.6388
2016-01-26 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.86% | 1224.5775 | 1508.0493 | 2732.6268 | 108.3641 | 0.45428 | 0.54572 | 1.1363 | 95.3671 | 2827.9939 | 1267.9007 | 1560.0932
2016-01-26 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.88% | 1224.8826 | 1507.6526 | 2732.5352 | 108.8321 | 0.45439 | 0.54561 | 1.1363 | 95.7761 | 2828.3113 | 1268.4025 | 1559.9088
2016-01-26 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.79% | 1223.6835 | 1509.2114 | 2732.8949 | 108.2911 | 0.45395 | 0.54605 | 1.1362 | 95.3112 | 2828.2062 | 1266.9498 | 1561.2564
2016-01-26 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.21% | 1215.8484 | 1519.3971 | 2735.2455 | 107.7527 | 0.45104 | 0.54896 | 1.1353 | 94.9102 | 2830.1556 | 1258.6567 | 1571.4989
2016-01-26 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.3% | 1217.1146 | 1517.751 | 2734.8656 | 87.8263 | 0.45151 | 0.54849 | 1.1355 | 77.3491 | 2812.2147 | 1252.0385 | 1560.1762
2016-01-26 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.56% | 1223.5703 | 1510.5371 | 2734.1074 | 75.6734 | 0.4528 | 0.5472 | 1.1132 | 67.9782 | 2802.0856 | 1254.3509 | 1547.7347
2016-01-26 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.02% | 1189.3114 | 1553.3608 | 2742.6722 | 76.7324 | 0.44012 | 0.55988 | 1.11 | 69.1264 | 2811.7985 | 1219.7355 | 1592.063
2016-01-26 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.59% | 1196.9296 | 1543.8381 | 2740.7676 | 78.679 | 0.44294 | 0.55706 | 1.1107 | 70.835 | 2811.6027 | 1228.3054 | 1583.2972
2016-01-26 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-26 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-26 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-26 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-26 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-26 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-26 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-26 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-26 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.07% | 1306.8345 | 1540.4317 | 2847.2662 | 67.4218 | 0.46534 | 0.53466 | 1.1861 | 56.8415 | 2904.1077 | 1333.2852 | 1570.8225
2016-01-26 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-26 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-26 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-26 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-26 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-26 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-27 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-27 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-27 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-27 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-27 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-27 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-27 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.56% | 1358.4045 | 1712.3932 | 3070.7977 | 151.3468 | 0.4528 | 0.5472 | 1.2264 | 123.4073 | 3194.205 | 1414.2835 | 1779.9215
2016-01-27 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.02% | 1236.0134 | 1639.5813 | 2875.5946 | 122.7718 | 0.44012 | 0.55988 | 1.176 | 104.3934 | 2979.9881 | 1281.9594 | 1698.0287
2016-01-27 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.59% | 1243.9307 | 1628.497 | 2872.4277 | 125.8864 | 0.44294 | 0.55706 | 1.1772 | 106.9392 | 2979.367 | 1291.2986 | 1688.0683
2016-01-27 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.93% | 1234.6342 | 1641.5122 | 2876.1463 | 113.9323 | 0.43963 | 0.56037 | 1.1759 | 96.8933 | 2973.0396 | 1277.2316 | 1695.808
2016-01-27 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.67% | 1330.0497 | 1754.9255 | 3084.9752 | 183.9763 | 0.44335 | 0.55665 | 1.2217 | 150.5935 | 3235.5687 | 1396.8153 | 1838.7534
2016-01-27 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.5% | 1357.454 | 1713.8191 | 3071.273 | 166.5129 | 0.45248 | 0.54752 | 1.2262 | 135.7912 | 3207.0642 | 1418.8974 | 1788.1668
2016-01-27 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.72% | 1390.7888 | 1663.8168 | 3054.6056 | 88.9373 | 0.4636 | 0.5364 | 1.2318 | 72.2012 | 3126.8068 | 1424.261 | 1702.5459
2016-01-27 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 93.06% | 1395.9426 | 1656.0861 | 3052.0287 | 93.9365 | 0.46531 | 0.53469 | 1.2327 | 76.2065 | 3128.2352 | 1431.4026 | 1696.8326
2016-01-27 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-27 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-27 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-27 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.07% | 1306.8345 | 1540.4317 | 2847.2662 | 67.4218 | 0.46534 | 0.53466 | 1.1861 | 56.8415 | 2904.1077 | 1333.2852 | 1570.8225
2016-01-27 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.06% | 1306.7446 | 1540.5575 | 2847.3021 | 63.9999 | 0.46531 | 0.53469 | 1.1861 | 53.9572 | 2901.2594 | 1331.8514 | 1569.4079
2016-01-27 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.42% | 1297.7646 | 1553.1295 | 2850.8941 | 112.853 | 0.46211 | 0.53789 | 1.1848 | 95.2471 | 2946.1412 | 1341.7794 | 1604.3618
2016-01-27 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.91% | 1378.6708 | 1681.9938 | 3060.6646 | 91.5414 | 0.45956 | 0.54044 | 1.2298 | 74.4373 | 3135.1019 | 1412.879 | 1722.2229
2016-01-27 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.36% | 1370.3482 | 1694.4778 | 3064.8259 | 84.6642 | 0.45678 | 0.54322 | 1.2284 | 68.9229 | 3133.7488 | 1401.8309 | 1731.9178
2016-01-27 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 90.19% | 1352.9024 | 1720.6463 | 3073.5488 | 103.272 | 0.45097 | 0.54903 | 1.2255 | 84.2704 | 3157.8191 | 1390.9056 | 1766.9135
2016-01-27 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-28 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-28 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-28 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-28 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-28 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-28 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-28 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.56% | 1418.7781 | 1862.4439 | 3281.2219 | 302.6935 | 0.4528 | 0.5472 | 1.4528 | 208.3516 | 3489.5735 | 1513.12 | 1976.4536
2016-01-28 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.02% | 1379.0535 | 1941.893 | 3320.9465 | 306.9296 | 0.44012 | 0.55988 | 1.4401 | 213.1273 | 3534.0738 | 1472.8558 | 2061.218
2016-01-28 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.59% | 1387.8871 | 1924.2259 | 3312.1129 | 314.716 | 0.44294 | 0.55706 | 1.4429 | 218.1071 | 3530.22 | 1484.496 | 2045.724
2016-01-28 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.93% | 1377.5147 | 1944.9707 | 3322.4853 | 284.8306 | 0.43963 | 0.56037 | 1.4396 | 197.8496 | 3520.3349 | 1464.4957 | 2055.8392
2016-01-28 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.67% | 1389.163 | 1921.674 | 3310.837 | 367.9527 | 0.44335 | 0.55665 | 1.4433 | 254.9297 | 3565.7667 | 1502.186 | 2063.5806
2016-01-28 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.5% | 1417.7852 | 1864.4295 | 3282.2148 | 333.0258 | 0.45248 | 0.54752 | 1.4525 | 229.2801 | 3511.4948 | 1521.531 | 1989.9639
2016-01-28 12:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 92.72% | 1506.6878 | 1885.2868 | 3391.9746 | 213.4496 | 0.4636 | 0.5364 | 1.5563 | 137.1506 | 3529.1252 | 1570.2703 | 1958.8549
2016-01-28 13:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 93.06% | 1512.2711 | 1873.0035 | 3385.2746 | 225.4476 | 0.46531 | 0.53469 | 1.5584 | 144.6682 | 3529.9428 | 1579.5873 | 1950.3555
2016-01-28 14:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 93.23% | 1514.9988 | 1867.0027 | 3382.0015 | 214.774 | 0.46615 | 0.53385 | 1.5594 | 137.73 | 3519.7315 | 1579.2021 | 1940.5294
2016-01-28 15:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 93.02% | 1511.5293 | 1874.6356 | 3386.1649 | 199.5798 | 0.46509 | 0.53491 | 1.5581 | 128.0916 | 3514.2564 | 1571.1028 | 1943.1536
2016-01-28 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.88% | 1455.1913 | 1789.6173 | 3244.8087 | 168.0497 | 0.46442 | 0.53558 | 1.4644 | 114.7549 | 3359.5636 | 1508.4861 | 1851.0774
2016-01-28 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.07% | 1458.0705 | 1783.859 | 3241.9295 | 168.5545 | 0.46534 | 0.53466 | 1.4653 | 115.0274 | 3356.9569 | 1511.5976 | 1845.3594
2016-01-28 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 93.06% | 1457.9703 | 1784.0595 | 3242.0297 | 159.9998 | 0.46531 | 0.53469 | 1.4653 | 109.1918 | 3351.2215 | 1508.7783 | 1842.4433
2016-01-28 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 92.42% | 1447.951 | 1804.0979 | 3252.049 | 282.1325 | 0.46211 | 0.53789 | 1.4621 | 192.9623 | 3445.0112 | 1537.1212 | 1907.89
2016-01-28 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.91% | 1439.9451 | 1820.1099 | 3260.0549 | 183.0828 | 0.45956 | 0.54044 | 1.4596 | 125.4373 | 3385.4922 | 1497.5906 | 1887.9016
2016-01-28 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.36% | 1431.2525 | 1837.495 | 3268.7475 | 169.3285 | 0.45678 | 0.54322 | 1.4568 | 116.2345 | 3384.982 | 1484.3465 | 1900.6356
2016-01-28 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.19% | 1413.0314 | 1873.9371 | 3286.9686 | 206.5439 | 0.45097 | 0.54903 | 1.451 | 142.3491 | 3429.3177 | 1477.2263 | 1952.0914
2016-01-28 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 91.32% | 1430.6291 | 1838.7419 | 3269.3709 | 224.9491 | 0.45658 | 0.54342 | 1.4566 | 154.4361 | 3423.807 | 1501.1421 | 1922.6649
2016-01-29 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.58% | 1419.0267 | 1861.9465 | 3280.9733 | 323.1136 | 0.45288 | 0.54712 | 1.4529 | 222.3951 | 3503.3683 | 1519.7452 | 1983.6231
2016-01-29 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.86% | 1423.4067 | 1853.1866 | 3276.5933 | 361.2137 | 0.45428 | 0.54572 | 1.4543 | 248.38 | 3524.9733 | 1536.2404 | 1988.7328
2016-01-29 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.88% | 1423.7614 | 1852.4771 | 3276.2386 | 362.7737 | 0.45439 | 0.54561 | 1.4544 | 249.4332 | 3525.6718 | 1537.1019 | 1988.5699
2016-01-29 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.79% | 1422.3676 | 1855.2647 | 3277.6324 | 360.9703 | 0.45395 | 0.54605 | 1.4539 | 248.2692 | 3525.9016 | 1535.0687 | 1990.8328
2016-01-29 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.21% | 1413.2604 | 1873.4793 | 3286.7396 | 359.1755 | 0.45104 | 0.54896 | 1.451 | 247.5296 | 3534.2693 | 1524.9063 | 2009.363
2016-01-29 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 90.3% | 1414.7321 | 1870.5357 | 3285.2679 | 292.7542 | 0.45151 | 0.54849 | 1.4515 | 201.6894 | 3486.9573 | 1505.797 | 1981.1603
2016-01-29 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 90.56% | 1271.6176 | 1589.7354 | 2861.353 | 121.0774 | 0.4528 | 0.5472 | 1.1811 | 102.5106 | 2963.8636 | 1318.0345 | 1645.8291
2016-01-29 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.02% | 1186.4198 | 1557.6543 | 2744.0741 | 92.0789 | 0.44012 | 0.55988 | 1.132 | 81.3391 | 2825.4132 | 1222.219 | 1603.1942
2016-01-29 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.59% | 1194.0194 | 1547.7748 | 2741.7942 | 94.4148 | 0.44294 | 0.55706 | 1.1329 | 83.3403 | 2825.1345 | 1230.9344 | 1594.2001
2016-01-29 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.93% | 1185.0959 | 1559.3754 | 2744.4712 | 85.4492 | 0.43963 | 0.56037 | 1.1319 | 75.4925 | 2819.9637 | 1218.2848 | 1601.6789
2016-01-29 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.67% | 1195.1171 | 1546.3478 | 2741.4649 | 110.3858 | 0.44335 | 0.55665 | 1.133 | 97.4275 | 2838.8923 | 1238.3116 | 1600.5808
2016-01-29 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.5% | 1219.7412 | 1514.3364 | 2734.0776 | 99.9077 | 0.45248 | 0.54752 | 1.1357 | 87.9667 | 2822.0443 | 1259.5448 | 1562.4995
2016-01-29 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.72% | 1249.6943 | 1475.3975 | 2725.0917 | 53.3624 | 0.4636 | 0.5364 | 1.1391 | 46.847 | 2771.9387 | 1271.4123 | 1500.5264
2016-01-29 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.3252 | 1469.3772 | 2723.7024 | 56.3619 | 0.46531 | 0.53469 | 1.1396 | 49.4579 | 2773.1603 | 1277.3387 | 1495.8216
2016-01-29 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.23% | 1309.1143 | 1537.2399 | 2846.3543 | 71.5913 | 0.46615 | 0.53385 | 1.1865 | 60.3402 | 2906.6945 | 1337.2421 | 1569.4523
2016-01-29 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.02% | 1306.1163 | 1541.4372 | 2847.5535 | 66.5266 | 0.46509 | 0.53491 | 1.186 | 56.0916 | 2903.6451 | 1332.2037 | 1571.4414
2016-01-29 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.88% | 1304.2539 | 1544.0445 | 2848.2984 | 67.2199 | 0.46442 | 0.53558 | 1.1858 | 56.6888 | 2904.9873 | 1330.5815 | 1574.4057
2016-01-29 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.07% | 1254.3992 | 1469.281 | 2723.6802 | 50.5664 | 0.46534 | 0.53466 | 1.1396 | 44.3719 | 2768.0521 | 1275.0473 | 1493.0048
2016-01-29 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.06% | 1254.313 | 1469.3931 | 2723.7061 | 47.9999 | 0.46531 | 0.53469 | 1.1396 | 42.1203 | 2765.8264 | 1273.912 | 1491.9144
2016-01-29 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-29 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-29 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-29 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-29 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.32% | 1233.7907 | 1497.7616 | 2731.5523 | 56.2373 | 0.45658 | 0.54342 | 1.1141 | 50.4757 | 2782.028 | 1256.8371 | 1525.1909
2016-01-30 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-30 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-30 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-30 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-30 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-30 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-30 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.56% | 1223.5703 | 1510.5371 | 2734.1074 | 75.6734 | 0.4528 | 0.5472 | 1.1132 | 67.9782 | 2802.0856 | 1254.3509 | 1547.7347
2016-01-30 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.02% | 1091.5062 | 1407.798 | 2499.3042 | 39.9009 | 0.44012 | 0.55988 | 1.0572 | 37.7414 | 2537.0456 | 1108.1171 | 1428.9286
2016-01-30 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-30 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.93% | 1090.2882 | 1409.1743 | 2499.4625 | 37.028 | 0.43963 | 0.56037 | 1.0572 | 35.0262 | 2534.4887 | 1105.6868 | 1428.8019
2016-01-30 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.67% | 1099.5077 | 1398.7563 | 2498.264 | 47.8338 | 0.44335 | 0.55665 | 1.0576 | 45.2272 | 2543.4912 | 1119.5592 | 1423.932
2016-01-30 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.5% | 1122.1619 | 1373.157 | 2495.3189 | 43.2934 | 0.45248 | 0.54752 | 1.0588 | 40.8882 | 2536.2071 | 1140.6632 | 1395.5439
2016-01-30 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.72% | 1149.7187 | 1342.0179 | 2491.7366 | 23.1237 | 0.4636 | 0.5364 | 1.0603 | 21.8093 | 2513.5459 | 1159.8294 | 1353.7164
2016-01-30 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.9792 | 1337.2035 | 2491.1827 | 24.4235 | 0.46531 | 0.53469 | 1.0605 | 23.0304 | 2514.2131 | 1164.6956 | 1349.5175
2016-01-30 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.23% | 1156.0606 | 1334.8515 | 2490.9121 | 23.2672 | 0.46615 | 0.53385 | 1.0606 | 21.9378 | 2512.8499 | 1166.287 | 1346.5629
2016-01-30 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.02% | 1153.4131 | 1337.8432 | 2491.2563 | 21.6212 | 0.46509 | 0.53491 | 1.0605 | 20.3884 | 2511.6447 | 1162.8955 | 1348.7493
2016-01-30 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.88% | 1151.7685 | 1339.7016 | 2491.4701 | 21.8465 | 0.46442 | 0.53558 | 1.0604 | 20.6026 | 2512.0727 | 1161.3368 | 1350.7359
2016-01-30 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.07% | 1154.0473 | 1337.1266 | 2491.1739 | 21.9121 | 0.46534 | 0.53466 | 1.0605 | 20.6621 | 2511.836 | 1163.6623 | 1348.1737
2016-01-30 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.968 | 1337.2162 | 2491.1842 | 20.8 | 0.46531 | 0.53469 | 1.0605 | 19.6135 | 2510.7977 | 1163.0943 | 1347.7034
2016-01-30 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.42% | 1146.0378 | 1346.1772 | 2492.2151 | 36.6772 | 0.46211 | 0.53789 | 1.0601 | 34.5987 | 2526.8138 | 1162.0263 | 1364.7875
2016-01-30 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.91% | 1139.7012 | 1353.3377 | 2493.0388 | 23.8008 | 0.45956 | 0.54044 | 1.0597 | 22.459 | 2515.4979 | 1150.0224 | 1365.4755
2016-01-30 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.36% | 1132.8211 | 1361.1121 | 2493.9333 | 22.0127 | 0.45678 | 0.54322 | 1.0594 | 20.7788 | 2514.7121 | 1142.3126 | 1372.3995
2016-01-30 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.19% | 1218.6143 | 1516.7321 | 2735.3464 | 51.636 | 0.45097 | 0.54903 | 1.1127 | 46.4043 | 2781.7507 | 1239.5412 | 1542.2095
2016-01-30 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.32% | 1233.7907 | 1497.7616 | 2731.5523 | 56.2373 | 0.45658 | 0.54342 | 1.1141 | 50.4757 | 2782.028 | 1256.8371 | 1525.1909
2016-01-31 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.58% | 1223.7848 | 1510.2691 | 2734.0538 | 80.7784 | 0.45288 | 0.54712 | 1.1132 | 72.5628 | 2806.6166 | 1256.6471 | 1549.9696
2016-01-31 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.86% | 1227.5621 | 1505.5474 | 2733.1095 | 90.3034 | 0.45428 | 0.54572 | 1.1136 | 81.0936 | 2814.2031 | 1264.4012 | 1549.8019
2016-01-31 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.88% | 1227.868 | 1505.165 | 2733.033 | 90.6934 | 0.45439 | 0.54561 | 1.1136 | 81.4418 | 2814.4748 | 1264.8745 | 1549.6003
2016-01-31 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.79% | 1226.666 | 1506.6675 | 2733.3335 | 90.2426 | 0.45395 | 0.54605 | 1.1135 | 81.045 | 2814.3785 | 1263.4561 | 1550.9224
2016-01-31 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.21% | 1218.8118 | 1516.4853 | 2735.2971 | 89.7939 | 0.45104 | 0.54896 | 1.1128 | 80.6947 | 2815.9918 | 1255.2084 | 1560.7834
2016-01-31 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.3% | 1220.081 | 1514.8987 | 2734.9797 | 73.1886 | 0.45151 | 0.54849 | 1.1129 | 65.7651 | 2800.7449 | 1249.7747 | 1550.9702
2016-01-31 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 90.56% | 1223.5703 | 1510.5371 | 2734.1074 | 75.6734 | 0.4528 | 0.5472 | 1.1132 | 67.9782 | 2802.0856 | 1254.3509 | 1547.7347
2016-01-31 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 88.02% | 1189.3114 | 1553.3608 | 2742.6722 | 76.7324 | 0.44012 | 0.55988 | 1.11 | 69.1264 | 2811.7985 | 1219.7355 | 1592.063
2016-01-31 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.59% | 1098.4978 | 1399.8974 | 2498.3953 | 40.9131 | 0.44294 | 0.55706 | 1.0576 | 38.6855 | 2537.0808 | 1115.6333 | 1421.4475
2016-01-31 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.93% | 1090.2882 | 1409.1743 | 2499.4625 | 37.028 | 0.43963 | 0.56037 | 1.0572 | 35.0262 | 2534.4887 | 1105.6868 | 1428.8019
2016-01-31 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 88.67% | 1099.5077 | 1398.7563 | 2498.264 | 47.8338 | 0.44335 | 0.55665 | 1.0576 | 45.2272 | 2543.4912 | 1119.5592 | 1423.932
2016-01-31 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 90.5% | 1122.1619 | 1373.157 | 2495.3189 | 43.2934 | 0.45248 | 0.54752 | 1.0588 | 40.8882 | 2536.2071 | 1140.6632 | 1395.5439
2016-01-31 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.72% | 1149.7187 | 1342.0179 | 2491.7366 | 23.1237 | 0.4636 | 0.5364 | 1.0603 | 21.8093 | 2513.5459 | 1159.8294 | 1353.7164
2016-01-31 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.06% | 1153.9792 | 1337.2035 | 2491.1827 | 24.4235 | 0.46531 | 0.53469 | 1.0605 | 23.0304 | 2514.2131 | 1164.6956 | 1349.5175
2016-01-31 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.23% | 1259.6503 | 1465.4372 | 2725.0874 | 44.7446 | 0.46615 | 0.53385 | 1.1165 | 40.0744 | 2765.1618 | 1278.3311 | 1486.8307
2016-01-31 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.02% | 1256.7655 | 1469.0431 | 2725.8086 | 41.5791 | 0.46509 | 0.53491 | 1.1163 | 37.2482 | 2763.0568 | 1274.0892 | 1488.9677
2016-01-31 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.88% | 1254.9735 | 1471.2831 | 2726.2566 | 42.0124 | 0.46442 | 0.53558 | 1.1161 | 37.642 | 2763.8986 | 1272.4553 | 1491.4433
2016-01-31 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.07% | 1257.4566 | 1468.1793 | 2725.6359 | 42.1386 | 0.46534 | 0.53466 | 1.1163 | 37.7473 | 2763.3831 | 1275.0219 | 1488.3612
2016-01-31 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.06% | 1257.3701 | 1468.2874 | 2725.6575 | 40 | 0.46531 | 0.53469 | 1.1163 | 35.8317 | 2761.4892 | 1274.043 | 1487.4463
2016-01-31 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.42% | 1248.7294 | 1479.0882 | 2727.8176 | 70.5331 | 0.46211 | 0.53789 | 1.1155 | 63.2285 | 2791.0461 | 1277.948 | 1513.0981
2016-01-31 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.91% | 1241.825 | 1487.7188 | 2729.5438 | 45.7707 | 0.45956 | 0.54044 | 1.1149 | 41.054 | 2770.5978 | 1260.6916 | 1509.9062
2016-01-31 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.36% | 1234.3284 | 1497.0895 | 2731.4179 | 42.3321 | 0.45678 | 0.54322 | 1.1142 | 37.9934 | 2769.4113 | 1251.6832 | 1517.7282
2016-01-31 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 90.19% | 1215.6515 | 1519.6531 | 2735.3046 | 61.9632 | 0.45097 | 0.54903 | 1.1353 | 54.5792 | 2789.8837 | 1240.2649 | 1549.6188
2016-01-31 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.32% | 1230.791 | 1499.9717 | 2730.7627 | 67.4847 | 0.45658 | 0.54342 | 1.137 | 59.3546 | 2790.1173 | 1257.8913 | 1532.226
2016-02-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-01 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-01 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-01 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-01 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-01 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7278 | 1421.5903 | 2716.3181 | 47.3015 | 0.47913 | 0.52087 | 1.1198 | 42.2416 | 2758.5597 | 1314.9672 | 1443.5925
2016-02-01 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.8804 | 1296.6351 | 2486.5155 | 14.4477 | 0.47979 | 0.52021 | 1.0624 | 13.5995 | 2500.115 | 1196.4053 | 1303.7097
2016-02-01 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.95% | 1189.802 | 1296.7237 | 2486.5257 | 15.7496 | 0.47976 | 0.52024 | 1.0624 | 14.8249 | 2501.3507 | 1196.9144 | 1304.4363
2016-02-01 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-01 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-01 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.15% | 1179.8677 | 1307.9495 | 2487.8172 | 14.8738 | 0.47575 | 0.52425 | 1.0618 | 14.0074 | 2501.8246 | 1186.5318 | 1315.2928
2016-02-01 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1506 | 1296.3298 | 2486.4804 | 15.0913 | 0.4799 | 0.5201 | 1.0624 | 14.2051 | 2500.6855 | 1196.9676 | 1303.7179
2016-02-01 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.25% | 1193.527 | 1292.5145 | 2486.0415 | 14.3946 | 0.48126 | 0.51874 | 1.0626 | 13.547 | 2499.5885 | 1200.0467 | 1299.5419
2016-02-01 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.6161 | 1286.7638 | 2485.3799 | 14.5293 | 0.48331 | 0.51669 | 1.0628 | 13.6704 | 2499.0503 | 1205.2232 | 1293.8271
2016-02-01 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.5871 | 1286.7966 | 2485.3837 | 14.6315 | 0.4833 | 0.5167 | 1.0628 | 13.7666 | 2499.1503 | 1205.2405 | 1293.9098
2016-02-01 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.34% | 1194.6053 | 1291.296 | 2485.9013 | 16.4939 | 0.4817 | 0.5183 | 1.0626 | 15.5219 | 2501.4232 | 1202.0821 | 1299.3411
2016-02-01 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.37% | 1195.0312 | 1290.8147 | 2485.8459 | 14.6889 | 0.48187 | 0.51813 | 1.0626 | 13.823 | 2499.669 | 1201.6921 | 1297.9769
2016-02-01 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.9499 | 1296.5566 | 2486.5065 | 11.4437 | 0.47982 | 0.52018 | 1.0624 | 10.7718 | 2497.2783 | 1195.1184 | 1302.1598
2016-02-01 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3289 | 1291.6083 | 2485.9372 | 12.137 | 0.48158 | 0.51842 | 1.0626 | 11.422 | 2497.3592 | 1199.8295 | 1297.5297
2016-02-01 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-01 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-01 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.8456 | 1418.943 | 2715.7886 | 26.5921 | 0.47992 | 0.52008 | 1.12 | 23.7434 | 2739.532 | 1308.2405 | 1431.2915
2016-02-01 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7466 | 1417.8167 | 2715.5633 | 28.527 | 0.48025 | 0.51975 | 1.1201 | 25.4691 | 2741.0325 | 1309.9782 | 1431.0543
2016-02-01 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.1% | 1298.4669 | 1416.9164 | 2715.3833 | 26.0696 | 0.48052 | 0.51948 | 1.1201 | 23.2737 | 2738.657 | 1309.6503 | 1429.0066
2016-02-02 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.9286 | 1417.5893 | 2715.5179 | 43.746 | 0.48032 | 0.51968 | 1.1201 | 39.0562 | 2754.574 | 1316.688 | 1437.886
2016-02-02 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.09% | 1298.3371 | 1417.0787 | 2715.4157 | 47.1754 | 0.48047 | 0.51953 | 1.1201 | 42.1165 | 2757.5322 | 1318.5728 | 1438.9594
2016-02-02 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8518 | 1417.6853 | 2715.5371 | 46.5446 | 0.48029 | 0.51971 | 1.1201 | 41.555 | 2757.092 | 1317.8102 | 1439.2818
2016-02-02 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-02 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-02 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7278 | 1421.5903 | 2716.3181 | 47.3015 | 0.47913 | 0.52087 | 1.1198 | 42.2416 | 2758.5597 | 1314.9672 | 1443.5925
2016-02-02 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.8804 | 1296.6351 | 2486.5155 | 14.4477 | 0.47979 | 0.52021 | 1.0624 | 13.5995 | 2500.115 | 1196.4053 | 1303.7097
2016-02-02 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.95% | 1189.802 | 1296.7237 | 2486.5257 | 15.7496 | 0.47976 | 0.52024 | 1.0624 | 14.8249 | 2501.3507 | 1196.9144 | 1304.4363
2016-02-02 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-02 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-02 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.15% | 1179.8677 | 1307.9495 | 2487.8172 | 14.8738 | 0.47575 | 0.52425 | 1.0618 | 14.0074 | 2501.8246 | 1186.5318 | 1315.2928
2016-02-02 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1506 | 1296.3298 | 2486.4804 | 15.0913 | 0.4799 | 0.5201 | 1.0624 | 14.2051 | 2500.6855 | 1196.9676 | 1303.7179
2016-02-02 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.25% | 1193.527 | 1292.5145 | 2486.0415 | 14.3946 | 0.48126 | 0.51874 | 1.0626 | 13.547 | 2499.5885 | 1200.0467 | 1299.5419
2016-02-02 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-02 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-02 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-02 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-02 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-02 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-02 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-02 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.43% | 1302.8592 | 1411.426 | 2714.2852 | 23.384 | 0.48214 | 0.51786 | 1.1205 | 20.8686 | 2735.1538 | 1312.9209 | 1422.2329
2016-02-02 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.8456 | 1418.943 | 2715.7886 | 26.5921 | 0.47992 | 0.52008 | 1.12 | 23.7434 | 2739.532 | 1308.2405 | 1431.2915
2016-02-02 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-03 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-03 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-03 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-03 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-03 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-03 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-03 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-03 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.7% | 1289.8973 | 1423.1335 | 2713.0308 | 35.9304 | 0.47851 | 0.52149 | 1.1436 | 31.42 | 2744.4508 | 1304.9321 | 1439.5187
2016-02-03 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2019 | 1424.0375 | 2713.2394 | 38.6527 | 0.47825 | 0.52175 | 1.1435 | 33.8028 | 2747.0423 | 1305.3682 | 1441.6741
2016-02-03 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.15% | 1336.0733 | 1499.4973 | 2835.5707 | 45.7654 | 0.47575 | 0.52425 | 1.1903 | 38.4486 | 2874.0193 | 1354.3654 | 1519.6539
2016-02-03 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7176 | 1483.1954 | 2830.913 | 46.4349 | 0.4799 | 0.5201 | 1.192 | 38.9567 | 2869.8697 | 1366.4129 | 1503.4568
2016-02-03 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.25% | 1351.541 | 1477.8426 | 2829.3836 | 44.2911 | 0.48126 | 0.51874 | 1.1925 | 37.1412 | 2866.5248 | 1369.4156 | 1497.1092
2016-02-03 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.3039 | 1469.7746 | 2827.0785 | 44.7055 | 0.48331 | 0.51669 | 1.1933 | 37.4629 | 2864.5414 | 1375.4102 | 1489.1312
2016-02-03 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9038 | 1575.1444 | 3025.0481 | 56.2752 | 0.4833 | 0.5167 | 1.2417 | 45.3229 | 3070.371 | 1471.8084 | 1598.5626
2016-02-03 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.34% | 1445.087 | 1582.3694 | 3027.4565 | 63.438 | 0.4817 | 0.5183 | 1.2408 | 51.1247 | 3078.5812 | 1469.7136 | 1608.8676
2016-02-03 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.37% | 1445.6023 | 1581.5965 | 3027.1988 | 56.496 | 0.48187 | 0.51813 | 1.2409 | 45.527 | 3072.7258 | 1467.5403 | 1605.1855
2016-02-03 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.96% | 1439.4556 | 1590.8166 | 3030.2722 | 44.0142 | 0.47982 | 0.52018 | 1.2399 | 35.4979 | 3065.7701 | 1456.4881 | 1609.282
2016-02-03 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.32% | 1444.7527 | 1582.8709 | 3027.6236 | 46.6809 | 0.48158 | 0.51842 | 1.2408 | 37.6219 | 3065.2455 | 1462.8708 | 1602.3747
2016-02-03 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.47% | 1354.5602 | 1473.6157 | 2828.1759 | 37.5749 | 0.48234 | 0.51766 | 1.1929 | 31.4979 | 2859.6738 | 1369.7528 | 1489.921
2016-02-03 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.43% | 1354.02 | 1474.372 | 2828.392 | 37.4144 | 0.48214 | 0.51786 | 1.1929 | 31.3653 | 2859.7573 | 1369.1426 | 1490.6147
2016-02-03 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-03 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7066 | 1481.8107 | 2830.5173 | 45.6433 | 0.48025 | 0.51975 | 1.1921 | 38.2881 | 2868.8054 | 1367.0946 | 1501.7109
2016-02-03 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.1% | 1349.4552 | 1480.7627 | 2830.2179 | 41.7113 | 0.48052 | 0.51948 | 1.1922 | 34.9866 | 2865.2045 | 1366.2669 | 1498.9376
2016-02-04 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-04 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-04 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-04 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-04 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-04 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-04 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-04 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-04 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-04 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-04 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-04 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-04 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-04 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-04 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-04 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-04 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-04 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-04 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-04 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-04 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.43% | 1302.8592 | 1411.426 | 2714.2852 | 23.384 | 0.48214 | 0.51786 | 1.1205 | 20.8686 | 2735.1538 | 1312.9209 | 1422.2329
2016-02-04 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-04 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-04 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.1% | 1349.4552 | 1480.7627 | 2830.2179 | 41.7113 | 0.48052 | 0.51948 | 1.1922 | 34.9866 | 2865.2045 | 1366.2669 | 1498.9376
2016-02-05 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8958 | 1481.5459 | 2830.4417 | 69.9936 | 0.48032 | 0.51968 | 1.1921 | 58.7132 | 2889.1549 | 1377.0968 | 1512.0581
2016-02-05 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.09% | 1349.3203 | 1480.9516 | 2830.2719 | 75.4806 | 0.48047 | 0.51953 | 1.1922 | 63.3127 | 2893.5845 | 1379.7401 | 1513.8444
2016-02-05 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8159 | 1481.6577 | 2830.4736 | 74.4713 | 0.48029 | 0.51971 | 1.1921 | 62.4699 | 2892.9435 | 1378.8196 | 1514.1239
2016-02-05 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.8% | 1345.1602 | 1486.7758 | 2831.9359 | 74.6255 | 0.47899 | 0.52101 | 1.1916 | 62.6266 | 2894.5625 | 1375.1576 | 1519.4049
2016-02-05 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-05 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-05 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4116 | 1483.6237 | 2831.0353 | 44.4546 | 0.47979 | 0.52021 | 1.1919 | 37.2967 | 2868.3321 | 1365.3063 | 1503.0258
2016-02-05 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.95% | 1347.3228 | 1483.748 | 2831.0709 | 48.4602 | 0.47976 | 0.52024 | 1.1919 | 40.6578 | 2871.7287 | 1366.8288 | 1504.8999
2016-02-05 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.7% | 1343.8164 | 1488.657 | 2832.4734 | 47.9072 | 0.47851 | 0.52149 | 1.1914 | 40.2107 | 2872.6842 | 1363.0577 | 1509.6265
2016-02-05 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.65% | 1343.0919 | 1489.6713 | 2832.7632 | 51.537 | 0.47825 | 0.52175 | 1.1913 | 43.2611 | 2876.0243 | 1363.7817 | 1512.2427
2016-02-05 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.15% | 1336.0733 | 1499.4973 | 2835.5707 | 45.7654 | 0.47575 | 0.52425 | 1.1903 | 38.4486 | 2874.0193 | 1354.3654 | 1519.6539
2016-02-05 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-05 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-05 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-05 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-05 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.34% | 1298.484 | 1411.9708 | 2710.4548 | 38.0628 | 0.4817 | 0.5183 | 1.1445 | 33.2569 | 2743.7117 | 1314.5037 | 1429.208
2016-02-05 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.37% | 1298.947 | 1411.3689 | 2710.3159 | 33.8976 | 0.48187 | 0.51813 | 1.1446 | 29.6162 | 2739.9321 | 1313.2181 | 1426.714
2016-02-05 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.4238 | 1418.549 | 2711.9728 | 26.4085 | 0.47982 | 0.52018 | 1.1439 | 23.0854 | 2735.0583 | 1304.5007 | 1430.5576
2016-02-05 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.1836 | 1412.3613 | 2710.5449 | 28.0085 | 0.48158 | 0.51842 | 1.1445 | 24.4728 | 2735.0177 | 1309.9693 | 1425.0484
2016-02-05 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-05 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-05 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-05 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-05 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-06 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-06 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-06 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-06 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-06 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-06 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-06 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-06 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-06 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-06 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-06 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.15% | 1179.8677 | 1307.9495 | 2487.8172 | 14.8738 | 0.47575 | 0.52425 | 1.0618 | 14.0074 | 2501.8246 | 1186.5318 | 1315.2928
2016-02-06 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-06 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-06 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-06 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-06 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-06 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-06 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-06 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-06 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-06 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-06 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-06 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7066 | 1481.8107 | 2830.5173 | 45.6433 | 0.48025 | 0.51975 | 1.1921 | 38.2881 | 2868.8054 | 1367.0946 | 1501.7109
2016-02-06 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.1% | 1349.4552 | 1480.7627 | 2830.2179 | 41.7113 | 0.48052 | 0.51948 | 1.1922 | 34.9866 | 2865.2045 | 1366.2669 | 1498.9376
2016-02-07 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8958 | 1481.5459 | 2830.4417 | 69.9936 | 0.48032 | 0.51968 | 1.1921 | 58.7132 | 2889.1549 | 1377.0968 | 1512.0581
2016-02-07 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.09% | 1349.3203 | 1480.9516 | 2830.2719 | 75.4806 | 0.48047 | 0.51953 | 1.1922 | 63.3127 | 2893.5845 | 1379.7401 | 1513.8444
2016-02-07 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8159 | 1481.6577 | 2830.4736 | 74.4713 | 0.48029 | 0.51971 | 1.1921 | 62.4699 | 2892.9435 | 1378.8196 | 1514.1239
2016-02-07 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.8% | 1345.1602 | 1486.7758 | 2831.9359 | 74.6255 | 0.47899 | 0.52101 | 1.1916 | 62.6266 | 2894.5625 | 1375.1576 | 1519.4049
2016-02-07 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-07 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-07 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-07 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-07 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.7% | 1289.8973 | 1423.1335 | 2713.0308 | 35.9304 | 0.47851 | 0.52149 | 1.1436 | 31.42 | 2744.4508 | 1304.9321 | 1439.5187
2016-02-07 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2019 | 1424.0375 | 2713.2394 | 38.6527 | 0.47825 | 0.52175 | 1.1435 | 33.8028 | 2747.0423 | 1305.3682 | 1441.6741
2016-02-07 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.15% | 1282.4649 | 1432.7956 | 2715.2605 | 34.3241 | 0.47575 | 0.52425 | 1.1427 | 30.037 | 2745.2975 | 1296.7551 | 1448.5424
2016-02-07 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-07 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-07 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-07 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.271 | 1469.8206 | 2827.0916 | 45.0201 | 0.4833 | 0.5167 | 1.1933 | 37.7268 | 2864.8184 | 1375.5044 | 1489.3139
2016-02-07 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.34% | 1352.762 | 1476.1332 | 2828.8952 | 50.7504 | 0.4817 | 0.5183 | 1.1927 | 42.5516 | 2871.4468 | 1373.259 | 1498.1878
2016-02-07 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.37% | 1353.2444 | 1475.4579 | 2828.7022 | 45.1968 | 0.48187 | 0.51813 | 1.1927 | 37.893 | 2866.5952 | 1371.5038 | 1495.0914
2016-02-07 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4904 | 1483.5135 | 2831.0039 | 35.2113 | 0.47982 | 0.52018 | 1.1919 | 29.5415 | 2860.5454 | 1361.6649 | 1498.8804
2016-02-07 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.32% | 1352.4491 | 1476.5713 | 2829.0204 | 37.3447 | 0.48158 | 0.51842 | 1.1926 | 31.3128 | 2860.3332 | 1367.5288 | 1492.8044
2016-02-07 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.47% | 1354.5602 | 1473.6157 | 2828.1759 | 37.5749 | 0.48234 | 0.51766 | 1.1929 | 31.4979 | 2859.6738 | 1369.7528 | 1489.921
2016-02-07 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.43% | 1354.02 | 1474.372 | 2828.392 | 37.4144 | 0.48214 | 0.51786 | 1.1929 | 31.3653 | 2859.7573 | 1369.1426 | 1490.6147
2016-02-07 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-07 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7066 | 1481.8107 | 2830.5173 | 45.6433 | 0.48025 | 0.51975 | 1.1921 | 38.2881 | 2868.8054 | 1367.0946 | 1501.7109
2016-02-07 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-08 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-08 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-08 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-08 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-08 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.61% | 1434.2202 | 1598.6697 | 3032.8899 | 92.4421 | 0.47807 | 0.52193 | 1.239 | 74.6081 | 3107.498 | 1469.8883 | 1637.6096
2016-02-08 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-08 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4116 | 1483.6237 | 2831.0353 | 44.4546 | 0.47979 | 0.52021 | 1.1919 | 37.2967 | 2868.3321 | 1365.3063 | 1503.0258
2016-02-08 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-08 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.7% | 1289.8973 | 1423.1335 | 2713.0308 | 35.9304 | 0.47851 | 0.52149 | 1.1436 | 31.42 | 2744.4508 | 1304.9321 | 1439.5187
2016-02-08 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2019 | 1424.0375 | 2713.2394 | 38.6527 | 0.47825 | 0.52175 | 1.1435 | 33.8028 | 2747.0423 | 1305.3682 | 1441.6741
2016-02-08 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.15% | 1282.4649 | 1432.7956 | 2715.2605 | 34.3241 | 0.47575 | 0.52425 | 1.1427 | 30.037 | 2745.2975 | 1296.7551 | 1448.5424
2016-02-08 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-08 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-08 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-08 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-08 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.34% | 1298.484 | 1411.9708 | 2710.4548 | 38.0628 | 0.4817 | 0.5183 | 1.1445 | 33.2569 | 2743.7117 | 1314.5037 | 1429.208
2016-02-08 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.37% | 1298.947 | 1411.3689 | 2710.3159 | 33.8976 | 0.48187 | 0.51813 | 1.1446 | 29.6162 | 2739.9321 | 1313.2181 | 1426.714
2016-02-08 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.4238 | 1418.549 | 2711.9728 | 26.4085 | 0.47982 | 0.52018 | 1.1439 | 23.0854 | 2735.0583 | 1304.5007 | 1430.5576
2016-02-08 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.1836 | 1412.3613 | 2710.5449 | 28.0085 | 0.48158 | 0.51842 | 1.1445 | 24.4728 | 2735.0177 | 1309.9693 | 1425.0484
2016-02-08 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-08 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-08 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-08 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-08 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-09 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-09 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-09 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-09 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-09 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-09 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-09 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.8804 | 1296.6351 | 2486.5155 | 14.4477 | 0.47979 | 0.52021 | 1.0624 | 13.5995 | 2500.115 | 1196.4053 | 1303.7097
2016-02-09 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.95% | 1189.802 | 1296.7237 | 2486.5257 | 15.7496 | 0.47976 | 0.52024 | 1.0624 | 14.8249 | 2501.3507 | 1196.9144 | 1304.4363
2016-02-09 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-09 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-09 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.15% | 1179.8677 | 1307.9495 | 2487.8172 | 14.8738 | 0.47575 | 0.52425 | 1.0618 | 14.0074 | 2501.8246 | 1186.5318 | 1315.2928
2016-02-09 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1506 | 1296.3298 | 2486.4804 | 15.0913 | 0.4799 | 0.5201 | 1.0624 | 14.2051 | 2500.6855 | 1196.9676 | 1303.7179
2016-02-09 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.25% | 1193.527 | 1292.5145 | 2486.0415 | 14.3946 | 0.48126 | 0.51874 | 1.0626 | 13.547 | 2499.5885 | 1200.0467 | 1299.5419
2016-02-09 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.6161 | 1286.7638 | 2485.3799 | 14.5293 | 0.48331 | 0.51669 | 1.0628 | 13.6704 | 2499.0503 | 1205.2232 | 1293.8271
2016-02-09 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.5871 | 1286.7966 | 2485.3837 | 14.6315 | 0.4833 | 0.5167 | 1.0628 | 13.7666 | 2499.1503 | 1205.2405 | 1293.9098
2016-02-09 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.34% | 1194.6053 | 1291.296 | 2485.9013 | 16.4939 | 0.4817 | 0.5183 | 1.0626 | 15.5219 | 2501.4232 | 1202.0821 | 1299.3411
2016-02-09 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.37% | 1195.0312 | 1290.8147 | 2485.8459 | 14.6889 | 0.48187 | 0.51813 | 1.0626 | 13.823 | 2499.669 | 1201.6921 | 1297.9769
2016-02-09 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.9499 | 1296.5566 | 2486.5065 | 11.4437 | 0.47982 | 0.52018 | 1.0624 | 10.7718 | 2497.2783 | 1195.1184 | 1302.1598
2016-02-09 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3289 | 1291.6083 | 2485.9372 | 12.137 | 0.48158 | 0.51842 | 1.0626 | 11.422 | 2497.3592 | 1199.8295 | 1297.5297
2016-02-09 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-09 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-09 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.8456 | 1418.943 | 2715.7886 | 26.5921 | 0.47992 | 0.52008 | 1.12 | 23.7434 | 2739.532 | 1308.2405 | 1431.2915
2016-02-09 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7466 | 1417.8167 | 2715.5633 | 28.527 | 0.48025 | 0.51975 | 1.1201 | 25.4691 | 2741.0325 | 1309.9782 | 1431.0543
2016-02-09 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-10 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-10 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-10 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-10 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-10 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-10 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-10 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-10 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-10 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-10 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-10 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.15% | 1282.4649 | 1432.7956 | 2715.2605 | 34.3241 | 0.47575 | 0.52425 | 1.1427 | 30.037 | 2745.2975 | 1296.7551 | 1448.5424
2016-02-10 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-10 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-10 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-10 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-10 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-10 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-10 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-10 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-10 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-10 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-10 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-10 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-10 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-11 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-11 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-11 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-11 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-11 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-11 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-11 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-11 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.95% | 1189.802 | 1296.7237 | 2486.5257 | 15.7496 | 0.47976 | 0.52024 | 1.0624 | 14.8249 | 2501.3507 | 1196.9144 | 1304.4363
2016-02-11 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-11 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-11 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-11 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-11 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-11 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.6161 | 1286.7638 | 2485.3799 | 14.5293 | 0.48331 | 0.51669 | 1.0628 | 13.6704 | 2499.0503 | 1205.2232 | 1293.8271
2016-02-11 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.66% | 1198.5871 | 1286.7966 | 2485.3837 | 14.6315 | 0.4833 | 0.5167 | 1.0628 | 13.7666 | 2499.1503 | 1205.2405 | 1293.9098
2016-02-11 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.34% | 1194.6053 | 1291.296 | 2485.9013 | 16.4939 | 0.4817 | 0.5183 | 1.0626 | 15.5219 | 2501.4232 | 1202.0821 | 1299.3411
2016-02-11 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.37% | 1195.0312 | 1290.8147 | 2485.8459 | 14.6889 | 0.48187 | 0.51813 | 1.0626 | 13.823 | 2499.669 | 1201.6921 | 1297.9769
2016-02-11 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.96% | 1189.9499 | 1296.5566 | 2486.5065 | 11.4437 | 0.47982 | 0.52018 | 1.0624 | 10.7718 | 2497.2783 | 1195.1184 | 1302.1598
2016-02-11 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3289 | 1291.6083 | 2485.9372 | 12.137 | 0.48158 | 0.51842 | 1.0626 | 11.422 | 2497.3592 | 1199.8295 | 1297.5297
2016-02-11 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-11 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-11 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1971 | 1296.2773 | 2486.4744 | 13.8279 | 0.47992 | 0.52008 | 1.0624 | 13.0158 | 2499.4902 | 1196.4436 | 1303.0466
2016-02-11 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7466 | 1417.8167 | 2715.5633 | 28.527 | 0.48025 | 0.51975 | 1.1201 | 25.4691 | 2741.0325 | 1309.9782 | 1431.0543
2016-02-11 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.1% | 1298.4669 | 1416.9164 | 2715.3833 | 26.0696 | 0.48052 | 0.51948 | 1.1201 | 23.2737 | 2738.657 | 1309.6503 | 1429.0066
2016-02-12 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.9286 | 1417.5893 | 2715.5179 | 43.746 | 0.48032 | 0.51968 | 1.1201 | 39.0562 | 2754.574 | 1316.688 | 1437.886
2016-02-12 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.09% | 1298.3371 | 1417.0787 | 2715.4157 | 47.1754 | 0.48047 | 0.51953 | 1.1201 | 42.1165 | 2757.5322 | 1318.5728 | 1438.9594
2016-02-12 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8518 | 1417.6853 | 2715.5371 | 46.5446 | 0.48029 | 0.51971 | 1.1201 | 41.555 | 2757.092 | 1317.8102 | 1439.2818
2016-02-12 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.8% | 1294.3341 | 1422.0823 | 2716.4165 | 46.641 | 0.47899 | 0.52101 | 1.1197 | 41.6531 | 2758.0696 | 1314.2855 | 1443.7841
2016-02-12 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.61% | 1291.8606 | 1425.1743 | 2717.0349 | 46.2211 | 0.47807 | 0.52193 | 1.1195 | 41.2866 | 2758.3214 | 1311.5986 | 1446.7229
2016-02-12 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7278 | 1421.5903 | 2716.3181 | 47.3015 | 0.47913 | 0.52087 | 1.1198 | 42.2416 | 2758.5597 | 1314.9672 | 1443.5925
2016-02-12 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-12 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-12 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-12 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-12 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-12 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-12 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-12 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-12 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-12 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-12 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-12 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-12 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-12 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-12 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.43% | 1302.8592 | 1411.426 | 2714.2852 | 23.384 | 0.48214 | 0.51786 | 1.1205 | 20.8686 | 2735.1538 | 1312.9209 | 1422.2329
2016-02-12 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-12 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7066 | 1481.8107 | 2830.5173 | 45.6433 | 0.48025 | 0.51975 | 1.1921 | 38.2881 | 2868.8054 | 1367.0946 | 1501.7109
2016-02-12 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.1% | 1349.4552 | 1480.7627 | 2830.2179 | 41.7113 | 0.48052 | 0.51948 | 1.1922 | 34.9866 | 2865.2045 | 1366.2669 | 1498.9376
2016-02-13 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8958 | 1481.5459 | 2830.4417 | 69.9936 | 0.48032 | 0.51968 | 1.1921 | 58.7132 | 2889.1549 | 1377.0968 | 1512.0581
2016-02-13 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.09% | 1349.3203 | 1480.9516 | 2830.2719 | 75.4806 | 0.48047 | 0.51953 | 1.1922 | 63.3127 | 2893.5845 | 1379.7401 | 1513.8444
2016-02-13 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8159 | 1481.6577 | 2830.4736 | 74.4713 | 0.48029 | 0.51971 | 1.1921 | 62.4699 | 2892.9435 | 1378.8196 | 1514.1239
2016-02-13 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.8% | 1345.1602 | 1486.7758 | 2831.9359 | 74.6255 | 0.47899 | 0.52101 | 1.1916 | 62.6266 | 2894.5625 | 1375.1576 | 1519.4049
2016-02-13 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-13 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-13 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-13 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-13 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-13 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-13 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-13 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-13 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-13 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-13 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-13 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-13 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-13 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-13 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-13 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.47% | 1303.379 | 1410.7762 | 2714.1552 | 23.4843 | 0.48234 | 0.51766 | 1.1206 | 20.9572 | 2735.1124 | 1313.4874 | 1421.625
2016-02-13 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.43% | 1302.8592 | 1411.426 | 2714.2852 | 23.384 | 0.48214 | 0.51786 | 1.1205 | 20.8686 | 2735.1538 | 1312.9209 | 1422.2329
2016-02-13 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.8456 | 1418.943 | 2715.7886 | 26.5921 | 0.47992 | 0.52008 | 1.12 | 23.7434 | 2739.532 | 1308.2405 | 1431.2915
2016-02-13 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7466 | 1417.8167 | 2715.5633 | 28.527 | 0.48025 | 0.51975 | 1.1201 | 25.4691 | 2741.0325 | 1309.9782 | 1431.0543
2016-02-13 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-14 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-14 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-14 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-14 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-14 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-14 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-14 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-14 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-14 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.7% | 1289.8973 | 1423.1335 | 2713.0308 | 35.9304 | 0.47851 | 0.52149 | 1.1436 | 31.42 | 2744.4508 | 1304.9321 | 1439.5187
2016-02-14 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2019 | 1424.0375 | 2713.2394 | 38.6527 | 0.47825 | 0.52175 | 1.1435 | 33.8028 | 2747.0423 | 1305.3682 | 1441.6741
2016-02-14 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.15% | 1282.4649 | 1432.7956 | 2715.2605 | 34.3241 | 0.47575 | 0.52425 | 1.1427 | 30.037 | 2745.2975 | 1296.7551 | 1448.5424
2016-02-14 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7176 | 1483.1954 | 2830.913 | 46.4349 | 0.4799 | 0.5201 | 1.192 | 38.9567 | 2869.8697 | 1366.4129 | 1503.4568
2016-02-14 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.25% | 1351.541 | 1477.8426 | 2829.3836 | 44.2911 | 0.48126 | 0.51874 | 1.1925 | 37.1412 | 2866.5248 | 1369.4156 | 1497.1092
2016-02-14 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.3039 | 1469.7746 | 2827.0785 | 44.7055 | 0.48331 | 0.51669 | 1.1933 | 37.4629 | 2864.5414 | 1375.4102 | 1489.1312
2016-02-14 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.271 | 1469.8206 | 2827.0916 | 45.0201 | 0.4833 | 0.5167 | 1.1933 | 37.7268 | 2864.8184 | 1375.5044 | 1489.3139
2016-02-14 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.34% | 1352.762 | 1476.1332 | 2828.8952 | 50.7504 | 0.4817 | 0.5183 | 1.1927 | 42.5516 | 2871.4468 | 1373.259 | 1498.1878
2016-02-14 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.37% | 1353.2444 | 1475.4579 | 2828.7022 | 45.1968 | 0.48187 | 0.51813 | 1.1927 | 37.893 | 2866.5952 | 1371.5038 | 1495.0914
2016-02-14 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4904 | 1483.5135 | 2831.0039 | 35.2113 | 0.47982 | 0.52018 | 1.1919 | 29.5415 | 2860.5454 | 1361.6649 | 1498.8804
2016-02-14 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.32% | 1352.4491 | 1476.5713 | 2829.0204 | 37.3447 | 0.48158 | 0.51842 | 1.1926 | 31.3128 | 2860.3332 | 1367.5288 | 1492.8044
2016-02-14 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-14 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.43% | 1302.8592 | 1411.426 | 2714.2852 | 23.384 | 0.48214 | 0.51786 | 1.1205 | 20.8686 | 2735.1538 | 1312.9209 | 1422.2329
2016-02-14 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.8456 | 1418.943 | 2715.7886 | 26.5921 | 0.47992 | 0.52008 | 1.12 | 23.7434 | 2739.532 | 1308.2405 | 1431.2915
2016-02-14 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7466 | 1417.8167 | 2715.5633 | 28.527 | 0.48025 | 0.51975 | 1.1201 | 25.4691 | 2741.0325 | 1309.9782 | 1431.0543
2016-02-14 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.1% | 1298.4669 | 1416.9164 | 2715.3833 | 26.0696 | 0.48052 | 0.51948 | 1.1201 | 23.2737 | 2738.657 | 1309.6503 | 1429.0066
2016-02-15 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.9286 | 1417.5893 | 2715.5179 | 43.746 | 0.48032 | 0.51968 | 1.1201 | 39.0562 | 2754.574 | 1316.688 | 1437.886
2016-02-15 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.09% | 1298.3371 | 1417.0787 | 2715.4157 | 47.1754 | 0.48047 | 0.51953 | 1.1201 | 42.1165 | 2757.5322 | 1318.5728 | 1438.9594
2016-02-15 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8518 | 1417.6853 | 2715.5371 | 46.5446 | 0.48029 | 0.51971 | 1.1201 | 41.555 | 2757.092 | 1317.8102 | 1439.2818
2016-02-15 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.8% | 1294.3341 | 1422.0823 | 2716.4165 | 46.641 | 0.47899 | 0.52101 | 1.1197 | 41.6531 | 2758.0696 | 1314.2855 | 1443.7841
2016-02-15 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.61% | 1291.8606 | 1425.1743 | 2717.0349 | 46.2211 | 0.47807 | 0.52193 | 1.1195 | 41.2866 | 2758.3214 | 1311.5986 | 1446.7229
2016-02-15 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7278 | 1421.5903 | 2716.3181 | 47.3015 | 0.47913 | 0.52087 | 1.1198 | 42.2416 | 2758.5597 | 1314.9672 | 1443.5925
2016-02-15 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-15 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-15 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-15 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2019 | 1424.0375 | 2713.2394 | 38.6527 | 0.47825 | 0.52175 | 1.1435 | 33.8028 | 2747.0423 | 1305.3682 | 1441.6741
2016-02-15 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-15 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-15 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-15 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-15 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-15 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.34% | 1298.484 | 1411.9708 | 2710.4548 | 38.0628 | 0.4817 | 0.5183 | 1.1445 | 33.2569 | 2743.7117 | 1314.5037 | 1429.208
2016-02-15 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.37% | 1298.947 | 1411.3689 | 2710.3159 | 33.8976 | 0.48187 | 0.51813 | 1.1446 | 29.6162 | 2739.9321 | 1313.2181 | 1426.714
2016-02-15 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.4238 | 1418.549 | 2711.9728 | 26.4085 | 0.47982 | 0.52018 | 1.1439 | 23.0854 | 2735.0583 | 1304.5007 | 1430.5576
2016-02-15 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-15 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-15 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-15 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1971 | 1296.2773 | 2486.4744 | 13.8279 | 0.47992 | 0.52008 | 1.0624 | 13.0158 | 2499.4902 | 1196.4436 | 1303.0466
2016-02-15 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.05% | 1191.024 | 1295.3428 | 2486.3669 | 14.8341 | 0.48025 | 0.51975 | 1.0624 | 13.9624 | 2500.3292 | 1197.7295 | 1302.5998
2016-02-15 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.1% | 1191.6851 | 1294.5959 | 2486.2809 | 13.5562 | 0.48052 | 0.51948 | 1.0625 | 12.7591 | 2499.0401 | 1197.8161 | 1301.224
2016-02-16 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.06% | 1191.191 | 1295.1541 | 2486.3452 | 22.7479 | 0.48032 | 0.51968 | 1.0624 | 21.411 | 2507.7562 | 1201.4752 | 1306.281
2016-02-16 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.09% | 1191.5659 | 1294.7305 | 2486.2964 | 24.5312 | 0.48047 | 0.51953 | 1.0625 | 23.089 | 2509.3855 | 1202.6595 | 1306.7259
2016-02-16 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.06% | 1191.1206 | 1295.2338 | 2486.3543 | 24.2032 | 0.48029 | 0.51971 | 1.0624 | 22.7808 | 2509.1351 | 1202.062 | 1307.0732
2016-02-16 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.8% | 1187.8922 | 1298.8818 | 2486.774 | 24.2533 | 0.47899 | 0.52101 | 1.0623 | 22.8316 | 2509.6056 | 1198.8283 | 1310.7774
2016-02-16 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.61% | 1185.622 | 1301.4471 | 2487.0691 | 24.035 | 0.47807 | 0.52193 | 1.0621 | 22.6286 | 2509.6977 | 1196.4402 | 1313.2576
2016-02-16 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2535 | 1298.4736 | 2486.7271 | 24.5968 | 0.47913 | 0.52087 | 1.0623 | 23.1545 | 2509.8816 | 1199.3476 | 1310.534
2016-02-16 06:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.96% | 1217.9297 | 1324.6359 | 2542.5656 | 8.8909 | 0.47979 | 0.52021 | 1.0384 | 8.5623 | 2551.1279 | 1222.0378 | 1329.0901
2016-02-16 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.95% | 1217.8494 | 1324.7226 | 2542.572 | 9.692 | 0.47976 | 0.52024 | 1.0384 | 9.3338 | 2551.9058 | 1222.3274 | 1329.5784
2016-02-16 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.7% | 1214.68 | 1328.1456 | 2542.8256 | 9.5814 | 0.47851 | 0.52149 | 1.0383 | 9.2282 | 2552.0538 | 1219.0958 | 1332.958
2016-02-16 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-16 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.15% | 1179.8677 | 1307.9495 | 2487.8172 | 14.8738 | 0.47575 | 0.52425 | 1.0618 | 14.0074 | 2501.8246 | 1186.5318 | 1315.2928
2016-02-16 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1506 | 1296.3298 | 2486.4804 | 15.0913 | 0.4799 | 0.5201 | 1.0624 | 14.2051 | 2500.6855 | 1196.9676 | 1303.7179
2016-02-16 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-16 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-16 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-16 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-16 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-16 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-16 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-16 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-16 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-16 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1971 | 1296.2773 | 2486.4744 | 13.8279 | 0.47992 | 0.52008 | 1.0624 | 13.0158 | 2499.4902 | 1196.4436 | 1303.0466
2016-02-16 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.05% | 1191.024 | 1295.3428 | 2486.3669 | 14.8341 | 0.48025 | 0.51975 | 1.0624 | 13.9624 | 2500.3292 | 1197.7295 | 1302.5998
2016-02-16 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.1% | 1298.4669 | 1416.9164 | 2715.3833 | 26.0696 | 0.48052 | 0.51948 | 1.1201 | 23.2737 | 2738.657 | 1309.6503 | 1429.0066
2016-02-17 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.9286 | 1417.5893 | 2715.5179 | 43.746 | 0.48032 | 0.51968 | 1.1201 | 39.0562 | 2754.574 | 1316.688 | 1437.886
2016-02-17 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.09% | 1298.3371 | 1417.0787 | 2715.4157 | 47.1754 | 0.48047 | 0.51953 | 1.1201 | 42.1165 | 2757.5322 | 1318.5728 | 1438.9594
2016-02-17 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8518 | 1417.6853 | 2715.5371 | 46.5446 | 0.48029 | 0.51971 | 1.1201 | 41.555 | 2757.092 | 1317.8102 | 1439.2818
2016-02-17 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.8% | 1294.3341 | 1422.0823 | 2716.4165 | 46.641 | 0.47899 | 0.52101 | 1.1197 | 41.6531 | 2758.0696 | 1314.2855 | 1443.7841
2016-02-17 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.61% | 1185.622 | 1301.4471 | 2487.0691 | 24.035 | 0.47807 | 0.52193 | 1.0621 | 22.6286 | 2509.6977 | 1196.4402 | 1313.2576
2016-02-17 05:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.83% | 1216.2644 | 1326.4345 | 2542.6988 | 15.1365 | 0.47913 | 0.52087 | 1.0383 | 14.5777 | 2557.2765 | 1223.2491 | 1334.0275
2016-02-17 06:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.96% | 1217.9297 | 1324.6359 | 2542.5656 | 8.8909 | 0.47979 | 0.52021 | 1.0384 | 8.5623 | 2551.1279 | 1222.0378 | 1329.0901
2016-02-17 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.95% | 1217.8494 | 1324.7226 | 2542.572 | 9.692 | 0.47976 | 0.52024 | 1.0384 | 9.3338 | 2551.9058 | 1222.3274 | 1329.5784
2016-02-17 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-17 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-17 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-17 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-17 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-17 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-17 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-17 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.34% | 1298.484 | 1411.9708 | 2710.4548 | 38.0628 | 0.4817 | 0.5183 | 1.1445 | 33.2569 | 2743.7117 | 1314.5037 | 1429.208
2016-02-17 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.37% | 1298.947 | 1411.3689 | 2710.3159 | 33.8976 | 0.48187 | 0.51813 | 1.1446 | 29.6162 | 2739.9321 | 1313.2181 | 1426.714
2016-02-17 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.4238 | 1418.549 | 2711.9728 | 26.4085 | 0.47982 | 0.52018 | 1.1439 | 23.0854 | 2735.0583 | 1304.5007 | 1430.5576
2016-02-17 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.1836 | 1412.3613 | 2710.5449 | 28.0085 | 0.48158 | 0.51842 | 1.1445 | 24.4728 | 2735.0177 | 1309.9693 | 1425.0484
2016-02-17 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-17 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-17 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-17 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7066 | 1481.8107 | 2830.5173 | 45.6433 | 0.48025 | 0.51975 | 1.1921 | 38.2881 | 2868.8054 | 1367.0946 | 1501.7109
2016-02-17 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.1% | 1349.4552 | 1480.7627 | 2830.2179 | 41.7113 | 0.48052 | 0.51948 | 1.1922 | 34.9866 | 2865.2045 | 1366.2669 | 1498.9376
2016-02-18 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8958 | 1481.5459 | 2830.4417 | 69.9936 | 0.48032 | 0.51968 | 1.1921 | 58.7132 | 2889.1549 | 1377.0968 | 1512.0581
2016-02-18 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.09% | 1349.3203 | 1480.9516 | 2830.2719 | 75.4806 | 0.48047 | 0.51953 | 1.1922 | 63.3127 | 2893.5845 | 1379.7401 | 1513.8444
2016-02-18 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8159 | 1481.6577 | 2830.4736 | 74.4713 | 0.48029 | 0.51971 | 1.1921 | 62.4699 | 2892.9435 | 1378.8196 | 1514.1239
2016-02-18 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.8% | 1345.1602 | 1486.7758 | 2831.9359 | 74.6255 | 0.47899 | 0.52101 | 1.1916 | 62.6266 | 2894.5625 | 1375.1576 | 1519.4049
2016-02-18 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-18 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-18 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.3483 | 1418.6472 | 2711.9955 | 33.3409 | 0.47979 | 0.52021 | 1.1439 | 29.1458 | 2741.1413 | 1307.3322 | 1433.8091
2016-02-18 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.95% | 1293.263 | 1418.758 | 2712.0211 | 36.3451 | 0.47976 | 0.52024 | 1.1439 | 31.7722 | 2743.7933 | 1308.5061 | 1435.2873
2016-02-18 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.7% | 1343.8164 | 1488.657 | 2832.4734 | 47.9072 | 0.47851 | 0.52149 | 1.1914 | 40.2107 | 2872.6842 | 1363.0577 | 1509.6265
2016-02-18 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.65% | 1434.757 | 1597.8646 | 3032.6215 | 64.4212 | 0.47825 | 0.52175 | 1.2391 | 51.9892 | 3084.6107 | 1459.6209 | 1624.9898
2016-02-18 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.15% | 1427.2594 | 1609.111 | 3036.3703 | 57.2068 | 0.47575 | 0.52425 | 1.2379 | 46.2137 | 3082.584 | 1449.2456 | 1633.3383
2016-02-18 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.98% | 1503.6849 | 1692.6302 | 3196.3151 | 116.0872 | 0.4799 | 0.5201 | 1.4799 | 78.4426 | 3274.7577 | 1541.3295 | 1733.4282
2016-02-18 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.25% | 1507.9508 | 1684.0985 | 3192.0492 | 110.7277 | 0.48126 | 0.51874 | 1.4813 | 74.7523 | 3266.8016 | 1543.9261 | 1722.8754
2016-02-18 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.66% | 1514.3806 | 1671.2389 | 3185.6194 | 111.7637 | 0.48331 | 0.51669 | 1.4833 | 75.3473 | 3260.9668 | 1550.7969 | 1710.1698
2016-02-18 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.66% | 1514.3439 | 1671.3121 | 3185.6561 | 112.5504 | 0.4833 | 0.5167 | 1.4833 | 75.8783 | 3261.5344 | 1551.016 | 1710.5184
2016-02-18 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.34% | 1509.3131 | 1681.3738 | 3190.6869 | 126.876 | 0.4817 | 0.5183 | 1.4817 | 85.6289 | 3276.3158 | 1550.5602 | 1725.7556
2016-02-18 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.37% | 1509.8513 | 1680.2974 | 3190.1487 | 112.9919 | 0.48187 | 0.51813 | 1.4819 | 76.2497 | 3266.3984 | 1546.5935 | 1719.8048
2016-02-18 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.96% | 1503.4314 | 1693.1373 | 3196.5686 | 88.0283 | 0.47982 | 0.52018 | 1.4798 | 59.4859 | 3256.0545 | 1531.9738 | 1724.0807
2016-02-18 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.32% | 1508.9639 | 1682.0721 | 3191.0361 | 93.3618 | 0.48158 | 0.51842 | 1.4816 | 63.0148 | 3254.0509 | 1539.3109 | 1714.74
2016-02-18 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.47% | 1511.3194 | 1677.3612 | 3188.6806 | 93.9372 | 0.48234 | 0.51766 | 1.4823 | 63.3711 | 3252.0517 | 1541.8856 | 1710.1661
2016-02-18 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.43% | 1510.7167 | 1678.5666 | 3189.2833 | 93.5359 | 0.48214 | 0.51786 | 1.4821 | 63.1085 | 3252.3918 | 1541.1441 | 1711.2478
2016-02-18 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.98% | 1503.7436 | 1692.5127 | 3196.2564 | 106.3685 | 0.47992 | 0.52008 | 1.4799 | 71.8746 | 3268.1309 | 1538.2375 | 1729.8934
2016-02-18 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.7884 | 1690.4232 | 3195.2116 | 114.1082 | 0.48025 | 0.51975 | 1.4803 | 77.087 | 3272.2986 | 1541.8096 | 1730.489
2016-02-18 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.1% | 1505.6236 | 1688.7527 | 3194.3764 | 104.2782 | 0.48052 | 0.51948 | 1.4805 | 70.4336 | 3264.81 | 1539.4683 | 1725.3417
2016-02-19 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9994 | 1690.0011 | 3195.0006 | 174.9841 | 0.48032 | 0.51968 | 1.4803 | 118.207 | 3313.2076 | 1561.7765 | 1751.4311
2016-02-19 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.09% | 1505.4731 | 1689.0539 | 3194.5269 | 188.7015 | 0.48047 | 0.51953 | 1.4805 | 127.4605 | 3321.9875 | 1566.714 | 1755.2734
2016-02-19 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9104 | 1690.1793 | 3195.0896 | 186.1784 | 0.48029 | 0.51971 | 1.4803 | 125.7715 | 3320.8611 | 1565.3172 | 1755.5439
2016-02-19 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.8% | 1500.8315 | 1698.337 | 3199.1685 | 186.5639 | 0.47899 | 0.52101 | 1.479 | 126.1429 | 3325.3114 | 1561.2525 | 1764.0588
2016-02-19 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.61% | 1497.9633 | 1704.0734 | 3202.0367 | 184.8843 | 0.47807 | 0.52193 | 1.4781 | 125.0846 | 3327.1213 | 1557.7629 | 1769.3584
2016-02-19 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.83% | 1501.288 | 1697.4241 | 3198.712 | 189.2059 | 0.47913 | 0.52087 | 1.4791 | 127.9166 | 3326.6287 | 1562.5772 | 1764.0514
2016-02-19 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4116 | 1483.6237 | 2831.0353 | 44.4546 | 0.47979 | 0.52021 | 1.1919 | 37.2967 | 2868.3321 | 1365.3063 | 1503.0258
2016-02-19 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.95% | 1347.3228 | 1483.748 | 2831.0709 | 48.4602 | 0.47976 | 0.52024 | 1.1919 | 40.6578 | 2871.7287 | 1366.8288 | 1504.8999
2016-02-19 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.7% | 1343.8164 | 1488.657 | 2832.4734 | 47.9072 | 0.47851 | 0.52149 | 1.1914 | 40.2107 | 2872.6842 | 1363.0577 | 1509.6265
2016-02-19 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.65% | 1343.0919 | 1489.6713 | 2832.7632 | 51.537 | 0.47825 | 0.52175 | 1.1913 | 43.2611 | 2876.0243 | 1363.7817 | 1512.2427
2016-02-19 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.15% | 1336.0733 | 1499.4973 | 2835.5707 | 45.7654 | 0.47575 | 0.52425 | 1.1903 | 38.4486 | 2874.0193 | 1354.3654 | 1519.6539
2016-02-19 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7176 | 1483.1954 | 2830.913 | 46.4349 | 0.4799 | 0.5201 | 1.192 | 38.9567 | 2869.8697 | 1366.4129 | 1503.4568
2016-02-19 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.25% | 1351.541 | 1477.8426 | 2829.3836 | 44.2911 | 0.48126 | 0.51874 | 1.1925 | 37.1412 | 2866.5248 | 1369.4156 | 1497.1092
2016-02-19 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.3039 | 1469.7746 | 2827.0785 | 44.7055 | 0.48331 | 0.51669 | 1.1933 | 37.4629 | 2864.5414 | 1375.4102 | 1489.1312
2016-02-19 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.271 | 1469.8206 | 2827.0916 | 45.0201 | 0.4833 | 0.5167 | 1.1933 | 37.7268 | 2864.8184 | 1375.5044 | 1489.3139
2016-02-19 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.34% | 1352.762 | 1476.1332 | 2828.8952 | 50.7504 | 0.4817 | 0.5183 | 1.1927 | 42.5516 | 2871.4468 | 1373.259 | 1498.1878
2016-02-19 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.37% | 1353.2444 | 1475.4579 | 2828.7022 | 45.1968 | 0.48187 | 0.51813 | 1.1927 | 37.893 | 2866.5952 | 1371.5038 | 1495.0914
2016-02-19 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4904 | 1483.5135 | 2831.0039 | 35.2113 | 0.47982 | 0.52018 | 1.1919 | 29.5415 | 2860.5454 | 1361.6649 | 1498.8804
2016-02-19 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.32% | 1352.4491 | 1476.5713 | 2829.0204 | 37.3447 | 0.48158 | 0.51842 | 1.1926 | 31.3128 | 2860.3332 | 1367.5288 | 1492.8044
2016-02-19 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.47% | 1354.5602 | 1473.6157 | 2828.1759 | 37.5749 | 0.48234 | 0.51766 | 1.1929 | 31.4979 | 2859.6738 | 1369.7528 | 1489.921
2016-02-19 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.43% | 1354.02 | 1474.372 | 2828.392 | 37.4144 | 0.48214 | 0.51786 | 1.1929 | 31.3653 | 2859.7573 | 1369.1426 | 1490.6147
2016-02-19 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-19 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7549 | 1588.8677 | 3029.6226 | 57.0541 | 0.48025 | 0.51975 | 1.2401 | 46.0067 | 3075.6293 | 1462.8497 | 1612.7796
2016-02-19 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-20 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-20 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-20 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-20 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-20 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.61% | 1434.2202 | 1598.6697 | 3032.8899 | 92.4421 | 0.47807 | 0.52193 | 1.239 | 74.6081 | 3107.498 | 1469.8883 | 1637.6096
2016-02-20 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.83% | 1437.4034 | 1593.8949 | 3031.2983 | 94.603 | 0.47913 | 0.52087 | 1.2396 | 76.3193 | 3107.6177 | 1473.9706 | 1633.6471
2016-02-20 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.96% | 1439.3715 | 1590.9428 | 3030.3143 | 55.5682 | 0.47979 | 0.52021 | 1.2399 | 44.8169 | 3075.1311 | 1460.8742 | 1614.2569
2016-02-20 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.95% | 1439.2766 | 1591.0851 | 3030.3617 | 60.5752 | 0.47976 | 0.52024 | 1.2399 | 48.8557 | 3079.2174 | 1462.7156 | 1616.5018
2016-02-20 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.7% | 1435.5309 | 1596.7037 | 3032.2346 | 59.8841 | 0.47851 | 0.52149 | 1.2393 | 48.3226 | 3080.5572 | 1458.6538 | 1621.9034
2016-02-20 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.65% | 1434.757 | 1597.8646 | 3032.6215 | 64.4212 | 0.47825 | 0.52175 | 1.2391 | 51.9892 | 3084.6107 | 1459.6209 | 1624.9898
2016-02-20 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.15% | 1427.2594 | 1609.111 | 3036.3703 | 57.2068 | 0.47575 | 0.52425 | 1.2379 | 46.2137 | 3082.584 | 1449.2456 | 1633.3383
2016-02-20 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.6983 | 1590.4525 | 3030.1508 | 58.0436 | 0.4799 | 0.5201 | 1.2399 | 46.8112 | 3076.9621 | 1462.163 | 1614.7991
2016-02-20 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.25% | 1443.7827 | 1584.326 | 3028.1087 | 55.3638 | 0.48126 | 0.51874 | 1.2406 | 44.6256 | 3072.7342 | 1465.2592 | 1607.4751
2016-02-20 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9388 | 1575.0917 | 3025.0306 | 55.8818 | 0.48331 | 0.51669 | 1.2417 | 45.0059 | 3070.0364 | 1471.6908 | 1598.3457
2016-02-20 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.66% | 1514.3439 | 1671.3121 | 3185.6561 | 112.5504 | 0.4833 | 0.5167 | 1.4833 | 75.8783 | 3261.5344 | 1551.016 | 1710.5184
2016-02-20 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.34% | 1509.3131 | 1681.3738 | 3190.6869 | 126.876 | 0.4817 | 0.5183 | 1.4817 | 85.6289 | 3276.3158 | 1550.5602 | 1725.7556
2016-02-20 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.37% | 1509.8513 | 1680.2974 | 3190.1487 | 112.9919 | 0.48187 | 0.51813 | 1.4819 | 76.2497 | 3266.3984 | 1546.5935 | 1719.8048
2016-02-20 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.96% | 1503.4314 | 1693.1373 | 3196.5686 | 88.0283 | 0.47982 | 0.52018 | 1.4798 | 59.4859 | 3256.0545 | 1531.9738 | 1724.0807
2016-02-20 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.32% | 1508.9639 | 1682.0721 | 3191.0361 | 93.3618 | 0.48158 | 0.51842 | 1.4816 | 63.0148 | 3254.0509 | 1539.3109 | 1714.74
2016-02-20 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.47% | 1511.3194 | 1677.3612 | 3188.6806 | 93.9372 | 0.48234 | 0.51766 | 1.4823 | 63.3711 | 3252.0517 | 1541.8856 | 1710.1661
2016-02-20 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.43% | 1510.7167 | 1678.5666 | 3189.2833 | 93.5359 | 0.48214 | 0.51786 | 1.4821 | 63.1085 | 3252.3918 | 1541.1441 | 1711.2478
2016-02-20 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.98% | 1503.7436 | 1692.5127 | 3196.2564 | 106.3685 | 0.47992 | 0.52008 | 1.4799 | 71.8746 | 3268.1309 | 1538.2375 | 1729.8934
2016-02-20 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.7884 | 1690.4232 | 3195.2116 | 114.1082 | 0.48025 | 0.51975 | 1.4803 | 77.087 | 3272.2986 | 1541.8096 | 1730.489
2016-02-20 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.1% | 1505.6236 | 1688.7527 | 3194.3764 | 104.2782 | 0.48052 | 0.51948 | 1.4805 | 70.4336 | 3264.81 | 1539.4683 | 1725.3417
2016-02-21 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9994 | 1690.0011 | 3195.0006 | 174.9841 | 0.48032 | 0.51968 | 1.4803 | 118.207 | 3313.2076 | 1561.7765 | 1751.4311
2016-02-21 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.09% | 1505.4731 | 1689.0539 | 3194.5269 | 188.7015 | 0.48047 | 0.51953 | 1.4805 | 127.4605 | 3321.9875 | 1566.714 | 1755.2734
2016-02-21 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9104 | 1690.1793 | 3195.0896 | 186.1784 | 0.48029 | 0.51971 | 1.4803 | 125.7715 | 3320.8611 | 1565.3172 | 1755.5439
2016-02-21 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.8% | 1500.8315 | 1698.337 | 3199.1685 | 186.5639 | 0.47899 | 0.52101 | 1.479 | 126.1429 | 3325.3114 | 1561.2525 | 1764.0588
2016-02-21 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.61% | 1497.9633 | 1704.0734 | 3202.0367 | 184.8843 | 0.47807 | 0.52193 | 1.4781 | 125.0846 | 3327.1213 | 1557.7629 | 1769.3584
2016-02-21 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.83% | 1501.288 | 1697.4241 | 3198.712 | 189.2059 | 0.47913 | 0.52087 | 1.4791 | 127.9166 | 3326.6287 | 1562.5772 | 1764.0514
2016-02-21 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.96% | 1503.3436 | 1693.3129 | 3196.6564 | 111.1364 | 0.47979 | 0.52021 | 1.4798 | 75.1028 | 3271.7593 | 1539.3772 | 1732.3821
2016-02-21 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.95% | 1439.2766 | 1591.0851 | 3030.3617 | 60.5752 | 0.47976 | 0.52024 | 1.2399 | 48.8557 | 3079.2174 | 1462.7156 | 1616.5018
2016-02-21 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.7% | 1435.5309 | 1596.7037 | 3032.2346 | 59.8841 | 0.47851 | 0.52149 | 1.2393 | 48.3226 | 3080.5572 | 1458.6538 | 1621.9034
2016-02-21 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.65% | 1343.0919 | 1489.6713 | 2832.7632 | 51.537 | 0.47825 | 0.52175 | 1.1913 | 43.2611 | 2876.0243 | 1363.7817 | 1512.2427
2016-02-21 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.15% | 1336.0733 | 1499.4973 | 2835.5707 | 45.7654 | 0.47575 | 0.52425 | 1.1903 | 38.4486 | 2874.0193 | 1354.3654 | 1519.6539
2016-02-21 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7176 | 1483.1954 | 2830.913 | 46.4349 | 0.4799 | 0.5201 | 1.192 | 38.9567 | 2869.8697 | 1366.4129 | 1503.4568
2016-02-21 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.25% | 1351.541 | 1477.8426 | 2829.3836 | 44.2911 | 0.48126 | 0.51874 | 1.1925 | 37.1412 | 2866.5248 | 1369.4156 | 1497.1092
2016-02-21 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.3039 | 1469.7746 | 2827.0785 | 44.7055 | 0.48331 | 0.51669 | 1.1933 | 37.4629 | 2864.5414 | 1375.4102 | 1489.1312
2016-02-21 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.271 | 1469.8206 | 2827.0916 | 45.0201 | 0.4833 | 0.5167 | 1.1933 | 37.7268 | 2864.8184 | 1375.5044 | 1489.3139
2016-02-21 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.34% | 1352.762 | 1476.1332 | 2828.8952 | 50.7504 | 0.4817 | 0.5183 | 1.1927 | 42.5516 | 2871.4468 | 1373.259 | 1498.1878
2016-02-21 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.37% | 1353.2444 | 1475.4579 | 2828.7022 | 45.1968 | 0.48187 | 0.51813 | 1.1927 | 37.893 | 2866.5952 | 1371.5038 | 1495.0914
2016-02-21 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4904 | 1483.5135 | 2831.0039 | 35.2113 | 0.47982 | 0.52018 | 1.1919 | 29.5415 | 2860.5454 | 1361.6649 | 1498.8804
2016-02-21 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.1836 | 1412.3613 | 2710.5449 | 28.0085 | 0.48158 | 0.51842 | 1.1445 | 24.4728 | 2735.0177 | 1309.9693 | 1425.0484
2016-02-21 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-21 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-21 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-21 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-21 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-22 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-22 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-22 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-22 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-22 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-22 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-22 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-22 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-22 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-22 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-22 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-22 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-22 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-22 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-22 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-22 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-22 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-22 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-22 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-22 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-22 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-22 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-22 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-22 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-23 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8958 | 1481.5459 | 2830.4417 | 69.9936 | 0.48032 | 0.51968 | 1.1921 | 58.7132 | 2889.1549 | 1377.0968 | 1512.0581
2016-02-23 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.09% | 1349.3203 | 1480.9516 | 2830.2719 | 75.4806 | 0.48047 | 0.51953 | 1.1922 | 63.3127 | 2893.5845 | 1379.7401 | 1513.8444
2016-02-23 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8159 | 1481.6577 | 2830.4736 | 74.4713 | 0.48029 | 0.51971 | 1.1921 | 62.4699 | 2892.9435 | 1378.8196 | 1514.1239
2016-02-23 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.8% | 1345.1602 | 1486.7758 | 2831.9359 | 74.6255 | 0.47899 | 0.52101 | 1.1916 | 62.6266 | 2894.5625 | 1375.1576 | 1519.4049
2016-02-23 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.61% | 1342.5895 | 1490.3748 | 2832.9642 | 73.9537 | 0.47807 | 0.52193 | 1.1912 | 62.0818 | 2895.046 | 1372.2691 | 1522.7769
2016-02-23 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.83% | 1291.5798 | 1420.9462 | 2712.526 | 56.7618 | 0.47913 | 0.52087 | 1.1437 | 49.6282 | 2762.1542 | 1315.3584 | 1446.7958
2016-02-23 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-23 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-23 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-23 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-23 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-23 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.98% | 1296.7949 | 1419.0063 | 2715.8013 | 29.0218 | 0.4799 | 0.5201 | 1.12 | 25.9129 | 2741.7142 | 1309.2305 | 1432.4837
2016-02-23 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.25% | 1300.4739 | 1414.4077 | 2714.8815 | 27.6819 | 0.48126 | 0.51874 | 1.1203 | 24.709 | 2739.5906 | 1312.3654 | 1427.2252
2016-02-23 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1306.019 | 1407.4763 | 2713.4953 | 27.9409 | 0.48331 | 0.51669 | 1.1208 | 24.9288 | 2738.4241 | 1318.0674 | 1420.3567
2016-02-23 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.66% | 1305.9874 | 1407.5158 | 2713.5032 | 28.1376 | 0.4833 | 0.5167 | 1.1208 | 25.1043 | 2738.6075 | 1318.1204 | 1420.4871
2016-02-23 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.34% | 1301.6488 | 1412.939 | 2714.5878 | 31.719 | 0.4817 | 0.5183 | 1.1204 | 28.3098 | 2742.8976 | 1315.2855 | 1427.6121
2016-02-23 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.37% | 1302.1129 | 1412.3589 | 2714.4718 | 28.248 | 0.48187 | 0.51813 | 1.1205 | 25.2109 | 2739.6827 | 1314.2612 | 1425.4215
2016-02-23 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5763 | 1419.2797 | 2715.8559 | 22.0071 | 0.47982 | 0.52018 | 1.12 | 19.65 | 2735.5059 | 1306.0047 | 1429.5012
2016-02-23 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3476 | 1413.3155 | 2714.6631 | 23.3404 | 0.48158 | 0.51842 | 1.1204 | 20.8323 | 2735.4954 | 1311.3801 | 1424.1153
2016-02-23 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.47% | 1196.1932 | 1289.5016 | 2485.6949 | 12.2118 | 0.48234 | 0.51766 | 1.0627 | 11.4913 | 2497.1862 | 1201.7359 | 1295.4503
2016-02-23 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.43% | 1195.7162 | 1290.0407 | 2485.7569 | 12.1597 | 0.48214 | 0.51786 | 1.0627 | 11.4425 | 2497.1994 | 1201.2331 | 1295.9663
2016-02-23 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.98% | 1190.1971 | 1296.2773 | 2486.4744 | 13.8279 | 0.47992 | 0.52008 | 1.0624 | 13.0158 | 2499.4902 | 1196.4436 | 1303.0466
2016-02-23 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.05% | 1191.024 | 1295.3428 | 2486.3669 | 14.8341 | 0.48025 | 0.51975 | 1.0624 | 13.9624 | 2500.3292 | 1197.7295 | 1302.5998
2016-02-23 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.1% | 1191.6851 | 1294.5959 | 2486.2809 | 13.5562 | 0.48052 | 0.51948 | 1.0625 | 12.7591 | 2499.0401 | 1197.8161 | 1301.224
2016-02-24 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.06% | 1191.191 | 1295.1541 | 2486.3452 | 22.7479 | 0.48032 | 0.51968 | 1.0624 | 21.411 | 2507.7562 | 1201.4752 | 1306.281
2016-02-24 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.09% | 1191.5659 | 1294.7305 | 2486.2964 | 24.5312 | 0.48047 | 0.51953 | 1.0625 | 23.089 | 2509.3855 | 1202.6595 | 1306.7259
2016-02-24 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.06% | 1191.1206 | 1295.2338 | 2486.3543 | 24.2032 | 0.48029 | 0.51971 | 1.0624 | 22.7808 | 2509.1351 | 1202.062 | 1307.0732
2016-02-24 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.8% | 1187.8922 | 1298.8818 | 2486.774 | 24.2533 | 0.47899 | 0.52101 | 1.0623 | 22.8316 | 2509.6056 | 1198.8283 | 1310.7774
2016-02-24 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.61% | 1185.622 | 1301.4471 | 2487.0691 | 24.035 | 0.47807 | 0.52193 | 1.0621 | 22.6286 | 2509.6977 | 1196.4402 | 1313.2576
2016-02-24 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2535 | 1298.4736 | 2486.7271 | 24.5968 | 0.47913 | 0.52087 | 1.0623 | 23.1545 | 2509.8816 | 1199.3476 | 1310.534
2016-02-24 06:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.96% | 1217.9297 | 1324.6359 | 2542.5656 | 8.8909 | 0.47979 | 0.52021 | 1.0384 | 8.5623 | 2551.1279 | 1222.0378 | 1329.0901
2016-02-24 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.95% | 1217.8494 | 1324.7226 | 2542.572 | 9.692 | 0.47976 | 0.52024 | 1.0384 | 9.3338 | 2551.9058 | 1222.3274 | 1329.5784
2016-02-24 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.7% | 1186.7055 | 1300.2227 | 2486.9283 | 15.5699 | 0.47851 | 0.52149 | 1.0622 | 14.658 | 2501.5863 | 1193.7196 | 1307.8668
2016-02-24 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.65% | 1186.0658 | 1300.9457 | 2487.0115 | 16.7495 | 0.47825 | 0.52175 | 1.0622 | 15.7691 | 2502.7806 | 1193.6074 | 1309.1732
2016-02-24 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-24 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-24 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-24 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8436 | 1406.3033 | 2709.1469 | 33.5291 | 0.48331 | 0.51669 | 1.145 | 29.2832 | 2738.4301 | 1316.9966 | 1421.4336
2016-02-24 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.66% | 1302.8121 | 1406.3443 | 2709.1564 | 33.7651 | 0.4833 | 0.5167 | 1.145 | 29.4894 | 2738.6458 | 1317.0644 | 1421.5814
2016-02-24 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.34% | 1298.484 | 1411.9708 | 2710.4548 | 38.0628 | 0.4817 | 0.5183 | 1.1445 | 33.2569 | 2743.7117 | 1314.5037 | 1429.208
2016-02-24 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.37% | 1298.947 | 1411.3689 | 2710.3159 | 33.8976 | 0.48187 | 0.51813 | 1.1446 | 29.6162 | 2739.9321 | 1313.2181 | 1426.714
2016-02-24 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.96% | 1293.4238 | 1418.549 | 2711.9728 | 26.4085 | 0.47982 | 0.52018 | 1.1439 | 23.0854 | 2735.0583 | 1304.5007 | 1430.5576
2016-02-24 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.1836 | 1412.3613 | 2710.5449 | 28.0085 | 0.48158 | 0.51842 | 1.1445 | 24.4728 | 2735.0177 | 1309.9693 | 1425.0484
2016-02-24 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.47% | 1300.21 | 1409.7269 | 2709.937 | 28.1812 | 0.48234 | 0.51766 | 1.1447 | 24.6188 | 2734.5558 | 1312.0846 | 1422.4712
2016-02-24 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-24 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.98% | 1347.7702 | 1483.1217 | 2830.8919 | 42.5474 | 0.47992 | 0.52008 | 1.192 | 35.6951 | 2866.587 | 1364.901 | 1501.6861
2016-02-24 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7549 | 1588.8677 | 3029.6226 | 57.0541 | 0.48025 | 0.51975 | 1.2401 | 46.0067 | 3075.6293 | 1462.8497 | 1612.7796
2016-02-24 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-25 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-25 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-25 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-25 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-25 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.61% | 1434.2202 | 1598.6697 | 3032.8899 | 92.4421 | 0.47807 | 0.52193 | 1.239 | 74.6081 | 3107.498 | 1469.8883 | 1637.6096
2016-02-25 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.83% | 1345.5693 | 1486.203 | 2831.7723 | 75.6824 | 0.47913 | 0.52087 | 1.1917 | 63.5104 | 2895.2827 | 1375.9993 | 1519.2834
2016-02-25 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4116 | 1483.6237 | 2831.0353 | 44.4546 | 0.47979 | 0.52021 | 1.1919 | 37.2967 | 2868.3321 | 1365.3063 | 1503.0258
2016-02-25 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.95% | 1347.3228 | 1483.748 | 2831.0709 | 48.4602 | 0.47976 | 0.52024 | 1.1919 | 40.6578 | 2871.7287 | 1366.8288 | 1504.8999
2016-02-25 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.7% | 1343.8164 | 1488.657 | 2832.4734 | 47.9072 | 0.47851 | 0.52149 | 1.1914 | 40.2107 | 2872.6842 | 1363.0577 | 1509.6265
2016-02-25 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.65% | 1434.757 | 1597.8646 | 3032.6215 | 64.4212 | 0.47825 | 0.52175 | 1.2391 | 51.9892 | 3084.6107 | 1459.6209 | 1624.9898
2016-02-25 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.15% | 1427.2594 | 1609.111 | 3036.3703 | 57.2068 | 0.47575 | 0.52425 | 1.2379 | 46.2137 | 3082.584 | 1449.2456 | 1633.3383
2016-02-25 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.6983 | 1590.4525 | 3030.1508 | 58.0436 | 0.4799 | 0.5201 | 1.2399 | 46.8112 | 3076.9621 | 1462.163 | 1614.7991
2016-02-25 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.25% | 1443.7827 | 1584.326 | 3028.1087 | 55.3638 | 0.48126 | 0.51874 | 1.2406 | 44.6256 | 3072.7342 | 1465.2592 | 1607.4751
2016-02-25 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9388 | 1575.0917 | 3025.0306 | 55.8818 | 0.48331 | 0.51669 | 1.2417 | 45.0059 | 3070.0364 | 1471.6908 | 1598.3457
2016-02-25 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9038 | 1575.1444 | 3025.0481 | 56.2752 | 0.4833 | 0.5167 | 1.2417 | 45.3229 | 3070.371 | 1471.8084 | 1598.5626
2016-02-25 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.34% | 1445.087 | 1582.3694 | 3027.4565 | 63.438 | 0.4817 | 0.5183 | 1.2408 | 51.1247 | 3078.5812 | 1469.7136 | 1608.8676
2016-02-25 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.37% | 1445.6023 | 1581.5965 | 3027.1988 | 56.496 | 0.48187 | 0.51813 | 1.2409 | 45.527 | 3072.7258 | 1467.5403 | 1605.1855
2016-02-25 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.96% | 1439.4556 | 1590.8166 | 3030.2722 | 44.0142 | 0.47982 | 0.52018 | 1.2399 | 35.4979 | 3065.7701 | 1456.4881 | 1609.282
2016-02-25 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.32% | 1444.7527 | 1582.8709 | 3027.6236 | 46.6809 | 0.48158 | 0.51842 | 1.2408 | 37.6219 | 3065.2455 | 1462.8708 | 1602.3747
2016-02-25 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.47% | 1447.008 | 1579.4881 | 3026.496 | 46.9686 | 0.48234 | 0.51766 | 1.2412 | 37.8423 | 3064.3383 | 1465.2606 | 1599.0776
2016-02-25 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.43% | 1446.4309 | 1580.3537 | 3026.7846 | 46.768 | 0.48214 | 0.51786 | 1.2411 | 37.6835 | 3064.4681 | 1464.5997 | 1599.8683
2016-02-25 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.7545 | 1590.3682 | 3030.1227 | 53.1842 | 0.47992 | 0.52008 | 1.24 | 42.8919 | 3073.0146 | 1460.3392 | 1612.6755
2016-02-25 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7549 | 1588.8677 | 3029.6226 | 57.0541 | 0.48025 | 0.51975 | 1.2401 | 46.0067 | 3075.6293 | 1462.8497 | 1612.7796
2016-02-25 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-26 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-26 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-26 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-26 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-26 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.61% | 1434.2202 | 1598.6697 | 3032.8899 | 92.4421 | 0.47807 | 0.52193 | 1.239 | 74.6081 | 3107.498 | 1469.8883 | 1637.6096
2016-02-26 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.83% | 1437.4034 | 1593.8949 | 3031.2983 | 94.603 | 0.47913 | 0.52087 | 1.2396 | 76.3193 | 3107.6177 | 1473.9706 | 1633.6471
2016-02-26 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4116 | 1483.6237 | 2831.0353 | 44.4546 | 0.47979 | 0.52021 | 1.1919 | 37.2967 | 2868.3321 | 1365.3063 | 1503.0258
2016-02-26 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.95% | 1347.3228 | 1483.748 | 2831.0709 | 48.4602 | 0.47976 | 0.52024 | 1.1919 | 40.6578 | 2871.7287 | 1366.8288 | 1504.8999
2016-02-26 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.7% | 1343.8164 | 1488.657 | 2832.4734 | 47.9072 | 0.47851 | 0.52149 | 1.1914 | 40.2107 | 2872.6842 | 1363.0577 | 1509.6265
2016-02-26 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.65% | 1434.757 | 1597.8646 | 3032.6215 | 64.4212 | 0.47825 | 0.52175 | 1.2391 | 51.9892 | 3084.6107 | 1459.6209 | 1624.9898
2016-02-26 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.15% | 1427.2594 | 1609.111 | 3036.3703 | 57.2068 | 0.47575 | 0.52425 | 1.2379 | 46.2137 | 3082.584 | 1449.2456 | 1633.3383
2016-02-26 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.6983 | 1590.4525 | 3030.1508 | 58.0436 | 0.4799 | 0.5201 | 1.2399 | 46.8112 | 3076.9621 | 1462.163 | 1614.7991
2016-02-26 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.25% | 1443.7827 | 1584.326 | 3028.1087 | 55.3638 | 0.48126 | 0.51874 | 1.2406 | 44.6256 | 3072.7342 | 1465.2592 | 1607.4751
2016-02-26 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9388 | 1575.0917 | 3025.0306 | 55.8818 | 0.48331 | 0.51669 | 1.2417 | 45.0059 | 3070.0364 | 1471.6908 | 1598.3457
2016-02-26 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.66% | 1449.9038 | 1575.1444 | 3025.0481 | 56.2752 | 0.4833 | 0.5167 | 1.2417 | 45.3229 | 3070.371 | 1471.8084 | 1598.5626
2016-02-26 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.34% | 1445.087 | 1582.3694 | 3027.4565 | 63.438 | 0.4817 | 0.5183 | 1.2408 | 51.1247 | 3078.5812 | 1469.7136 | 1608.8676
2016-02-26 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.37% | 1445.6023 | 1581.5965 | 3027.1988 | 56.496 | 0.48187 | 0.51813 | 1.2409 | 45.527 | 3072.7258 | 1467.5403 | 1605.1855
2016-02-26 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.96% | 1439.4556 | 1590.8166 | 3030.2722 | 44.0142 | 0.47982 | 0.52018 | 1.2399 | 35.4979 | 3065.7701 | 1456.4881 | 1609.282
2016-02-26 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.32% | 1444.7527 | 1582.8709 | 3027.6236 | 46.6809 | 0.48158 | 0.51842 | 1.2408 | 37.6219 | 3065.2455 | 1462.8708 | 1602.3747
2016-02-26 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.47% | 1354.5602 | 1473.6157 | 2828.1759 | 37.5749 | 0.48234 | 0.51766 | 1.1929 | 31.4979 | 2859.6738 | 1369.7528 | 1489.921
2016-02-26 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.43% | 1299.6915 | 1410.401 | 2710.0925 | 28.0608 | 0.48214 | 0.51786 | 1.1446 | 24.5149 | 2734.6074 | 1311.5112 | 1423.0962
2016-02-26 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.6925 | 1418.1998 | 2711.8923 | 31.9105 | 0.47992 | 0.52008 | 1.144 | 27.8944 | 2739.7867 | 1307.0795 | 1432.7071
2016-02-26 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.5913 | 1417.0313 | 2711.6226 | 34.2324 | 0.48025 | 0.51975 | 1.1441 | 29.9215 | 2741.5441 | 1308.9612 | 1432.5829
2016-02-26 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.1% | 1295.3099 | 1416.0972 | 2711.407 | 31.2835 | 0.48052 | 0.51948 | 1.1442 | 27.342 | 2738.749 | 1308.4482 | 1430.3008
2016-02-27 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.7729 | 1416.7953 | 2711.5681 | 52.4952 | 0.48032 | 0.51968 | 1.1441 | 45.8836 | 2757.4517 | 1316.8116 | 1440.6401
2016-02-27 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.09% | 1295.1803 | 1416.2655 | 2711.4459 | 56.6104 | 0.48047 | 0.51953 | 1.1441 | 49.4786 | 2760.9245 | 1318.9533 | 1441.9711
2016-02-27 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6963 | 1416.8949 | 2711.5911 | 55.8535 | 0.48029 | 0.51971 | 1.1441 | 48.8193 | 2760.4104 | 1318.1437 | 1442.2667
2016-02-27 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.8% | 1291.1871 | 1421.4567 | 2712.6439 | 55.9692 | 0.47899 | 0.52101 | 1.1437 | 48.9371 | 2761.5809 | 1314.6274 | 1446.9535
2016-02-27 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.61% | 1288.7196 | 1424.6645 | 2713.3841 | 55.4653 | 0.47807 | 0.52193 | 1.1434 | 48.5081 | 2761.8923 | 1311.91 | 1449.9822
2016-02-27 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7278 | 1421.5903 | 2716.3181 | 47.3015 | 0.47913 | 0.52087 | 1.1198 | 42.2416 | 2758.5597 | 1314.9672 | 1443.5925
2016-02-27 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.96% | 1296.5005 | 1419.3743 | 2715.8749 | 27.7841 | 0.47979 | 0.52021 | 1.1199 | 24.8084 | 2740.6833 | 1308.4034 | 1432.2799
2016-02-27 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.95% | 1296.4151 | 1419.4811 | 2715.8962 | 30.2876 | 0.47976 | 0.52024 | 1.1199 | 27.044 | 2742.9402 | 1309.3897 | 1433.5505
2016-02-27 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.7% | 1293.0412 | 1423.6986 | 2716.7397 | 29.942 | 0.47851 | 0.52149 | 1.1196 | 26.7428 | 2743.4826 | 1305.8379 | 1437.6447
2016-02-27 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3441 | 1424.5699 | 2716.914 | 32.2106 | 0.47825 | 0.52175 | 1.1196 | 28.7707 | 2745.6847 | 1306.1037 | 1439.581
2016-02-27 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.15% | 1285.5906 | 1433.0117 | 2718.6023 | 28.6034 | 0.47575 | 0.52425 | 1.1189 | 25.563 | 2744.1653 | 1297.7523 | 1446.413
2016-02-27 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.98% | 1293.642 | 1418.2654 | 2711.9074 | 34.8261 | 0.4799 | 0.5201 | 1.144 | 30.4432 | 2742.3507 | 1308.2517 | 1434.099
2016-02-27 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.25% | 1297.3119 | 1413.4945 | 2710.8064 | 33.2183 | 0.48126 | 0.51874 | 1.1444 | 29.0274 | 2739.8338 | 1311.2817 | 1428.5521
2016-02-27 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.3039 | 1469.7746 | 2827.0785 | 44.7055 | 0.48331 | 0.51669 | 1.1933 | 37.4629 | 2864.5414 | 1375.4102 | 1489.1312
2016-02-27 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.66% | 1357.271 | 1469.8206 | 2827.0916 | 45.0201 | 0.4833 | 0.5167 | 1.1933 | 37.7268 | 2864.8184 | 1375.5044 | 1489.3139
2016-02-27 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.34% | 1352.762 | 1476.1332 | 2828.8952 | 50.7504 | 0.4817 | 0.5183 | 1.1927 | 42.5516 | 2871.4468 | 1373.259 | 1498.1878
2016-02-27 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.37% | 1353.2444 | 1475.4579 | 2828.7022 | 45.1968 | 0.48187 | 0.51813 | 1.1927 | 37.893 | 2866.5952 | 1371.5038 | 1495.0914
2016-02-27 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.96% | 1347.4904 | 1483.5135 | 2831.0039 | 35.2113 | 0.47982 | 0.52018 | 1.1919 | 29.5415 | 2860.5454 | 1361.6649 | 1498.8804
2016-02-27 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.32% | 1352.4491 | 1476.5713 | 2829.0204 | 37.3447 | 0.48158 | 0.51842 | 1.1926 | 31.3128 | 2860.3332 | 1367.5288 | 1492.8044
2016-02-27 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.47% | 1354.5602 | 1473.6157 | 2828.1759 | 37.5749 | 0.48234 | 0.51766 | 1.1929 | 31.4979 | 2859.6738 | 1369.7528 | 1489.921
2016-02-27 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.43% | 1446.4309 | 1580.3537 | 3026.7846 | 46.768 | 0.48214 | 0.51786 | 1.2411 | 37.6835 | 3064.4681 | 1464.5997 | 1599.8683
2016-02-27 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.7545 | 1590.3682 | 3030.1227 | 53.1842 | 0.47992 | 0.52008 | 1.24 | 42.8919 | 3073.0146 | 1460.3392 | 1612.6755
2016-02-27 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7549 | 1588.8677 | 3029.6226 | 57.0541 | 0.48025 | 0.51975 | 1.2401 | 46.0067 | 3075.6293 | 1462.8497 | 1612.7796
2016-02-27 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-28 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.9569 | 1588.5646 | 3029.5215 | 87.492 | 0.48032 | 0.51968 | 1.2402 | 70.549 | 3100.0706 | 1474.8429 | 1625.2276
2016-02-28 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.09% | 1441.4104 | 1587.8844 | 3029.2948 | 94.3507 | 0.48047 | 0.51953 | 1.2402 | 76.0749 | 3105.3697 | 1477.9621 | 1627.4076
2016-02-28 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8716 | 1588.6925 | 3029.5642 | 93.0892 | 0.48029 | 0.51971 | 1.2401 | 75.0631 | 3104.6273 | 1476.9237 | 1627.7036
2016-02-28 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.8% | 1436.9663 | 1594.5505 | 3031.5168 | 93.2819 | 0.47899 | 0.52101 | 1.2395 | 75.2581 | 3106.7749 | 1473.0141 | 1633.7608
2016-02-28 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.61% | 1434.2202 | 1598.6697 | 3032.8899 | 92.4421 | 0.47807 | 0.52193 | 1.239 | 74.6081 | 3107.498 | 1469.8883 | 1637.6096
2016-02-28 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.83% | 1437.4034 | 1593.8949 | 3031.2983 | 94.603 | 0.47913 | 0.52087 | 1.2396 | 76.3193 | 3107.6177 | 1473.9706 | 1633.6471
2016-02-28 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.96% | 1439.3715 | 1590.9428 | 3030.3143 | 55.5682 | 0.47979 | 0.52021 | 1.2399 | 44.8169 | 3075.1311 | 1460.8742 | 1614.2569
2016-02-28 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.95% | 1439.2766 | 1591.0851 | 3030.3617 | 60.5752 | 0.47976 | 0.52024 | 1.2399 | 48.8557 | 3079.2174 | 1462.7156 | 1616.5018
2016-02-28 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.7% | 1435.5309 | 1596.7037 | 3032.2346 | 59.8841 | 0.47851 | 0.52149 | 1.2393 | 48.3226 | 3080.5572 | 1458.6538 | 1621.9034
2016-02-28 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.65% | 1434.757 | 1597.8646 | 3032.6215 | 64.4212 | 0.47825 | 0.52175 | 1.2391 | 51.9892 | 3084.6107 | 1459.6209 | 1624.9898
2016-02-28 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.15% | 1490.6931 | 1718.6138 | 3209.3069 | 114.4136 | 0.47575 | 0.52425 | 1.4758 | 77.529 | 3286.8359 | 1527.5777 | 1759.2581
2016-02-28 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.98% | 1503.6849 | 1692.6302 | 3196.3151 | 116.0872 | 0.4799 | 0.5201 | 1.4799 | 78.4426 | 3274.7577 | 1541.3295 | 1733.4282
2016-02-28 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.25% | 1507.9508 | 1684.0985 | 3192.0492 | 110.7277 | 0.48126 | 0.51874 | 1.4813 | 74.7523 | 3266.8016 | 1543.9261 | 1722.8754
2016-02-28 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.66% | 1514.3806 | 1671.2389 | 3185.6194 | 111.7637 | 0.48331 | 0.51669 | 1.4833 | 75.3473 | 3260.9668 | 1550.7969 | 1710.1698
2016-02-28 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.66% | 1514.3439 | 1671.3121 | 3185.6561 | 112.5504 | 0.4833 | 0.5167 | 1.4833 | 75.8783 | 3261.5344 | 1551.016 | 1710.5184
2016-02-28 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.34% | 1509.3131 | 1681.3738 | 3190.6869 | 126.876 | 0.4817 | 0.5183 | 1.4817 | 85.6289 | 3276.3158 | 1550.5602 | 1725.7556
2016-02-28 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.37% | 1509.8513 | 1680.2974 | 3190.1487 | 112.9919 | 0.48187 | 0.51813 | 1.4819 | 76.2497 | 3266.3984 | 1546.5935 | 1719.8048
2016-02-28 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.96% | 1503.4314 | 1693.1373 | 3196.5686 | 88.0283 | 0.47982 | 0.52018 | 1.4798 | 59.4859 | 3256.0545 | 1531.9738 | 1724.0807
2016-02-28 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.32% | 1444.7527 | 1582.8709 | 3027.6236 | 46.6809 | 0.48158 | 0.51842 | 1.2408 | 37.6219 | 3065.2455 | 1462.8708 | 1602.3747
2016-02-28 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.47% | 1447.008 | 1579.4881 | 3026.496 | 46.9686 | 0.48234 | 0.51766 | 1.2412 | 37.8423 | 3064.3383 | 1465.2606 | 1599.0776
2016-02-28 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.43% | 1446.4309 | 1580.3537 | 3026.7846 | 46.768 | 0.48214 | 0.51786 | 1.2411 | 37.6835 | 3064.4681 | 1464.5997 | 1599.8683
2016-02-28 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.98% | 1439.7545 | 1590.3682 | 3030.1227 | 53.1842 | 0.47992 | 0.52008 | 1.24 | 42.8919 | 3073.0146 | 1460.3392 | 1612.6755
2016-02-28 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7549 | 1588.8677 | 3029.6226 | 57.0541 | 0.48025 | 0.51975 | 1.2401 | 46.0067 | 3075.6293 | 1462.8497 | 1612.7796
2016-02-28 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.1% | 1441.5545 | 1587.6682 | 3029.2227 | 52.1391 | 0.48052 | 0.51948 | 1.2403 | 42.0389 | 3071.2616 | 1461.755 | 1609.5066
2016-02-29 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 62.4232 | 0.48858 | 0.51142 | 1.2443 | 50.1676 | 3067.2901 | 1490.2662 | 1577.024
2016-02-29 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.422 | 0.48848 | 0.51152 | 1.2442 | 50.1688 | 3067.4488 | 1489.9465 | 1577.5023
2016-02-29 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 64.482 | 0.48784 | 0.51216 | 1.2439 | 51.8376 | 3070.0734 | 1488.817 | 1581.2564
2016-02-29 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 69.3902 | 0.48725 | 0.51275 | 1.2436 | 55.7967 | 3074.9203 | 1488.9398 | 1585.9805
2016-02-29 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 60.2845 | 0.48895 | 0.51105 | 1.2445 | 48.4417 | 3065.0207 | 1490.5275 | 1574.4931
2016-02-29 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 58.4031 | 0.4884 | 0.5116 | 1.2442 | 46.9403 | 3064.3366 | 1488.1331 | 1576.2035
2016-02-29 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 61.4342 | 0.48777 | 0.51223 | 1.2439 | 49.3889 | 3067.731 | 1487.4064 | 1580.3247
2016-02-29 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 64.1704 | 0.48569 | 0.51431 | 1.2428 | 51.6319 | 3073.0996 | 1482.1418 | 1590.9578
2016-02-29 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 66.6889 | 0.48648 | 0.51352 | 1.2432 | 53.6412 | 3073.9201 | 1485.5374 | 1588.3827
2016-02-29 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 51.4158 | 0.48615 | 0.51385 | 1.2431 | 41.3617 | 3062.1293 | 1478.5731 | 1583.5562
2016-02-29 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 87.4781 | 0.48704 | 0.51296 | 1.487 | 58.8269 | 3232.7629 | 1554.7152 | 1678.0477
2016-02-29 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 93.8846 | 0.48756 | 0.51244 | 1.4876 | 63.113 | 3235.4178 | 1558.4668 | 1676.951
2016-02-29 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 94.3511 | 0.48731 | 0.51269 | 1.4873 | 63.4376 | 3236.5457 | 1557.8054 | 1678.7403
2016-02-29 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 136.1067 | 0.48354 | 0.51646 | 1.4835 | 91.7443 | 3276.6369 | 1559.4699 | 1717.167
2016-02-29 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.95% | 1518.8915 | 1662.217 | 3181.1085 | 133.6256 | 0.48475 | 0.51525 | 1.4848 | 89.9986 | 3271.1071 | 1562.5186 | 1708.5885
2016-02-29 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 101.7382 | 0.48484 | 0.51516 | 1.4848 | 68.518 | 3249.3544 | 1552.3838 | 1696.9706
2016-02-29 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 66.0752 | 0.48702 | 0.51298 | 1.487 | 44.4346 | 3218.4366 | 1547.6386 | 1670.7981
2016-02-29 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 43.9597 | 0.48784 | 0.51216 | 1.4878 | 29.546 | 3200.9785 | 1542.9812 | 1657.9973
2016-02-29 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 48.0935 | 0.48845 | 0.51155 | 1.4884 | 32.3112 | 3201.8379 | 1546.2556 | 1655.5823
2016-02-29 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 46.3855 | 0.48603 | 0.51397 | 1.243 | 37.317 | 3058.2782 | 1476.2146 | 1582.0636
2016-02-29 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 22.2519 | 0.48894 | 0.51106 | 1.2445 | 17.8807 | 3034.4758 | 1475.5523 | 1558.9235
2016-02-29 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 32.7901 | 0.48715 | 0.51285 | 1.2436 | 26.3676 | 3045.6444 | 1474.2913 | 1571.3531
2016-02-29 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 59.3942 | 0.48693 | 0.51307 | 1.2435 | 47.765 | 3067.3632 | 1484.0619 | 1583.3014
2016-02-29 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 64.0949 | 0.4873 | 0.5127 | 1.2437 | 51.5376 | 3070.5803 | 1487.0292 | 1583.551
2016-03-01 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 124.8464 | 0.48858 | 0.51142 | 1.4886 | 83.8692 | 3252.9695 | 1571.8769 | 1681.0926
2016-03-01 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8441 | 0.48848 | 0.51152 | 1.4885 | 83.8735 | 3253.3029 | 1571.5412 | 1681.7616
2016-03-01 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 128.9639 | 0.48784 | 0.51216 | 1.4878 | 86.6784 | 3258.1044 | 1570.8596 | 1687.2448
2016-03-01 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 69.3902 | 0.48725 | 0.51275 | 1.2436 | 55.7967 | 3074.9203 | 1488.9398 | 1585.9805
2016-03-01 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 60.2845 | 0.48895 | 0.51105 | 1.2445 | 48.4417 | 3065.0207 | 1490.5275 | 1574.4931
2016-03-01 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.68% | 1371.5969 | 1449.7644 | 2821.3612 | 46.7225 | 0.4884 | 0.5116 | 1.1954 | 39.0865 | 2860.4478 | 1390.6869 | 1469.7609
2016-03-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.55% | 1314.8635 | 1390.6774 | 2705.5409 | 36.8605 | 0.48777 | 0.51223 | 1.1463 | 32.1552 | 2737.6962 | 1330.5479 | 1407.1482
2016-03-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.14% | 1309.2466 | 1397.9794 | 2707.226 | 38.5023 | 0.48569 | 0.51431 | 1.1457 | 33.6057 | 2740.8317 | 1325.5685 | 1415.2632
2016-03-01 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3827 | 1395.2025 | 2706.5852 | 40.0133 | 0.48648 | 0.51352 | 1.1459 | 34.9173 | 2741.5025 | 1328.3693 | 1413.1332
2016-03-01 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.23% | 1310.5047 | 1396.3439 | 2706.8486 | 30.8495 | 0.48615 | 0.51385 | 1.1458 | 26.9229 | 2733.7715 | 1323.5934 | 1410.1781
2016-03-01 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.41% | 1367.7755 | 1455.1144 | 2822.8898 | 34.9912 | 0.48704 | 0.51296 | 1.1948 | 29.2859 | 2852.1757 | 1382.0389 | 1470.1368
2016-03-01 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 37.5538 | 0.48756 | 0.51244 | 1.195 | 31.4251 | 2853.7301 | 1384.5592 | 1469.171
2016-03-01 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.7404 | 0.48731 | 0.51269 | 1.1949 | 31.584 | 2854.177 | 1383.9085 | 1470.2685
2016-03-01 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 54.4427 | 0.48354 | 0.51646 | 1.1934 | 45.6191 | 2872.437 | 1380.0142 | 1492.4228
2016-03-01 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 53.4503 | 0.48475 | 0.51525 | 1.1939 | 44.7694 | 2870.2307 | 1383.049 | 1487.1816
2016-03-01 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 40.6953 | 0.48484 | 0.51516 | 1.1939 | 34.085 | 2859.4487 | 1378.1165 | 1481.3322
2016-03-01 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 26.4301 | 0.48702 | 0.51298 | 1.1948 | 22.1208 | 2845.0343 | 1378.4896 | 1466.5447
2016-03-01 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 17.5839 | 0.48784 | 0.51216 | 1.1951 | 14.7129 | 2836.7052 | 1377.1968 | 1459.5084
2016-03-01 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 19.2374 | 0.48845 | 0.51155 | 1.1954 | 16.0931 | 2837.4022 | 1379.5881 | 1457.8141
2016-03-01 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.21% | 1310.1567 | 1396.7963 | 2706.953 | 27.8313 | 0.48603 | 0.51397 | 1.1458 | 24.2897 | 2731.2427 | 1321.9621 | 1409.2806
2016-03-01 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.003 | 1386.5961 | 2704.5991 | 13.3512 | 0.48894 | 0.51106 | 1.1467 | 11.6433 | 2716.2424 | 1323.6958 | 1392.5466
2016-03-01 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.43% | 1313.1837 | 1392.8612 | 2706.0449 | 19.6741 | 0.48715 | 0.51285 | 1.1461 | 17.1654 | 2723.2103 | 1321.5458 | 1401.6645
2016-03-01 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.39% | 1312.606 | 1393.6122 | 2706.2182 | 35.6365 | 0.48693 | 0.51307 | 1.1461 | 31.0942 | 2737.3124 | 1327.7469 | 1409.5656
2016-03-01 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6045 | 1392.3141 | 2705.9186 | 38.4569 | 0.4873 | 0.5127 | 1.1462 | 33.5519 | 2739.4706 | 1329.9545 | 1409.516
2016-03-02 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.0552 | 1387.8282 | 2704.8834 | 37.4539 | 0.48858 | 0.51142 | 1.1466 | 32.6659 | 2737.5493 | 1333.0153 | 1404.5341
2016-03-02 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.7% | 1316.7722 | 1388.1962 | 2704.9683 | 37.4532 | 0.48848 | 0.51152 | 1.1465 | 32.6662 | 2737.6345 | 1332.729 | 1404.9056
2016-03-02 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0545 | 1390.4292 | 2705.4837 | 38.6892 | 0.48784 | 0.51216 | 1.1464 | 33.7498 | 2739.2334 | 1331.5191 | 1407.7144
2016-03-02 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.459 | 1392.5032 | 2705.9623 | 41.6341 | 0.48725 | 0.51275 | 1.1462 | 36.3244 | 2742.2867 | 1331.1581 | 1411.1285
2016-03-02 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.032 | 1386.5584 | 2704.5904 | 36.1707 | 0.48895 | 0.51105 | 1.1467 | 31.5437 | 2736.1341 | 1333.4552 | 1402.6789
2016-03-02 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.68% | 1316.5631 | 1388.4679 | 2705.0311 | 35.0419 | 0.4884 | 0.5116 | 1.1465 | 30.5637 | 2735.5947 | 1331.4905 | 1404.1042
2016-03-02 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.55% | 1318.0682 | 1392.4148 | 2710.483 | 30.7171 | 0.48777 | 0.51223 | 1.1219 | 27.3785 | 2737.8614 | 1331.4226 | 1406.4388
2016-03-02 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.14% | 1312.4376 | 1399.453 | 2711.8906 | 32.0852 | 0.48569 | 0.51431 | 1.1214 | 28.6112 | 2740.5018 | 1326.3337 | 1414.1681
2016-03-02 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.3% | 1314.5789 | 1396.7764 | 2711.3553 | 33.3444 | 0.48648 | 0.51352 | 1.1216 | 29.7288 | 2741.0841 | 1329.0414 | 1412.0427
2016-03-02 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.23% | 1313.6987 | 1397.8766 | 2711.5753 | 25.7079 | 0.48615 | 0.51385 | 1.1215 | 22.922 | 2734.4973 | 1324.8424 | 1409.6549
2016-03-02 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.41% | 1316.0949 | 1394.8813 | 2710.9763 | 21.8695 | 0.48704 | 0.51296 | 1.1218 | 19.4957 | 2730.472 | 1325.5901 | 1404.8818
2016-03-02 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.51% | 1317.5017 | 1393.1229 | 2710.6246 | 23.4711 | 0.48756 | 0.51244 | 1.1219 | 20.9211 | 2731.5456 | 1327.702 | 1403.8436
2016-03-02 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.46% | 1316.8089 | 1393.9889 | 2710.7978 | 23.5878 | 0.48731 | 0.51269 | 1.1218 | 21.0262 | 2731.824 | 1327.0551 | 1404.7689
2016-03-02 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.71% | 1306.6458 | 1406.6927 | 2713.3385 | 34.0267 | 0.48354 | 0.51646 | 1.1209 | 30.3569 | 2743.6955 | 1321.3248 | 1422.3707
2016-03-02 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.95% | 1309.9093 | 1402.6134 | 2712.5227 | 33.4064 | 0.48475 | 0.51525 | 1.1212 | 29.7955 | 2742.3182 | 1324.3527 | 1417.9655
2016-03-02 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.97% | 1310.1439 | 1402.3201 | 2712.464 | 25.4346 | 0.48484 | 0.51516 | 1.1212 | 22.6849 | 2735.1489 | 1321.1424 | 1414.0065
2016-03-02 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.4% | 1316.038 | 1394.9525 | 2710.9905 | 16.5188 | 0.48702 | 0.51298 | 1.1218 | 14.7259 | 2725.7164 | 1323.2098 | 1402.5066
2016-03-02 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2539 | 1392.1826 | 2710.4365 | 10.9899 | 0.48784 | 0.51216 | 1.122 | 9.7953 | 2720.2318 | 1323.0325 | 1397.1993
2016-03-02 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8975 | 1390.1281 | 2710.0256 | 12.0234 | 0.48845 | 0.51155 | 1.1221 | 10.715 | 2720.7406 | 1325.1312 | 1395.6093
2016-03-02 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.21% | 1313.3499 | 1398.3127 | 2711.6625 | 23.1928 | 0.48603 | 0.51397 | 1.1215 | 20.68 | 2732.3425 | 1323.4009 | 1408.9417
2016-03-02 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.79% | 1321.2153 | 1388.4808 | 2709.6962 | 11.126 | 0.48894 | 0.51106 | 1.1222 | 9.9141 | 2719.6103 | 1326.0627 | 1393.5476
2016-03-02 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.43% | 1316.3843 | 1394.5196 | 2710.9039 | 16.395 | 0.48715 | 0.51285 | 1.1218 | 14.6151 | 2725.519 | 1323.504 | 1402.015
2016-03-02 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.39% | 1312.606 | 1393.6122 | 2706.2182 | 35.6365 | 0.48693 | 0.51307 | 1.1461 | 31.0942 | 2737.3124 | 1327.7469 | 1409.5656
2016-03-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6045 | 1392.3141 | 2705.9186 | 38.4569 | 0.4873 | 0.5127 | 1.1462 | 33.5519 | 2739.4706 | 1329.9545 | 1409.516
2016-03-03 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.0552 | 1387.8282 | 2704.8834 | 37.4539 | 0.48858 | 0.51142 | 1.1466 | 32.6659 | 2737.5493 | 1333.0153 | 1404.5341
2016-03-03 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.7% | 1316.7722 | 1388.1962 | 2704.9683 | 37.4532 | 0.48848 | 0.51152 | 1.1465 | 32.6662 | 2737.6345 | 1332.729 | 1404.9056
2016-03-03 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0545 | 1390.4292 | 2705.4837 | 38.6892 | 0.48784 | 0.51216 | 1.1464 | 33.7498 | 2739.2334 | 1331.5191 | 1407.7144
2016-03-03 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.459 | 1392.5032 | 2705.9623 | 41.6341 | 0.48725 | 0.51275 | 1.1462 | 36.3244 | 2742.2867 | 1331.1581 | 1411.1285
2016-03-03 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.032 | 1386.5584 | 2704.5904 | 36.1707 | 0.48895 | 0.51105 | 1.1467 | 31.5437 | 2736.1341 | 1333.4552 | 1402.6789
2016-03-03 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.68% | 1316.5631 | 1388.4679 | 2705.0311 | 35.0419 | 0.4884 | 0.5116 | 1.1465 | 30.5637 | 2735.5947 | 1331.4905 | 1404.1042
2016-03-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.55% | 1314.8635 | 1390.6774 | 2705.5409 | 36.8605 | 0.48777 | 0.51223 | 1.1463 | 32.1552 | 2737.6962 | 1330.5479 | 1407.1482
2016-03-03 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.14% | 1309.2466 | 1397.9794 | 2707.226 | 38.5023 | 0.48569 | 0.51431 | 1.1457 | 33.6057 | 2740.8317 | 1325.5685 | 1415.2632
2016-03-03 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3827 | 1395.2025 | 2706.5852 | 40.0133 | 0.48648 | 0.51352 | 1.1459 | 34.9173 | 2741.5025 | 1328.3693 | 1413.1332
2016-03-03 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.23% | 1310.5047 | 1396.3439 | 2706.8486 | 30.8495 | 0.48615 | 0.51385 | 1.1458 | 26.9229 | 2733.7715 | 1323.5934 | 1410.1781
2016-03-03 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 26.2434 | 0.48704 | 0.51296 | 1.1461 | 22.8978 | 2729.0293 | 1324.0472 | 1404.9821
2016-03-03 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 37.5538 | 0.48756 | 0.51244 | 1.195 | 31.4251 | 2853.7301 | 1384.5592 | 1469.171
2016-03-03 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.7404 | 0.48731 | 0.51269 | 1.1949 | 31.584 | 2854.177 | 1383.9085 | 1470.2685
2016-03-03 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 54.4427 | 0.48354 | 0.51646 | 1.1934 | 45.6191 | 2872.437 | 1380.0142 | 1492.4228
2016-03-03 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 53.4503 | 0.48475 | 0.51525 | 1.1939 | 44.7694 | 2870.2307 | 1383.049 | 1487.1816
2016-03-03 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 40.6953 | 0.48484 | 0.51516 | 1.1939 | 34.085 | 2859.4487 | 1378.1165 | 1481.3322
2016-03-03 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 26.4301 | 0.48702 | 0.51298 | 1.1948 | 22.1208 | 2845.0343 | 1378.4896 | 1466.5447
2016-03-03 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 17.5839 | 0.48784 | 0.51216 | 1.1951 | 14.7129 | 2836.7052 | 1377.1968 | 1459.5084
2016-03-03 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 19.2374 | 0.48845 | 0.51155 | 1.1954 | 16.0931 | 2837.4022 | 1379.5881 | 1457.8141
2016-03-03 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 46.3855 | 0.48603 | 0.51397 | 1.243 | 37.317 | 3058.2782 | 1476.2146 | 1582.0636
2016-03-03 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 22.2519 | 0.48894 | 0.51106 | 1.2445 | 17.8807 | 3034.4758 | 1475.5523 | 1558.9235
2016-03-03 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 65.5802 | 0.48715 | 0.51285 | 1.4871 | 44.0979 | 3217.6984 | 1547.8818 | 1669.8166
2016-03-03 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 118.7883 | 0.48693 | 0.51307 | 1.4869 | 79.8881 | 3254.16 | 1564.6283 | 1689.5317
2016-03-03 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 128.1898 | 0.4873 | 0.5127 | 1.4873 | 86.1893 | 3259.3006 | 1568.8892 | 1690.4115
2016-03-04 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 124.8464 | 0.48858 | 0.51142 | 1.4886 | 83.8692 | 3252.9695 | 1571.8769 | 1681.0926
2016-03-04 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8441 | 0.48848 | 0.51152 | 1.4885 | 83.8735 | 3253.3029 | 1571.5412 | 1681.7616
2016-03-04 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 128.9639 | 0.48784 | 0.51216 | 1.4878 | 86.6784 | 3258.1044 | 1570.8596 | 1687.2448
2016-03-04 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 138.7804 | 0.48725 | 0.51275 | 1.4873 | 93.3134 | 3266.5938 | 1572.1866 | 1694.4072
2016-03-04 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 60.2845 | 0.48895 | 0.51105 | 1.2445 | 48.4417 | 3065.0207 | 1490.5275 | 1574.4931
2016-03-04 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 58.4031 | 0.4884 | 0.5116 | 1.2442 | 46.9403 | 3064.3366 | 1488.1331 | 1576.2035
2016-03-04 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 61.4342 | 0.48777 | 0.51223 | 1.2439 | 49.3889 | 3067.731 | 1487.4064 | 1580.3247
2016-03-04 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 64.1704 | 0.48569 | 0.51431 | 1.2428 | 51.6319 | 3073.0996 | 1482.1418 | 1590.9578
2016-03-04 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 66.6889 | 0.48648 | 0.51352 | 1.2432 | 53.6412 | 3073.9201 | 1485.5374 | 1588.3827
2016-03-04 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 51.4158 | 0.48615 | 0.51385 | 1.2431 | 41.3617 | 3062.1293 | 1478.5731 | 1583.5562
2016-03-04 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 87.4781 | 0.48704 | 0.51296 | 1.487 | 58.8269 | 3232.7629 | 1554.7152 | 1678.0477
2016-03-04 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 93.8846 | 0.48756 | 0.51244 | 1.4876 | 63.113 | 3235.4178 | 1558.4668 | 1676.951
2016-03-04 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 94.3511 | 0.48731 | 0.51269 | 1.4873 | 63.4376 | 3236.5457 | 1557.8054 | 1678.7403
2016-03-04 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 136.1067 | 0.48354 | 0.51646 | 1.4835 | 91.7443 | 3276.6369 | 1559.4699 | 1717.167
2016-03-04 14:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 96.95% | 1575.446 | 1734.0188 | 3309.4648 | 160.3508 | 0.48475 | 0.51525 | 1.5817 | 101.3785 | 3410.8434 | 1624.5895 | 1786.2539
2016-03-04 15:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 96.97% | 1575.7282 | 1733.398 | 3309.1262 | 122.0859 | 0.48484 | 0.51516 | 1.5818 | 77.1812 | 3386.3074 | 1613.1487 | 1773.1588
2016-03-04 16:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.4% | 1582.8171 | 1717.8025 | 3300.6195 | 79.2903 | 0.48702 | 0.51298 | 1.5844 | 50.0436 | 3350.6631 | 1607.1893 | 1743.4738
2016-03-04 17:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.57% | 1585.4822 | 1711.9391 | 3297.4213 | 52.7517 | 0.48784 | 0.51216 | 1.5854 | 33.2732 | 3330.6946 | 1601.7142 | 1728.9803
2016-03-04 18:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.69% | 1587.459 | 1707.5902 | 3295.0492 | 57.7123 | 0.48845 | 0.51155 | 1.5861 | 36.3854 | 3331.4346 | 1605.2314 | 1726.2032
2016-03-04 19:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.21% | 1579.584 | 1724.9151 | 3304.4992 | 111.3253 | 0.48603 | 0.51397 | 1.5832 | 70.3152 | 3374.8144 | 1613.7591 | 1761.0553
2016-03-04 20:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.79% | 1589.0439 | 1704.1033 | 3293.1473 | 53.4046 | 0.48894 | 0.51106 | 1.5867 | 33.6572 | 3326.8044 | 1605.5002 | 1721.3043
2016-03-04 21:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.43% | 1583.2336 | 1716.8861 | 3300.1197 | 78.6962 | 0.48715 | 0.51285 | 1.5846 | 49.6638 | 3349.7835 | 1607.4272 | 1742.3563
2016-03-04 22:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.39% | 1582.5371 | 1718.4184 | 3300.9555 | 142.546 | 0.48693 | 0.51307 | 1.5843 | 89.9729 | 3390.9284 | 1626.348 | 1764.5804
2016-03-04 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.46% | 1583.7409 | 1715.77 | 3299.5109 | 153.8277 | 0.4873 | 0.5127 | 1.5848 | 97.0665 | 3396.5774 | 1631.0419 | 1765.5355
2016-03-05 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9012 | 1706.6173 | 3294.5185 | 149.8157 | 0.48858 | 0.51142 | 1.5863 | 94.4434 | 3388.9619 | 1634.0449 | 1754.917
2016-03-05 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.7% | 1587.56 | 1707.368 | 3294.928 | 149.8129 | 0.48848 | 0.51152 | 1.5862 | 94.4491 | 3389.3771 | 1633.6965 | 1755.6806
2016-03-05 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.57% | 1585.4891 | 1711.924 | 3297.4131 | 154.7567 | 0.48784 | 0.51216 | 1.5854 | 97.613 | 3395.026 | 1633.1089 | 1761.9172
2016-03-05 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.45% | 1583.5655 | 1716.1558 | 3299.7214 | 166.5365 | 0.48725 | 0.51275 | 1.5847 | 105.0902 | 3404.8115 | 1634.7708 | 1770.0407
2016-03-05 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 120.5689 | 0.48895 | 0.51105 | 1.4889 | 80.9759 | 3248.9409 | 1571.628 | 1677.3128
2016-03-05 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 116.8063 | 0.4884 | 0.5116 | 1.4884 | 78.4776 | 3248.1499 | 1568.6564 | 1679.4936
2016-03-05 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 61.4342 | 0.48777 | 0.51223 | 1.2439 | 49.3889 | 3067.731 | 1487.4064 | 1580.3247
2016-03-05 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 64.1704 | 0.48569 | 0.51431 | 1.2428 | 51.6319 | 3073.0996 | 1482.1418 | 1590.9578
2016-03-05 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 66.6889 | 0.48648 | 0.51352 | 1.2432 | 53.6412 | 3073.9201 | 1485.5374 | 1588.3827
2016-03-05 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 51.4158 | 0.48615 | 0.51385 | 1.2431 | 41.3617 | 3062.1293 | 1478.5731 | 1583.5562
2016-03-05 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 43.739 | 0.48704 | 0.51296 | 1.2435 | 35.1735 | 3054.611 | 1478.2561 | 1576.3549
2016-03-05 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 46.9423 | 0.48756 | 0.51244 | 1.2438 | 37.7416 | 3056.3981 | 1481.0883 | 1575.3098
2016-03-05 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 47.1755 | 0.48731 | 0.51269 | 1.2437 | 37.933 | 3056.9742 | 1480.4027 | 1576.5714
2016-03-05 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 68.0534 | 0.48354 | 0.51646 | 1.2418 | 54.8034 | 3079.486 | 1477.1347 | 1602.3514
2016-03-05 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 66.8128 | 0.48475 | 0.51525 | 1.2424 | 53.7782 | 3076.6493 | 1480.327 | 1596.3223
2016-03-05 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 50.8691 | 0.48484 | 0.51516 | 1.2424 | 40.9436 | 3063.6844 | 1474.3694 | 1589.3151
2016-03-05 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 33.0376 | 0.48702 | 0.51298 | 1.2435 | 26.568 | 3046.0371 | 1474.0011 | 1572.036
2016-03-05 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 21.9799 | 0.48784 | 0.51216 | 1.2439 | 17.6698 | 3035.9088 | 1472.1421 | 1563.7667
2016-03-05 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 24.0468 | 0.48845 | 0.51155 | 1.2442 | 19.3267 | 3036.6533 | 1474.7869 | 1561.8665
2016-03-05 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 46.3855 | 0.48603 | 0.51397 | 1.243 | 37.317 | 3058.2782 | 1476.2146 | 1582.0636
2016-03-05 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 22.2519 | 0.48894 | 0.51106 | 1.2445 | 17.8807 | 3034.4758 | 1475.5523 | 1558.9235
2016-03-05 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 65.5802 | 0.48715 | 0.51285 | 1.4871 | 44.0979 | 3217.6984 | 1547.8818 | 1669.8166
2016-03-05 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 118.7883 | 0.48693 | 0.51307 | 1.4869 | 79.8881 | 3254.16 | 1564.6283 | 1689.5317
2016-03-05 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 128.1898 | 0.4873 | 0.5127 | 1.4873 | 86.1893 | 3259.3006 | 1568.8892 | 1690.4115
2016-03-06 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 124.8464 | 0.48858 | 0.51142 | 1.4886 | 83.8692 | 3252.9695 | 1571.8769 | 1681.0926
2016-03-06 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8441 | 0.48848 | 0.51152 | 1.4885 | 83.8735 | 3253.3029 | 1571.5412 | 1681.7616
2016-03-06 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 128.9639 | 0.48784 | 0.51216 | 1.4878 | 86.6784 | 3258.1044 | 1570.8596 | 1687.2448
2016-03-06 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 138.7804 | 0.48725 | 0.51275 | 1.4873 | 93.3134 | 3266.5938 | 1572.1866 | 1694.4072
2016-03-06 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 120.5689 | 0.48895 | 0.51105 | 1.4889 | 80.9759 | 3248.9409 | 1571.628 | 1677.3128
2016-03-06 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 58.4031 | 0.4884 | 0.5116 | 1.2442 | 46.9403 | 3064.3366 | 1488.1331 | 1576.2035
2016-03-06 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 61.4342 | 0.48777 | 0.51223 | 1.2439 | 49.3889 | 3067.731 | 1487.4064 | 1580.3247
2016-03-06 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 64.1704 | 0.48569 | 0.51431 | 1.2428 | 51.6319 | 3073.0996 | 1482.1418 | 1590.9578
2016-03-06 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 66.6889 | 0.48648 | 0.51352 | 1.2432 | 53.6412 | 3073.9201 | 1485.5374 | 1588.3827
2016-03-06 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 51.4158 | 0.48615 | 0.51385 | 1.2431 | 41.3617 | 3062.1293 | 1478.5731 | 1583.5562
2016-03-06 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 43.739 | 0.48704 | 0.51296 | 1.2435 | 35.1735 | 3054.611 | 1478.2561 | 1576.3549
2016-03-06 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 46.9423 | 0.48756 | 0.51244 | 1.2438 | 37.7416 | 3056.3981 | 1481.0883 | 1575.3098
2016-03-06 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 47.1755 | 0.48731 | 0.51269 | 1.2437 | 37.933 | 3056.9742 | 1480.4027 | 1576.5714
2016-03-06 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 68.0534 | 0.48354 | 0.51646 | 1.2418 | 54.8034 | 3079.486 | 1477.1347 | 1602.3514
2016-03-06 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 66.8128 | 0.48475 | 0.51525 | 1.2424 | 53.7782 | 3076.6493 | 1480.327 | 1596.3223
2016-03-06 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 50.8691 | 0.48484 | 0.51516 | 1.2424 | 40.9436 | 3063.6844 | 1474.3694 | 1589.3151
2016-03-06 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 33.0376 | 0.48702 | 0.51298 | 1.2435 | 26.568 | 3046.0371 | 1474.0011 | 1572.036
2016-03-06 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 21.9799 | 0.48784 | 0.51216 | 1.2439 | 17.6698 | 3035.9088 | 1472.1421 | 1563.7667
2016-03-06 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 24.0468 | 0.48845 | 0.51155 | 1.2442 | 19.3267 | 3036.6533 | 1474.7869 | 1561.8665
2016-03-06 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 46.3855 | 0.48603 | 0.51397 | 1.243 | 37.317 | 3058.2782 | 1476.2146 | 1582.0636
2016-03-06 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 22.2519 | 0.48894 | 0.51106 | 1.2445 | 17.8807 | 3034.4758 | 1475.5523 | 1558.9235
2016-03-06 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 65.5802 | 0.48715 | 0.51285 | 1.4871 | 44.0979 | 3217.6984 | 1547.8818 | 1669.8166
2016-03-06 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 118.7883 | 0.48693 | 0.51307 | 1.4869 | 79.8881 | 3254.16 | 1564.6283 | 1689.5317
2016-03-06 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 128.1898 | 0.4873 | 0.5127 | 1.4873 | 86.1893 | 3259.3006 | 1568.8892 | 1690.4115
2016-03-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 124.8464 | 0.48858 | 0.51142 | 1.4886 | 83.8692 | 3252.9695 | 1571.8769 | 1681.0926
2016-03-07 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8441 | 0.48848 | 0.51152 | 1.4885 | 83.8735 | 3253.3029 | 1571.5412 | 1681.7616
2016-03-07 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 128.9639 | 0.48784 | 0.51216 | 1.4878 | 86.6784 | 3258.1044 | 1570.8596 | 1687.2448
2016-03-07 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 138.7804 | 0.48725 | 0.51275 | 1.4873 | 93.3134 | 3266.5938 | 1572.1866 | 1694.4072
2016-03-07 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 120.5689 | 0.48895 | 0.51105 | 1.4889 | 80.9759 | 3248.9409 | 1571.628 | 1677.3128
2016-03-07 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 116.8063 | 0.4884 | 0.5116 | 1.4884 | 78.4776 | 3248.1499 | 1568.6564 | 1679.4936
2016-03-07 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 122.8684 | 0.48777 | 0.51223 | 1.4878 | 82.5855 | 3254.2334 | 1568.635 | 1685.5984
2016-03-07 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 128.3409 | 0.48569 | 0.51431 | 1.4857 | 86.3848 | 3264.5616 | 1563.7793 | 1700.7823
2016-03-07 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 66.6889 | 0.48648 | 0.51352 | 1.2432 | 53.6412 | 3073.9201 | 1485.5374 | 1588.3827
2016-03-07 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 51.4158 | 0.48615 | 0.51385 | 1.2431 | 41.3617 | 3062.1293 | 1478.5731 | 1583.5562
2016-03-07 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 43.739 | 0.48704 | 0.51296 | 1.2435 | 35.1735 | 3054.611 | 1478.2561 | 1576.3549
2016-03-07 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 46.9423 | 0.48756 | 0.51244 | 1.2438 | 37.7416 | 3056.3981 | 1481.0883 | 1575.3098
2016-03-07 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 47.1755 | 0.48731 | 0.51269 | 1.2437 | 37.933 | 3056.9742 | 1480.4027 | 1576.5714
2016-03-07 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 68.0534 | 0.48354 | 0.51646 | 1.2418 | 54.8034 | 3079.486 | 1477.1347 | 1602.3514
2016-03-07 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 66.8128 | 0.48475 | 0.51525 | 1.2424 | 53.7782 | 3076.6493 | 1480.327 | 1596.3223
2016-03-07 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 50.8691 | 0.48484 | 0.51516 | 1.2424 | 40.9436 | 3063.6844 | 1474.3694 | 1589.3151
2016-03-07 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 33.0376 | 0.48702 | 0.51298 | 1.2435 | 26.568 | 3046.0371 | 1474.0011 | 1572.036
2016-03-07 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 21.9799 | 0.48784 | 0.51216 | 1.2439 | 17.6698 | 3035.9088 | 1472.1421 | 1563.7667
2016-03-07 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 24.0468 | 0.48845 | 0.51155 | 1.2442 | 19.3267 | 3036.6533 | 1474.7869 | 1561.8665
2016-03-07 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 46.3855 | 0.48603 | 0.51397 | 1.243 | 37.317 | 3058.2782 | 1476.2146 | 1582.0636
2016-03-07 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 22.2519 | 0.48894 | 0.51106 | 1.2445 | 17.8807 | 3034.4758 | 1475.5523 | 1558.9235
2016-03-07 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 32.7901 | 0.48715 | 0.51285 | 1.2436 | 26.3676 | 3045.6444 | 1474.2913 | 1571.3531
2016-03-07 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 59.3942 | 0.48693 | 0.51307 | 1.2435 | 47.765 | 3067.3632 | 1484.0619 | 1583.3014
2016-03-07 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 128.1898 | 0.4873 | 0.5127 | 1.4873 | 86.1893 | 3259.3006 | 1568.8892 | 1690.4115
2016-03-08 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 124.8464 | 0.48858 | 0.51142 | 1.4886 | 83.8692 | 3252.9695 | 1571.8769 | 1681.0926
2016-03-08 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8441 | 0.48848 | 0.51152 | 1.4885 | 83.8735 | 3253.3029 | 1571.5412 | 1681.7616
2016-03-08 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-08 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-08 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-08 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-08 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-08 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-08 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-08 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 102.8316 | 0.48704 | 0.51296 | 1.487 | 69.1518 | 3243.0878 | 1559.7438 | 1683.344
2016-03-08 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 87.4781 | 0.48756 | 0.51244 | 1.4876 | 58.8063 | 3231.1111 | 1556.367 | 1674.7441
2016-03-08 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-08 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 94.3511 | 0.48354 | 0.51646 | 1.4835 | 63.5984 | 3248.491 | 1545.8601 | 1702.6309
2016-03-08 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.95% | 1518.8915 | 1662.217 | 3181.1085 | 136.1067 | 0.48475 | 0.51525 | 1.4848 | 91.6696 | 3272.7781 | 1563.3286 | 1709.4495
2016-03-08 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 133.6256 | 0.48484 | 0.51516 | 1.4848 | 89.9933 | 3270.8298 | 1562.7959 | 1708.0339
2016-03-08 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 101.7382 | 0.48702 | 0.51298 | 1.487 | 68.4175 | 3242.4195 | 1559.3187 | 1683.1008
2016-03-08 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 66.0752 | 0.48784 | 0.51216 | 1.4878 | 44.4101 | 3215.8427 | 1550.2325 | 1665.6101
2016-03-08 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 43.9597 | 0.48845 | 0.51155 | 1.4884 | 29.5339 | 3199.0606 | 1544.8991 | 1654.1615
2016-03-08 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-08 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-08 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 44.5038 | 0.48715 | 0.51285 | 1.4871 | 29.9256 | 3203.5261 | 1540.9778 | 1662.5483
2016-03-08 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-08 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-08 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-09 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-09 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-09 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-09 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-09 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-09 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-09 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-09 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-09 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-09 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-09 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-09 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-09 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-09 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-09 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-09 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-09 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-09 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-09 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-09 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.0969 | 1447.6643 | 2820.7612 | 37.1084 | 0.48894 | 0.51106 | 1.1956 | 31.0381 | 2851.7994 | 1388.2726 | 1463.5267
2016-03-09 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-09 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.39% | 1367.4744 | 1455.5359 | 2823.0103 | 26.2321 | 0.48693 | 0.51307 | 1.1948 | 21.9557 | 2844.9659 | 1378.1653 | 1466.8006
2016-03-09 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-09 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-10 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-10 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-10 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.45% | 1583.5655 | 1716.1558 | 3299.7214 | 154.7567 | 0.48725 | 0.51275 | 1.5847 | 97.6567 | 3397.3781 | 1631.1489 | 1766.2292
2016-03-10 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.79% | 1589.0789 | 1704.0263 | 3293.1053 | 166.5365 | 0.48895 | 0.51105 | 1.5867 | 104.9553 | 3398.0606 | 1640.3966 | 1757.664
2016-03-10 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.68% | 1587.308 | 1707.9225 | 3295.2304 | 144.6827 | 0.4884 | 0.5116 | 1.5861 | 91.2201 | 3386.4506 | 1631.8601 | 1754.5904
2016-03-10 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.55% | 1585.2588 | 1712.4306 | 3297.6894 | 140.1675 | 0.48777 | 0.51223 | 1.5853 | 88.4156 | 3386.105 | 1628.3855 | 1757.7195
2016-03-10 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-10 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-10 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-10 09:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.41% | 1582.8855 | 1717.6518 | 3300.5373 | 123.3979 | 0.48704 | 0.51296 | 1.5845 | 77.8806 | 3378.4179 | 1620.8166 | 1757.6013
2016-03-10 10:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.51% | 1584.5775 | 1713.9295 | 3298.507 | 104.9737 | 0.48756 | 0.51244 | 1.5851 | 66.2263 | 3364.7333 | 1616.867 | 1747.8664
2016-03-10 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-10 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 94.3511 | 0.48354 | 0.51646 | 1.4835 | 63.5984 | 3248.491 | 1545.8601 | 1702.6309
2016-03-10 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.95% | 1518.8915 | 1662.217 | 3181.1085 | 136.1067 | 0.48475 | 0.51525 | 1.4848 | 91.6696 | 3272.7781 | 1563.3286 | 1709.4495
2016-03-10 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 133.6256 | 0.48484 | 0.51516 | 1.4848 | 89.9933 | 3270.8298 | 1562.7959 | 1708.0339
2016-03-10 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 101.7382 | 0.48702 | 0.51298 | 1.487 | 68.4175 | 3242.4195 | 1559.3187 | 1683.1008
2016-03-10 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 66.0752 | 0.48784 | 0.51216 | 1.4878 | 44.4101 | 3215.8427 | 1550.2325 | 1665.6101
2016-03-10 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 43.9597 | 0.48845 | 0.51155 | 1.4884 | 29.5339 | 3199.0606 | 1544.8991 | 1654.1615
2016-03-10 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-10 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-10 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-10 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.39% | 1367.4744 | 1455.5359 | 2823.0103 | 26.2321 | 0.48693 | 0.51307 | 1.1948 | 21.9557 | 2844.9659 | 1378.1653 | 1466.8006
2016-03-10 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-10 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-11 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-11 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-11 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-11 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-11 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-11 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-11 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-11 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-11 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-11 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-11 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-11 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-11 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-11 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-11 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-11 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-11 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-11 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-11 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-11 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-11 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-11 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-11 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-11 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-12 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-12 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-12 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-12 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-12 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-12 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-12 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-12 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-12 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.23% | 1365.2852 | 1458.6007 | 2823.8859 | 53.3511 | 0.48615 | 0.51385 | 1.1945 | 44.6654 | 2868.5513 | 1386.9995 | 1481.5518
2016-03-12 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.41% | 1367.7755 | 1455.1144 | 2822.8898 | 41.1326 | 0.48704 | 0.51296 | 1.1948 | 34.4259 | 2857.3157 | 1384.5423 | 1472.7734
2016-03-12 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 34.9912 | 0.48756 | 0.51244 | 1.195 | 29.2808 | 2851.5858 | 1383.5137 | 1468.0721
2016-03-12 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.5538 | 0.48731 | 0.51269 | 1.1949 | 31.4278 | 2854.0209 | 1383.8324 | 1470.1884
2016-03-12 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-12 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-12 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-12 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-12 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-12 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-12 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-12 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-12 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-12 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-12 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-12 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-13 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-13 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0252 | 1451.9647 | 2821.9899 | 49.9376 | 0.48784 | 0.51216 | 1.1951 | 41.784 | 2863.7739 | 1390.4092 | 1473.3647
2016-03-13 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.363 | 1454.2917 | 2822.6548 | 51.5856 | 0.48725 | 0.51275 | 1.1949 | 43.1714 | 2865.8262 | 1389.3984 | 1476.4278
2016-03-13 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-13 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-13 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.55% | 1369.8262 | 1452.2433 | 2822.0695 | 46.7225 | 0.48777 | 0.51223 | 1.1951 | 39.0948 | 2861.1643 | 1388.8955 | 1472.2688
2016-03-13 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.14% | 1363.9745 | 1460.4357 | 2824.4102 | 49.1474 | 0.48569 | 0.51431 | 1.1943 | 41.1525 | 2865.5627 | 1383.9618 | 1481.6009
2016-03-13 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3827 | 1395.2025 | 2706.5852 | 38.5023 | 0.48648 | 0.51352 | 1.1459 | 33.5987 | 2740.1839 | 1327.7278 | 1412.4561
2016-03-13 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.23% | 1310.5047 | 1396.3439 | 2706.8486 | 40.0133 | 0.48615 | 0.51385 | 1.1458 | 34.9203 | 2741.7689 | 1327.4814 | 1414.2875
2016-03-13 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 30.8495 | 0.48704 | 0.51296 | 1.1461 | 26.9166 | 2733.0481 | 1326.0046 | 1407.0436
2016-03-13 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-13 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6073 | 1392.3106 | 2705.9178 | 28.1654 | 0.48731 | 0.51269 | 1.1462 | 24.573 | 2730.4908 | 1325.5818 | 1404.909
2016-03-13 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.71% | 1303.4689 | 1405.4904 | 2708.9593 | 28.3053 | 0.48354 | 0.51646 | 1.1451 | 24.7194 | 2733.6788 | 1315.4219 | 1418.2569
2016-03-13 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.95% | 1306.7244 | 1401.2582 | 2707.9827 | 40.832 | 0.48475 | 0.51525 | 1.1454 | 35.6479 | 2743.6306 | 1324.0048 | 1419.6257
2016-03-13 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.97% | 1306.9585 | 1400.954 | 2707.9125 | 40.0877 | 0.48484 | 0.51516 | 1.1455 | 34.9973 | 2742.9097 | 1323.9265 | 1418.9832
2016-03-13 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.4% | 1312.8382 | 1393.3103 | 2706.1485 | 30.5215 | 0.48702 | 0.51298 | 1.1461 | 26.6306 | 2732.7791 | 1325.8079 | 1406.9712
2016-03-13 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0488 | 1390.4366 | 2705.4854 | 19.8226 | 0.48784 | 0.51216 | 1.1464 | 17.2919 | 2722.7772 | 1323.4845 | 1399.2928
2016-03-13 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6884 | 1388.3051 | 2704.9935 | 13.1879 | 0.48845 | 0.51155 | 1.1465 | 11.5024 | 2716.4959 | 1322.3067 | 1394.1892
2016-03-13 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.21% | 1310.1567 | 1396.7963 | 2706.953 | 14.4281 | 0.48603 | 0.51397 | 1.1458 | 12.592 | 2719.545 | 1316.2767 | 1403.2683
2016-03-13 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.003 | 1386.5961 | 2704.5991 | 27.8313 | 0.48894 | 0.51106 | 1.1467 | 24.2712 | 2728.8703 | 1329.8701 | 1399.0002
2016-03-13 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-13 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-13 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-13 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-14 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-14 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-14 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-14 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-14 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-14 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-14 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-14 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.1999 | 1457.3201 | 2823.52 | 51.3364 | 0.48648 | 0.51352 | 1.1946 | 42.974 | 2866.494 | 1387.1059 | 1479.3881
2016-03-14 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.23% | 1365.2852 | 1458.6007 | 2823.8859 | 53.3511 | 0.48615 | 0.51385 | 1.1945 | 44.6654 | 2868.5513 | 1386.9995 | 1481.5518
2016-03-14 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.41% | 1367.7755 | 1455.1144 | 2822.8898 | 41.1326 | 0.48704 | 0.51296 | 1.1948 | 34.4259 | 2857.3157 | 1384.5423 | 1472.7734
2016-03-14 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 34.9912 | 0.48756 | 0.51244 | 1.195 | 29.2808 | 2851.5858 | 1383.5137 | 1468.0721
2016-03-14 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.5538 | 0.48731 | 0.51269 | 1.1949 | 31.4278 | 2854.0209 | 1383.8324 | 1470.1884
2016-03-14 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-14 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-14 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-14 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-14 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-14 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-14 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-14 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-14 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-14 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-14 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-14 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-15 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-15 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-15 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-15 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-15 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-15 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-15 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-15 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-15 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-15 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-15 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-15 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-15 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-15 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-15 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-15 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-15 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-15 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-15 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-15 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-15 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-15 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-15 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-15 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-16 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-16 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-16 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-16 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-16 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-16 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-16 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.14% | 1363.9745 | 1460.4357 | 2824.4102 | 49.1474 | 0.48569 | 0.51431 | 1.1943 | 41.1525 | 2865.5627 | 1383.9618 | 1481.6009
2016-03-16 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.1999 | 1457.3201 | 2823.52 | 51.3364 | 0.48648 | 0.51352 | 1.1946 | 42.974 | 2866.494 | 1387.1059 | 1479.3881
2016-03-16 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.23% | 1365.2852 | 1458.6007 | 2823.8859 | 53.3511 | 0.48615 | 0.51385 | 1.1945 | 44.6654 | 2868.5513 | 1386.9995 | 1481.5518
2016-03-16 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.41% | 1367.7755 | 1455.1144 | 2822.8898 | 41.1326 | 0.48704 | 0.51296 | 1.1948 | 34.4259 | 2857.3157 | 1384.5423 | 1472.7734
2016-03-16 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 34.9912 | 0.48756 | 0.51244 | 1.195 | 29.2808 | 2851.5858 | 1383.5137 | 1468.0721
2016-03-16 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6073 | 1392.3106 | 2705.9178 | 28.1654 | 0.48731 | 0.51269 | 1.1462 | 24.573 | 2730.4908 | 1325.5818 | 1404.909
2016-03-16 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.71% | 1303.4689 | 1405.4904 | 2708.9593 | 28.3053 | 0.48354 | 0.51646 | 1.1451 | 24.7194 | 2733.6788 | 1315.4219 | 1418.2569
2016-03-16 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.95% | 1306.7244 | 1401.2582 | 2707.9827 | 40.832 | 0.48475 | 0.51525 | 1.1454 | 35.6479 | 2743.6306 | 1324.0048 | 1419.6257
2016-03-16 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.97% | 1306.9585 | 1400.954 | 2707.9125 | 40.0877 | 0.48484 | 0.51516 | 1.1455 | 34.9973 | 2742.9097 | 1323.9265 | 1418.9832
2016-03-16 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.4% | 1312.8382 | 1393.3103 | 2706.1485 | 30.5215 | 0.48702 | 0.51298 | 1.1461 | 26.6306 | 2732.7791 | 1325.8079 | 1406.9712
2016-03-16 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0488 | 1390.4366 | 2705.4854 | 19.8226 | 0.48784 | 0.51216 | 1.1464 | 17.2919 | 2722.7772 | 1323.4845 | 1399.2928
2016-03-16 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6884 | 1388.3051 | 2704.9935 | 13.1879 | 0.48845 | 0.51155 | 1.1465 | 11.5024 | 2716.4959 | 1322.3067 | 1394.1892
2016-03-16 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.21% | 1313.3499 | 1398.3127 | 2711.6625 | 12.0234 | 0.48603 | 0.51397 | 1.1215 | 10.7207 | 2722.3833 | 1318.5604 | 1403.8228
2016-03-16 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.79% | 1321.2153 | 1388.4808 | 2709.6962 | 23.1928 | 0.48894 | 0.51106 | 1.1222 | 20.6666 | 2730.3628 | 1331.32 | 1399.0428
2016-03-16 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.43% | 1316.3843 | 1394.5196 | 2710.9039 | 11.126 | 0.48715 | 0.51285 | 1.1218 | 9.9181 | 2720.822 | 1321.2159 | 1399.6061
2016-03-16 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.39% | 1315.8052 | 1395.2435 | 2711.0487 | 16.395 | 0.48693 | 0.51307 | 1.1217 | 14.6158 | 2725.6645 | 1322.9221 | 1402.7424
2016-03-16 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6045 | 1392.3141 | 2705.9186 | 35.6365 | 0.4873 | 0.5127 | 1.1462 | 31.0912 | 2737.0099 | 1328.7554 | 1408.2545
2016-03-16 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.0552 | 1387.8282 | 2704.8834 | 38.4569 | 0.48858 | 0.51142 | 1.1466 | 33.5407 | 2738.4241 | 1333.4427 | 1404.9814
2016-03-17 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.7% | 1316.7722 | 1388.1962 | 2704.9683 | 37.4539 | 0.48848 | 0.51152 | 1.1465 | 32.6668 | 2737.6352 | 1332.7293 | 1404.9059
2016-03-17 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0545 | 1390.4292 | 2705.4837 | 37.4532 | 0.48784 | 0.51216 | 1.1464 | 32.6716 | 2738.1553 | 1330.9931 | 1407.1622
2016-03-17 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.363 | 1454.2917 | 2822.6548 | 51.5856 | 0.48725 | 0.51275 | 1.1949 | 43.1714 | 2865.8262 | 1389.3984 | 1476.4278
2016-03-17 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.1272 | 1447.6219 | 2820.7491 | 55.5122 | 0.48895 | 0.51105 | 1.1956 | 46.4312 | 2867.1803 | 1395.8296 | 1471.3507
2016-03-17 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.68% | 1371.5969 | 1449.7644 | 2821.3612 | 48.2276 | 0.4884 | 0.5116 | 1.1954 | 40.3456 | 2861.7068 | 1391.3018 | 1470.4051
2016-03-17 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.55% | 1369.8262 | 1452.2433 | 2822.0695 | 46.7225 | 0.48777 | 0.51223 | 1.1951 | 39.0948 | 2861.1643 | 1388.8955 | 1472.2688
2016-03-17 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.14% | 1363.9745 | 1460.4357 | 2824.4102 | 49.1474 | 0.48569 | 0.51431 | 1.1943 | 41.1525 | 2865.5627 | 1383.9618 | 1481.6009
2016-03-17 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.1999 | 1457.3201 | 2823.52 | 51.3364 | 0.48648 | 0.51352 | 1.1946 | 42.974 | 2866.494 | 1387.1059 | 1479.3881
2016-03-17 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.23% | 1365.2852 | 1458.6007 | 2823.8859 | 53.3511 | 0.48615 | 0.51385 | 1.1945 | 44.6654 | 2868.5513 | 1386.9995 | 1481.5518
2016-03-17 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 30.8495 | 0.48704 | 0.51296 | 1.1461 | 26.9166 | 2733.0481 | 1326.0046 | 1407.0436
2016-03-17 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-17 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6073 | 1392.3106 | 2705.9178 | 28.1654 | 0.48731 | 0.51269 | 1.1462 | 24.573 | 2730.4908 | 1325.5818 | 1404.909
2016-03-17 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.71% | 1303.4689 | 1405.4904 | 2708.9593 | 28.3053 | 0.48354 | 0.51646 | 1.1451 | 24.7194 | 2733.6788 | 1315.4219 | 1418.2569
2016-03-17 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-17 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-17 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-17 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-17 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 17.5839 | 0.48845 | 0.51155 | 1.1954 | 14.7099 | 2836.0189 | 1378.9124 | 1457.1065
2016-03-17 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-17 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.0969 | 1447.6643 | 2820.7612 | 37.1084 | 0.48894 | 0.51106 | 1.1956 | 31.0381 | 2851.7994 | 1388.2726 | 1463.5267
2016-03-17 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-17 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-17 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-17 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-18 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-18 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-18 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-18 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-18 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-18 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-18 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.14% | 1363.9745 | 1460.4357 | 2824.4102 | 49.1474 | 0.48569 | 0.51431 | 1.1943 | 41.1525 | 2865.5627 | 1383.9618 | 1481.6009
2016-03-18 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3827 | 1395.2025 | 2706.5852 | 38.5023 | 0.48648 | 0.51352 | 1.1459 | 33.5987 | 2740.1839 | 1327.7278 | 1412.4561
2016-03-18 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.23% | 1310.5047 | 1396.3439 | 2706.8486 | 40.0133 | 0.48615 | 0.51385 | 1.1458 | 34.9203 | 2741.7689 | 1327.4814 | 1414.2875
2016-03-18 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 30.8495 | 0.48704 | 0.51296 | 1.1461 | 26.9166 | 2733.0481 | 1326.0046 | 1407.0436
2016-03-18 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-18 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.5538 | 0.48731 | 0.51269 | 1.1949 | 31.4278 | 2854.0209 | 1383.8324 | 1470.1884
2016-03-18 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-18 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-18 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-18 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-18 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-18 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 17.5839 | 0.48845 | 0.51155 | 1.1954 | 14.7099 | 2836.0189 | 1378.9124 | 1457.1065
2016-03-18 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-18 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-18 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 44.5038 | 0.48715 | 0.51285 | 1.4871 | 29.9256 | 3203.5261 | 1540.9778 | 1662.5483
2016-03-18 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-18 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-18 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-19 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-19 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-19 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-19 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-19 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-19 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-19 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-19 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-19 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-19 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 102.8316 | 0.48704 | 0.51296 | 1.487 | 69.1518 | 3243.0878 | 1559.7438 | 1683.344
2016-03-19 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 87.4781 | 0.48756 | 0.51244 | 1.4876 | 58.8063 | 3231.1111 | 1556.367 | 1674.7441
2016-03-19 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-19 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 94.3511 | 0.48354 | 0.51646 | 1.4835 | 63.5984 | 3248.491 | 1545.8601 | 1702.6309
2016-03-19 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-19 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-19 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-19 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-19 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-19 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-19 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-19 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 44.5038 | 0.48715 | 0.51285 | 1.4871 | 29.9256 | 3203.5261 | 1540.9778 | 1662.5483
2016-03-19 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-19 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-19 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-20 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-20 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-20 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-20 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-20 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-20 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-20 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-20 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-20 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-20 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 102.8316 | 0.48704 | 0.51296 | 1.487 | 69.1518 | 3243.0878 | 1559.7438 | 1683.344
2016-03-20 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-20 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-20 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-20 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-20 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-20 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-20 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-20 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-20 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.21% | 1310.1567 | 1396.7963 | 2706.953 | 14.4281 | 0.48603 | 0.51397 | 1.1458 | 12.592 | 2719.545 | 1316.2767 | 1403.2683
2016-03-20 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.003 | 1386.5961 | 2704.5991 | 27.8313 | 0.48894 | 0.51106 | 1.1467 | 24.2712 | 2728.8703 | 1329.8701 | 1399.0002
2016-03-20 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.43% | 1316.3843 | 1394.5196 | 2710.9039 | 11.126 | 0.48715 | 0.51285 | 1.1218 | 9.9181 | 2720.822 | 1321.2159 | 1399.6061
2016-03-20 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.39% | 1315.8052 | 1395.2435 | 2711.0487 | 16.395 | 0.48693 | 0.51307 | 1.1217 | 14.6158 | 2725.6645 | 1322.9221 | 1402.7424
2016-03-20 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.46% | 1316.8061 | 1393.9923 | 2710.7985 | 29.6971 | 0.4873 | 0.5127 | 1.1218 | 26.4721 | 2737.2706 | 1329.7061 | 1407.5644
2016-03-20 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.2652 | 1389.6684 | 2709.9337 | 32.0474 | 0.48858 | 0.51142 | 1.1221 | 28.5591 | 2738.4927 | 1334.2188 | 1404.274
2016-03-21 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.7% | 1319.9815 | 1390.0231 | 2710.0046 | 31.2116 | 0.48848 | 0.51152 | 1.1221 | 27.8149 | 2737.8195 | 1333.5685 | 1404.2509
2016-03-21 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2596 | 1392.1754 | 2710.4351 | 31.211 | 0.48784 | 0.51216 | 1.122 | 27.8183 | 2738.2534 | 1331.8306 | 1406.4228
2016-03-21 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.459 | 1392.5032 | 2705.9623 | 38.6892 | 0.48725 | 0.51275 | 1.1462 | 33.755 | 2739.7173 | 1329.9062 | 1409.8111
2016-03-21 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.032 | 1386.5584 | 2704.5904 | 41.6341 | 0.48895 | 0.51105 | 1.1467 | 36.3083 | 2740.8987 | 1335.7849 | 1405.1138
2016-03-21 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.68% | 1316.5631 | 1388.4679 | 2705.0311 | 36.1707 | 0.4884 | 0.5116 | 1.1465 | 31.5482 | 2736.5793 | 1331.9714 | 1404.6079
2016-03-21 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.55% | 1314.8635 | 1390.6774 | 2705.5409 | 35.0419 | 0.48777 | 0.51223 | 1.1463 | 30.5687 | 2736.1097 | 1329.7741 | 1406.3356
2016-03-21 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.14% | 1309.2466 | 1397.9794 | 2707.226 | 36.8605 | 0.48569 | 0.51431 | 1.1457 | 32.1727 | 2739.3988 | 1324.8725 | 1414.5263
2016-03-21 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3827 | 1395.2025 | 2706.5852 | 38.5023 | 0.48648 | 0.51352 | 1.1459 | 33.5987 | 2740.1839 | 1327.7278 | 1412.4561
2016-03-21 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.23% | 1310.5047 | 1396.3439 | 2706.8486 | 40.0133 | 0.48615 | 0.51385 | 1.1458 | 34.9203 | 2741.7689 | 1327.4814 | 1414.2875
2016-03-21 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 30.8495 | 0.48704 | 0.51296 | 1.1461 | 26.9166 | 2733.0481 | 1326.0046 | 1407.0436
2016-03-21 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-21 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.5538 | 0.48731 | 0.51269 | 1.1949 | 31.4278 | 2854.0209 | 1383.8324 | 1470.1884
2016-03-21 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-21 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-21 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-21 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-21 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-21 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 17.5839 | 0.48845 | 0.51155 | 1.1954 | 14.7099 | 2836.0189 | 1378.9124 | 1457.1065
2016-03-21 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-21 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.003 | 1386.5961 | 2704.5991 | 27.8313 | 0.48894 | 0.51106 | 1.1467 | 24.2712 | 2728.8703 | 1329.8701 | 1399.0002
2016-03-21 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.43% | 1316.3843 | 1394.5196 | 2710.9039 | 11.126 | 0.48715 | 0.51285 | 1.1218 | 9.9181 | 2720.822 | 1321.2159 | 1399.6061
2016-03-21 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.39% | 1315.8052 | 1395.2435 | 2711.0487 | 16.395 | 0.48693 | 0.51307 | 1.1217 | 14.6158 | 2725.6645 | 1322.9221 | 1402.7424
2016-03-21 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6045 | 1392.3141 | 2705.9186 | 35.6365 | 0.4873 | 0.5127 | 1.1462 | 31.0912 | 2737.0099 | 1328.7554 | 1408.2545
2016-03-21 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.0552 | 1387.8282 | 2704.8834 | 38.4569 | 0.48858 | 0.51142 | 1.1466 | 33.5407 | 2738.4241 | 1333.4427 | 1404.9814
2016-03-22 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.7% | 1319.9815 | 1390.0231 | 2710.0046 | 31.2116 | 0.48848 | 0.51152 | 1.1221 | 27.8149 | 2737.8195 | 1333.5685 | 1404.2509
2016-03-22 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2596 | 1392.1754 | 2710.4351 | 31.211 | 0.48784 | 0.51216 | 1.122 | 27.8183 | 2738.2534 | 1331.8306 | 1406.4228
2016-03-22 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6603 | 1394.1746 | 2710.8349 | 32.241 | 0.48725 | 0.51275 | 1.1218 | 28.7401 | 2739.575 | 1330.6639 | 1408.9111
2016-03-22 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.79% | 1321.2444 | 1388.4445 | 2709.6889 | 34.6951 | 0.48895 | 0.51105 | 1.1222 | 30.916 | 2740.6049 | 1336.3607 | 1404.2442
2016-03-22 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.68% | 1319.772 | 1390.285 | 2710.057 | 30.1422 | 0.4884 | 0.5116 | 1.1221 | 26.8623 | 2736.9193 | 1332.8916 | 1404.0277
2016-03-22 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.55% | 1318.0682 | 1392.4148 | 2710.483 | 29.2016 | 0.48777 | 0.51223 | 1.1219 | 26.0277 | 2736.5106 | 1330.7638 | 1405.7469
2016-03-22 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.14% | 1312.4376 | 1399.453 | 2711.8906 | 30.7171 | 0.48569 | 0.51431 | 1.1214 | 27.3912 | 2739.2818 | 1325.7412 | 1413.5406
2016-03-22 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.3% | 1314.5789 | 1396.7764 | 2711.3553 | 32.0852 | 0.48648 | 0.51352 | 1.1216 | 28.6061 | 2739.9614 | 1328.4953 | 1411.4662
2016-03-22 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.23% | 1313.6987 | 1397.8766 | 2711.5753 | 33.3444 | 0.48615 | 0.51385 | 1.1215 | 29.731 | 2741.3063 | 1328.1526 | 1413.1537
2016-03-22 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.41% | 1316.0949 | 1394.8813 | 2710.9763 | 25.7079 | 0.48704 | 0.51296 | 1.1218 | 22.9175 | 2733.8937 | 1327.2567 | 1406.637
2016-03-22 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-22 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6073 | 1392.3106 | 2705.9178 | 28.1654 | 0.48731 | 0.51269 | 1.1462 | 24.573 | 2730.4908 | 1325.5818 | 1404.909
2016-03-22 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-22 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-22 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-22 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-22 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-22 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 17.5839 | 0.48845 | 0.51155 | 1.1954 | 14.7099 | 2836.0189 | 1378.9124 | 1457.1065
2016-03-22 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-22 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-22 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-22 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-22 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-22 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-23 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-23 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-23 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-23 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-23 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-23 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-23 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-23 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-23 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-23 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-23 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-23 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-23 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-23 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-23 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-23 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-23 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-23 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-23 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-23 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-23 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-23 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-23 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-23 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-24 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-24 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-24 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-24 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-24 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-24 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-24 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-24 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-24 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-24 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-24 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-24 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-24 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-24 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-24 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 133.6256 | 0.48484 | 0.51516 | 1.4848 | 89.9933 | 3270.8298 | 1562.7959 | 1708.0339
2016-03-24 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 101.7382 | 0.48702 | 0.51298 | 1.487 | 68.4175 | 3242.4195 | 1559.3187 | 1683.1008
2016-03-24 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 66.0752 | 0.48784 | 0.51216 | 1.4878 | 44.4101 | 3215.8427 | 1550.2325 | 1665.6101
2016-03-24 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 43.9597 | 0.48845 | 0.51155 | 1.4884 | 29.5339 | 3199.0606 | 1544.8991 | 1654.1615
2016-03-24 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-24 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-24 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 44.5038 | 0.48715 | 0.51285 | 1.4871 | 29.9256 | 3203.5261 | 1540.9778 | 1662.5483
2016-03-24 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-24 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-24 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-25 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-25 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-25 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-25 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-25 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-25 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-25 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-25 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-25 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-25 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 102.8316 | 0.48704 | 0.51296 | 1.487 | 69.1518 | 3243.0878 | 1559.7438 | 1683.344
2016-03-25 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 87.4781 | 0.48756 | 0.51244 | 1.4876 | 58.8063 | 3231.1111 | 1556.367 | 1674.7441
2016-03-25 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-25 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-25 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-25 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-25 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.4% | 1367.7163 | 1455.1972 | 2822.9135 | 40.6953 | 0.48702 | 0.51298 | 1.1948 | 34.0601 | 2856.9736 | 1384.3043 | 1472.6693
2016-03-25 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0192 | 1451.9731 | 2821.9923 | 26.4301 | 0.48784 | 0.51216 | 1.1951 | 22.1147 | 2844.107 | 1380.8077 | 1463.2993
2016-03-25 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7274 | 1449.5817 | 2821.309 | 17.5839 | 0.48845 | 0.51155 | 1.1954 | 14.7099 | 2836.0189 | 1378.9124 | 1457.1065
2016-03-25 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-25 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.0969 | 1447.6643 | 2820.7612 | 37.1084 | 0.48894 | 0.51106 | 1.1956 | 31.0381 | 2851.7994 | 1388.2726 | 1463.5267
2016-03-25 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-25 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.39% | 1367.4744 | 1455.5359 | 2823.0103 | 26.2321 | 0.48693 | 0.51307 | 1.1948 | 21.9557 | 2844.9659 | 1378.1653 | 1466.8006
2016-03-25 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5146 | 1454.0796 | 2822.5942 | 47.5153 | 0.4873 | 0.5127 | 1.1949 | 39.7644 | 2862.3585 | 1387.892 | 1474.4666
2016-03-25 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-26 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-26 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-26 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-26 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-26 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-26 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-26 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-26 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-26 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-26 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-26 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-26 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-26 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 94.3511 | 0.48354 | 0.51646 | 1.4835 | 63.5984 | 3248.491 | 1545.8601 | 1702.6309
2016-03-26 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.95% | 1518.8915 | 1662.217 | 3181.1085 | 136.1067 | 0.48475 | 0.51525 | 1.4848 | 91.6696 | 3272.7781 | 1563.3286 | 1709.4495
2016-03-26 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 133.6256 | 0.48484 | 0.51516 | 1.4848 | 89.9933 | 3270.8298 | 1562.7959 | 1708.0339
2016-03-26 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 101.7382 | 0.48702 | 0.51298 | 1.487 | 68.4175 | 3242.4195 | 1559.3187 | 1683.1008
2016-03-26 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 66.0752 | 0.48784 | 0.51216 | 1.4878 | 44.4101 | 3215.8427 | 1550.2325 | 1665.6101
2016-03-26 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 43.9597 | 0.48845 | 0.51155 | 1.4884 | 29.5339 | 3199.0606 | 1544.8991 | 1654.1615
2016-03-26 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-26 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-26 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.43% | 1526.3995 | 1647.2009 | 3173.6005 | 44.5038 | 0.48715 | 0.51285 | 1.4871 | 29.9256 | 3203.5261 | 1540.9778 | 1662.5483
2016-03-26 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.39% | 1525.7281 | 1648.5439 | 3174.2719 | 65.5802 | 0.48693 | 0.51307 | 1.4869 | 44.1043 | 3218.3762 | 1547.204 | 1671.1723
2016-03-26 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-26 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-27 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-27 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-27 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-27 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-27 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-27 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-27 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-27 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.3061 | 1651.3877 | 3175.6939 | 128.3409 | 0.48648 | 0.51352 | 1.4865 | 86.3388 | 3262.0326 | 1566.3083 | 1695.7243
2016-03-27 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.23% | 1523.2855 | 1653.4289 | 3176.7145 | 133.3777 | 0.48615 | 0.51385 | 1.4862 | 89.7468 | 3266.4613 | 1566.9164 | 1699.5449
2016-03-27 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.41% | 1526.064 | 1647.872 | 3173.936 | 102.8316 | 0.48704 | 0.51296 | 1.487 | 69.1518 | 3243.0878 | 1559.7438 | 1683.344
2016-03-27 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.51% | 1527.6952 | 1644.6095 | 3172.3048 | 87.4781 | 0.48756 | 0.51244 | 1.4876 | 58.8063 | 3231.1111 | 1556.367 | 1674.7441
2016-03-27 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8919 | 1646.2162 | 3173.1081 | 93.8846 | 0.48731 | 0.51269 | 1.4873 | 63.1239 | 3236.232 | 1557.6525 | 1678.5795
2016-03-27 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.71% | 1515.1074 | 1669.7852 | 3184.8926 | 94.3511 | 0.48354 | 0.51646 | 1.4835 | 63.5984 | 3248.491 | 1545.8601 | 1702.6309
2016-03-27 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.95% | 1518.8915 | 1662.217 | 3181.1085 | 136.1067 | 0.48475 | 0.51525 | 1.4848 | 91.6696 | 3272.7781 | 1563.3286 | 1709.4495
2016-03-27 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.97% | 1519.1636 | 1661.6729 | 3180.8364 | 133.6256 | 0.48484 | 0.51516 | 1.4848 | 89.9933 | 3270.8298 | 1562.7959 | 1708.0339
2016-03-27 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.4% | 1525.998 | 1648.004 | 3174.002 | 101.7382 | 0.48702 | 0.51298 | 1.487 | 68.4175 | 3242.4195 | 1559.3187 | 1683.1008
2016-03-27 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5675 | 1642.8651 | 3171.4325 | 66.0752 | 0.48784 | 0.51216 | 1.4878 | 44.4101 | 3215.8427 | 1550.2325 | 1665.6101
2016-03-27 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4733 | 1639.0534 | 3169.5267 | 43.9597 | 0.48845 | 0.51155 | 1.4884 | 29.5339 | 3199.0606 | 1544.8991 | 1654.1615
2016-03-27 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.21% | 1522.881 | 1654.238 | 3177.119 | 48.0935 | 0.48603 | 0.51397 | 1.486 | 32.3639 | 3209.4829 | 1538.6107 | 1670.8722
2016-03-27 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0013 | 1635.9973 | 3167.9987 | 92.7711 | 0.48894 | 0.51106 | 1.4889 | 62.3069 | 3230.3056 | 1562.4655 | 1667.8401
2016-03-27 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-27 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-27 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9147 | 1557.128 | 3019.0427 | 59.3942 | 0.4873 | 0.5127 | 1.2437 | 47.7578 | 3066.8005 | 1485.1873 | 1581.6132
2016-03-27 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.755 | 1551.3675 | 3017.1225 | 64.0949 | 0.48858 | 0.51142 | 1.2443 | 51.5111 | 3068.6336 | 1490.9226 | 1577.7111
2016-03-28 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.7% | 1465.44 | 1551.84 | 3017.28 | 62.4232 | 0.48848 | 0.51152 | 1.2442 | 50.1698 | 3067.4498 | 1489.9469 | 1577.5028
2016-03-28 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5284 | 1554.7074 | 3018.2358 | 62.422 | 0.48784 | 0.51216 | 1.2439 | 50.1817 | 3068.4175 | 1488.0092 | 1580.4083
2016-03-28 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.7528 | 1557.3708 | 3019.1236 | 64.482 | 0.48725 | 0.51275 | 1.2436 | 51.85 | 3070.9736 | 1487.0168 | 1583.9568
2016-03-28 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8421 | 1549.7369 | 3016.579 | 69.3902 | 0.48895 | 0.51105 | 1.2445 | 55.7587 | 3072.3376 | 1494.1052 | 1578.2325
2016-03-28 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.68% | 1465.2074 | 1552.189 | 3017.3963 | 60.2845 | 0.4884 | 0.5116 | 1.2442 | 48.4523 | 3065.8487 | 1488.8716 | 1576.9771
2016-03-28 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.55% | 1463.3158 | 1555.0263 | 3018.3421 | 58.4031 | 0.48777 | 0.51223 | 1.2439 | 46.9522 | 3065.2943 | 1486.2178 | 1579.0765
2016-03-28 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.14% | 1457.0648 | 1564.4029 | 3021.4676 | 61.4342 | 0.48569 | 0.51431 | 1.2428 | 49.4303 | 3070.898 | 1481.0725 | 1589.8255
2016-03-28 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-28 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-28 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.41% | 1461.1251 | 1558.3123 | 3019.4374 | 51.4158 | 0.48704 | 0.51296 | 1.2435 | 41.347 | 3060.7844 | 1481.2628 | 1579.5216
2016-03-28 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6869 | 1555.9696 | 3018.6565 | 43.739 | 0.48756 | 0.51244 | 1.2438 | 35.1662 | 3053.8227 | 1479.8326 | 1573.9901
2016-03-28 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9178 | 1557.1234 | 3019.0411 | 46.9423 | 0.48731 | 0.51269 | 1.2437 | 37.7455 | 3056.7866 | 1480.3114 | 1576.4753
2016-03-28 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.71% | 1450.6347 | 1574.0479 | 3024.6826 | 47.1755 | 0.48354 | 0.51646 | 1.2418 | 37.9905 | 3062.6731 | 1469.0049 | 1593.6683
2016-03-28 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.95% | 1454.2578 | 1568.6132 | 3022.8711 | 68.0534 | 0.48475 | 0.51525 | 1.2424 | 54.7768 | 3077.6479 | 1480.811 | 1596.8368
2016-03-28 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.97% | 1454.5183 | 1568.2225 | 3022.7408 | 66.8128 | 0.48484 | 0.51516 | 1.2424 | 53.7764 | 3076.5172 | 1480.5912 | 1595.926
2016-03-28 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-28 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-28 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-28 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.21% | 1364.9226 | 1459.1083 | 2824.031 | 19.2374 | 0.48603 | 0.51397 | 1.1944 | 16.1062 | 2840.1372 | 1372.7506 | 1467.3865
2016-03-28 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.79% | 1318.003 | 1386.5961 | 2704.5991 | 27.8313 | 0.48894 | 0.51106 | 1.1467 | 24.2712 | 2728.8703 | 1329.8701 | 1399.0002
2016-03-28 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.43% | 1316.3843 | 1394.5196 | 2710.9039 | 11.126 | 0.48715 | 0.51285 | 1.1218 | 9.9181 | 2720.822 | 1321.2159 | 1399.6061
2016-03-28 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.39% | 1315.8052 | 1395.2435 | 2711.0487 | 16.395 | 0.48693 | 0.51307 | 1.1217 | 14.6158 | 2725.6645 | 1322.9221 | 1402.7424
2016-03-28 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6045 | 1392.3141 | 2705.9186 | 35.6365 | 0.4873 | 0.5127 | 1.1462 | 31.0912 | 2737.0099 | 1328.7554 | 1408.2545
2016-03-28 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.0552 | 1387.8282 | 2704.8834 | 38.4569 | 0.48858 | 0.51142 | 1.1466 | 33.5407 | 2738.4241 | 1333.4427 | 1404.9814
2016-03-29 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.7% | 1316.7722 | 1388.1962 | 2704.9683 | 37.4539 | 0.48848 | 0.51152 | 1.1465 | 32.6668 | 2737.6352 | 1332.7293 | 1404.9059
2016-03-29 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0545 | 1390.4292 | 2705.4837 | 37.4532 | 0.48784 | 0.51216 | 1.1464 | 32.6716 | 2738.1553 | 1330.9931 | 1407.1622
2016-03-29 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.363 | 1454.2917 | 2822.6548 | 51.5856 | 0.48725 | 0.51275 | 1.1949 | 43.1714 | 2865.8262 | 1389.3984 | 1476.4278
2016-03-29 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.1272 | 1447.6219 | 2820.7491 | 55.5122 | 0.48895 | 0.51105 | 1.1956 | 46.4312 | 2867.1803 | 1395.8296 | 1471.3507
2016-03-29 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.68% | 1371.5969 | 1449.7644 | 2821.3612 | 48.2276 | 0.4884 | 0.5116 | 1.1954 | 40.3456 | 2861.7068 | 1391.3018 | 1470.4051
2016-03-29 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.55% | 1369.8262 | 1452.2433 | 2822.0695 | 46.7225 | 0.48777 | 0.51223 | 1.1951 | 39.0948 | 2861.1643 | 1388.8955 | 1472.2688
2016-03-29 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.14% | 1363.9745 | 1460.4357 | 2824.4102 | 49.1474 | 0.48569 | 0.51431 | 1.1943 | 41.1525 | 2865.5627 | 1383.9618 | 1481.6009
2016-03-29 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.1999 | 1457.3201 | 2823.52 | 51.3364 | 0.48648 | 0.51352 | 1.1946 | 42.974 | 2866.494 | 1387.1059 | 1479.3881
2016-03-29 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.23% | 1365.2852 | 1458.6007 | 2823.8859 | 53.3511 | 0.48615 | 0.51385 | 1.1945 | 44.6654 | 2868.5513 | 1386.9995 | 1481.5518
2016-03-29 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.41% | 1312.895 | 1393.2365 | 2706.1315 | 30.8495 | 0.48704 | 0.51296 | 1.1461 | 26.9166 | 2733.0481 | 1326.0046 | 1407.0436
2016-03-29 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.2984 | 1391.4121 | 2705.7105 | 26.2434 | 0.48756 | 0.51244 | 1.1463 | 22.8947 | 2728.6051 | 1325.461 | 1403.1442
2016-03-29 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.6073 | 1392.3106 | 2705.9178 | 28.1654 | 0.48731 | 0.51269 | 1.1462 | 24.573 | 2730.4908 | 1325.5818 | 1404.909
2016-03-29 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.71% | 1303.4689 | 1405.4904 | 2708.9593 | 28.3053 | 0.48354 | 0.51646 | 1.1451 | 24.7194 | 2733.6788 | 1315.4219 | 1418.2569
2016-03-29 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.95% | 1306.7244 | 1401.2582 | 2707.9827 | 40.832 | 0.48475 | 0.51525 | 1.1454 | 35.6479 | 2743.6306 | 1324.0048 | 1419.6257
2016-03-29 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.97% | 1306.9585 | 1400.954 | 2707.9125 | 40.0877 | 0.48484 | 0.51516 | 1.1455 | 34.9973 | 2742.9097 | 1323.9265 | 1418.9832
2016-03-29 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.4% | 1312.8382 | 1393.3103 | 2706.1485 | 30.5215 | 0.48702 | 0.51298 | 1.1461 | 26.6306 | 2732.7791 | 1325.8079 | 1406.9712
2016-03-29 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0488 | 1390.4366 | 2705.4854 | 19.8226 | 0.48784 | 0.51216 | 1.1464 | 17.2919 | 2722.7772 | 1323.4845 | 1399.2928
2016-03-29 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6884 | 1388.3051 | 2704.9935 | 13.1879 | 0.48845 | 0.51155 | 1.1465 | 11.5024 | 2716.4959 | 1322.3067 | 1394.1892
2016-03-29 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.21% | 1310.1567 | 1396.7963 | 2706.953 | 14.4281 | 0.48603 | 0.51397 | 1.1458 | 12.592 | 2719.545 | 1316.2767 | 1403.2683
2016-03-29 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.79% | 1373.0969 | 1447.6643 | 2820.7612 | 37.1084 | 0.48894 | 0.51106 | 1.1956 | 31.0381 | 2851.7994 | 1388.2726 | 1463.5267
2016-03-29 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.43% | 1368.0762 | 1454.6933 | 2822.7695 | 17.8015 | 0.48715 | 0.51285 | 1.1949 | 14.8984 | 2837.668 | 1375.3339 | 1462.334
2016-03-29 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-29 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-29 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.8997 | 1638.2007 | 3169.1003 | 128.1898 | 0.48858 | 0.51142 | 1.4886 | 86.1152 | 3255.2155 | 1572.9743 | 1682.2413
2016-03-30 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.7% | 1530.5707 | 1638.8586 | 3169.4293 | 124.8464 | 0.48848 | 0.51152 | 1.4885 | 83.8751 | 3253.3044 | 1571.542 | 1681.7624
2016-03-30 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5741 | 1642.8518 | 3171.4259 | 124.8441 | 0.48784 | 0.51216 | 1.4878 | 83.9095 | 3255.3354 | 1569.5087 | 1685.8266
2016-03-30 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.7196 | 1646.5608 | 3173.2804 | 128.9639 | 0.48725 | 0.51275 | 1.4873 | 86.7129 | 3259.9933 | 1568.9706 | 1691.0228
2016-03-30 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.79% | 1532.0351 | 1635.9299 | 3167.9649 | 138.7804 | 0.48895 | 0.51105 | 1.4889 | 93.2071 | 3261.172 | 1577.6084 | 1683.5636
2016-03-30 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.68% | 1530.3277 | 1639.3446 | 3169.6723 | 120.5689 | 0.4884 | 0.5116 | 1.4884 | 81.0056 | 3250.6779 | 1569.891 | 1680.7869
2016-03-30 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.55% | 1528.3521 | 1643.2958 | 3171.6479 | 116.8063 | 0.48777 | 0.51223 | 1.4878 | 78.5109 | 3250.1588 | 1566.6475 | 1683.5113
2016-03-30 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.14% | 1521.8232 | 1656.3536 | 3178.1768 | 122.8684 | 0.48569 | 0.51431 | 1.4857 | 82.7013 | 3260.8782 | 1561.9903 | 1698.8879
2016-03-30 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4421 | 1560.8369 | 3020.279 | 64.1704 | 0.48648 | 0.51352 | 1.2432 | 51.6155 | 3071.8945 | 1484.552 | 1587.3425
2016-03-30 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.23% | 1458.4649 | 1562.3027 | 3020.7676 | 66.6889 | 0.48615 | 0.51385 | 1.2431 | 53.6482 | 3074.4157 | 1484.5462 | 1589.8695
2016-03-30 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.41% | 1367.7755 | 1455.1144 | 2822.8898 | 41.1326 | 0.48704 | 0.51296 | 1.1948 | 34.4259 | 2857.3157 | 1384.5423 | 1472.7734
2016-03-30 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2375 | 1453.0675 | 2822.305 | 34.9912 | 0.48756 | 0.51244 | 1.195 | 29.2808 | 2851.5858 | 1383.5137 | 1468.0721
2016-03-30 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.5175 | 1454.0756 | 2822.593 | 37.5538 | 0.48731 | 0.51269 | 1.1949 | 31.4278 | 2854.0209 | 1383.8324 | 1470.1884
2016-03-30 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.71% | 1357.9553 | 1468.8626 | 2826.8179 | 37.7404 | 0.48354 | 0.51646 | 1.1934 | 31.6238 | 2858.4417 | 1373.2468 | 1485.1948
2016-03-30 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.95% | 1361.3469 | 1464.1143 | 2825.4612 | 54.4427 | 0.48475 | 0.51525 | 1.1939 | 45.6007 | 2871.0619 | 1383.452 | 1487.6099
2016-03-30 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.97% | 1361.5907 | 1463.773 | 2825.3637 | 53.4503 | 0.48484 | 0.51516 | 1.1939 | 44.7681 | 2870.1318 | 1383.2961 | 1486.8357
2016-03-30 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.4% | 1461.0619 | 1558.4071 | 3019.469 | 50.8691 | 0.48702 | 0.51298 | 1.2435 | 40.9077 | 3060.3767 | 1480.9848 | 1579.3919
2016-03-30 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.522 | 1554.7169 | 3018.239 | 33.0376 | 0.48784 | 0.51216 | 1.2439 | 26.5593 | 3044.7982 | 1476.4787 | 1568.3195
2016-03-30 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.69% | 1465.3468 | 1551.9799 | 3017.3266 | 21.9799 | 0.48845 | 0.51155 | 1.2442 | 17.6655 | 3034.9921 | 1473.9755 | 1561.0167
2016-03-30 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.21% | 1458.0776 | 1562.8836 | 3020.9612 | 24.0468 | 0.48603 | 0.51397 | 1.243 | 19.3456 | 3040.3068 | 1467.48 | 1572.8268
2016-03-30 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.79% | 1466.8098 | 1549.7853 | 3016.5951 | 46.3855 | 0.48894 | 0.51106 | 1.2445 | 37.2734 | 3053.8685 | 1485.0341 | 1568.8344
2016-03-30 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.43% | 1461.4464 | 1557.8304 | 3019.2768 | 22.2519 | 0.48715 | 0.51285 | 1.2436 | 17.8935 | 3037.1703 | 1470.1632 | 1567.0071
2016-03-30 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.39% | 1460.8035 | 1558.7948 | 3019.5983 | 32.7901 | 0.48693 | 0.51307 | 1.2435 | 26.3699 | 3045.9682 | 1473.6439 | 1572.3243
2016-03-30 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8887 | 1646.2226 | 3173.1113 | 118.7883 | 0.4873 | 0.5127 | 1.4873 | 79.8682 | 3252.9795 | 1565.8088 | 1687.1706
2016-03-30 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 153.8277 | 0.48814 | 0.51186 | 1.5858 | 97.0049 | 3393.2422 | 1633.8213 | 1759.4209
2016-03-31 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-03-31 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-03-31 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-03-31 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-03-31 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-03-31 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-03-31 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-03-31 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-03-31 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.019 | 1629.9621 | 3164.981 | 88.6912 | 0.4899 | 0.5101 | 1.4899 | 59.5283 | 3224.5094 | 1564.1819 | 1660.3275
2016-03-31 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.0343 | 1629.9313 | 3164.9657 | 104.6008 | 0.4899 | 0.5101 | 1.4899 | 70.2064 | 3235.172 | 1569.4288 | 1665.7432
2016-03-31 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-03-31 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-03-31 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.3408 | 1454.3229 | 2822.6637 | 44.265 | 0.48724 | 0.51276 | 1.1949 | 37.045 | 2859.7087 | 1386.3907 | 1473.318
2016-03-31 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-03-31 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-03-31 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-03-31 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-03-31 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.11% | 1471.7126 | 1542.4312 | 3014.1437 | 39.6958 | 0.49057 | 0.50943 | 1.2453 | 31.8769 | 3046.0206 | 1487.3504 | 1558.6702
2016-03-31 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8382 | 1540.7427 | 3013.5809 | 33.2752 | 0.49095 | 0.50905 | 1.2455 | 26.7169 | 3040.2978 | 1485.9547 | 1554.3431
2016-03-31 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-03-31 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-03-31 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-03-31 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-03-31 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-01 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-01 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-01 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-01 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-01 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-01 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-01 06:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98% | 1592.518 | 1696.4605 | 3288.9784 | 91.6262 | 0.49001 | 0.50999 | 1.588 | 57.6988 | 3346.6773 | 1620.7907 | 1725.8865
2016-04-01 07:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.92% | 1591.2409 | 1699.2701 | 3290.5109 | 114.7188 | 0.48961 | 0.51039 | 1.5875 | 72.2622 | 3362.7732 | 1626.6214 | 1736.1518
2016-04-01 08:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1739 | 1697.2174 | 3289.3913 | 106.4295 | 0.4899 | 0.5101 | 1.5879 | 67.0262 | 3356.4175 | 1625.01 | 1731.4074
2016-04-01 09:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1899 | 1697.1823 | 3289.3721 | 125.5209 | 0.4899 | 0.5101 | 1.5879 | 79.0491 | 3368.4213 | 1630.9164 | 1737.5049
2016-04-01 10:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.42% | 1582.9963 | 1717.4082 | 3300.4045 | 141.3816 | 0.48708 | 0.51292 | 1.5845 | 89.2284 | 3389.6329 | 1626.4573 | 1763.1756
2016-04-01 11:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.46% | 1583.7298 | 1715.7945 | 3299.5243 | 138.0281 | 0.4873 | 0.5127 | 1.5848 | 87.097 | 3386.6213 | 1626.1723 | 1760.449
2016-04-01 12:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.45% | 1583.5398 | 1716.2124 | 3299.7522 | 132.7951 | 0.48724 | 0.51276 | 1.5847 | 83.7987 | 3383.5509 | 1624.3701 | 1759.1808
2016-04-01 13:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.54% | 1585.0952 | 1712.7905 | 3297.8857 | 135.5527 | 0.48772 | 0.51228 | 1.5853 | 85.5079 | 3383.3936 | 1626.7993 | 1756.5944
2016-04-01 14:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.51% | 1584.5372 | 1714.0181 | 3298.5553 | 135.9674 | 0.48755 | 0.51245 | 1.5851 | 85.7806 | 3384.3359 | 1626.3595 | 1757.9764
2016-04-01 15:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.76% | 1588.6069 | 1705.0649 | 3293.6718 | 117.5066 | 0.4888 | 0.5112 | 1.5866 | 74.0637 | 3367.7354 | 1624.8093 | 1742.9261
2016-04-01 16:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.95% | 1591.6623 | 1698.343 | 3290.0052 | 96.6314 | 0.48974 | 0.51026 | 1.5877 | 60.8629 | 3350.8681 | 1621.4694 | 1729.3987
2016-04-01 17:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.11% | 1594.3553 | 1692.4184 | 3286.7737 | 95.27 | 0.49057 | 0.50943 | 1.5887 | 59.9678 | 3346.7415 | 1623.7737 | 1722.9677
2016-04-01 18:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.19% | 1595.5747 | 1689.7357 | 3285.3104 | 79.8604 | 0.49095 | 0.50905 | 1.5891 | 50.254 | 3335.5644 | 1620.2467 | 1715.3177
2016-04-01 19:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.19% | 1595.6123 | 1689.6529 | 3285.2652 | 76.3982 | 0.49096 | 0.50904 | 1.5891 | 48.0749 | 3333.3401 | 1619.215 | 1714.1251
2016-04-01 20:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.4741 | 1703.1569 | 3292.631 | 90.0336 | 0.48907 | 0.51093 | 1.5869 | 56.7361 | 3349.3672 | 1617.222 | 1732.1451
2016-04-01 21:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.77% | 1588.7984 | 1704.6436 | 3293.442 | 90.4059 | 0.48886 | 0.51114 | 1.5866 | 56.9797 | 3350.4217 | 1616.6535 | 1733.7682
2016-04-01 22:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.77% | 1588.7811 | 1704.6816 | 3293.4627 | 92.3968 | 0.48886 | 0.51114 | 1.5866 | 58.2347 | 3351.6974 | 1617.2495 | 1734.4479
2016-04-01 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 80.1717 | 0.48814 | 0.51186 | 1.5858 | 50.5569 | 3346.7942 | 1611.148 | 1735.6462
2016-04-02 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-02 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-02 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-02 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-02 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-02 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-02 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-02 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-02 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-02 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-02 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-02 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-02 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-02 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-02 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-02 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4063 | 1550.3905 | 3016.7968 | 48.9611 | 0.4888 | 0.5112 | 1.2444 | 39.3451 | 3056.1419 | 1485.6383 | 1570.5036
2016-04-02 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.95% | 1469.2267 | 1546.1599 | 3015.3866 | 40.2631 | 0.48974 | 0.51026 | 1.2449 | 32.3432 | 3047.7298 | 1485.0666 | 1562.6633
2016-04-02 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.11% | 1471.7126 | 1542.4312 | 3014.1437 | 39.6958 | 0.49057 | 0.50943 | 1.2453 | 31.8769 | 3046.0206 | 1487.3504 | 1558.6702
2016-04-02 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8382 | 1540.7427 | 3013.5809 | 33.2752 | 0.49095 | 0.50905 | 1.2455 | 26.7169 | 3040.2978 | 1485.9547 | 1554.3431
2016-04-02 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-04-02 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-04-02 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-02 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-02 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-03 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.75% | 1466.2986 | 1550.5521 | 3016.8507 | 32.1999 | 0.48877 | 0.51123 | 1.2444 | 25.8762 | 3042.7269 | 1478.946 | 1563.7808
2016-04-03 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.62% | 1464.2833 | 1553.5751 | 3017.8584 | 31.0174 | 0.48809 | 0.51191 | 1.244 | 24.9326 | 3042.791 | 1476.4528 | 1566.3383
2016-04-03 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.0795 | 1549.3808 | 3016.4603 | 30.9428 | 0.48903 | 0.51097 | 1.2445 | 24.8634 | 3041.3237 | 1479.2383 | 1562.0854
2016-04-03 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.8413 | 1551.238 | 3017.0793 | 32.4872 | 0.48861 | 0.51139 | 1.2443 | 26.1087 | 3043.188 | 1478.5984 | 1564.5896
2016-04-03 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.78% | 1466.6291 | 1550.0563 | 3016.6854 | 32.8362 | 0.48888 | 0.51112 | 1.2444 | 26.3864 | 3043.0718 | 1479.5288 | 1563.543
2016-04-03 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.14% | 1378.0243 | 1440.766 | 2818.7903 | 25.7358 | 0.49069 | 0.50931 | 1.1963 | 21.5132 | 2840.3035 | 1388.5806 | 1451.7229
2016-04-03 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98% | 1376.0989 | 1443.4616 | 2819.5605 | 30.5421 | 0.49001 | 0.50999 | 1.196 | 25.5368 | 2845.0972 | 1388.612 | 1456.4852
2016-04-03 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.92% | 1374.9953 | 1445.0065 | 2820.0019 | 38.2396 | 0.48961 | 0.51039 | 1.1958 | 31.9771 | 2851.9789 | 1390.6517 | 1461.3272
2016-04-03 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-03 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-03 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-03 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-03 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-03 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-03 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-03 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-03 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-03 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-03 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-03 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-03 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-03 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-03 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-03 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-04 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-04 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-04 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-04 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-04 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-04 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-04 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-04 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-04 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-04 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-04 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-04 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-04 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-04 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-04 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-04 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-04 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-04 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-04 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-04 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-04 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-04 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-04 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-04 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-05 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-05 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-05 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-05 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-05 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-05 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-05 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98% | 1470.0166 | 1544.9751 | 3014.9917 | 38.1776 | 0.49001 | 0.50999 | 1.245 | 30.6646 | 3045.6563 | 1485.0424 | 1560.6139
2016-04-05 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-05 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-05 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-05 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-05 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-05 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-05 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-05 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-05 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-05 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-05 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-05 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-05 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-05 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-05 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-05 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-05 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 80.1717 | 0.48814 | 0.51186 | 1.5858 | 50.5569 | 3346.7942 | 1611.148 | 1735.6462
2016-04-06 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-06 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-06 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-06 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-06 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-06 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-06 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-06 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-06 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.019 | 1629.9621 | 3164.981 | 88.6912 | 0.4899 | 0.5101 | 1.4899 | 59.5283 | 3224.5094 | 1564.1819 | 1660.3275
2016-04-06 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.0343 | 1629.9313 | 3164.9657 | 104.6008 | 0.4899 | 0.5101 | 1.4899 | 70.2064 | 3235.172 | 1569.4288 | 1665.7432
2016-04-06 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.42% | 1526.1708 | 1647.6585 | 3173.8292 | 117.818 | 0.48708 | 0.51292 | 1.4871 | 79.228 | 3253.0572 | 1564.7608 | 1688.2964
2016-04-06 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-06 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-06 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-06 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-06 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-06 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-06 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-06 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-06 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-06 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-06 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-06 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-06 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-07 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-07 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-07 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-07 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-07 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-07 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-07 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-07 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-07 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-07 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-07 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-07 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-07 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-07 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-07 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4063 | 1550.3905 | 3016.7968 | 48.9611 | 0.4888 | 0.5112 | 1.2444 | 39.3451 | 3056.1419 | 1485.6383 | 1570.5036
2016-04-07 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.95% | 1469.2267 | 1546.1599 | 3015.3866 | 40.2631 | 0.48974 | 0.51026 | 1.2449 | 32.3432 | 3047.7298 | 1485.0666 | 1562.6633
2016-04-07 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.11% | 1471.7126 | 1542.4312 | 3014.1437 | 39.6958 | 0.49057 | 0.50943 | 1.2453 | 31.8769 | 3046.0206 | 1487.3504 | 1558.6702
2016-04-07 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8382 | 1540.7427 | 3013.5809 | 33.2752 | 0.49095 | 0.50905 | 1.2455 | 26.7169 | 3040.2978 | 1485.9547 | 1554.3431
2016-04-07 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-04-07 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-04-07 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-07 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-07 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-08 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.75% | 1466.2986 | 1550.5521 | 3016.8507 | 32.1999 | 0.48877 | 0.51123 | 1.2444 | 25.8762 | 3042.7269 | 1478.946 | 1563.7808
2016-04-08 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.62% | 1464.2833 | 1553.5751 | 3017.8584 | 31.0174 | 0.48809 | 0.51191 | 1.244 | 24.9326 | 3042.791 | 1476.4528 | 1566.3383
2016-04-08 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.0795 | 1549.3808 | 3016.4603 | 30.9428 | 0.48903 | 0.51097 | 1.2445 | 24.8634 | 3041.3237 | 1479.2383 | 1562.0854
2016-04-08 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.8413 | 1551.238 | 3017.0793 | 32.4872 | 0.48861 | 0.51139 | 1.2443 | 26.1087 | 3043.188 | 1478.5984 | 1564.5896
2016-04-08 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.78% | 1466.6291 | 1550.0563 | 3016.6854 | 32.8362 | 0.48888 | 0.51112 | 1.2444 | 26.3864 | 3043.0718 | 1479.5288 | 1563.543
2016-04-08 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.14% | 1472.0734 | 1541.8899 | 3013.9633 | 32.1697 | 0.49069 | 0.50931 | 1.2453 | 25.832 | 3039.7953 | 1484.7489 | 1555.0464
2016-04-08 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98% | 1376.0989 | 1443.4616 | 2819.5605 | 30.5421 | 0.49001 | 0.50999 | 1.196 | 25.5368 | 2845.0972 | 1388.612 | 1456.4852
2016-04-08 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.92% | 1319.8252 | 1384.2272 | 2704.0524 | 28.6797 | 0.48961 | 0.51039 | 1.1469 | 25.0066 | 2729.0591 | 1332.0688 | 1396.9903
2016-04-08 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-08 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-08 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-08 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-08 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-08 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-08 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-08 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-08 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-08 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-08 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-08 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-08 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-08 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-08 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-08 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-09 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-09 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-09 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-09 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-09 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-09 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-09 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98% | 1470.0166 | 1544.9751 | 3014.9917 | 38.1776 | 0.49001 | 0.50999 | 1.245 | 30.6646 | 3045.6563 | 1485.0424 | 1560.6139
2016-04-09 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.92% | 1374.9953 | 1445.0065 | 2820.0019 | 38.2396 | 0.48961 | 0.51039 | 1.1958 | 31.9771 | 2851.9789 | 1390.6517 | 1461.3272
2016-04-09 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-09 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-09 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-09 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-09 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-09 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-09 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-09 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-09 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-09 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-09 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-09 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-04-09 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-04-09 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-09 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-09 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-10 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-10 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-10 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-10 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-10 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-10 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-10 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-10 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-10 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-10 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-10 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-10 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-10 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-10 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-10 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-10 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-10 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-10 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-10 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-10 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-10 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-10 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-10 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-10 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-11 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-11 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-11 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-11 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-11 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-11 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-11 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-11 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-11 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-11 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-11 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-11 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-11 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-11 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-11 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-11 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-11 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-11 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-11 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-11 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-11 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-11 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-11 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-11 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-12 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.75% | 1466.2986 | 1550.5521 | 3016.8507 | 32.1999 | 0.48877 | 0.51123 | 1.2444 | 25.8762 | 3042.7269 | 1478.946 | 1563.7808
2016-04-12 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.62% | 1464.2833 | 1553.5751 | 3017.8584 | 31.0174 | 0.48809 | 0.51191 | 1.244 | 24.9326 | 3042.791 | 1476.4528 | 1566.3383
2016-04-12 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.0795 | 1549.3808 | 3016.4603 | 30.9428 | 0.48903 | 0.51097 | 1.2445 | 24.8634 | 3041.3237 | 1479.2383 | 1562.0854
2016-04-12 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.8413 | 1551.238 | 3017.0793 | 32.4872 | 0.48861 | 0.51139 | 1.2443 | 26.1087 | 3043.188 | 1478.5984 | 1564.5896
2016-04-12 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.78% | 1466.6291 | 1550.0563 | 3016.6854 | 32.8362 | 0.48888 | 0.51112 | 1.2444 | 26.3864 | 3043.0718 | 1479.5288 | 1563.543
2016-04-12 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.14% | 1472.0734 | 1541.8899 | 3013.9633 | 32.1697 | 0.49069 | 0.50931 | 1.2453 | 25.832 | 3039.7953 | 1484.7489 | 1555.0464
2016-04-12 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98% | 1376.0989 | 1443.4616 | 2819.5605 | 30.5421 | 0.49001 | 0.50999 | 1.196 | 25.5368 | 2845.0972 | 1388.612 | 1456.4852
2016-04-12 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.92% | 1374.9953 | 1445.0065 | 2820.0019 | 38.2396 | 0.48961 | 0.51039 | 1.1958 | 31.9771 | 2851.9789 | 1390.6517 | 1461.3272
2016-04-12 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-12 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-12 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-12 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-12 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.3408 | 1454.3229 | 2822.6637 | 44.265 | 0.48724 | 0.51276 | 1.1949 | 37.045 | 2859.7087 | 1386.3907 | 1473.318
2016-04-12 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-12 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-12 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-12 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-12 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-12 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-12 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-12 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-12 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-12 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-12 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-13 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-13 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-13 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-13 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-13 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-13 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-13 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98% | 1470.0166 | 1544.9751 | 3014.9917 | 38.1776 | 0.49001 | 0.50999 | 1.245 | 30.6646 | 3045.6563 | 1485.0424 | 1560.6139
2016-04-13 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-13 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-13 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-13 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-13 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-13 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-13 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-13 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-13 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4063 | 1550.3905 | 3016.7968 | 48.9611 | 0.4888 | 0.5112 | 1.2444 | 39.3451 | 3056.1419 | 1485.6383 | 1570.5036
2016-04-13 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.95% | 1469.2267 | 1546.1599 | 3015.3866 | 40.2631 | 0.48974 | 0.51026 | 1.2449 | 32.3432 | 3047.7298 | 1485.0666 | 1562.6633
2016-04-13 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.11% | 1471.7126 | 1542.4312 | 3014.1437 | 39.6958 | 0.49057 | 0.50943 | 1.2453 | 31.8769 | 3046.0206 | 1487.3504 | 1558.6702
2016-04-13 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-13 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-13 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-13 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-13 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-13 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-14 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-14 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-14 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-14 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-14 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-14 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-14 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-14 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-14 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-14 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-14 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-14 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-14 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-14 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-14 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-14 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-14 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-14 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-14 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-14 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-14 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-14 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-14 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-14 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.63% | 1370.8718 | 1450.7794 | 2821.6513 | 26.7239 | 0.48814 | 0.51186 | 1.1953 | 22.3583 | 2844.0095 | 1381.7859 | 1462.2236
2016-04-15 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.75% | 1372.6184 | 1448.3342 | 2820.9526 | 25.7599 | 0.48877 | 0.51123 | 1.1955 | 21.5473 | 2842.4999 | 1383.15 | 1459.3499
2016-04-15 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.62% | 1370.7318 | 1450.9754 | 2821.7073 | 24.8139 | 0.48809 | 0.51191 | 1.1952 | 20.7607 | 2842.4679 | 1380.865 | 1461.6029
2016-04-15 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.3494 | 1447.3109 | 2820.6602 | 24.7543 | 0.48903 | 0.51097 | 1.1956 | 20.7043 | 2841.3645 | 1383.4743 | 1457.8902
2016-04-15 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.72% | 1372.1904 | 1448.9335 | 2821.1239 | 25.9897 | 0.48861 | 0.51139 | 1.1954 | 21.7406 | 2842.8645 | 1382.8131 | 1460.0513
2016-04-15 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.78% | 1372.9278 | 1447.901 | 2820.8289 | 26.2689 | 0.48888 | 0.51112 | 1.1956 | 21.9723 | 2842.8011 | 1383.6696 | 1459.1316
2016-04-15 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.14% | 1378.0243 | 1440.766 | 2818.7903 | 25.7358 | 0.49069 | 0.50931 | 1.1963 | 21.5132 | 2840.3035 | 1388.5806 | 1451.7229
2016-04-15 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98% | 1376.0989 | 1443.4616 | 2819.5605 | 30.5421 | 0.49001 | 0.50999 | 1.196 | 25.5368 | 2845.0972 | 1388.612 | 1456.4852
2016-04-15 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.92% | 1374.9953 | 1445.0065 | 2820.0019 | 38.2396 | 0.48961 | 0.51039 | 1.1958 | 31.9771 | 2851.9789 | 1390.6517 | 1461.3272
2016-04-15 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-15 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-15 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-15 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-15 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.3408 | 1454.3229 | 2822.6637 | 44.265 | 0.48724 | 0.51276 | 1.1949 | 37.045 | 2859.7087 | 1386.3907 | 1473.318
2016-04-15 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-15 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-15 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-15 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-15 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-15 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-15 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-15 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-15 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-15 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-15 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.63% | 1370.8718 | 1450.7794 | 2821.6513 | 26.7239 | 0.48814 | 0.51186 | 1.1953 | 22.3583 | 2844.0095 | 1381.7859 | 1462.2236
2016-04-16 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.75% | 1372.6184 | 1448.3342 | 2820.9526 | 25.7599 | 0.48877 | 0.51123 | 1.1955 | 21.5473 | 2842.4999 | 1383.15 | 1459.3499
2016-04-16 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.62% | 1370.7318 | 1450.9754 | 2821.7073 | 24.8139 | 0.48809 | 0.51191 | 1.1952 | 20.7607 | 2842.4679 | 1380.865 | 1461.6029
2016-04-16 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.3494 | 1447.3109 | 2820.6602 | 24.7543 | 0.48903 | 0.51097 | 1.1956 | 20.7043 | 2841.3645 | 1383.4743 | 1457.8902
2016-04-16 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.72% | 1372.1904 | 1448.9335 | 2821.1239 | 25.9897 | 0.48861 | 0.51139 | 1.1954 | 21.7406 | 2842.8645 | 1382.8131 | 1460.0513
2016-04-16 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.78% | 1372.9278 | 1447.901 | 2820.8289 | 26.2689 | 0.48888 | 0.51112 | 1.1956 | 21.9723 | 2842.8011 | 1383.6696 | 1459.1316
2016-04-16 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.14% | 1378.0243 | 1440.766 | 2818.7903 | 25.7358 | 0.49069 | 0.50931 | 1.1963 | 21.5132 | 2840.3035 | 1388.5806 | 1451.7229
2016-04-16 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98% | 1320.8845 | 1382.8502 | 2703.7347 | 22.9065 | 0.49001 | 0.50999 | 1.147 | 19.9708 | 2723.7055 | 1330.6703 | 1393.0352
2016-04-16 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.92% | 1319.8252 | 1384.2272 | 2704.0524 | 28.6797 | 0.48961 | 0.51039 | 1.1469 | 25.0066 | 2729.0591 | 1332.0688 | 1396.9903
2016-04-16 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-16 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-16 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.42% | 1316.187 | 1394.7663 | 2710.9533 | 29.4545 | 0.48708 | 0.51292 | 1.1218 | 26.2572 | 2737.2104 | 1328.9762 | 1408.2342
2016-04-16 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.46% | 1316.7969 | 1394.0039 | 2710.8008 | 28.7558 | 0.4873 | 0.5127 | 1.1218 | 25.6331 | 2736.4339 | 1329.2879 | 1407.146
2016-04-16 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6389 | 1394.2014 | 2710.8403 | 27.6656 | 0.48724 | 0.51276 | 1.1218 | 24.6616 | 2735.5019 | 1328.6551 | 1406.8468
2016-04-16 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.54% | 1317.9322 | 1392.5848 | 2710.517 | 28.2401 | 0.48772 | 0.51228 | 1.1219 | 25.171 | 2735.688 | 1330.2086 | 1405.4794
2016-04-16 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.51% | 1317.4682 | 1393.1647 | 2710.6329 | 28.3265 | 0.48755 | 0.51245 | 1.1219 | 25.249 | 2735.8819 | 1329.7784 | 1406.1036
2016-04-16 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.76% | 1320.8519 | 1388.9351 | 2709.787 | 24.4806 | 0.4888 | 0.5112 | 1.1222 | 21.8148 | 2731.6018 | 1331.515 | 1400.0868
2016-04-16 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.95% | 1323.3924 | 1385.7595 | 2709.1519 | 20.1315 | 0.48974 | 0.51026 | 1.1224 | 17.9356 | 2727.0875 | 1332.1762 | 1394.9113
2016-04-16 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.11% | 1325.6315 | 1382.9607 | 2708.5921 | 19.8479 | 0.49057 | 0.50943 | 1.1226 | 17.6796 | 2726.2718 | 1334.3046 | 1391.9672
2016-04-16 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-16 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-16 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.81% | 1321.573 | 1388.0337 | 2709.6067 | 18.757 | 0.48907 | 0.51093 | 1.1223 | 16.7135 | 2726.3202 | 1329.7471 | 1396.5731
2016-04-16 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-16 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.785 | 1386.8795 | 2704.6645 | 23.0992 | 0.48886 | 0.51114 | 1.1467 | 20.1448 | 2724.8093 | 1327.6329 | 1397.1764
2016-04-16 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.63% | 1315.8672 | 1389.3727 | 2705.2398 | 20.0429 | 0.48814 | 0.51186 | 1.1464 | 17.4827 | 2722.7226 | 1324.4013 | 1398.3213
2016-04-17 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.75% | 1317.5437 | 1387.1932 | 2704.7369 | 19.3199 | 0.48877 | 0.51123 | 1.1466 | 16.8493 | 2721.5862 | 1325.7791 | 1395.8071
2016-04-17 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.62% | 1315.7328 | 1389.5474 | 2705.2802 | 18.6104 | 0.48809 | 0.51191 | 1.1464 | 16.2334 | 2721.5136 | 1323.6562 | 1397.8573
2016-04-17 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.2453 | 1386.2811 | 2704.5264 | 18.5657 | 0.48903 | 0.51097 | 1.1467 | 16.1904 | 2720.7168 | 1326.1629 | 1394.554
2016-04-17 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.1328 | 1387.7274 | 2704.8602 | 19.4923 | 0.48861 | 0.51139 | 1.1466 | 17.0003 | 2721.8605 | 1325.4394 | 1396.4211
2016-04-17 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.8407 | 1386.8071 | 2704.6478 | 19.7017 | 0.48888 | 0.51112 | 1.1467 | 17.1818 | 2721.8296 | 1326.2404 | 1395.5891
2016-04-17 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.14% | 1322.7326 | 1380.4476 | 2703.1802 | 19.3018 | 0.49069 | 0.50931 | 1.1472 | 16.8251 | 2720.0053 | 1330.9885 | 1389.0168
2016-04-17 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98% | 1320.8845 | 1382.8502 | 2703.7347 | 22.9065 | 0.49001 | 0.50999 | 1.147 | 19.9708 | 2723.7055 | 1330.6703 | 1393.0352
2016-04-17 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.92% | 1319.8252 | 1384.2272 | 2704.0524 | 28.6797 | 0.48961 | 0.51039 | 1.1469 | 25.0066 | 2729.0591 | 1332.0688 | 1396.9903
2016-04-17 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-17 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-17 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-17 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-17 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-17 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-17 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-17 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-17 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-17 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-17 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-17 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-17 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-17 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-17 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.785 | 1386.8795 | 2704.6645 | 23.0992 | 0.48886 | 0.51114 | 1.1467 | 20.1448 | 2724.8093 | 1327.6329 | 1397.1764
2016-04-17 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.63% | 1315.8672 | 1389.3727 | 2705.2398 | 20.0429 | 0.48814 | 0.51186 | 1.1464 | 17.4827 | 2722.7226 | 1324.4013 | 1398.3213
2016-04-18 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.75% | 1317.5437 | 1387.1932 | 2704.7369 | 19.3199 | 0.48877 | 0.51123 | 1.1466 | 16.8493 | 2721.5862 | 1325.7791 | 1395.8071
2016-04-18 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.62% | 1315.7328 | 1389.5474 | 2705.2802 | 18.6104 | 0.48809 | 0.51191 | 1.1464 | 16.2334 | 2721.5136 | 1323.6562 | 1397.8573
2016-04-18 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.2453 | 1386.2811 | 2704.5264 | 18.5657 | 0.48903 | 0.51097 | 1.1467 | 16.1904 | 2720.7168 | 1326.1629 | 1394.554
2016-04-18 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.1328 | 1387.7274 | 2704.8602 | 19.4923 | 0.48861 | 0.51139 | 1.1466 | 17.0003 | 2721.8605 | 1325.4394 | 1396.4211
2016-04-18 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.8407 | 1386.8071 | 2704.6478 | 19.7017 | 0.48888 | 0.51112 | 1.1467 | 17.1818 | 2721.8296 | 1326.2404 | 1395.5891
2016-04-18 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.14% | 1322.7326 | 1380.4476 | 2703.1802 | 19.3018 | 0.49069 | 0.50931 | 1.1472 | 16.8251 | 2720.0053 | 1330.9885 | 1389.0168
2016-04-18 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98% | 1320.8845 | 1382.8502 | 2703.7347 | 22.9065 | 0.49001 | 0.50999 | 1.147 | 19.9708 | 2723.7055 | 1330.6703 | 1393.0352
2016-04-18 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.92% | 1319.8252 | 1384.2272 | 2704.0524 | 28.6797 | 0.48961 | 0.51039 | 1.1469 | 25.0066 | 2729.0591 | 1332.0688 | 1396.9903
2016-04-18 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-18 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-18 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-18 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-18 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-18 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-18 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-18 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-18 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-18 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.11% | 1325.6315 | 1382.9607 | 2708.5921 | 19.8479 | 0.49057 | 0.50943 | 1.1226 | 17.6796 | 2726.2718 | 1334.3046 | 1391.9672
2016-04-18 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6453 | 1381.6933 | 2708.3387 | 16.6376 | 0.49095 | 0.50905 | 1.1227 | 14.8188 | 2723.1574 | 1333.9206 | 1389.2369
2016-04-18 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6766 | 1381.6542 | 2708.3308 | 15.9163 | 0.49096 | 0.50904 | 1.1227 | 14.1763 | 2722.5071 | 1333.6366 | 1388.8706
2016-04-18 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.81% | 1321.573 | 1388.0337 | 2709.6067 | 18.757 | 0.48907 | 0.51093 | 1.1223 | 16.7135 | 2726.3202 | 1329.7471 | 1396.5731
2016-04-18 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.77% | 1321.0111 | 1388.7361 | 2709.7472 | 18.8346 | 0.48886 | 0.51114 | 1.1222 | 16.7834 | 2726.5306 | 1329.2159 | 1397.3147
2016-04-18 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.785 | 1386.8795 | 2704.6645 | 23.0992 | 0.48886 | 0.51114 | 1.1467 | 20.1448 | 2724.8093 | 1327.6329 | 1397.1764
2016-04-18 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.63% | 1315.8672 | 1389.3727 | 2705.2398 | 20.0429 | 0.48814 | 0.51186 | 1.1464 | 17.4827 | 2722.7226 | 1324.4013 | 1398.3213
2016-04-19 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.75% | 1317.5437 | 1387.1932 | 2704.7369 | 19.3199 | 0.48877 | 0.51123 | 1.1466 | 16.8493 | 2721.5862 | 1325.7791 | 1395.8071
2016-04-19 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.62% | 1315.7328 | 1389.5474 | 2705.2802 | 18.6104 | 0.48809 | 0.51191 | 1.1464 | 16.2334 | 2721.5136 | 1323.6562 | 1397.8573
2016-04-19 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.2453 | 1386.2811 | 2704.5264 | 18.5657 | 0.48903 | 0.51097 | 1.1467 | 16.1904 | 2720.7168 | 1326.1629 | 1394.554
2016-04-19 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.1328 | 1387.7274 | 2704.8602 | 19.4923 | 0.48861 | 0.51139 | 1.1466 | 17.0003 | 2721.8605 | 1325.4394 | 1396.4211
2016-04-19 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.8407 | 1386.8071 | 2704.6478 | 19.7017 | 0.48888 | 0.51112 | 1.1467 | 17.1818 | 2721.8296 | 1326.2404 | 1395.5891
2016-04-19 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.14% | 1322.7326 | 1380.4476 | 2703.1802 | 19.3018 | 0.49069 | 0.50931 | 1.1472 | 16.8251 | 2720.0053 | 1330.9885 | 1389.0168
2016-04-19 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98% | 1320.8845 | 1382.8502 | 2703.7347 | 22.9065 | 0.49001 | 0.50999 | 1.147 | 19.9708 | 2723.7055 | 1330.6703 | 1393.0352
2016-04-19 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.92% | 1323.042 | 1386.1975 | 2709.2395 | 23.8998 | 0.48961 | 0.51039 | 1.1224 | 21.2934 | 2730.5329 | 1333.4675 | 1397.0654
2016-04-19 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.98% | 1323.8178 | 1385.2278 | 2709.0456 | 22.1728 | 0.4899 | 0.5101 | 1.1225 | 19.7535 | 2728.7991 | 1333.495 | 1395.3041
2016-04-19 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.98% | 1323.831 | 1385.2112 | 2709.0422 | 26.1502 | 0.4899 | 0.5101 | 1.1225 | 23.2969 | 2732.3391 | 1335.2443 | 1397.0948
2016-04-19 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.42% | 1316.187 | 1394.7663 | 2710.9533 | 29.4545 | 0.48708 | 0.51292 | 1.1218 | 26.2572 | 2737.2104 | 1328.9762 | 1408.2342
2016-04-19 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.46% | 1316.7969 | 1394.0039 | 2710.8008 | 28.7558 | 0.4873 | 0.5127 | 1.1218 | 25.6331 | 2736.4339 | 1329.2879 | 1407.146
2016-04-19 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6389 | 1394.2014 | 2710.8403 | 27.6656 | 0.48724 | 0.51276 | 1.1218 | 24.6616 | 2735.5019 | 1328.6551 | 1406.8468
2016-04-19 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.54% | 1317.9322 | 1392.5848 | 2710.517 | 28.2401 | 0.48772 | 0.51228 | 1.1219 | 25.171 | 2735.688 | 1330.2086 | 1405.4794
2016-04-19 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.51% | 1317.4682 | 1393.1647 | 2710.6329 | 28.3265 | 0.48755 | 0.51245 | 1.1219 | 25.249 | 2735.8819 | 1329.7784 | 1406.1036
2016-04-19 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.76% | 1320.8519 | 1388.9351 | 2709.787 | 24.4806 | 0.4888 | 0.5112 | 1.1222 | 21.8148 | 2731.6018 | 1331.515 | 1400.0868
2016-04-19 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.95% | 1323.3924 | 1385.7595 | 2709.1519 | 20.1315 | 0.48974 | 0.51026 | 1.1224 | 17.9356 | 2727.0875 | 1332.1762 | 1394.9113
2016-04-19 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-19 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-19 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-19 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-19 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-19 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-19 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.63% | 1370.8718 | 1450.7794 | 2821.6513 | 26.7239 | 0.48814 | 0.51186 | 1.1953 | 22.3583 | 2844.0095 | 1381.7859 | 1462.2236
2016-04-20 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.75% | 1466.2986 | 1550.5521 | 3016.8507 | 32.1999 | 0.48877 | 0.51123 | 1.2444 | 25.8762 | 3042.7269 | 1478.946 | 1563.7808
2016-04-20 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.62% | 1464.2833 | 1553.5751 | 3017.8584 | 31.0174 | 0.48809 | 0.51191 | 1.244 | 24.9326 | 3042.791 | 1476.4528 | 1566.3383
2016-04-20 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.0795 | 1549.3808 | 3016.4603 | 30.9428 | 0.48903 | 0.51097 | 1.2445 | 24.8634 | 3041.3237 | 1479.2383 | 1562.0854
2016-04-20 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.8413 | 1551.238 | 3017.0793 | 32.4872 | 0.48861 | 0.51139 | 1.2443 | 26.1087 | 3043.188 | 1478.5984 | 1564.5896
2016-04-20 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.78% | 1466.6291 | 1550.0563 | 3016.6854 | 32.8362 | 0.48888 | 0.51112 | 1.2444 | 26.3864 | 3043.0718 | 1479.5288 | 1563.543
2016-04-20 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.14% | 1472.0734 | 1541.8899 | 3013.9633 | 32.1697 | 0.49069 | 0.50931 | 1.2453 | 25.832 | 3039.7953 | 1484.7489 | 1555.0464
2016-04-20 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98% | 1376.0989 | 1443.4616 | 2819.5605 | 30.5421 | 0.49001 | 0.50999 | 1.196 | 25.5368 | 2845.0972 | 1388.612 | 1456.4852
2016-04-20 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.92% | 1374.9953 | 1445.0065 | 2820.0019 | 38.2396 | 0.48961 | 0.51039 | 1.1958 | 31.9771 | 2851.9789 | 1390.6517 | 1461.3272
2016-04-20 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-20 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-20 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.42% | 1312.9869 | 1393.1171 | 2706.1039 | 35.3454 | 0.48708 | 0.51292 | 1.1461 | 30.8391 | 2736.943 | 1328.0078 | 1408.9352
2016-04-20 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-20 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-20 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-20 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-20 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6405 | 1387.0674 | 2704.7079 | 29.3767 | 0.4888 | 0.5112 | 1.1466 | 25.6198 | 2730.3276 | 1330.1635 | 1400.1642
2016-04-20 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-20 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-20 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-20 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-20 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-20 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-20 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-20 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 80.1717 | 0.48814 | 0.51186 | 1.5858 | 50.5569 | 3346.7942 | 1611.148 | 1735.6462
2016-04-21 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-21 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-21 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-21 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-21 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-21 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-21 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-21 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-21 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-21 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-21 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-21 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-21 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.3408 | 1454.3229 | 2822.6637 | 44.265 | 0.48724 | 0.51276 | 1.1949 | 37.045 | 2859.7087 | 1386.3907 | 1473.318
2016-04-21 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-21 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-21 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-21 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-21 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-21 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-21 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-21 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-21 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-21 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-21 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 80.1717 | 0.48814 | 0.51186 | 1.5858 | 50.5569 | 3346.7942 | 1611.148 | 1735.6462
2016-04-22 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-22 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-22 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-22 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-22 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-22 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-22 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-22 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-22 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.019 | 1629.9621 | 3164.981 | 88.6912 | 0.4899 | 0.5101 | 1.4899 | 59.5283 | 3224.5094 | 1564.1819 | 1660.3275
2016-04-22 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.0343 | 1629.9313 | 3164.9657 | 104.6008 | 0.4899 | 0.5101 | 1.4899 | 70.2064 | 3235.172 | 1569.4288 | 1665.7432
2016-04-22 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-22 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-22 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-22 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-22 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-22 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-22 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-22 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-22 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-22 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-22 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-22 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-22 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5672 | 1550.1493 | 3016.7164 | 38.4986 | 0.48886 | 0.51114 | 1.2444 | 30.9368 | 3047.6532 | 1481.6908 | 1565.9624
2016-04-22 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-23 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-23 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-23 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-23 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-23 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-23 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-23 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-23 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-23 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-23 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-23 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-23 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-23 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.45% | 1368.3408 | 1454.3229 | 2822.6637 | 44.265 | 0.48724 | 0.51276 | 1.1949 | 37.045 | 2859.7087 | 1386.3907 | 1473.318
2016-04-23 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.54% | 1369.6848 | 1452.4412 | 2822.1261 | 45.1842 | 0.48772 | 0.51228 | 1.1951 | 37.8083 | 2859.9343 | 1388.1248 | 1471.8096
2016-04-23 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-23 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-23 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.95% | 1320.1747 | 1383.7728 | 2703.9476 | 24.1579 | 0.48974 | 0.51026 | 1.1469 | 21.0632 | 2725.0108 | 1330.4903 | 1394.5205
2016-04-23 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.11% | 1322.4084 | 1380.8691 | 2703.2775 | 23.8175 | 0.49057 | 0.50943 | 1.1472 | 20.7619 | 2724.0394 | 1332.5936 | 1391.4458
2016-04-23 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7402 | 1439.7637 | 2818.5039 | 26.6201 | 0.49095 | 0.50905 | 1.1964 | 22.2506 | 2840.7545 | 1389.664 | 1451.0905
2016-04-23 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.19% | 1378.7727 | 1439.7182 | 2818.4909 | 25.4661 | 0.49096 | 0.50904 | 1.1964 | 21.2859 | 2839.7768 | 1389.2231 | 1450.5537
2016-04-23 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.4687 | 1447.1438 | 2820.6125 | 30.0112 | 0.48907 | 0.51093 | 1.1956 | 25.1008 | 2845.7133 | 1385.7447 | 1459.9686
2016-04-23 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8847 | 1447.9614 | 2820.8461 | 30.1353 | 0.48886 | 0.51114 | 1.1955 | 25.2063 | 2846.0525 | 1385.2071 | 1460.8453
2016-04-23 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-23 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.63% | 1529.5187 | 1640.9625 | 3170.4813 | 66.8098 | 0.48814 | 0.51186 | 1.4881 | 44.8947 | 3215.376 | 1551.4338 | 1663.9421
2016-04-24 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-24 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-24 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-24 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-24 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-24 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-24 06:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98% | 1592.518 | 1696.4605 | 3288.9784 | 91.6262 | 0.49001 | 0.50999 | 1.588 | 57.6988 | 3346.6773 | 1620.7907 | 1725.8865
2016-04-24 07:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.92% | 1591.2409 | 1699.2701 | 3290.5109 | 114.7188 | 0.48961 | 0.51039 | 1.5875 | 72.2622 | 3362.7732 | 1626.6214 | 1736.1518
2016-04-24 08:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1739 | 1697.2174 | 3289.3913 | 106.4295 | 0.4899 | 0.5101 | 1.5879 | 67.0262 | 3356.4175 | 1625.01 | 1731.4074
2016-04-24 09:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1899 | 1697.1823 | 3289.3721 | 125.5209 | 0.4899 | 0.5101 | 1.5879 | 79.0491 | 3368.4213 | 1630.9164 | 1737.5049
2016-04-24 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.42% | 1526.1708 | 1647.6585 | 3173.8292 | 117.818 | 0.48708 | 0.51292 | 1.4871 | 79.228 | 3253.0572 | 1564.7608 | 1688.2964
2016-04-24 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.46% | 1526.8779 | 1646.2441 | 3173.1221 | 115.0234 | 0.4873 | 0.5127 | 1.4873 | 77.337 | 3250.459 | 1564.5643 | 1685.8947
2016-04-24 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.6948 | 1646.6104 | 3173.3052 | 110.6626 | 0.48724 | 0.51276 | 1.4872 | 74.4079 | 3247.7131 | 1562.9495 | 1684.7636
2016-04-24 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-24 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-24 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4063 | 1550.3905 | 3016.7968 | 48.9611 | 0.4888 | 0.5112 | 1.2444 | 39.3451 | 3056.1419 | 1485.6383 | 1570.5036
2016-04-24 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-24 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-24 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-24 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-24 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-24 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-24 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.785 | 1386.8795 | 2704.6645 | 23.0992 | 0.48886 | 0.51114 | 1.1467 | 20.1448 | 2724.8093 | 1327.6329 | 1397.1764
2016-04-24 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.63% | 1315.8672 | 1389.3727 | 2705.2398 | 20.0429 | 0.48814 | 0.51186 | 1.1464 | 17.4827 | 2722.7226 | 1324.4013 | 1398.3213
2016-04-25 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.75% | 1372.6184 | 1448.3342 | 2820.9526 | 25.7599 | 0.48877 | 0.51123 | 1.1955 | 21.5473 | 2842.4999 | 1383.15 | 1459.3499
2016-04-25 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.62% | 1370.7318 | 1450.9754 | 2821.7073 | 24.8139 | 0.48809 | 0.51191 | 1.1952 | 20.7607 | 2842.4679 | 1380.865 | 1461.6029
2016-04-25 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.0795 | 1549.3808 | 3016.4603 | 30.9428 | 0.48903 | 0.51097 | 1.2445 | 24.8634 | 3041.3237 | 1479.2383 | 1562.0854
2016-04-25 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.72% | 1465.8413 | 1551.238 | 3017.0793 | 32.4872 | 0.48861 | 0.51139 | 1.2443 | 26.1087 | 3043.188 | 1478.5984 | 1564.5896
2016-04-25 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.78% | 1466.6291 | 1550.0563 | 3016.6854 | 32.8362 | 0.48888 | 0.51112 | 1.2444 | 26.3864 | 3043.0718 | 1479.5288 | 1563.543
2016-04-25 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.14% | 1472.0734 | 1541.8899 | 3013.9633 | 32.1697 | 0.49069 | 0.50931 | 1.2453 | 25.832 | 3039.7953 | 1484.7489 | 1555.0464
2016-04-25 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98% | 1470.0166 | 1544.9751 | 3014.9917 | 38.1776 | 0.49001 | 0.50999 | 1.245 | 30.6646 | 3045.6563 | 1485.0424 | 1560.6139
2016-04-25 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-25 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.699 | 1545.4515 | 3015.1505 | 44.3456 | 0.4899 | 0.5101 | 1.2449 | 35.6204 | 3050.7709 | 1487.1494 | 1563.6215
2016-04-25 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-25 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-25 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.46% | 1368.505 | 1454.0931 | 2822.598 | 46.0094 | 0.4873 | 0.5127 | 1.1949 | 38.5041 | 2861.1021 | 1387.2681 | 1473.8341
2016-04-25 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.45% | 1313.4377 | 1392.531 | 2705.9687 | 33.1988 | 0.48724 | 0.51276 | 1.1462 | 28.9649 | 2734.9336 | 1327.5506 | 1407.3829
2016-04-25 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.54% | 1314.7278 | 1390.8539 | 2705.5817 | 33.8882 | 0.48772 | 0.51228 | 1.1463 | 29.5627 | 2735.1443 | 1329.1462 | 1405.9982
2016-04-25 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.51% | 1314.265 | 1391.4555 | 2705.7205 | 33.9918 | 0.48755 | 0.51245 | 1.1463 | 29.6544 | 2735.3749 | 1328.723 | 1406.6519
2016-04-25 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.76% | 1320.8519 | 1388.9351 | 2709.787 | 24.4806 | 0.4888 | 0.5112 | 1.1222 | 21.8148 | 2731.6018 | 1331.515 | 1400.0868
2016-04-25 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.95% | 1323.3924 | 1385.7595 | 2709.1519 | 20.1315 | 0.48974 | 0.51026 | 1.1224 | 17.9356 | 2727.0875 | 1332.1762 | 1394.9113
2016-04-25 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.11% | 1325.6315 | 1382.9607 | 2708.5921 | 19.8479 | 0.49057 | 0.50943 | 1.1226 | 17.6796 | 2726.2718 | 1334.3046 | 1391.9672
2016-04-25 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6453 | 1381.6933 | 2708.3387 | 16.6376 | 0.49095 | 0.50905 | 1.1227 | 14.8188 | 2723.1574 | 1333.9206 | 1389.2369
2016-04-25 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6766 | 1381.6542 | 2708.3308 | 15.9163 | 0.49096 | 0.50904 | 1.1227 | 14.1763 | 2722.5071 | 1333.6366 | 1388.8706
2016-04-25 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.81% | 1321.573 | 1388.0337 | 2709.6067 | 18.757 | 0.48907 | 0.51093 | 1.1223 | 16.7135 | 2726.3202 | 1329.7471 | 1396.5731
2016-04-25 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.77% | 1321.0111 | 1388.7361 | 2709.7472 | 18.8346 | 0.48886 | 0.51114 | 1.1222 | 16.7834 | 2726.5306 | 1329.2159 | 1397.3147
2016-04-25 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.785 | 1386.8795 | 2704.6645 | 23.0992 | 0.48886 | 0.51114 | 1.1467 | 20.1448 | 2724.8093 | 1327.6329 | 1397.1764
2016-04-25 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-26 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-26 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-26 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-26 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-26 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-26 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-26 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98% | 1470.0166 | 1544.9751 | 3014.9917 | 38.1776 | 0.49001 | 0.50999 | 1.245 | 30.6646 | 3045.6563 | 1485.0424 | 1560.6139
2016-04-26 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.92% | 1468.8377 | 1546.7434 | 3015.5811 | 47.7995 | 0.48961 | 0.51039 | 1.2448 | 38.3992 | 3053.9803 | 1487.6384 | 1566.3418
2016-04-26 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8016 | 1443.8778 | 2819.6794 | 35.4765 | 0.4899 | 0.5101 | 1.196 | 29.6636 | 2849.343 | 1390.3338 | 1459.0092
2016-04-26 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.98% | 1375.8154 | 1443.8585 | 2819.6739 | 41.8403 | 0.4899 | 0.5101 | 1.196 | 34.9847 | 2854.6585 | 1392.9545 | 1461.704
2016-04-26 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.42% | 1367.8711 | 1454.9804 | 2822.8515 | 47.1272 | 0.48708 | 0.51292 | 1.1948 | 39.4426 | 2862.2941 | 1387.0827 | 1475.2115
2016-04-26 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.46% | 1313.5953 | 1392.3262 | 2705.9214 | 34.507 | 0.4873 | 0.5127 | 1.1462 | 30.1058 | 2736.0273 | 1328.2659 | 1407.7614
2016-04-26 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6389 | 1394.2014 | 2710.8403 | 27.6656 | 0.48724 | 0.51276 | 1.1218 | 24.6616 | 2735.5019 | 1328.6551 | 1406.8468
2016-04-26 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.54% | 1317.9322 | 1392.5848 | 2710.517 | 28.2401 | 0.48772 | 0.51228 | 1.1219 | 25.171 | 2735.688 | 1330.2086 | 1405.4794
2016-04-26 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.51% | 1317.4682 | 1393.1647 | 2710.6329 | 28.3265 | 0.48755 | 0.51245 | 1.1219 | 25.249 | 2735.8819 | 1329.7784 | 1406.1036
2016-04-26 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.76% | 1320.8519 | 1388.9351 | 2709.787 | 24.4806 | 0.4888 | 0.5112 | 1.1222 | 21.8148 | 2731.6018 | 1331.515 | 1400.0868
2016-04-26 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.95% | 1323.3924 | 1385.7595 | 2709.1519 | 20.1315 | 0.48974 | 0.51026 | 1.1224 | 17.9356 | 2727.0875 | 1332.1762 | 1394.9113
2016-04-26 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.11% | 1325.6315 | 1382.9607 | 2708.5921 | 19.8479 | 0.49057 | 0.50943 | 1.1226 | 17.6796 | 2726.2718 | 1334.3046 | 1391.9672
2016-04-26 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.4198 | 1379.5542 | 2702.9741 | 19.9651 | 0.49095 | 0.50905 | 1.1473 | 17.4021 | 2720.3761 | 1331.9633 | 1388.4128
2016-04-26 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.19% | 1323.451 | 1379.5137 | 2702.9647 | 19.0995 | 0.49096 | 0.50904 | 1.1473 | 16.6476 | 2719.6123 | 1331.6243 | 1387.988
2016-04-26 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.81% | 1318.3598 | 1386.1322 | 2704.4921 | 22.5084 | 0.48907 | 0.51093 | 1.1467 | 19.6285 | 2724.1205 | 1327.9595 | 1396.161
2016-04-26 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-26 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-26 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.63% | 1370.8718 | 1450.7794 | 2821.6513 | 26.7239 | 0.48814 | 0.51186 | 1.1953 | 22.3583 | 2844.0095 | 1381.7859 | 1462.2236
2016-04-27 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.75% | 1372.6184 | 1448.3342 | 2820.9526 | 25.7599 | 0.48877 | 0.51123 | 1.1955 | 21.5473 | 2842.4999 | 1383.15 | 1459.3499
2016-04-27 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.62% | 1370.7318 | 1450.9754 | 2821.7073 | 24.8139 | 0.48809 | 0.51191 | 1.1952 | 20.7607 | 2842.4679 | 1380.865 | 1461.6029
2016-04-27 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.81% | 1373.3494 | 1447.3109 | 2820.6602 | 24.7543 | 0.48903 | 0.51097 | 1.1956 | 20.7043 | 2841.3645 | 1383.4743 | 1457.8902
2016-04-27 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.72% | 1372.1904 | 1448.9335 | 2821.1239 | 25.9897 | 0.48861 | 0.51139 | 1.1954 | 21.7406 | 2842.8645 | 1382.8131 | 1460.0513
2016-04-27 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.78% | 1372.9278 | 1447.901 | 2820.8289 | 26.2689 | 0.48888 | 0.51112 | 1.1956 | 21.9723 | 2842.8011 | 1383.6696 | 1459.1316
2016-04-27 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.14% | 1378.0243 | 1440.766 | 2818.7903 | 25.7358 | 0.49069 | 0.50931 | 1.1963 | 21.5132 | 2840.3035 | 1388.5806 | 1451.7229
2016-04-27 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98% | 1320.8845 | 1382.8502 | 2703.7347 | 22.9065 | 0.49001 | 0.50999 | 1.147 | 19.9708 | 2723.7055 | 1330.6703 | 1393.0352
2016-04-27 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.92% | 1319.8252 | 1384.2272 | 2704.0524 | 28.6797 | 0.48961 | 0.51039 | 1.1469 | 25.0066 | 2729.0591 | 1332.0688 | 1396.9903
2016-04-27 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.5991 | 1383.2212 | 2703.8203 | 26.6074 | 0.4899 | 0.5101 | 1.147 | 23.198 | 2727.0182 | 1331.9638 | 1395.0545
2016-04-27 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.98% | 1320.6123 | 1383.204 | 2703.8163 | 31.3802 | 0.4899 | 0.5101 | 1.147 | 27.3592 | 2731.1755 | 1334.0157 | 1397.1598
2016-04-27 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.42% | 1316.187 | 1394.7663 | 2710.9533 | 29.4545 | 0.48708 | 0.51292 | 1.1218 | 26.2572 | 2737.2104 | 1328.9762 | 1408.2342
2016-04-27 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.46% | 1316.7969 | 1394.0039 | 2710.8008 | 28.7558 | 0.4873 | 0.5127 | 1.1218 | 25.6331 | 2736.4339 | 1329.2879 | 1407.146
2016-04-27 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6389 | 1394.2014 | 2710.8403 | 27.6656 | 0.48724 | 0.51276 | 1.1218 | 24.6616 | 2735.5019 | 1328.6551 | 1406.8468
2016-04-27 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.54% | 1317.9322 | 1392.5848 | 2710.517 | 28.2401 | 0.48772 | 0.51228 | 1.1219 | 25.171 | 2735.688 | 1330.2086 | 1405.4794
2016-04-27 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.51% | 1317.4682 | 1393.1647 | 2710.6329 | 28.3265 | 0.48755 | 0.51245 | 1.1219 | 25.249 | 2735.8819 | 1329.7784 | 1406.1036
2016-04-27 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.76% | 1320.8519 | 1388.9351 | 2709.787 | 24.4806 | 0.4888 | 0.5112 | 1.1222 | 21.8148 | 2731.6018 | 1331.515 | 1400.0868
2016-04-27 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.95% | 1323.3924 | 1385.7595 | 2709.1519 | 20.1315 | 0.48974 | 0.51026 | 1.1224 | 17.9356 | 2727.0875 | 1332.1762 | 1394.9113
2016-04-27 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.11% | 1325.6315 | 1382.9607 | 2708.5921 | 19.8479 | 0.49057 | 0.50943 | 1.1226 | 17.6796 | 2726.2718 | 1334.3046 | 1391.9672
2016-04-27 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6453 | 1381.6933 | 2708.3387 | 16.6376 | 0.49095 | 0.50905 | 1.1227 | 14.8188 | 2723.1574 | 1333.9206 | 1389.2369
2016-04-27 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.19% | 1326.6766 | 1381.6542 | 2708.3308 | 15.9163 | 0.49096 | 0.50904 | 1.1227 | 14.1763 | 2722.5071 | 1333.6366 | 1388.8706
2016-04-27 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.81% | 1321.573 | 1388.0337 | 2709.6067 | 18.757 | 0.48907 | 0.51093 | 1.1223 | 16.7135 | 2726.3202 | 1329.7471 | 1396.5731
2016-04-27 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.7993 | 1386.8609 | 2704.6602 | 22.6015 | 0.48886 | 0.51114 | 1.1467 | 19.7107 | 2724.3709 | 1327.4351 | 1396.9358
2016-04-27 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.8698 | 1447.9823 | 2820.8521 | 30.7989 | 0.48886 | 0.51114 | 1.1955 | 25.7615 | 2846.6135 | 1385.4634 | 1461.1501
2016-04-27 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.63% | 1464.4328 | 1553.3507 | 3017.7836 | 33.4049 | 0.48814 | 0.51186 | 1.2441 | 26.8512 | 3044.6348 | 1477.5401 | 1567.0947
2016-04-28 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.75% | 1531.4674 | 1637.0651 | 3168.5326 | 64.3997 | 0.48877 | 0.51123 | 1.4888 | 43.2571 | 3211.7897 | 1552.6101 | 1659.1796
2016-04-28 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.62% | 1529.3625 | 1641.275 | 3170.6375 | 62.0348 | 0.48809 | 0.51191 | 1.4881 | 41.6874 | 3212.3249 | 1549.7099 | 1662.615
2016-04-28 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.81% | 1532.283 | 1635.434 | 3167.717 | 61.8857 | 0.48903 | 0.51097 | 1.489 | 41.5612 | 3209.2782 | 1552.6075 | 1656.6707
2016-04-28 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.72% | 1530.9898 | 1638.0203 | 3169.0102 | 64.9744 | 0.48861 | 0.51139 | 1.4886 | 43.6476 | 3212.6577 | 1552.3166 | 1660.3411
2016-04-28 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.78% | 1531.8127 | 1636.3747 | 3168.1873 | 65.6724 | 0.48888 | 0.51112 | 1.4889 | 44.1087 | 3212.296 | 1553.3763 | 1658.9197
2016-04-28 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.14% | 1537.4989 | 1625.0022 | 3162.5011 | 64.3395 | 0.49069 | 0.50931 | 1.4907 | 43.1608 | 3205.6619 | 1558.6775 | 1646.9844
2016-04-28 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98% | 1535.3507 | 1629.2987 | 3164.6493 | 76.3551 | 0.49001 | 0.50999 | 1.49 | 51.2449 | 3215.8942 | 1560.4609 | 1655.4333
2016-04-28 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.92% | 1534.1194 | 1631.7612 | 3165.8806 | 95.599 | 0.48961 | 0.51039 | 1.4896 | 64.1771 | 3230.0577 | 1565.5413 | 1664.5164
2016-04-28 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.98% | 1535.019 | 1629.9621 | 3164.981 | 88.6912 | 0.4899 | 0.5101 | 1.4899 | 59.5283 | 3224.5094 | 1564.1819 | 1660.3275
2016-04-28 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.98% | 1469.7137 | 1545.4294 | 3015.1431 | 52.3004 | 0.4899 | 0.5101 | 1.245 | 42.01 | 3057.1531 | 1490.2946 | 1566.8585
2016-04-28 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.42% | 1461.2273 | 1558.159 | 3019.3863 | 58.909 | 0.48708 | 0.51292 | 1.2435 | 47.3721 | 3066.7584 | 1484.3011 | 1582.4573
2016-04-28 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.46% | 1461.9044 | 1557.1434 | 3019.0478 | 57.5117 | 0.4873 | 0.5127 | 1.2437 | 46.2442 | 3065.292 | 1484.4393 | 1580.8528
2016-04-28 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.45% | 1461.729 | 1557.4064 | 3019.1355 | 55.3313 | 0.48724 | 0.51276 | 1.2436 | 44.4921 | 3063.6275 | 1483.4075 | 1580.22
2016-04-28 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.54% | 1463.1648 | 1555.2528 | 3018.4176 | 56.4803 | 0.48772 | 0.51228 | 1.2439 | 45.4072 | 3063.8248 | 1485.3109 | 1578.5139
2016-04-28 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.51% | 1369.2027 | 1453.1163 | 2822.3189 | 45.3225 | 0.48755 | 0.51245 | 1.195 | 37.9261 | 2860.245 | 1387.6935 | 1472.5515
2016-04-28 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7193 | 1448.193 | 2820.9123 | 39.1689 | 0.4888 | 0.5112 | 1.1955 | 32.763 | 2853.6753 | 1388.7339 | 1464.9414
2016-04-28 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.95% | 1375.3595 | 1444.4967 | 2819.8562 | 32.2105 | 0.48974 | 0.51026 | 1.1959 | 26.9342 | 2846.7904 | 1388.5503 | 1458.2401
2016-04-28 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.11% | 1377.6865 | 1441.2389 | 2818.9254 | 31.7567 | 0.49057 | 0.50943 | 1.1962 | 26.5473 | 2845.4727 | 1390.7098 | 1454.7629
2016-04-28 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8382 | 1540.7427 | 3013.5809 | 33.2752 | 0.49095 | 0.50905 | 1.2455 | 26.7169 | 3040.2978 | 1485.9547 | 1554.3431
2016-04-28 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-04-28 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-04-28 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-28 22:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.77% | 1588.7811 | 1704.6816 | 3293.4627 | 92.3968 | 0.48886 | 0.51114 | 1.5866 | 58.2347 | 3351.6974 | 1617.2495 | 1734.4479
2016-04-28 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.63% | 1586.4689 | 1709.7684 | 3296.2373 | 80.1717 | 0.48814 | 0.51186 | 1.5858 | 50.5569 | 3346.7942 | 1611.148 | 1735.6462
2016-04-29 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.75% | 1588.4902 | 1705.3216 | 3293.8118 | 77.2797 | 0.48877 | 0.51123 | 1.5865 | 48.7102 | 3342.522 | 1612.2981 | 1730.2239
2016-04-29 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.62% | 1586.3069 | 1710.1249 | 3296.4318 | 74.4417 | 0.48809 | 0.51191 | 1.5857 | 46.9453 | 3343.377 | 1609.2206 | 1734.1564
2016-04-29 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.81% | 1589.3361 | 1703.4606 | 3292.7967 | 74.2628 | 0.48903 | 0.51097 | 1.5868 | 46.7994 | 3339.5961 | 1612.2222 | 1727.3739
2016-04-29 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.72% | 1587.9948 | 1706.4115 | 3294.4063 | 77.9692 | 0.48861 | 0.51139 | 1.5863 | 49.1505 | 3343.5568 | 1612.0104 | 1731.5464
2016-04-29 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.78% | 1588.8482 | 1704.5339 | 3293.3821 | 78.8068 | 0.48888 | 0.51112 | 1.5867 | 49.6686 | 3343.0508 | 1613.1301 | 1729.9207
2016-04-29 05:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98.14% | 1594.7462 | 1691.5584 | 3286.3046 | 77.2074 | 0.49069 | 0.50931 | 1.5888 | 48.5939 | 3334.8984 | 1618.5908 | 1716.3077
2016-04-29 06:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 98% | 1592.518 | 1696.4605 | 3288.9784 | 91.6262 | 0.49001 | 0.50999 | 1.588 | 57.6988 | 3346.6773 | 1620.7907 | 1725.8865
2016-04-29 07:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.92% | 1591.2409 | 1699.2701 | 3290.5109 | 114.7188 | 0.48961 | 0.51039 | 1.5875 | 72.2622 | 3362.7732 | 1626.6214 | 1736.1518
2016-04-29 08:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1739 | 1697.2174 | 3289.3913 | 106.4295 | 0.4899 | 0.5101 | 1.5879 | 67.0262 | 3356.4175 | 1625.01 | 1731.4074
2016-04-29 09:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.98% | 1592.1899 | 1697.1823 | 3289.3721 | 125.5209 | 0.4899 | 0.5101 | 1.5879 | 79.0491 | 3368.4213 | 1630.9164 | 1737.5049
2016-04-29 10:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.42% | 1582.9963 | 1717.4082 | 3300.4045 | 141.3816 | 0.48708 | 0.51292 | 1.5845 | 89.2284 | 3389.6329 | 1626.4573 | 1763.1756
2016-04-29 11:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.46% | 1583.7298 | 1715.7945 | 3299.5243 | 138.0281 | 0.4873 | 0.5127 | 1.5848 | 87.097 | 3386.6213 | 1626.1723 | 1760.449
2016-04-29 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.45% | 1526.6948 | 1646.6104 | 3173.3052 | 110.6626 | 0.48724 | 0.51276 | 1.4872 | 74.4079 | 3247.7131 | 1562.9495 | 1684.7636
2016-04-29 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.54% | 1528.1944 | 1643.6113 | 3171.8056 | 112.9606 | 0.48772 | 0.51228 | 1.4877 | 75.9286 | 3247.7342 | 1565.2264 | 1682.5078
2016-04-29 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.51% | 1462.6497 | 1556.0254 | 3018.6751 | 56.6531 | 0.48755 | 0.51245 | 1.2438 | 45.5493 | 3064.2244 | 1484.8573 | 1579.3671
2016-04-29 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4063 | 1550.3905 | 3016.7968 | 48.9611 | 0.4888 | 0.5112 | 1.2444 | 39.3451 | 3056.1419 | 1485.6383 | 1570.5036
2016-04-29 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.95% | 1469.2267 | 1546.1599 | 3015.3866 | 40.2631 | 0.48974 | 0.51026 | 1.2449 | 32.3432 | 3047.7298 | 1485.0666 | 1562.6633
2016-04-29 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.11% | 1471.7126 | 1542.4312 | 3014.1437 | 39.6958 | 0.49057 | 0.50943 | 1.2453 | 31.8769 | 3046.0206 | 1487.3504 | 1558.6702
2016-04-29 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8382 | 1540.7427 | 3013.5809 | 33.2752 | 0.49095 | 0.50905 | 1.2455 | 26.7169 | 3040.2978 | 1485.9547 | 1554.3431
2016-04-29 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.19% | 1472.8729 | 1540.6907 | 3013.5636 | 31.8326 | 0.49096 | 0.50904 | 1.2455 | 25.5585 | 3039.1221 | 1485.421 | 1553.701
2016-04-29 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.81% | 1467.2069 | 1549.1896 | 3016.3965 | 37.514 | 0.48907 | 0.51093 | 1.2445 | 30.143 | 3046.5395 | 1481.9489 | 1564.5906
2016-04-29 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.5831 | 1550.1254 | 3016.7085 | 37.6691 | 0.48886 | 0.51114 | 1.2444 | 30.2702 | 3046.9786 | 1481.381 | 1565.5976
2016-04-29 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7479 | 1636.5042 | 3168.2521 | 76.9973 | 0.48886 | 0.51114 | 1.4889 | 51.7158 | 3219.9678 | 1557.0295 | 1662.9384
2016-04-29 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.11% | 1521.3988 | 1657.2023 | 3178.6012 | 66.8098 | 0.48555 | 0.51445 | 1.4856 | 44.973 | 3223.5742 | 1543.2356 | 1680.3386
2016-04-30 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-04-30 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-04-30 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-04-30 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-04-30 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-04-30 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-04-30 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-04-30 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-04-30 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-04-30 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-04-30 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-04-30 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-04-30 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.6971 | 1449.624 | 2821.3212 | 24.5474 | 0.48844 | 0.51156 | 1.1954 | 20.5353 | 2841.8565 | 1381.7273 | 1460.1291
2016-04-30 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0256 | 1451.9642 | 2821.9898 | 24.0814 | 0.48784 | 0.51216 | 1.1951 | 20.1495 | 2842.1392 | 1379.8554 | 1462.2838
2016-04-30 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-04-30 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-04-30 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-04-30 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-04-30 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-04-30 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-04-30 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-04-30 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-04-30 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-04-30 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-01 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-01 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-01 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-01 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-01 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-01 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-01 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-01 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-01 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-01 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-01 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-01 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-01 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-01 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-01 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-01 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-01 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.87% | 1322.2661 | 1387.1674 | 2709.4335 | 10.3243 | 0.48933 | 0.51067 | 1.1223 | 9.1989 | 2718.6324 | 1326.7674 | 1391.8651
2016-05-01 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-01 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-01 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-01 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-02 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4591 | 1560.8113 | 3020.2704 | 39.9753 | 0.48649 | 0.51351 | 1.2432 | 32.1541 | 3052.4245 | 1475.1016 | 1577.3229
2016-05-02 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.34% | 1460.0645 | 1559.9033 | 3019.9678 | 41.7107 | 0.48669 | 0.51331 | 1.2433 | 33.5472 | 3053.515 | 1476.3915 | 1577.1235
2016-05-02 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.33% | 1459.9794 | 1560.031 | 3020.0103 | 44.4969 | 0.48666 | 0.51334 | 1.2433 | 35.7885 | 3055.7988 | 1477.3962 | 1578.4026
2016-05-02 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.56% | 1463.3251 | 1555.0124 | 3018.3375 | 44.767 | 0.48778 | 0.51222 | 1.2439 | 35.9896 | 3054.3271 | 1480.8799 | 1573.4472
2016-05-02 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.49% | 1462.3598 | 1556.4604 | 3018.8201 | 38.4243 | 0.48745 | 0.51255 | 1.2437 | 30.8945 | 3049.7146 | 1477.4194 | 1572.2952
2016-05-02 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.09% | 1471.3842 | 1542.9237 | 3014.3079 | 28.0673 | 0.49046 | 0.50954 | 1.2452 | 22.5399 | 3036.8478 | 1482.4391 | 1554.4086
2016-05-02 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-02 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-02 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.74% | 1466.0478 | 1550.9282 | 3016.9761 | 30.657 | 0.48868 | 0.51132 | 1.2443 | 24.6371 | 3041.6132 | 1478.0876 | 1563.5256
2016-05-02 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-02 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-02 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-02 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.6971 | 1449.624 | 2821.3212 | 24.5474 | 0.48844 | 0.51156 | 1.1954 | 20.5353 | 2841.8565 | 1381.7273 | 1460.1291
2016-05-02 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0256 | 1451.9642 | 2821.9898 | 24.0814 | 0.48784 | 0.51216 | 1.1951 | 20.1495 | 2842.1392 | 1379.8554 | 1462.2838
2016-05-02 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.61% | 1370.5935 | 1451.1691 | 2821.7626 | 24.5922 | 0.48805 | 0.51195 | 1.1952 | 20.5755 | 2842.338 | 1380.6353 | 1461.7028
2016-05-02 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-02 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-02 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-05-02 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-02 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.87% | 1322.2661 | 1387.1674 | 2709.4335 | 10.3243 | 0.48933 | 0.51067 | 1.1223 | 9.1989 | 2718.6324 | 1326.7674 | 1391.8651
2016-05-02 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-02 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-02 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-03 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-03 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-03 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.33% | 1459.9794 | 1560.031 | 3020.0103 | 44.4969 | 0.48666 | 0.51334 | 1.2433 | 35.7885 | 3055.7988 | 1477.3962 | 1578.4026
2016-05-03 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.56% | 1463.3251 | 1555.0124 | 3018.3375 | 44.767 | 0.48778 | 0.51222 | 1.2439 | 35.9896 | 3054.3271 | 1480.8799 | 1573.4472
2016-05-03 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.49% | 1462.3598 | 1556.4604 | 3018.8201 | 38.4243 | 0.48745 | 0.51255 | 1.2437 | 30.8945 | 3049.7146 | 1477.4194 | 1572.2952
2016-05-03 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.09% | 1471.3842 | 1542.9237 | 3014.3079 | 28.0673 | 0.49046 | 0.50954 | 1.2452 | 22.5399 | 3036.8478 | 1482.4391 | 1554.4086
2016-05-03 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-03 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-03 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-03 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-03 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-03 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-03 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-03 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-03 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-03 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-03 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-03 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-03 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-03 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.87% | 1322.2661 | 1387.1674 | 2709.4335 | 10.3243 | 0.48933 | 0.51067 | 1.1223 | 9.1989 | 2718.6324 | 1326.7674 | 1391.8651
2016-05-03 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-03 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-03 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-03 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-04 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4591 | 1560.8113 | 3020.2704 | 39.9753 | 0.48649 | 0.51351 | 1.2432 | 32.1541 | 3052.4245 | 1475.1016 | 1577.3229
2016-05-04 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.34% | 1460.0645 | 1559.9033 | 3019.9678 | 41.7107 | 0.48669 | 0.51331 | 1.2433 | 33.5472 | 3053.515 | 1476.3915 | 1577.1235
2016-05-04 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.33% | 1459.9794 | 1560.031 | 3020.0103 | 44.4969 | 0.48666 | 0.51334 | 1.2433 | 35.7885 | 3055.7988 | 1477.3962 | 1578.4026
2016-05-04 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.56% | 1463.3251 | 1555.0124 | 3018.3375 | 44.767 | 0.48778 | 0.51222 | 1.2439 | 35.9896 | 3054.3271 | 1480.8799 | 1573.4472
2016-05-04 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.49% | 1462.3598 | 1556.4604 | 3018.8201 | 38.4243 | 0.48745 | 0.51255 | 1.2437 | 30.8945 | 3049.7146 | 1477.4194 | 1572.2952
2016-05-04 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.09% | 1471.3842 | 1542.9237 | 3014.3079 | 28.0673 | 0.49046 | 0.50954 | 1.2452 | 22.5399 | 3036.8478 | 1482.4391 | 1554.4086
2016-05-04 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-04 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-04 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-04 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-04 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-04 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-04 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-04 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-04 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-05-04 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-04 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-04 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-04 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-04 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-04 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-04 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-04 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-04 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.11% | 1521.3988 | 1657.2023 | 3178.6012 | 71.4398 | 0.48555 | 0.51445 | 1.4856 | 48.0897 | 3226.6908 | 1544.7489 | 1681.9419
2016-05-05 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-05 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.34% | 1581.7365 | 1720.1797 | 3301.9162 | 100.1058 | 0.48669 | 0.51331 | 1.584 | 63.197 | 3365.1133 | 1612.4937 | 1752.6195
2016-05-05 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.33% | 1581.6443 | 1720.3825 | 3302.0268 | 106.7926 | 0.48666 | 0.51334 | 1.584 | 67.4199 | 3369.4467 | 1614.4549 | 1754.9919
2016-05-05 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.56% | 1585.2688 | 1712.4086 | 3297.6774 | 107.4408 | 0.48778 | 0.51222 | 1.5853 | 67.7719 | 3365.4493 | 1618.3262 | 1747.1231
2016-05-05 04:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.49% | 1584.2231 | 1714.7092 | 3298.9323 | 92.2182 | 0.48745 | 0.51255 | 1.5849 | 58.1839 | 3357.1162 | 1612.585 | 1744.5312
2016-05-05 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-05 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.82% | 1532.5066 | 1634.9867 | 3167.4934 | 65.4778 | 0.4891 | 0.5109 | 1.4891 | 43.9715 | 3211.4648 | 1554.013 | 1657.4518
2016-05-05 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-05 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-05 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-05 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-05 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-05 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-05 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.57% | 1209.8505 | 1274.0689 | 2483.9194 | 7.8265 | 0.48784 | 0.51216 | 1.0634 | 7.3597 | 2491.2791 | 1213.4409 | 1277.8383
2016-05-05 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-05 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-05 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-05 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-05 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6834 | 1298.9819 | 2540.6653 | 3.6053 | 0.48915 | 0.51085 | 1.0391 | 3.4695 | 2544.1349 | 1243.3805 | 1300.7544
2016-05-05 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-05 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-05 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-05 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-05 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.11% | 1456.6585 | 1565.0123 | 3021.6708 | 35.7199 | 0.48555 | 0.51445 | 1.2428 | 28.742 | 3050.4128 | 1470.6142 | 1579.7985
2016-05-06 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-06 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-05-06 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-05-06 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-05-06 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-05-06 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-06 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.82% | 1532.5066 | 1634.9867 | 3167.4934 | 65.4778 | 0.4891 | 0.5109 | 1.4891 | 43.9715 | 3211.4648 | 1554.013 | 1657.4518
2016-05-06 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.76% | 1531.5832 | 1636.8336 | 3168.4168 | 60.5553 | 0.4888 | 0.5112 | 1.4888 | 40.6738 | 3209.0906 | 1551.4647 | 1657.6259
2016-05-06 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.74% | 1466.0478 | 1550.9282 | 3016.9761 | 30.657 | 0.48868 | 0.51132 | 1.2443 | 24.6371 | 3041.6132 | 1478.0876 | 1563.5256
2016-05-06 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.57% | 1463.5341 | 1554.6988 | 3018.2329 | 31.9062 | 0.48784 | 0.51216 | 1.2439 | 25.6497 | 3043.8826 | 1476.0472 | 1567.8354
2016-05-06 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-06 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-06 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-06 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-06 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-05-06 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-06 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-06 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-05-06 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-05-06 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.87% | 1374.1889 | 1446.1355 | 2820.3244 | 16.5188 | 0.48933 | 0.51067 | 1.1957 | 13.8148 | 2834.1393 | 1380.9489 | 1453.1904
2016-05-06 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.25% | 1365.4921 | 1458.3111 | 2823.8032 | 24.5515 | 0.48623 | 0.51377 | 1.1945 | 20.5539 | 2844.3571 | 1375.4859 | 1468.8711
2016-05-06 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.36% | 1367.0906 | 1456.0731 | 2823.1637 | 21.601 | 0.4868 | 0.5132 | 1.1947 | 18.0804 | 2841.2442 | 1375.8922 | 1465.352
2016-05-06 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.34% | 1460.0649 | 1559.9027 | 3019.9676 | 28.963 | 0.48669 | 0.51331 | 1.2433 | 23.2944 | 3043.262 | 1471.402 | 1571.86
2016-05-06 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.11% | 1456.6585 | 1565.0123 | 3021.6708 | 35.7199 | 0.48555 | 0.51445 | 1.2428 | 28.742 | 3050.4128 | 1470.6142 | 1579.7985
2016-05-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-07 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-05-07 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-05-07 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-05-07 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-05-07 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-07 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-07 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-07 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-07 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-07 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-07 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-07 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-07 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-07 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.352 | 1273.5022 | 2483.8542 | 7.9925 | 0.48805 | 0.51195 | 1.0634 | 7.5156 | 2491.3699 | 1214.02 | 1277.3499
2016-05-07 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.3653 | 1273.4872 | 2483.8525 | 8.2387 | 0.48805 | 0.51195 | 1.0634 | 7.7472 | 2491.5997 | 1214.1463 | 1277.4534
2016-05-07 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.72% | 1211.7394 | 1271.9345 | 2483.6739 | 6.054 | 0.4886 | 0.5114 | 1.0635 | 5.6925 | 2489.3663 | 1214.5207 | 1274.8456
2016-05-07 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.66% | 1211.0428 | 1272.7216 | 2483.7644 | 5.3438 | 0.48832 | 0.51168 | 1.0635 | 5.0248 | 2488.7893 | 1213.4965 | 1275.2927
2016-05-07 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-07 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-07 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-07 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-07 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-07 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-08 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-08 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-08 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-08 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-08 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-08 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-08 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-08 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-08 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-08 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-08 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-08 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-08 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-08 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-08 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-05-08 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-08 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-08 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-05-08 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-05-08 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-08 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-08 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-08 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-08 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-09 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-09 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-09 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-09 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-09 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-09 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-09 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-09 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-09 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-09 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-09 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-09 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-09 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.6971 | 1449.624 | 2821.3212 | 24.5474 | 0.48844 | 0.51156 | 1.1954 | 20.5353 | 2841.8565 | 1381.7273 | 1460.1291
2016-05-09 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0256 | 1451.9642 | 2821.9898 | 24.0814 | 0.48784 | 0.51216 | 1.1951 | 20.1495 | 2842.1392 | 1379.8554 | 1462.2838
2016-05-09 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.61% | 1370.5935 | 1451.1691 | 2821.7626 | 24.5922 | 0.48805 | 0.51195 | 1.1952 | 20.5755 | 2842.338 | 1380.6353 | 1461.7028
2016-05-09 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.61% | 1370.6085 | 1451.1481 | 2821.7566 | 25.3499 | 0.48805 | 0.51195 | 1.1952 | 21.2094 | 2842.966 | 1380.9598 | 1462.0062
2016-05-09 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.72% | 1372.1646 | 1448.9696 | 2821.1342 | 18.6278 | 0.4886 | 0.5114 | 1.1954 | 15.5823 | 2836.7165 | 1379.7782 | 1456.9383
2016-05-09 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.66% | 1371.3757 | 1450.074 | 2821.4497 | 16.4425 | 0.48832 | 0.51168 | 1.1953 | 13.7556 | 2835.2053 | 1378.093 | 1457.1124
2016-05-09 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.83% | 1373.6906 | 1446.8331 | 2820.5237 | 18.0265 | 0.48915 | 0.51085 | 1.1957 | 15.0766 | 2835.6003 | 1381.0653 | 1454.535
2016-05-09 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.87% | 1467.9763 | 1548.0355 | 3016.0118 | 20.6485 | 0.48933 | 0.51067 | 1.2447 | 16.5897 | 3032.6015 | 1476.0941 | 1556.5074
2016-05-09 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.25% | 1458.6859 | 1561.9712 | 3020.6571 | 30.6893 | 0.48623 | 0.51377 | 1.2431 | 24.6875 | 3045.3445 | 1470.6896 | 1574.6549
2016-05-09 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.36% | 1460.3936 | 1559.4097 | 3019.8032 | 27.0013 | 0.4868 | 0.5132 | 1.2434 | 21.7157 | 3041.5189 | 1470.9647 | 1570.5542
2016-05-09 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.34% | 1460.0649 | 1559.9027 | 3019.9676 | 28.963 | 0.48669 | 0.51331 | 1.2433 | 23.2944 | 3043.262 | 1471.402 | 1571.86
2016-05-09 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.11% | 1521.3988 | 1657.2023 | 3178.6012 | 71.4398 | 0.48555 | 0.51445 | 1.4856 | 48.0897 | 3226.6908 | 1544.7489 | 1681.9419
2016-05-10 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-10 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-05-10 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-05-10 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-05-10 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-05-10 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-10 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.82% | 1532.5066 | 1634.9867 | 3167.4934 | 65.4778 | 0.4891 | 0.5109 | 1.4891 | 43.9715 | 3211.4648 | 1554.013 | 1657.4518
2016-05-10 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.76% | 1531.5832 | 1636.8336 | 3168.4168 | 60.5553 | 0.4888 | 0.5112 | 1.4888 | 40.6738 | 3209.0906 | 1551.4647 | 1657.6259
2016-05-10 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.74% | 1531.2055 | 1637.5889 | 3168.7945 | 61.3139 | 0.48868 | 0.51132 | 1.4887 | 41.1867 | 3209.9812 | 1551.3328 | 1658.6484
2016-05-10 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.57% | 1528.5801 | 1642.8398 | 3171.4199 | 63.8123 | 0.48784 | 0.51216 | 1.4878 | 42.8891 | 3214.309 | 1549.5033 | 1664.8057
2016-05-10 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.69% | 1530.4589 | 1639.0822 | 3169.5411 | 62.9951 | 0.48844 | 0.51156 | 1.4884 | 42.3228 | 3211.8639 | 1551.1312 | 1660.7327
2016-05-10 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.58% | 1463.6294 | 1554.556 | 3018.1853 | 30.6257 | 0.48788 | 0.51212 | 1.2439 | 24.62 | 3042.8053 | 1475.6409 | 1567.1644
2016-05-10 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.6971 | 1449.624 | 2821.3212 | 24.5474 | 0.48844 | 0.51156 | 1.1954 | 20.5353 | 2841.8565 | 1381.7273 | 1460.1291
2016-05-10 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0256 | 1451.9642 | 2821.9898 | 24.0814 | 0.48784 | 0.51216 | 1.1951 | 20.1495 | 2842.1392 | 1379.8554 | 1462.2838
2016-05-10 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.61% | 1370.5935 | 1451.1691 | 2821.7626 | 24.5922 | 0.48805 | 0.51195 | 1.1952 | 20.5755 | 2842.338 | 1380.6353 | 1461.7028
2016-05-10 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-10 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-10 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-05-10 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-05-10 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-10 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-10 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-10 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-10 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-11 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.3% | 1459.4591 | 1560.8113 | 3020.2704 | 39.9753 | 0.48649 | 0.51351 | 1.2432 | 32.1541 | 3052.4245 | 1475.1016 | 1577.3229
2016-05-11 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.34% | 1460.0645 | 1559.9033 | 3019.9678 | 41.7107 | 0.48669 | 0.51331 | 1.2433 | 33.5472 | 3053.515 | 1476.3915 | 1577.1235
2016-05-11 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.33% | 1459.9794 | 1560.031 | 3020.0103 | 44.4969 | 0.48666 | 0.51334 | 1.2433 | 35.7885 | 3055.7988 | 1477.3962 | 1578.4026
2016-05-11 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.56% | 1463.3251 | 1555.0124 | 3018.3375 | 44.767 | 0.48778 | 0.51222 | 1.2439 | 35.9896 | 3054.3271 | 1480.8799 | 1573.4472
2016-05-11 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.49% | 1462.3598 | 1556.4604 | 3018.8201 | 38.4243 | 0.48745 | 0.51255 | 1.2437 | 30.8945 | 3049.7146 | 1477.4194 | 1572.2952
2016-05-11 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.09% | 1471.3842 | 1542.9237 | 3014.3079 | 28.0673 | 0.49046 | 0.50954 | 1.2452 | 22.5399 | 3036.8478 | 1482.4391 | 1554.4086
2016-05-11 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-11 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-11 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-11 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-11 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-11 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-11 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-11 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-11 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-11 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-11 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-11 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-11 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-05-11 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-11 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-11 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-11 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-11 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.11% | 1456.6585 | 1565.0123 | 3021.6708 | 35.7199 | 0.48555 | 0.51445 | 1.2428 | 28.742 | 3050.4128 | 1470.6142 | 1579.7985
2016-05-12 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-12 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-05-12 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-05-12 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-05-12 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-05-12 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-12 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-12 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-12 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.74% | 1466.0478 | 1550.9282 | 3016.9761 | 30.657 | 0.48868 | 0.51132 | 1.2443 | 24.6371 | 3041.6132 | 1478.0876 | 1563.5256
2016-05-12 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-12 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-12 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-12 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-12 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-12 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-05-12 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-12 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-12 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.66% | 1316.3509 | 1388.7439 | 2705.0947 | 12.3319 | 0.48832 | 0.51168 | 1.1465 | 10.7562 | 2715.8509 | 1321.6033 | 1394.2475
2016-05-12 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5729 | 1385.8553 | 2704.4281 | 13.5198 | 0.48915 | 0.51085 | 1.1467 | 11.7898 | 2716.2179 | 1324.3398 | 1391.8781
2016-05-12 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-12 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-12 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-12 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-12 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-13 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-13 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-13 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-13 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-13 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-13 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-13 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-13 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-13 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-13 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-13 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-13 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-13 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-13 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-13 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-13 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-13 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-13 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-13 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-13 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-13 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-13 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-13 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-13 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-14 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-14 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-14 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-14 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-14 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-14 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-14 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-14 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-14 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-14 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-14 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-14 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-14 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-14 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0549 | 1390.4286 | 2705.4835 | 18.061 | 0.48784 | 0.51216 | 1.1464 | 15.7552 | 2721.2387 | 1322.741 | 1398.4978
2016-05-14 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6 | 1389.72 | 2705.32 | 18.4441 | 0.48805 | 0.51195 | 1.1464 | 16.0885 | 2721.4085 | 1323.452 | 1397.9566
2016-05-14 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.61% | 1315.6144 | 1389.7012 | 2705.3157 | 19.0124 | 0.48805 | 0.51195 | 1.1464 | 16.5843 | 2721.8999 | 1323.7084 | 1398.1915
2016-05-14 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.72% | 1317.108 | 1387.7596 | 2704.8676 | 13.9708 | 0.4886 | 0.5114 | 1.1466 | 12.1848 | 2717.0524 | 1323.0616 | 1393.9908
2016-05-14 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.66% | 1371.3757 | 1450.074 | 2821.4497 | 16.4425 | 0.48832 | 0.51168 | 1.1953 | 13.7556 | 2835.2053 | 1378.093 | 1457.1124
2016-05-14 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.83% | 1373.6906 | 1446.8331 | 2820.5237 | 18.0265 | 0.48915 | 0.51085 | 1.1957 | 15.0766 | 2835.6003 | 1381.0653 | 1454.535
2016-05-14 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.87% | 1374.1889 | 1446.1355 | 2820.3244 | 16.5188 | 0.48933 | 0.51067 | 1.1957 | 13.8148 | 2834.1393 | 1380.9489 | 1453.1904
2016-05-14 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.25% | 1365.4921 | 1458.3111 | 2823.8032 | 24.5515 | 0.48623 | 0.51377 | 1.1945 | 20.5539 | 2844.3571 | 1375.4859 | 1468.8711
2016-05-14 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.36% | 1367.0906 | 1456.0731 | 2823.1637 | 21.601 | 0.4868 | 0.5132 | 1.1947 | 18.0804 | 2841.2442 | 1375.8922 | 1465.352
2016-05-14 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-14 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-15 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-15 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-15 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-15 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-15 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-15 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-15 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-15 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-15 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-15 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-15 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-15 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-15 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-15 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-15 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-15 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-15 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-15 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-15 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-15 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.87% | 1322.2661 | 1387.1674 | 2709.4335 | 10.3243 | 0.48933 | 0.51067 | 1.1223 | 9.1989 | 2718.6324 | 1326.7674 | 1391.8651
2016-05-15 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-15 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-15 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-15 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-16 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-16 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-16 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-16 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-16 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-16 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-16 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-16 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-16 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-16 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-16 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-16 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-16 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3266 | 1272.401 | 2483.7275 | 7.9779 | 0.48844 | 0.51156 | 1.0635 | 7.5016 | 2491.2291 | 1214.9906 | 1276.2385
2016-05-16 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.57% | 1209.8505 | 1274.0689 | 2483.9194 | 7.8265 | 0.48784 | 0.51216 | 1.0634 | 7.3597 | 2491.2791 | 1213.4409 | 1277.8383
2016-05-16 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-16 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-16 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-16 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-16 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6834 | 1298.9819 | 2540.6653 | 3.6053 | 0.48915 | 0.51085 | 1.0391 | 3.4695 | 2544.1349 | 1243.3805 | 1300.7544
2016-05-16 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.87% | 1242.1338 | 1298.4955 | 2540.6293 | 3.3038 | 0.48933 | 0.51067 | 1.0391 | 3.1793 | 2543.8086 | 1243.6895 | 1300.1191
2016-05-16 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.25% | 1234.2727 | 1306.9855 | 2541.2582 | 4.9103 | 0.48623 | 0.51377 | 1.0389 | 4.7264 | 2545.9846 | 1236.5708 | 1309.4138
2016-05-16 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-16 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.34% | 1206.987 | 1277.3047 | 2484.2917 | 7.5304 | 0.48669 | 0.51331 | 1.0633 | 7.0823 | 2491.374 | 1210.4338 | 1280.9401
2016-05-16 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.0716 | 1399.9105 | 2711.9821 | 17.8599 | 0.48555 | 0.51445 | 1.1214 | 15.9266 | 2727.9087 | 1319.8048 | 1408.1039
2016-05-17 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-17 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-17 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-17 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-17 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-17 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-17 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-17 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-17 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.74% | 1320.529 | 1389.3387 | 2709.8677 | 15.3285 | 0.48868 | 0.51132 | 1.1222 | 13.6597 | 2723.5274 | 1327.2043 | 1396.3231
2016-05-17 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-17 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3419 | 1272.3836 | 2483.7256 | 8.1894 | 0.48844 | 0.51156 | 1.0635 | 7.7004 | 2491.426 | 1215.1031 | 1276.3228
2016-05-17 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.58% | 1238.4556 | 1302.4679 | 2540.9236 | 4.9001 | 0.48788 | 0.51212 | 1.039 | 4.716 | 2545.6396 | 1240.7565 | 1304.8831
2016-05-17 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.69% | 1239.8814 | 1300.928 | 2540.8095 | 4.9095 | 0.48844 | 0.51156 | 1.0391 | 4.7249 | 2545.5343 | 1242.1892 | 1303.3451
2016-05-17 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.57% | 1209.8505 | 1270.1495 | 2480 | 0 | 0.48784 | 0.51216 | 1 | 0 | 2480 | 1209.8505 | 1270.1495
2016-05-17 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.61% | 1210.352 | 1269.648 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.352 | 1269.648
2016-05-17 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.61% | 1210.3653 | 1269.6347 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.3653 | 1269.6347
2016-05-17 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-17 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-17 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6834 | 1298.9819 | 2540.6653 | 3.6053 | 0.48915 | 0.51085 | 1.0391 | 3.4695 | 2544.1349 | 1243.3805 | 1300.7544
2016-05-17 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-17 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-17 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-17 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-17 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-18 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-18 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-18 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-18 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-18 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-18 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-18 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-18 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-18 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-18 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-18 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-18 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-18 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-18 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-18 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.352 | 1273.5022 | 2483.8542 | 7.9925 | 0.48805 | 0.51195 | 1.0634 | 7.5156 | 2491.3699 | 1214.02 | 1277.3499
2016-05-18 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.3653 | 1273.4872 | 2483.8525 | 8.2387 | 0.48805 | 0.51195 | 1.0634 | 7.7472 | 2491.5997 | 1214.1463 | 1277.4534
2016-05-18 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.72% | 1211.7394 | 1271.9345 | 2483.6739 | 6.054 | 0.4886 | 0.5114 | 1.0635 | 5.6925 | 2489.3663 | 1214.5207 | 1274.8456
2016-05-18 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.66% | 1211.0428 | 1272.7216 | 2483.7644 | 5.3438 | 0.48832 | 0.51168 | 1.0635 | 5.0248 | 2488.7893 | 1213.4965 | 1275.2927
2016-05-18 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-18 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.87% | 1319.0512 | 1385.2335 | 2704.2846 | 12.3891 | 0.48933 | 0.51067 | 1.1468 | 10.8032 | 2715.0879 | 1324.3375 | 1390.7504
2016-05-18 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-18 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-18 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.783 | 1456.5039 | 2823.2868 | 23.1704 | 0.48669 | 0.51331 | 1.1947 | 19.3947 | 2842.6815 | 1376.2221 | 1466.4594
2016-05-18 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.11% | 1456.6585 | 1565.0123 | 3021.6708 | 35.7199 | 0.48555 | 0.51445 | 1.2428 | 28.742 | 3050.4128 | 1470.6142 | 1579.7985
2016-05-19 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.3% | 1524.324 | 1651.3521 | 3175.676 | 79.9506 | 0.48649 | 0.51351 | 1.4865 | 53.785 | 3229.461 | 1550.4896 | 1678.9714
2016-05-19 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.34% | 1524.9562 | 1650.0876 | 3175.0438 | 83.4215 | 0.48669 | 0.51331 | 1.4867 | 56.1123 | 3231.1561 | 1552.2654 | 1678.8907
2016-05-19 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.33% | 1524.8673 | 1650.2653 | 3175.1327 | 88.9938 | 0.48666 | 0.51334 | 1.4867 | 59.8616 | 3234.9943 | 1553.9996 | 1680.9947
2016-05-19 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.56% | 1528.3617 | 1643.2766 | 3171.6383 | 89.534 | 0.48778 | 0.51222 | 1.4878 | 60.1798 | 3231.8181 | 1557.7159 | 1674.1022
2016-05-19 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.49% | 1527.3535 | 1645.293 | 3172.6465 | 76.8485 | 0.48745 | 0.51255 | 1.4875 | 51.6645 | 3224.311 | 1552.5375 | 1671.7734
2016-05-19 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.09% | 1536.7791 | 1626.4419 | 3163.2209 | 56.1347 | 0.49046 | 0.50954 | 1.4905 | 37.6626 | 3200.8836 | 1555.2511 | 1645.6325
2016-05-19 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.82% | 1532.5066 | 1634.9867 | 3167.4934 | 65.4778 | 0.4891 | 0.5109 | 1.4891 | 43.9715 | 3211.4648 | 1554.013 | 1657.4518
2016-05-19 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-19 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.74% | 1466.0478 | 1550.9282 | 3016.9761 | 30.657 | 0.48868 | 0.51132 | 1.2443 | 24.6371 | 3041.6132 | 1478.0876 | 1563.5256
2016-05-19 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-19 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-19 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-19 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-19 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-19 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-19 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-19 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-19 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-19 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.087 | 1270.4116 | 2483.4987 | 5.8586 | 0.48915 | 0.51085 | 1.0636 | 5.5083 | 2489.007 | 1215.7814 | 1273.2256
2016-05-19 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-19 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-19 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-19 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-19 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-20 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-20 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-20 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-20 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-20 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-20 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-20 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-20 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-20 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-20 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.57% | 1315.0597 | 1390.4224 | 2705.4821 | 19.1437 | 0.48784 | 0.51216 | 1.1464 | 16.6997 | 2722.1818 | 1323.2065 | 1398.9753
2016-05-20 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-20 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-20 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3266 | 1272.401 | 2483.7275 | 7.9779 | 0.48844 | 0.51156 | 1.0635 | 7.5016 | 2491.2291 | 1214.9906 | 1276.2385
2016-05-20 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.57% | 1209.8505 | 1274.0689 | 2483.9194 | 7.8265 | 0.48784 | 0.51216 | 1.0634 | 7.3597 | 2491.2791 | 1213.4409 | 1277.8383
2016-05-20 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.352 | 1273.5022 | 2483.8542 | 7.9925 | 0.48805 | 0.51195 | 1.0634 | 7.5156 | 2491.3699 | 1214.02 | 1277.3499
2016-05-20 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-20 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-20 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-20 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.087 | 1270.4116 | 2483.4987 | 5.8586 | 0.48915 | 0.51085 | 1.0636 | 5.5083 | 2489.007 | 1215.7814 | 1273.2256
2016-05-20 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-20 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-20 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-20 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-20 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-21 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-21 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-21 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-21 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-21 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-21 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-21 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-21 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-21 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-21 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-21 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-21 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.58% | 1318.3506 | 1392.0618 | 2710.4124 | 15.3129 | 0.48788 | 0.51212 | 1.122 | 13.6482 | 2724.0606 | 1325.0092 | 1399.0513
2016-05-21 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3266 | 1272.401 | 2483.7275 | 7.9779 | 0.48844 | 0.51156 | 1.0635 | 7.5016 | 2491.2291 | 1214.9906 | 1276.2385
2016-05-21 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.57% | 1238.3706 | 1302.5598 | 2540.9304 | 4.8163 | 0.48784 | 0.51216 | 1.039 | 4.6354 | 2545.5657 | 1240.6319 | 1304.9338
2016-05-21 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-21 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-21 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-21 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-21 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6834 | 1298.9819 | 2540.6653 | 3.6053 | 0.48915 | 0.51085 | 1.0391 | 3.4695 | 2544.1349 | 1243.3805 | 1300.7544
2016-05-21 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-21 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-21 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-21 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-21 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-22 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-22 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-22 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-22 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-22 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-22 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-22 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-22 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-22 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-22 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-22 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-22 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.58% | 1370.1197 | 1451.8324 | 2821.9521 | 24.5006 | 0.48788 | 0.51212 | 1.1952 | 20.5 | 2842.4521 | 1380.1212 | 1462.3309
2016-05-22 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-22 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-22 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8065 | 1391.4919 | 2710.2984 | 15.3701 | 0.48805 | 0.51195 | 1.122 | 13.6987 | 2723.9971 | 1325.4921 | 1398.505
2016-05-22 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.61% | 1318.8209 | 1391.4738 | 2710.2948 | 15.8437 | 0.48805 | 0.51195 | 1.122 | 14.1208 | 2724.4155 | 1325.7126 | 1398.7029
2016-05-22 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.72% | 1320.3182 | 1389.6023 | 2709.9205 | 11.6424 | 0.4886 | 0.5114 | 1.1222 | 10.375 | 2720.2955 | 1325.3875 | 1394.908
2016-05-22 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.66% | 1319.5592 | 1390.551 | 2710.1102 | 10.2766 | 0.48832 | 0.51168 | 1.1221 | 9.1585 | 2719.2687 | 1324.0315 | 1395.2372
2016-05-22 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7866 | 1387.7668 | 2709.5534 | 11.2665 | 0.48915 | 0.51085 | 1.1223 | 10.0389 | 2719.5923 | 1326.6971 | 1392.8952
2016-05-22 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.87% | 1322.2661 | 1387.1674 | 2709.4335 | 10.3243 | 0.48933 | 0.51067 | 1.1223 | 9.1989 | 2718.6324 | 1326.7674 | 1391.8651
2016-05-22 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.25% | 1310.7032 | 1396.0858 | 2706.789 | 18.4136 | 0.48623 | 0.51377 | 1.1459 | 16.0696 | 2722.8586 | 1318.5167 | 1404.3419
2016-05-22 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.36% | 1312.2377 | 1394.091 | 2706.3287 | 16.2008 | 0.4868 | 0.5132 | 1.146 | 14.1363 | 2720.465 | 1319.1192 | 1401.3458
2016-05-22 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-22 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-23 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-23 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-23 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.33% | 1459.9794 | 1560.031 | 3020.0103 | 44.4969 | 0.48666 | 0.51334 | 1.2433 | 35.7885 | 3055.7988 | 1477.3962 | 1578.4026
2016-05-23 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.56% | 1463.3251 | 1555.0124 | 3018.3375 | 44.767 | 0.48778 | 0.51222 | 1.2439 | 35.9896 | 3054.3271 | 1480.8799 | 1573.4472
2016-05-23 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.49% | 1462.3598 | 1556.4604 | 3018.8201 | 38.4243 | 0.48745 | 0.51255 | 1.2437 | 30.8945 | 3049.7146 | 1477.4194 | 1572.2952
2016-05-23 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.09% | 1471.3842 | 1542.9237 | 3014.3079 | 28.0673 | 0.49046 | 0.50954 | 1.2452 | 22.5399 | 3036.8478 | 1482.4391 | 1554.4086
2016-05-23 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.82% | 1467.2936 | 1549.0596 | 3016.3532 | 32.7389 | 0.4891 | 0.5109 | 1.2445 | 26.3058 | 3042.659 | 1480.1597 | 1562.4993
2016-05-23 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.76% | 1466.4094 | 1550.3858 | 3016.7953 | 30.2776 | 0.4888 | 0.5112 | 1.2444 | 24.3311 | 3041.1264 | 1478.3026 | 1562.8238
2016-05-23 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.74% | 1466.0478 | 1550.9282 | 3016.9761 | 30.657 | 0.48868 | 0.51132 | 1.2443 | 24.6371 | 3041.6132 | 1478.0876 | 1563.5256
2016-05-23 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-23 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.69% | 1371.7145 | 1449.5997 | 2821.3142 | 25.198 | 0.48844 | 0.51156 | 1.1954 | 21.0796 | 2842.3938 | 1382.0107 | 1460.3831
2016-05-23 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-23 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.6593 | 1388.3429 | 2705.0022 | 18.4106 | 0.48844 | 0.51156 | 1.1465 | 16.0576 | 2721.0598 | 1324.5025 | 1396.5573
2016-05-23 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.26 | 1392.1749 | 2710.435 | 15.0509 | 0.48784 | 0.51216 | 1.122 | 13.4148 | 2723.8498 | 1324.8044 | 1399.0454
2016-05-23 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.352 | 1273.5022 | 2483.8542 | 7.9925 | 0.48805 | 0.51195 | 1.0634 | 7.5156 | 2491.3699 | 1214.02 | 1277.3499
2016-05-23 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.61% | 1210.3653 | 1273.4872 | 2483.8525 | 8.2387 | 0.48805 | 0.51195 | 1.0634 | 7.7472 | 2491.5997 | 1214.1463 | 1277.4534
2016-05-23 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.72% | 1211.7394 | 1271.9345 | 2483.6739 | 6.054 | 0.4886 | 0.5114 | 1.0635 | 5.6925 | 2489.3663 | 1214.5207 | 1274.8456
2016-05-23 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.66% | 1211.0428 | 1272.7216 | 2483.7644 | 5.3438 | 0.48832 | 0.51168 | 1.0635 | 5.0248 | 2488.7893 | 1213.4965 | 1275.2927
2016-05-23 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.087 | 1270.4116 | 2483.4987 | 5.8586 | 0.48915 | 0.51085 | 1.0636 | 5.5083 | 2489.007 | 1215.7814 | 1273.2256
2016-05-23 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-23 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-23 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-23 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-23 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-24 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.3% | 1366.2159 | 1457.2977 | 2823.5136 | 31.9803 | 0.48649 | 0.51351 | 1.1946 | 26.7708 | 2850.2844 | 1379.2395 | 1471.0449
2016-05-24 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.34% | 1366.7826 | 1456.5044 | 2823.287 | 33.3686 | 0.48669 | 0.51331 | 1.1947 | 27.9311 | 2851.2181 | 1380.3763 | 1470.8418
2016-05-24 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.33% | 1366.7029 | 1456.6159 | 2823.3188 | 35.5975 | 0.48666 | 0.51334 | 1.1947 | 29.7971 | 2853.1159 | 1381.2039 | 1471.912
2016-05-24 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.56% | 1369.8348 | 1452.2312 | 2822.0661 | 35.8136 | 0.48778 | 0.51222 | 1.1951 | 29.9668 | 2852.0328 | 1384.4519 | 1467.581
2016-05-24 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.49% | 1368.9312 | 1453.4963 | 2822.4275 | 30.7394 | 0.48745 | 0.51255 | 1.195 | 25.7238 | 2848.1513 | 1381.4703 | 1466.6809
2016-05-24 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-24 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-24 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-24 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.74% | 1372.3837 | 1448.6628 | 2821.0465 | 24.5256 | 0.48868 | 0.51132 | 1.1955 | 20.5154 | 2841.5619 | 1382.4092 | 1459.1527
2016-05-24 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.57% | 1370.0306 | 1451.9572 | 2821.9878 | 25.5249 | 0.48784 | 0.51216 | 1.1951 | 21.3573 | 2843.3451 | 1380.4496 | 1462.8955
2016-05-24 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.69% | 1316.676 | 1388.3212 | 2704.9972 | 18.8985 | 0.48844 | 0.51156 | 1.1465 | 16.4832 | 2721.4804 | 1324.7271 | 1396.7533
2016-05-24 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.58% | 1315.1452 | 1390.3112 | 2705.4564 | 18.3754 | 0.48788 | 0.51212 | 1.1464 | 16.0293 | 2721.4858 | 1322.9656 | 1398.5202
2016-05-24 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8684 | 1390.1645 | 2710.0329 | 15.3421 | 0.48844 | 0.51156 | 1.1221 | 13.6726 | 2723.7055 | 1326.5466 | 1397.1589
2016-05-24 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.57% | 1209.8505 | 1274.0689 | 2483.9194 | 7.8265 | 0.48784 | 0.51216 | 1.0634 | 7.3597 | 2491.2791 | 1213.4409 | 1277.8383
2016-05-24 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-24 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-24 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-24 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.66% | 1211.0428 | 1272.7216 | 2483.7644 | 5.3438 | 0.48832 | 0.51168 | 1.0635 | 5.0248 | 2488.7893 | 1213.4965 | 1275.2927
2016-05-24 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.087 | 1270.4116 | 2483.4987 | 5.8586 | 0.48915 | 0.51085 | 1.0636 | 5.5083 | 2489.007 | 1215.7814 | 1273.2256
2016-05-24 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-24 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-24 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-24 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-24 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-25 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-25 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-25 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-25 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-25 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-25 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-25 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-25 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-25 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-25 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-25 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-25 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.58% | 1209.9336 | 1273.975 | 2483.9086 | 7.9627 | 0.48788 | 0.51212 | 1.0634 | 7.4878 | 2491.3964 | 1213.5867 | 1277.8097
2016-05-25 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3266 | 1272.401 | 2483.7275 | 7.9779 | 0.48844 | 0.51156 | 1.0635 | 7.5016 | 2491.2291 | 1214.9906 | 1276.2385
2016-05-25 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.57% | 1238.3706 | 1302.5598 | 2540.9304 | 4.8163 | 0.48784 | 0.51216 | 1.039 | 4.6354 | 2545.5657 | 1240.6319 | 1304.9338
2016-05-25 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-25 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-25 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.72% | 1240.304 | 1300.4717 | 2540.7757 | 3.7256 | 0.4886 | 0.5114 | 1.0391 | 3.5854 | 2544.3611 | 1242.0558 | 1302.3053
2016-05-25 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.66% | 1239.5909 | 1301.2418 | 2540.8327 | 3.2885 | 0.48832 | 0.51168 | 1.0391 | 3.1649 | 2543.9976 | 1241.1364 | 1302.8612
2016-05-25 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.087 | 1270.4116 | 2483.4987 | 5.8586 | 0.48915 | 0.51085 | 1.0636 | 5.5083 | 2489.007 | 1215.7814 | 1273.2256
2016-05-25 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.87% | 1213.5271 | 1269.9144 | 2483.4415 | 5.3686 | 0.48933 | 0.51067 | 1.0636 | 5.0475 | 2488.489 | 1215.997 | 1272.492
2016-05-25 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.25% | 1313.8978 | 1397.6278 | 2711.5256 | 15.3447 | 0.48623 | 0.51377 | 1.1216 | 13.6816 | 2725.2071 | 1320.5502 | 1404.657
2016-05-25 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-25 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-25 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-26 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-26 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-26 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-26 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-26 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-26 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-26 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-26 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-26 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-26 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-26 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-26 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.58% | 1209.9336 | 1273.975 | 2483.9086 | 7.9627 | 0.48788 | 0.51212 | 1.0634 | 7.4878 | 2491.3964 | 1213.5867 | 1277.8097
2016-05-26 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3266 | 1272.401 | 2483.7275 | 7.9779 | 0.48844 | 0.51156 | 1.0635 | 7.5016 | 2491.2291 | 1214.9906 | 1276.2385
2016-05-26 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.57% | 1238.3706 | 1302.5598 | 2540.9304 | 4.8163 | 0.48784 | 0.51216 | 1.039 | 4.6354 | 2545.5657 | 1240.6319 | 1304.9338
2016-05-26 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8839 | 1302.0054 | 2540.8893 | 4.9184 | 0.48805 | 0.51195 | 1.039 | 4.7336 | 2545.6229 | 1241.1941 | 1304.4288
2016-05-26 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.61% | 1238.8975 | 1301.9907 | 2540.8882 | 5.07 | 0.48805 | 0.51195 | 1.039 | 4.8795 | 2545.7677 | 1241.2789 | 1304.4888
2016-05-26 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-26 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.66% | 1211.0428 | 1268.9572 | 2480 | 0 | 0.48832 | 0.51168 | 1 | 0 | 2480 | 1211.0428 | 1268.9572
2016-05-26 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6834 | 1298.9819 | 2540.6653 | 3.6053 | 0.48915 | 0.51085 | 1.0391 | 3.4695 | 2544.1349 | 1243.3805 | 1300.7544
2016-05-26 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.87% | 1242.1338 | 1298.4955 | 2540.6293 | 3.3038 | 0.48933 | 0.51067 | 1.0391 | 3.1793 | 2543.8086 | 1243.6895 | 1300.1191
2016-05-26 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-26 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-26 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-26 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.11% | 1363.5942 | 1460.9682 | 2824.5623 | 28.5759 | 0.48555 | 0.51445 | 1.1942 | 23.9285 | 2848.4908 | 1375.2127 | 1473.2781
2016-05-27 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-27 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-27 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-27 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-27 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-27 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.09% | 1377.3791 | 1441.6693 | 2819.0484 | 22.4539 | 0.49046 | 0.50954 | 1.1962 | 18.7712 | 2837.8196 | 1386.5857 | 1451.2339
2016-05-27 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.82% | 1373.5498 | 1447.0302 | 2820.5801 | 26.1911 | 0.4891 | 0.5109 | 1.1956 | 21.9055 | 2842.4856 | 1384.2638 | 1458.2218
2016-05-27 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.76% | 1372.7222 | 1448.1889 | 2820.9111 | 24.2221 | 0.4888 | 0.5112 | 1.1955 | 20.2607 | 2841.1718 | 1382.6257 | 1458.5462
2016-05-27 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-27 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-27 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.69% | 1319.8851 | 1390.1436 | 2710.0287 | 15.7488 | 0.48844 | 0.51156 | 1.1221 | 14.0349 | 2724.0637 | 1326.7404 | 1397.3233
2016-05-27 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.58% | 1209.9336 | 1273.975 | 2483.9086 | 7.9627 | 0.48788 | 0.51212 | 1.0634 | 7.4878 | 2491.3964 | 1213.5867 | 1277.8097
2016-05-27 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.69% | 1239.8814 | 1300.928 | 2540.8095 | 4.9095 | 0.48844 | 0.51156 | 1.0391 | 4.7249 | 2545.5343 | 1242.1892 | 1303.3451
2016-05-27 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.57% | 1238.3706 | 1302.5598 | 2540.9304 | 4.8163 | 0.48784 | 0.51216 | 1.039 | 4.6354 | 2545.5657 | 1240.6319 | 1304.9338
2016-05-27 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.61% | 1210.352 | 1269.648 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.352 | 1269.648
2016-05-27 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.61% | 1210.3653 | 1269.6347 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.3653 | 1269.6347
2016-05-27 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-27 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.66% | 1211.0428 | 1268.9572 | 2480 | 0 | 0.48832 | 0.51168 | 1 | 0 | 2480 | 1211.0428 | 1268.9572
2016-05-27 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.087 | 1266.913 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.087 | 1266.913
2016-05-27 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.87% | 1242.1338 | 1298.4955 | 2540.6293 | 3.3038 | 0.48933 | 0.51067 | 1.0391 | 3.1793 | 2543.8086 | 1243.6895 | 1300.1191
2016-05-27 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-27 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.36% | 1315.436 | 1395.705 | 2711.141 | 13.5006 | 0.4868 | 0.5132 | 1.1217 | 12.0359 | 2723.1769 | 1321.295 | 1401.8819
2016-05-27 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.9424 | 1394.4749 | 2706.4173 | 17.3778 | 0.48669 | 0.51331 | 1.146 | 15.1638 | 2721.5811 | 1319.3224 | 1402.2587
2016-05-27 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-28 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-28 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-28 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-28 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-28 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-28 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-28 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-28 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-28 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.74% | 1320.529 | 1389.3387 | 2709.8677 | 15.3285 | 0.48868 | 0.51132 | 1.1222 | 13.6597 | 2723.5274 | 1327.2043 | 1396.3231
2016-05-28 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-28 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3419 | 1272.3836 | 2483.7256 | 8.1894 | 0.48844 | 0.51156 | 1.0635 | 7.7004 | 2491.426 | 1215.1031 | 1276.3228
2016-05-28 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.58% | 1238.4556 | 1302.4679 | 2540.9236 | 4.9001 | 0.48788 | 0.51212 | 1.039 | 4.716 | 2545.6396 | 1240.7565 | 1304.8831
2016-05-28 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.69% | 1211.3266 | 1268.6734 | 2480 | 0 | 0.48844 | 0.51156 | 1 | 0 | 2480 | 1211.3266 | 1268.6734
2016-05-28 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.57% | 1209.8505 | 1270.1495 | 2480 | 0 | 0.48784 | 0.51216 | 1 | 0 | 2480 | 1209.8505 | 1270.1495
2016-05-28 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.352 | 1269.648 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.352 | 1269.648
2016-05-28 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.3653 | 1269.6347 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.3653 | 1269.6347
2016-05-28 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-28 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.66% | 1211.0428 | 1268.9572 | 2480 | 0 | 0.48832 | 0.51168 | 1 | 0 | 2480 | 1211.0428 | 1268.9572
2016-05-28 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.087 | 1266.913 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.087 | 1266.913
2016-05-28 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.87% | 1213.5271 | 1266.4729 | 2480 | 0 | 0.48933 | 0.51067 | 1 | 0 | 2480 | 1213.5271 | 1266.4729
2016-05-28 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.25% | 1234.2727 | 1306.9855 | 2541.2582 | 4.9103 | 0.48623 | 0.51377 | 1.0389 | 4.7264 | 2545.9846 | 1236.5708 | 1309.4138
2016-05-28 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-28 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-28 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-29 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-29 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-29 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-29 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-29 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-29 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-29 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-29 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-29 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-29 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-29 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3419 | 1272.3836 | 2483.7256 | 8.1894 | 0.48844 | 0.51156 | 1.0635 | 7.7004 | 2491.426 | 1215.1031 | 1276.3228
2016-05-29 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.58% | 1238.4556 | 1302.4679 | 2540.9236 | 4.9001 | 0.48788 | 0.51212 | 1.039 | 4.716 | 2545.6396 | 1240.7565 | 1304.8831
2016-05-29 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.69% | 1211.3266 | 1268.6734 | 2480 | 0 | 0.48844 | 0.51156 | 1 | 0 | 2480 | 1211.3266 | 1268.6734
2016-05-29 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.57% | 1209.8505 | 1270.1495 | 2480 | 0 | 0.48784 | 0.51216 | 1 | 0 | 2480 | 1209.8505 | 1270.1495
2016-05-29 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.352 | 1269.648 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.352 | 1269.648
2016-05-29 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.3653 | 1269.6347 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.3653 | 1269.6347
2016-05-29 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-29 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.66% | 1211.0428 | 1268.9572 | 2480 | 0 | 0.48832 | 0.51168 | 1 | 0 | 2480 | 1211.0428 | 1268.9572
2016-05-29 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.087 | 1266.913 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.087 | 1266.913
2016-05-29 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.87% | 1213.5271 | 1266.4729 | 2480 | 0 | 0.48933 | 0.51067 | 1 | 0 | 2480 | 1213.5271 | 1266.4729
2016-05-29 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.25% | 1205.847 | 1278.5929 | 2484.4399 | 7.9792 | 0.48623 | 0.51377 | 1.0632 | 7.5048 | 2491.9447 | 1209.4961 | 1282.4487
2016-05-29 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-29 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-29 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.8815 | 1398.454 | 2707.3355 | 21.4319 | 0.48555 | 0.51445 | 1.1457 | 18.707 | 2726.0425 | 1317.9647 | 1408.0778
2016-05-30 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.3% | 1311.3981 | 1395.1825 | 2706.5806 | 23.9852 | 0.48649 | 0.51351 | 1.1459 | 20.9305 | 2727.5111 | 1321.5804 | 1405.9306
2016-05-30 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.34% | 1311.942 | 1394.4754 | 2706.4174 | 25.0264 | 0.48669 | 0.51331 | 1.146 | 21.838 | 2728.2554 | 1322.5703 | 1405.6851
2016-05-30 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.33% | 1311.8655 | 1394.5748 | 2706.4403 | 26.6981 | 0.48666 | 0.51334 | 1.146 | 23.2969 | 2729.7372 | 1323.2031 | 1406.5341
2016-05-30 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.56% | 1314.8718 | 1390.6667 | 2705.5385 | 26.8602 | 0.48778 | 0.51222 | 1.1463 | 23.4314 | 2728.9699 | 1326.301 | 1402.6688
2016-05-30 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1314.0044 | 1391.7943 | 2705.7987 | 23.0546 | 0.48745 | 0.51255 | 1.1462 | 20.1133 | 2725.9119 | 1323.8087 | 1402.1032
2016-05-30 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.09% | 1322.1133 | 1381.2527 | 2703.366 | 16.8404 | 0.49046 | 0.50954 | 1.1471 | 14.6804 | 2718.0464 | 1329.3135 | 1388.7329
2016-05-30 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.82% | 1318.4377 | 1386.031 | 2704.4687 | 19.6433 | 0.4891 | 0.5109 | 1.1467 | 17.1299 | 2721.5986 | 1326.8159 | 1394.7827
2016-05-30 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.76% | 1317.6433 | 1387.0637 | 2704.707 | 18.1666 | 0.4888 | 0.5112 | 1.1466 | 15.8433 | 2720.5503 | 1325.3875 | 1395.1628
2016-05-30 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.74% | 1317.3184 | 1387.4861 | 2704.8045 | 18.3942 | 0.48868 | 0.51132 | 1.1466 | 16.0423 | 2720.8468 | 1325.1579 | 1395.6888
2016-05-30 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.57% | 1318.2648 | 1392.169 | 2710.4338 | 15.9531 | 0.48784 | 0.51216 | 1.122 | 14.2189 | 2724.6527 | 1325.2015 | 1399.4513
2016-05-30 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.69% | 1211.3419 | 1272.3836 | 2483.7256 | 8.1894 | 0.48844 | 0.51156 | 1.0635 | 7.7004 | 2491.426 | 1215.1031 | 1276.3228
2016-05-30 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.58% | 1238.4556 | 1302.4679 | 2540.9236 | 4.9001 | 0.48788 | 0.51212 | 1.039 | 4.716 | 2545.6396 | 1240.7565 | 1304.8831
2016-05-30 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.69% | 1211.3266 | 1268.6734 | 2480 | 0 | 0.48844 | 0.51156 | 1 | 0 | 2480 | 1211.3266 | 1268.6734
2016-05-30 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.57% | 1209.8505 | 1270.1495 | 2480 | 0 | 0.48784 | 0.51216 | 1 | 0 | 2480 | 1209.8505 | 1270.1495
2016-05-30 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.352 | 1269.648 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.352 | 1269.648
2016-05-30 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.61% | 1210.3653 | 1269.6347 | 2480 | 0 | 0.48805 | 0.51195 | 1 | 0 | 2480 | 1210.3653 | 1269.6347
2016-05-30 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.72% | 1211.7394 | 1268.2606 | 2480 | 0 | 0.4886 | 0.5114 | 1 | 0 | 2480 | 1211.7394 | 1268.2606
2016-05-30 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.66% | 1211.0428 | 1268.9572 | 2480 | 0 | 0.48832 | 0.51168 | 1 | 0 | 2480 | 1211.0428 | 1268.9572
2016-05-30 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.087 | 1266.913 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.087 | 1266.913
2016-05-30 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.87% | 1213.5271 | 1266.4729 | 2480 | 0 | 0.48933 | 0.51067 | 1 | 0 | 2480 | 1213.5271 | 1266.4729
2016-05-30 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.25% | 1234.2727 | 1306.9855 | 2541.2582 | 4.9103 | 0.48623 | 0.51377 | 1.0389 | 4.7264 | 2545.9846 | 1236.5708 | 1309.4138
2016-05-30 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.36% | 1207.2587 | 1276.9977 | 2484.2564 | 7.0203 | 0.4868 | 0.5132 | 1.0633 | 6.6025 | 2490.8589 | 1210.4728 | 1280.3861
2016-05-30 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.34% | 1315.1399 | 1396.0751 | 2711.215 | 14.4815 | 0.48669 | 0.51331 | 1.1217 | 12.9106 | 2724.1256 | 1321.4234 | 1402.7023
2016-05-30 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 17.8599 | 0.48799 | 0.51201 | 1.122 | 15.918 | 2726.2542 | 1326.4231 | 1399.831
2016-05-31 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-05-31 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-05-31 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-05-31 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-05-31 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-05-31 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-05-31 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-05-31 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-05-31 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-05-31 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-05-31 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-05-31 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.084 | 1289.9093 | 2539.9933 | 10.0914 | 0.49246 | 0.50754 | 1.0394 | 9.7089 | 2549.7022 | 1254.8652 | 1294.837
2016-05-31 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-05-31 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-05-31 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-05-31 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-05-31 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-05-31 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-05-31 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-05-31 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-05-31 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-05-31 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-05-31 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-05-31 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-01 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-01 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-01 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-01 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-01 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-01 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-01 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-01 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-01 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2942 | 1261.1376 | 2482.4318 | 16.3986 | 0.49246 | 0.50754 | 1.064 | 15.4119 | 2497.8437 | 1228.8839 | 1268.9598
2016-06-01 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-01 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-01 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-01 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-01 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-01 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-01 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-01 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-01 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-01 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-01 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-01 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-02 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-02 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-02 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.52% | 1341.2404 | 1492.2635 | 2833.5039 | 48.4995 | 0.47759 | 0.52241 | 1.191 | 40.7204 | 2874.2242 | 1360.6881 | 1513.5361
2016-06-02 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.73% | 1344.149 | 1488.1914 | 2832.3404 | 48.9351 | 0.47863 | 0.52137 | 1.1915 | 41.0718 | 2873.4122 | 1363.8071 | 1509.6051
2016-06-02 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.64% | 1370.9681 | 1450.6447 | 2821.6128 | 56.1051 | 0.48818 | 0.51182 | 1.1953 | 46.9392 | 2868.5519 | 1393.8828 | 1474.6691
2016-06-02 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.66% | 1385.3694 | 1430.4828 | 2815.8522 | 37.9902 | 0.49331 | 0.50669 | 1.1973 | 31.7293 | 2847.5815 | 1401.0217 | 1446.5598
2016-06-02 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5043 | 1430.294 | 2815.7983 | 29.8043 | 0.49335 | 0.50665 | 1.1973 | 24.892 | 2840.6903 | 1397.7849 | 1442.9055
2016-06-02 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.58% | 1384.2054 | 1432.1124 | 2816.3178 | 51.3466 | 0.49289 | 0.50711 | 1.1972 | 42.8904 | 2859.2083 | 1405.3458 | 1453.8625
2016-06-02 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-02 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-02 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7297 | 1376.5879 | 2707.3176 | 31.8886 | 0.49246 | 0.50754 | 1.1231 | 28.3931 | 2735.7106 | 1344.7121 | 1390.9985
2016-06-02 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.084 | 1289.9093 | 2539.9933 | 10.0914 | 0.49246 | 0.50754 | 1.0394 | 9.7089 | 2549.7022 | 1254.8652 | 1294.837
2016-06-02 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-02 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-02 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-02 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-02 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-02 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-02 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-02 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-02 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-02 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-02 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1313.9883 | 1391.8153 | 2705.8035 | 39.6842 | 0.48745 | 0.51255 | 1.1462 | 34.6214 | 2740.4249 | 1330.8643 | 1409.5605
2016-06-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-03 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-03 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-03 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-03 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-03 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-03 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-03 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-03 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-03 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-03 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-03 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2942 | 1261.1376 | 2482.4318 | 16.3986 | 0.49246 | 0.50754 | 1.064 | 15.4119 | 2497.8437 | 1228.8839 | 1268.9598
2016-06-03 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-03 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-03 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-03 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-03 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-03 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-03 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.29% | 1234.78 | 1306.4376 | 2541.2176 | 8.1644 | 0.48643 | 0.51357 | 1.0389 | 7.8586 | 2549.0762 | 1238.6026 | 1310.4736
2016-06-03 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-03 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-03 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-03 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-03 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-04 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-04 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-04 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-04 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-04 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-04 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-04 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-04 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-04 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-04 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-04 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-04 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-04 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-04 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-04 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-04 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-04 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-04 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-04 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-04 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-04 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-04 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0559 | 1274.9668 | 2484.0227 | 14.2831 | 0.48752 | 0.51248 | 1.0634 | 13.4318 | 2497.4545 | 1215.6042 | 1281.8503
2016-06-04 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-04 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-05 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-05 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-05 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-05 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-05 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-05 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-05 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-05 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-05 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-05 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-05 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-05 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-05 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-05 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-05 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-05 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-05 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-05 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-05 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-05 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-05 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-05 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-05 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.49% | 1237.3661 | 1303.6446 | 2541.0107 | 10.5824 | 0.48745 | 0.51255 | 1.039 | 10.1853 | 2551.196 | 1242.3309 | 1308.8651
2016-06-05 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-06 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-06 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-06 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-06 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-06 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-06 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-06 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-06 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-06 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-06 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-06 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-06 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-06 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-06 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-06 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-06 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-06 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-06 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-06 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-06 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-06 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-06 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-06 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-06 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-07 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-07 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-07 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-07 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-07 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-07 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-07 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-07 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.58% | 1222.3725 | 1259.919 | 2482.2916 | 16.6876 | 0.49289 | 0.50711 | 1.0641 | 15.6828 | 2497.9743 | 1230.1024 | 1267.8719
2016-06-07 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-07 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9724 | 1290.0298 | 2540.0022 | 10.5316 | 0.49241 | 0.50759 | 1.0394 | 10.1325 | 2550.1347 | 1254.9618 | 1295.1729
2016-06-07 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-07 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-07 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-07 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-07 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-07 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-07 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-07 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-07 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-07 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-07 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-07 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0559 | 1274.9668 | 2484.0227 | 14.2831 | 0.48752 | 0.51248 | 1.0634 | 13.4318 | 2497.4545 | 1215.6042 | 1281.8503
2016-06-07 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-07 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-08 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-08 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-08 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-08 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-08 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-08 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-08 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-08 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-08 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-08 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-08 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-08 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.084 | 1289.9093 | 2539.9933 | 10.0914 | 0.49246 | 0.50754 | 1.0394 | 9.7089 | 2549.7022 | 1254.8652 | 1294.837
2016-06-08 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-08 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-08 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-08 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-08 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-08 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-08 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-08 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-08 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-08 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0559 | 1274.9668 | 2484.0227 | 14.2831 | 0.48752 | 0.51248 | 1.0634 | 13.4318 | 2497.4545 | 1215.6042 | 1281.8503
2016-06-08 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-08 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-09 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-09 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-09 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-09 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-09 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-09 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-09 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-09 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-09 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-09 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-09 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7297 | 1376.5879 | 2707.3176 | 31.8886 | 0.49246 | 0.50754 | 1.1231 | 28.3931 | 2735.7106 | 1344.7121 | 1390.9985
2016-06-09 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2942 | 1261.1376 | 2482.4318 | 16.3986 | 0.49246 | 0.50754 | 1.064 | 15.4119 | 2497.8437 | 1228.8839 | 1268.9598
2016-06-09 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.3261 | 1261.1015 | 2482.4276 | 16.7043 | 0.49247 | 0.50753 | 1.064 | 15.6992 | 2498.1268 | 1229.0575 | 1269.0693
2016-06-09 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.753 | 1296.7468 | 2540.4998 | 10.0552 | 0.48996 | 0.51004 | 1.0392 | 9.6759 | 2550.1757 | 1248.4938 | 1301.6818
2016-06-09 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.67% | 1239.6134 | 1301.2175 | 2540.8309 | 10.8934 | 0.48833 | 0.51167 | 1.0391 | 10.4838 | 2551.3148 | 1244.733 | 1306.5817
2016-06-09 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.31% | 1235.114 | 1306.0768 | 2541.1909 | 12.2875 | 0.48656 | 0.51344 | 1.0389 | 11.8271 | 2553.018 | 1240.8686 | 1312.1493
2016-06-09 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.38% | 1235.9724 | 1305.1499 | 2541.1222 | 10.9352 | 0.4869 | 0.5131 | 1.039 | 10.5252 | 2551.6474 | 1241.0971 | 1310.5504
2016-06-09 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.71% | 1227.4714 | 1314.3309 | 2541.8023 | 11.256 | 0.48355 | 0.51645 | 1.0387 | 10.8368 | 2552.6391 | 1232.7115 | 1319.9276
2016-06-09 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.29% | 1234.78 | 1306.4376 | 2541.2176 | 8.1644 | 0.48643 | 0.51357 | 1.0389 | 7.8586 | 2549.0762 | 1238.6026 | 1310.4736
2016-06-09 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0434 | 1274.9809 | 2484.0244 | 17.724 | 0.48752 | 0.51248 | 1.0634 | 16.6677 | 2500.692 | 1217.1692 | 1283.5228
2016-06-09 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-09 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-09 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1313.9883 | 1391.8153 | 2705.8035 | 39.6842 | 0.48745 | 0.51255 | 1.1462 | 34.6214 | 2740.4249 | 1330.8643 | 1409.5605
2016-06-09 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-10 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-10 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-10 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-10 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-10 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-10 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-10 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-10 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-10 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-10 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.48% | 1327.3752 | 1374.4123 | 2701.7874 | 39.4937 | 0.49241 | 0.50759 | 1.1477 | 34.4104 | 2736.1979 | 1344.3193 | 1391.8785
2016-06-10 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4942 | 1374.2575 | 2701.7517 | 38.2664 | 0.49246 | 0.50754 | 1.1477 | 33.3407 | 2735.0924 | 1343.9131 | 1391.1793
2016-06-10 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7291 | 1376.5886 | 2707.3177 | 31.5357 | 0.49246 | 0.50754 | 1.1231 | 28.0788 | 2735.3965 | 1344.5567 | 1390.8398
2016-06-10 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7639 | 1376.5451 | 2707.309 | 32.1237 | 0.49247 | 0.50753 | 1.1231 | 28.6022 | 2735.9112 | 1344.8497 | 1391.0616
2016-06-10 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.109 | 1268.1268 | 2483.2358 | 16.3397 | 0.48996 | 0.51004 | 1.0637 | 15.3612 | 2498.597 | 1222.6354 | 1275.9616
2016-06-10 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.67% | 1239.6134 | 1301.2175 | 2540.8309 | 10.8934 | 0.48833 | 0.51167 | 1.0391 | 10.4838 | 2551.3148 | 1244.733 | 1306.5817
2016-06-10 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.31% | 1235.114 | 1306.0768 | 2541.1909 | 12.2875 | 0.48656 | 0.51344 | 1.0389 | 11.8271 | 2553.018 | 1240.8686 | 1312.1493
2016-06-10 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.38% | 1235.9724 | 1305.1499 | 2541.1222 | 10.9352 | 0.4869 | 0.5131 | 1.039 | 10.5252 | 2551.6474 | 1241.0971 | 1310.5504
2016-06-10 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.71% | 1227.4714 | 1314.3309 | 2541.8023 | 11.256 | 0.48355 | 0.51645 | 1.0387 | 10.8368 | 2552.6391 | 1232.7115 | 1319.9276
2016-06-10 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.29% | 1234.78 | 1306.4376 | 2541.2176 | 8.1644 | 0.48643 | 0.51357 | 1.0389 | 7.8586 | 2549.0762 | 1238.6026 | 1310.4736
2016-06-10 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0434 | 1274.9809 | 2484.0244 | 17.724 | 0.48752 | 0.51248 | 1.0634 | 16.6677 | 2500.692 | 1217.1692 | 1283.5228
2016-06-10 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-10 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-10 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1313.9883 | 1391.8153 | 2705.8035 | 39.6842 | 0.48745 | 0.51255 | 1.1462 | 34.6214 | 2740.4249 | 1330.8643 | 1409.5605
2016-06-10 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-11 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.41% | 1353.7824 | 1474.7046 | 2828.487 | 54.0909 | 0.48206 | 0.51794 | 1.1928 | 45.3469 | 2873.8339 | 1375.6423 | 1498.1916
2016-06-11 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.3% | 1352.2339 | 1476.8725 | 2829.1064 | 50.3754 | 0.48151 | 0.51849 | 1.1926 | 42.2399 | 2871.3463 | 1372.5727 | 1498.7736
2016-06-11 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.52% | 1341.2404 | 1492.2635 | 2833.5039 | 48.4995 | 0.47759 | 0.52241 | 1.191 | 40.7204 | 2874.2242 | 1360.6881 | 1513.5361
2016-06-11 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.73% | 1344.149 | 1488.1914 | 2832.3404 | 48.9351 | 0.47863 | 0.52137 | 1.1915 | 41.0718 | 2873.4122 | 1363.8071 | 1509.6051
2016-06-11 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.64% | 1370.9681 | 1450.6447 | 2821.6128 | 56.1051 | 0.48818 | 0.51182 | 1.1953 | 46.9392 | 2868.5519 | 1393.8828 | 1474.6691
2016-06-11 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.66% | 1385.3694 | 1430.4828 | 2815.8522 | 37.9902 | 0.49331 | 0.50669 | 1.1973 | 31.7293 | 2847.5815 | 1401.0217 | 1446.5598
2016-06-11 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5043 | 1430.294 | 2815.7983 | 29.8043 | 0.49335 | 0.50665 | 1.1973 | 24.892 | 2840.6903 | 1397.7849 | 1442.9055
2016-06-11 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-11 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-11 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.48% | 1327.3752 | 1374.4123 | 2701.7874 | 39.4937 | 0.49241 | 0.50759 | 1.1477 | 34.4104 | 2736.1979 | 1344.3193 | 1391.8785
2016-06-11 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7297 | 1376.5879 | 2707.3176 | 31.8886 | 0.49246 | 0.50754 | 1.1231 | 28.3931 | 2735.7106 | 1344.7121 | 1390.9985
2016-06-11 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7291 | 1376.5886 | 2707.3177 | 31.5357 | 0.49246 | 0.50754 | 1.1231 | 28.0788 | 2735.3965 | 1344.5567 | 1390.8398
2016-06-11 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-11 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-11 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-11 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-11 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-11 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-11 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-11 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0434 | 1274.9809 | 2484.0244 | 17.724 | 0.48752 | 0.51248 | 1.0634 | 16.6677 | 2500.692 | 1217.1692 | 1283.5228
2016-06-11 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.41% | 1316.079 | 1394.9012 | 2710.9802 | 27.0084 | 0.48704 | 0.51296 | 1.1218 | 24.0768 | 2735.0571 | 1327.8053 | 1407.2518
2016-06-11 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-11 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.49% | 1313.9883 | 1391.8153 | 2705.8035 | 39.6842 | 0.48745 | 0.51255 | 1.1462 | 34.6214 | 2740.4249 | 1330.8643 | 1409.5605
2016-06-11 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-12 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.41% | 1353.7824 | 1474.7046 | 2828.487 | 54.0909 | 0.48206 | 0.51794 | 1.1928 | 45.3469 | 2873.8339 | 1375.6423 | 1498.1916
2016-06-12 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.3% | 1352.2339 | 1476.8725 | 2829.1064 | 50.3754 | 0.48151 | 0.51849 | 1.1926 | 42.2399 | 2871.3463 | 1372.5727 | 1498.7736
2016-06-12 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.52% | 1341.2404 | 1492.2635 | 2833.5039 | 48.4995 | 0.47759 | 0.52241 | 1.191 | 40.7204 | 2874.2242 | 1360.6881 | 1513.5361
2016-06-12 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.73% | 1344.149 | 1488.1914 | 2832.3404 | 48.9351 | 0.47863 | 0.52137 | 1.1915 | 41.0718 | 2873.4122 | 1363.8071 | 1509.6051
2016-06-12 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.64% | 1370.9681 | 1450.6447 | 2821.6128 | 56.1051 | 0.48818 | 0.51182 | 1.1953 | 46.9392 | 2868.5519 | 1393.8828 | 1474.6691
2016-06-12 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.66% | 1385.3694 | 1430.4828 | 2815.8522 | 37.9902 | 0.49331 | 0.50669 | 1.1973 | 31.7293 | 2847.5815 | 1401.0217 | 1446.5598
2016-06-12 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5043 | 1430.294 | 2815.7983 | 29.8043 | 0.49335 | 0.50665 | 1.1973 | 24.892 | 2840.6903 | 1397.7849 | 1442.9055
2016-06-12 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.58% | 1384.2054 | 1432.1124 | 2816.3178 | 51.3466 | 0.49289 | 0.50711 | 1.1972 | 42.8904 | 2859.2083 | 1405.3458 | 1453.8625
2016-06-12 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-12 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.48% | 1327.3752 | 1374.4123 | 2701.7874 | 39.4937 | 0.49241 | 0.50759 | 1.1477 | 34.4104 | 2736.1979 | 1344.3193 | 1391.8785
2016-06-12 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7297 | 1376.5879 | 2707.3176 | 31.8886 | 0.49246 | 0.50754 | 1.1231 | 28.3931 | 2735.7106 | 1344.7121 | 1390.9985
2016-06-12 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7291 | 1376.5886 | 2707.3177 | 31.5357 | 0.49246 | 0.50754 | 1.1231 | 28.0788 | 2735.3965 | 1344.5567 | 1390.8398
2016-06-12 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.3261 | 1261.1015 | 2482.4276 | 16.7043 | 0.49247 | 0.50753 | 1.064 | 15.6992 | 2498.1268 | 1229.0575 | 1269.0693
2016-06-12 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.109 | 1268.1268 | 2483.2358 | 16.3397 | 0.48996 | 0.51004 | 1.0637 | 15.3612 | 2498.597 | 1222.6354 | 1275.9616
2016-06-12 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.67% | 1239.6134 | 1301.2175 | 2540.8309 | 10.8934 | 0.48833 | 0.51167 | 1.0391 | 10.4838 | 2551.3148 | 1244.733 | 1306.5817
2016-06-12 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.31% | 1235.114 | 1306.0768 | 2541.1909 | 12.2875 | 0.48656 | 0.51344 | 1.0389 | 11.8271 | 2553.018 | 1240.8686 | 1312.1493
2016-06-12 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.38% | 1235.9724 | 1305.1499 | 2541.1222 | 10.9352 | 0.4869 | 0.5131 | 1.039 | 10.5252 | 2551.6474 | 1241.0971 | 1310.5504
2016-06-12 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.71% | 1227.4714 | 1314.3309 | 2541.8023 | 11.256 | 0.48355 | 0.51645 | 1.0387 | 10.8368 | 2552.6391 | 1232.7115 | 1319.9276
2016-06-12 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.29% | 1234.78 | 1306.4376 | 2541.2176 | 8.1644 | 0.48643 | 0.51357 | 1.0389 | 7.8586 | 2549.0762 | 1238.6026 | 1310.4736
2016-06-12 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-12 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-12 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0559 | 1274.9668 | 2484.0227 | 14.2831 | 0.48752 | 0.51248 | 1.0634 | 13.4318 | 2497.4545 | 1215.6042 | 1281.8503
2016-06-12 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-12 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-13 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-13 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-13 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-13 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-13 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-13 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-13 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-13 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-13 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-13 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-13 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-13 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2942 | 1261.1376 | 2482.4318 | 16.3986 | 0.49246 | 0.50754 | 1.064 | 15.4119 | 2497.8437 | 1228.8839 | 1268.9598
2016-06-13 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-13 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-13 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-13 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-13 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-13 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-13 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-13 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-13 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-13 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-13 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.49% | 1208.8692 | 1271.1308 | 2480 | 0 | 0.48745 | 0.51255 | 1 | 0 | 2480 | 1208.8692 | 1271.1308
2016-06-13 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-14 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-14 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-14 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-14 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-14 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-14 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-14 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-14 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-14 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-14 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-14 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-14 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-14 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-14 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-14 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-14 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-14 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-14 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-14 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-14 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-14 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-14 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-14 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.49% | 1237.3661 | 1303.6446 | 2541.0107 | 10.5824 | 0.48745 | 0.51255 | 1.039 | 10.1853 | 2551.196 | 1242.3309 | 1308.8651
2016-06-14 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-15 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-15 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-15 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-15 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-15 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-15 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-15 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-15 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-15 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-15 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-15 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-15 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.084 | 1289.9093 | 2539.9933 | 10.0914 | 0.49246 | 0.50754 | 1.0394 | 9.7089 | 2549.7022 | 1254.8652 | 1294.837
2016-06-15 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-15 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-15 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-15 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-15 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-15 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-15 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-15 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-15 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-15 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-15 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-15 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-16 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-16 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-16 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-16 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-16 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-16 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-16 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-16 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-16 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-16 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-16 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-16 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2942 | 1261.1376 | 2482.4318 | 16.3986 | 0.49246 | 0.50754 | 1.064 | 15.4119 | 2497.8437 | 1228.8839 | 1268.9598
2016-06-16 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.1167 | 1289.874 | 2539.9907 | 10.2796 | 0.49247 | 0.50753 | 1.0394 | 9.8899 | 2549.8806 | 1254.9872 | 1294.8934
2016-06-16 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-16 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-16 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-16 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-16 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-16 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-16 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-16 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-16 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-16 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-16 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-17 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-17 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-17 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-17 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-17 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-17 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-17 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-17 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-17 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-17 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.48% | 1327.3752 | 1374.4123 | 2701.7874 | 39.4937 | 0.49241 | 0.50759 | 1.1477 | 34.4104 | 2736.1979 | 1344.3193 | 1391.8785
2016-06-17 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7297 | 1376.5879 | 2707.3176 | 31.8886 | 0.49246 | 0.50754 | 1.1231 | 28.3931 | 2735.7106 | 1344.7121 | 1390.9985
2016-06-17 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.7291 | 1376.5886 | 2707.3177 | 31.5357 | 0.49246 | 0.50754 | 1.1231 | 28.0788 | 2735.3965 | 1344.5567 | 1390.8398
2016-06-17 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.3261 | 1261.1015 | 2482.4276 | 16.7043 | 0.49247 | 0.50753 | 1.064 | 15.6992 | 2498.1268 | 1229.0575 | 1269.0693
2016-06-17 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-17 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-17 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-17 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-17 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-17 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-17 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-17 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.41% | 1207.8488 | 1276.3308 | 2484.1797 | 14.0444 | 0.48704 | 0.51296 | 1.0633 | 13.2081 | 2497.3877 | 1214.2817 | 1283.1061
2016-06-17 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.5% | 1317.3943 | 1393.2572 | 2710.6514 | 27.4674 | 0.48752 | 0.51248 | 1.1219 | 24.4834 | 2735.1348 | 1329.3305 | 1405.8044
2016-06-17 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-17 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-18 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-18 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-18 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-18 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-18 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-18 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-18 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-18 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-18 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-18 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-18 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2947 | 1261.137 | 2482.4317 | 16.5821 | 0.49246 | 0.50754 | 1.064 | 15.5844 | 2498.0161 | 1228.9694 | 1269.0467
2016-06-18 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.084 | 1289.9093 | 2539.9933 | 10.0914 | 0.49246 | 0.50754 | 1.0394 | 9.7089 | 2549.7022 | 1254.8652 | 1294.837
2016-06-18 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-18 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-18 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-18 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-18 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-18 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-18 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-18 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-18 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-18 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.5% | 1209.0559 | 1274.9668 | 2484.0227 | 14.2831 | 0.48752 | 0.51248 | 1.0634 | 13.4318 | 2497.4545 | 1215.6042 | 1281.8503
2016-06-18 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-18 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.6% | 1315.4492 | 1389.916 | 2705.3652 | 39.9141 | 0.48799 | 0.51201 | 1.1464 | 34.817 | 2740.1823 | 1332.4395 | 1407.7427
2016-06-19 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-19 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-19 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-19 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-19 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-19 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-19 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-19 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-19 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2206 | 1372.0132 | 2701.2338 | 38.3631 | 0.4931 | 0.5069 | 1.1479 | 33.4194 | 2734.6532 | 1345.6997 | 1388.9535
2016-06-19 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-19 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-19 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-19 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-19 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-19 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-19 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-19 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-19 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-19 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-19 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-19 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-19 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-19 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-19 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-20 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-20 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-20 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-20 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-20 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-20 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-20 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-20 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-20 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-20 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-20 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-20 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-20 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-20 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-20 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-20 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-20 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-20 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-20 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-20 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-20 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-20 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-20 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-20 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-21 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-21 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-21 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-21 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-21 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-21 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-21 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-21 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.58% | 1328.6658 | 1372.7345 | 2701.4003 | 38.5099 | 0.49289 | 0.50711 | 1.1479 | 33.5491 | 2734.9494 | 1345.2019 | 1389.7475
2016-06-21 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-21 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-21 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-21 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-21 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-21 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-21 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-21 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-21 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-21 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-21 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-21 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-21 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-21 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-21 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-21 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-22 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-22 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-22 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-22 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-22 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-22 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-22 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-22 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-22 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-22 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1852 | 1261.2608 | 2482.4459 | 17.1139 | 0.49241 | 0.50759 | 1.064 | 16.0843 | 2498.5302 | 1229.1053 | 1269.4249
2016-06-22 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-22 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-22 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-22 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-22 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-22 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-22 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-22 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-22 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-22 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-22 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-22 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-22 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.49% | 1317.1908 | 1393.5115 | 2710.7023 | 33.0701 | 0.48745 | 0.51255 | 1.1219 | 29.4779 | 2740.1802 | 1331.5597 | 1408.6205
2016-06-22 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-23 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.41% | 1299.4635 | 1410.6975 | 2710.161 | 40.5681 | 0.48206 | 0.51794 | 1.1446 | 35.4425 | 2745.6035 | 1316.5488 | 1429.0546
2016-06-23 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.3% | 1297.9771 | 1412.6298 | 2710.6069 | 37.7816 | 0.48151 | 0.51849 | 1.1445 | 33.0128 | 2743.6197 | 1313.873 | 1429.7467
2016-06-23 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.52% | 1287.4246 | 1426.348 | 2713.7726 | 36.3746 | 0.47759 | 0.52241 | 1.1433 | 31.8161 | 2745.5887 | 1302.6198 | 1442.9689
2016-06-23 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.73% | 1290.2165 | 1422.7185 | 2712.935 | 36.7013 | 0.47863 | 0.52137 | 1.1436 | 32.0931 | 2745.0282 | 1305.5772 | 1439.4509
2016-06-23 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.64% | 1315.9596 | 1389.2526 | 2705.2121 | 42.0788 | 0.48818 | 0.51182 | 1.1465 | 36.7034 | 2741.9156 | 1333.8774 | 1408.0382
2016-06-23 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.66% | 1329.783 | 1371.282 | 2701.0651 | 28.4926 | 0.49331 | 0.50669 | 1.148 | 24.8195 | 2725.8846 | 1342.0267 | 1383.8579
2016-06-23 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9125 | 1371.1138 | 2701.0263 | 22.3532 | 0.49335 | 0.50665 | 1.148 | 19.4713 | 2720.4976 | 1339.5188 | 1380.9788
2016-06-23 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-23 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-23 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9724 | 1290.0298 | 2540.0022 | 10.5316 | 0.49241 | 0.50759 | 1.0394 | 10.1325 | 2550.1347 | 1254.9618 | 1295.1729
2016-06-23 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-23 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-23 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-23 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-23 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-23 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-23 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-23 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-23 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-23 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-23 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-23 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-23 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.49% | 1237.3661 | 1303.6446 | 2541.0107 | 10.5824 | 0.48745 | 0.51255 | 1.039 | 10.1853 | 2551.196 | 1242.3309 | 1308.8651
2016-06-23 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-24 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-24 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-24 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-24 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-24 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-24 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-24 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-24 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-24 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-24 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9724 | 1290.0298 | 2540.0022 | 10.5316 | 0.49241 | 0.50759 | 1.0394 | 10.1325 | 2550.1347 | 1254.9618 | 1295.1729
2016-06-24 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-24 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-24 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-24 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-24 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-24 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-24 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-24 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-24 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-24 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-24 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-24 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-24 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-24 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.6% | 1318.6553 | 1391.6808 | 2710.3362 | 33.2618 | 0.48799 | 0.51201 | 1.122 | 29.6451 | 2739.9813 | 1333.1218 | 1406.8595
2016-06-25 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-25 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-25 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-25 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-25 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-25 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-25 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-25 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-25 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-25 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9724 | 1290.0298 | 2540.0022 | 10.5316 | 0.49241 | 0.50759 | 1.0394 | 10.1325 | 2550.1347 | 1254.9618 | 1295.1729
2016-06-25 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-25 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-25 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-25 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-25 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-25 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-25 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-25 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-25 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-25 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-25 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-25 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-25 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-25 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-26 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-26 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-26 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-26 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-26 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-26 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-26 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-26 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-26 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.883 | 1259.3422 | 2482.2252 | 16.624 | 0.4931 | 0.5069 | 1.0641 | 15.6226 | 2497.8478 | 1230.5864 | 1267.2613
2016-06-26 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9724 | 1290.0298 | 2540.0022 | 10.5316 | 0.49241 | 0.50759 | 1.0394 | 10.1325 | 2550.1347 | 1254.9618 | 1295.1729
2016-06-26 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-26 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-26 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-26 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-26 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-26 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-26 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-26 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-26 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-26 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-26 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-26 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-26 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-26 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-27 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.41% | 1302.6306 | 1411.7117 | 2714.3423 | 33.8068 | 0.48206 | 0.51794 | 1.1205 | 30.1708 | 2744.5131 | 1317.1747 | 1427.3384
2016-06-27 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.3% | 1301.1406 | 1413.5743 | 2714.7149 | 31.4846 | 0.48151 | 0.51849 | 1.1204 | 28.1018 | 2742.8167 | 1314.6718 | 1428.1448
2016-06-27 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.52% | 1290.5624 | 1426.7969 | 2717.3594 | 30.3122 | 0.47759 | 0.52241 | 1.1194 | 27.079 | 2744.4384 | 1303.4952 | 1440.9432
2016-06-27 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.73% | 1293.3611 | 1423.2986 | 2716.6597 | 30.5844 | 0.47863 | 0.52137 | 1.1197 | 27.3159 | 2743.9756 | 1306.4353 | 1437.5403
2016-06-27 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.64% | 1319.1669 | 1391.0413 | 2710.2083 | 35.0657 | 0.48818 | 0.51182 | 1.122 | 31.2516 | 2741.4598 | 1334.4233 | 1407.0366
2016-06-27 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.66% | 1333.0241 | 1373.7199 | 2706.744 | 23.7438 | 0.49331 | 0.50669 | 1.1233 | 21.1371 | 2727.8811 | 1343.4512 | 1384.4299
2016-06-27 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1538 | 1373.5577 | 2706.7115 | 18.6277 | 0.49335 | 0.50665 | 1.1233 | 16.5824 | 2723.294 | 1341.3349 | 1381.9591
2016-06-27 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.58% | 1331.9041 | 1375.1199 | 2707.024 | 32.0916 | 0.49289 | 0.50711 | 1.1232 | 28.571 | 2735.595 | 1345.9865 | 1389.6084
2016-06-27 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4603 | 1374.4246 | 2706.8849 | 31.9693 | 0.4931 | 0.5069 | 1.1233 | 28.4608 | 2735.3457 | 1346.4943 | 1388.8514
2016-06-27 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.6103 | 1376.7371 | 2707.3474 | 32.9114 | 0.49241 | 0.50759 | 1.1231 | 29.304 | 2736.6514 | 1345.04 | 1391.6114
2016-06-27 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.49% | 1250.0845 | 1289.9087 | 2539.9932 | 10.2044 | 0.49246 | 0.50754 | 1.0394 | 9.8176 | 2549.8108 | 1254.9193 | 1294.8915
2016-06-27 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-27 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-27 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-27 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-27 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-27 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-27 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-27 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-27 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-27 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-27 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-27 22:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.49% | 1208.8692 | 1271.1308 | 2480 | 0 | 0.48745 | 0.51255 | 1 | 0 | 2480 | 1208.8692 | 1271.1308
2016-06-27 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.6% | 1238.7419 | 1302.1588 | 2540.9006 | 10.6438 | 0.48799 | 0.51201 | 1.039 | 10.2439 | 2551.1445 | 1243.7408 | 1307.4037
2016-06-28 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.41% | 1195.5064 | 1290.2778 | 2485.7842 | 17.5795 | 0.48206 | 0.51794 | 1.0627 | 16.5428 | 2502.327 | 1203.481 | 1298.846
2016-06-28 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.3% | 1194.1389 | 1291.823 | 2485.9619 | 16.372 | 0.48151 | 0.51849 | 1.0626 | 15.4076 | 2501.3695 | 1201.5578 | 1299.8118
2016-06-28 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.52% | 1184.4307 | 1302.7933 | 2487.224 | 15.7623 | 0.47759 | 0.52241 | 1.0621 | 14.8409 | 2502.0649 | 1191.5186 | 1310.5463
2016-06-28 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.73% | 1186.9992 | 1299.8909 | 2486.8901 | 15.9039 | 0.47863 | 0.52137 | 1.0622 | 14.9723 | 2501.8624 | 1194.1654 | 1307.697
2016-06-28 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.64% | 1210.6828 | 1273.1284 | 2483.8112 | 18.2341 | 0.48818 | 0.51182 | 1.0635 | 17.146 | 2500.9572 | 1219.0531 | 1281.9041
2016-06-28 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.66% | 1223.4004 | 1258.7576 | 2482.1579 | 12.3468 | 0.49331 | 0.50669 | 1.0641 | 11.6027 | 2493.7607 | 1229.1241 | 1264.6366
2016-06-28 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.67% | 1223.5195 | 1258.623 | 2482.1425 | 9.6864 | 0.49335 | 0.50665 | 1.0641 | 9.1026 | 2491.245 | 1228.0103 | 1263.2348
2016-06-28 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.58% | 1222.3725 | 1259.919 | 2482.2916 | 16.6876 | 0.49289 | 0.50711 | 1.0641 | 15.6828 | 2497.9743 | 1230.1024 | 1267.8719
2016-06-28 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.62% | 1251.7103 | 1288.1529 | 2539.8632 | 10.2302 | 0.4931 | 0.5069 | 1.0394 | 9.8419 | 2549.7051 | 1256.5633 | 1293.1418
2016-06-28 09:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.48% | 1221.1852 | 1258.8148 | 2480 | 0 | 0.49241 | 0.50759 | 1 | 0 | 2480 | 1221.1852 | 1258.8148
2016-06-28 10:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-28 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-28 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-28 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-28 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-28 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-28 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-28 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-28 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.29% | 1206.3426 | 1273.6574 | 2480 | 0 | 0.48643 | 0.51357 | 1 | 0 | 2480 | 1206.3426 | 1273.6574
2016-06-28 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0434 | 1270.9566 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0434 | 1270.9566
2016-06-28 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.41% | 1207.8488 | 1272.1512 | 2480 | 0 | 0.48704 | 0.51296 | 1 | 0 | 2480 | 1207.8488 | 1272.1512
2016-06-28 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.5% | 1209.0559 | 1270.9441 | 2480 | 0 | 0.48752 | 0.51248 | 1 | 0 | 2480 | 1209.0559 | 1270.9441
2016-06-28 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.49% | 1208.8692 | 1271.1308 | 2480 | 0 | 0.48745 | 0.51255 | 1 | 0 | 2480 | 1208.8692 | 1271.1308
2016-06-28 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.6% | 1210.2133 | 1273.659 | 2483.8723 | 17.2961 | 0.48799 | 0.51201 | 1.0634 | 16.2643 | 2500.1366 | 1218.1501 | 1281.9865
2016-06-29 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.41% | 1195.5064 | 1290.2778 | 2485.7842 | 17.5795 | 0.48206 | 0.51794 | 1.0627 | 16.5428 | 2502.327 | 1203.481 | 1298.846
2016-06-29 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.3% | 1194.1389 | 1291.823 | 2485.9619 | 16.372 | 0.48151 | 0.51849 | 1.0626 | 15.4076 | 2501.3695 | 1201.5578 | 1299.8118
2016-06-29 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.52% | 1184.4307 | 1302.7933 | 2487.224 | 15.7623 | 0.47759 | 0.52241 | 1.0621 | 14.8409 | 2502.0649 | 1191.5186 | 1310.5463
2016-06-29 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.73% | 1186.9992 | 1299.8909 | 2486.8901 | 15.9039 | 0.47863 | 0.52137 | 1.0622 | 14.9723 | 2501.8624 | 1194.1654 | 1307.697
2016-06-29 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.64% | 1210.6828 | 1273.1284 | 2483.8112 | 18.2341 | 0.48818 | 0.51182 | 1.0635 | 17.146 | 2500.9572 | 1219.0531 | 1281.9041
2016-06-29 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.66% | 1223.4004 | 1258.7576 | 2482.1579 | 12.3468 | 0.49331 | 0.50669 | 1.0641 | 11.6027 | 2493.7607 | 1229.1241 | 1264.6366
2016-06-29 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.67% | 1223.5195 | 1258.623 | 2482.1425 | 9.6864 | 0.49335 | 0.50665 | 1.0641 | 9.1026 | 2491.245 | 1228.0103 | 1263.2348
2016-06-29 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.58% | 1222.3725 | 1259.919 | 2482.2916 | 16.6876 | 0.49289 | 0.50711 | 1.0641 | 15.6828 | 2497.9743 | 1230.1024 | 1267.8719
2016-06-29 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.62% | 1251.7103 | 1288.1529 | 2539.8632 | 10.2302 | 0.4931 | 0.5069 | 1.0394 | 9.8419 | 2549.7051 | 1256.5633 | 1293.1418
2016-06-29 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1852 | 1258.8148 | 2480 | 0 | 0.49241 | 0.50759 | 1 | 0 | 2480 | 1221.1852 | 1258.8148
2016-06-29 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2947 | 1258.7053 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2947 | 1258.7053
2016-06-29 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.2942 | 1258.7058 | 2480 | 0 | 0.49246 | 0.50754 | 1 | 0 | 2480 | 1221.2942 | 1258.7058
2016-06-29 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.49% | 1221.3261 | 1258.6739 | 2480 | 0 | 0.49247 | 0.50753 | 1 | 0 | 2480 | 1221.3261 | 1258.6739
2016-06-29 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.109 | 1264.891 | 2480 | 0 | 0.48996 | 0.51004 | 1 | 0 | 2480 | 1215.109 | 1264.891
2016-06-29 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.67% | 1211.0647 | 1268.9353 | 2480 | 0 | 0.48833 | 0.51167 | 1 | 0 | 2480 | 1211.0647 | 1268.9353
2016-06-29 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.31% | 1206.669 | 1273.331 | 2480 | 0 | 0.48656 | 0.51344 | 1 | 0 | 2480 | 1206.669 | 1273.331
2016-06-29 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.38% | 1207.5075 | 1272.4925 | 2480 | 0 | 0.4869 | 0.5131 | 1 | 0 | 2480 | 1207.5075 | 1272.4925
2016-06-29 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.71% | 1199.2023 | 1280.7977 | 2480 | 0 | 0.48355 | 0.51645 | 1 | 0 | 2480 | 1199.2023 | 1280.7977
2016-06-29 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.29% | 1234.78 | 1306.4376 | 2541.2176 | 8.1644 | 0.48643 | 0.51357 | 1.0389 | 7.8586 | 2549.0762 | 1238.6026 | 1310.4736
2016-06-29 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5445 | 1303.452 | 2540.9964 | 10.9071 | 0.48752 | 0.51248 | 1.039 | 10.4977 | 2551.4941 | 1242.6622 | 1308.8319
2016-06-29 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.41% | 1236.3217 | 1304.7726 | 2541.0943 | 8.6427 | 0.48704 | 0.51296 | 1.039 | 8.3186 | 2549.4128 | 1240.3732 | 1309.0397
2016-06-29 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.5% | 1237.5572 | 1303.4382 | 2540.9954 | 8.7896 | 0.48752 | 0.51248 | 1.039 | 8.4596 | 2549.4551 | 1241.6815 | 1307.7736
2016-06-29 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.49% | 1208.8692 | 1275.1778 | 2484.047 | 17.1965 | 0.48745 | 0.51255 | 1.0634 | 16.1717 | 2500.2187 | 1216.752 | 1283.4667
2016-06-29 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 17.2961 | 0.49325 | 0.50675 | 1.0641 | 16.2539 | 2498.4314 | 1231.267 | 1267.1644
2016-06-30 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-06-30 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-06-30 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-06-30 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-06-30 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-06-30 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-06-30 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-06-30 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-06-30 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-06-30 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-06-30 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-06-30 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.34% | 1219.4741 | 1263.1943 | 2482.6684 | 12.5814 | 0.49172 | 0.50828 | 1.0639 | 11.8255 | 2494.4938 | 1225.2889 | 1269.2049
2016-06-30 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.21% | 1217.7947 | 1265.092 | 2482.8867 | 11.9732 | 0.49105 | 0.50895 | 1.0638 | 11.2547 | 2494.1414 | 1223.3213 | 1270.8202
2016-06-30 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.81% | 1200.4377 | 1284.7054 | 2485.1431 | 14.0099 | 0.48405 | 0.51595 | 1.0629 | 13.1805 | 2498.3236 | 1206.8177 | 1291.5059
2016-06-30 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.7897 | 1301.2577 | 2487.0473 | 20.9867 | 0.47814 | 0.52186 | 1.0622 | 19.7586 | 2506.8059 | 1195.237 | 1311.5689
2016-06-30 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.783 | 1301.2652 | 2487.0482 | 21.2371 | 0.47814 | 0.52186 | 1.0622 | 19.9943 | 2507.0425 | 1195.343 | 1311.6995
2016-06-30 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.64% | 1292.1438 | 1424.8203 | 2716.9641 | 42.2804 | 0.47818 | 0.52182 | 1.1195 | 37.7657 | 2754.7298 | 1310.2025 | 1444.5273
2016-06-30 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.83% | 1294.7751 | 1421.5311 | 2716.3062 | 35.0315 | 0.47915 | 0.52085 | 1.1198 | 31.284 | 2747.5902 | 1309.7649 | 1437.8253
2016-06-30 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.45% | 1316.6308 | 1394.2115 | 2710.8423 | 26.4916 | 0.48724 | 0.51276 | 1.1218 | 23.6151 | 2734.4574 | 1328.137 | 1406.3203
2016-06-30 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1996 | 1383.5005 | 2708.7001 | 20.101 | 0.49041 | 0.50959 | 1.1226 | 17.9057 | 2726.6058 | 1333.9807 | 1392.6251
2016-06-30 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.16% | 1326.2227 | 1382.2216 | 2708.4443 | 21.453 | 0.49079 | 0.50921 | 1.1227 | 19.1084 | 2727.5528 | 1335.6009 | 1391.9519
2016-06-30 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.8106 | 1378.9868 | 2707.7974 | 18.6544 | 0.49175 | 0.50825 | 1.1229 | 16.6122 | 2724.4095 | 1336.9796 | 1387.43
2016-06-30 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0691 | 1376.1102 | 2702.1793 | 31.0425 | 0.49193 | 0.50807 | 1.1476 | 27.0505 | 2729.2297 | 1339.376 | 1389.8538
2016-06-30 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.65% | 1329.6194 | 1371.4948 | 2701.1142 | 34.4209 | 0.49325 | 0.50675 | 1.148 | 29.9841 | 2731.0983 | 1344.4089 | 1386.6893
2016-07-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-01 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-01 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-01 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-01 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-01 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-01 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-01 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-01 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-01 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.34% | 1219.4741 | 1263.1943 | 2482.6684 | 12.5814 | 0.49172 | 0.50828 | 1.0639 | 11.8255 | 2494.4938 | 1225.2889 | 1269.2049
2016-07-01 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.21% | 1246.502 | 1293.7779 | 2540.2798 | 7.3681 | 0.49105 | 0.50895 | 1.0393 | 7.0896 | 2547.3695 | 1249.9833 | 1297.3861
2016-07-01 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.81% | 1228.7359 | 1312.9653 | 2541.7011 | 8.6215 | 0.48405 | 0.51595 | 1.0387 | 8.3001 | 2550.0012 | 1232.7535 | 1317.2477
2016-07-01 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.63% | 1213.7425 | 1329.1581 | 2542.9006 | 12.9149 | 0.47814 | 0.52186 | 1.0383 | 12.4391 | 2555.3397 | 1219.6902 | 1335.6495
2016-07-01 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.63% | 1213.7357 | 1329.1655 | 2542.9011 | 13.069 | 0.47814 | 0.52186 | 1.0383 | 12.5875 | 2555.4886 | 1219.7542 | 1335.7344
2016-07-01 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.64% | 1213.837 | 1329.0561 | 2542.893 | 13.5297 | 0.47818 | 0.52182 | 1.0383 | 13.0312 | 2555.9243 | 1220.0682 | 1335.856
2016-07-01 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2969 | 1298.4245 | 2486.7214 | 18.2164 | 0.47915 | 0.52085 | 1.0623 | 17.1482 | 2503.8696 | 1196.5135 | 1307.3561
2016-07-01 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.45% | 1208.3553 | 1275.7585 | 2484.1138 | 13.7756 | 0.48724 | 0.51276 | 1.0633 | 12.955 | 2497.0689 | 1214.6675 | 1282.4014
2016-07-01 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.2194 | 1266.8721 | 2483.0915 | 10.4525 | 0.49041 | 0.50959 | 1.0638 | 9.8261 | 2492.9175 | 1221.0382 | 1271.8794
2016-07-01 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-01 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-01 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-01 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-02 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-02 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-02 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-02 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-02 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-02 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-02 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-02 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.67% | 1223.5487 | 1258.59 | 2482.1387 | 13.5978 | 0.49337 | 0.50663 | 1.0641 | 12.7783 | 2494.9169 | 1229.8531 | 1265.0639
2016-07-02 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.59% | 1251.3284 | 1288.5653 | 2539.8937 | 8.7527 | 0.49295 | 0.50705 | 1.0394 | 8.4206 | 2548.3143 | 1255.4793 | 1292.835
2016-07-02 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-02 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-02 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-02 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-02 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-02 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-02 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.63% | 1213.7357 | 1329.1655 | 2542.9011 | 13.069 | 0.47814 | 0.52186 | 1.0383 | 12.5875 | 2555.4886 | 1219.7542 | 1335.7344
2016-07-02 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.64% | 1185.8819 | 1301.1534 | 2487.0353 | 21.9858 | 0.47818 | 0.52182 | 1.0622 | 20.6991 | 2507.7344 | 1195.7798 | 1311.9546
2016-07-02 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2969 | 1298.4245 | 2486.7214 | 18.2164 | 0.47915 | 0.52085 | 1.0623 | 17.1482 | 2503.8696 | 1196.5135 | 1307.3561
2016-07-02 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.45% | 1208.3553 | 1275.7585 | 2484.1138 | 13.7756 | 0.48724 | 0.51276 | 1.0633 | 12.955 | 2497.0689 | 1214.6675 | 1282.4014
2016-07-02 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.2194 | 1266.8721 | 2483.0915 | 10.4525 | 0.49041 | 0.50959 | 1.0638 | 9.8261 | 2492.9175 | 1221.0382 | 1271.8794
2016-07-02 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-02 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-02 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-02 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-03 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-03 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-03 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-03 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-03 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-03 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-03 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-03 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-03 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-03 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-03 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-03 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.34% | 1219.4741 | 1263.1943 | 2482.6684 | 12.5814 | 0.49172 | 0.50828 | 1.0639 | 11.8255 | 2494.4938 | 1225.2889 | 1269.2049
2016-07-03 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.21% | 1217.7947 | 1265.092 | 2482.8867 | 11.9732 | 0.49105 | 0.50895 | 1.0638 | 11.2547 | 2494.1414 | 1223.3213 | 1270.8202
2016-07-03 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.81% | 1200.4377 | 1284.7054 | 2485.1431 | 14.0099 | 0.48405 | 0.51595 | 1.0629 | 13.1805 | 2498.3236 | 1206.8177 | 1291.5059
2016-07-03 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.7897 | 1301.2577 | 2487.0473 | 20.9867 | 0.47814 | 0.52186 | 1.0622 | 19.7586 | 2506.8059 | 1195.237 | 1311.5689
2016-07-03 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.783 | 1301.2652 | 2487.0482 | 21.2371 | 0.47814 | 0.52186 | 1.0622 | 19.9943 | 2507.0425 | 1195.343 | 1311.6995
2016-07-03 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.64% | 1185.8819 | 1301.1534 | 2487.0353 | 21.9858 | 0.47818 | 0.52182 | 1.0622 | 20.6991 | 2507.7344 | 1195.7798 | 1311.9546
2016-07-03 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2969 | 1298.4245 | 2486.7214 | 18.2164 | 0.47915 | 0.52085 | 1.0623 | 17.1482 | 2503.8696 | 1196.5135 | 1307.3561
2016-07-03 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.45% | 1208.3553 | 1275.7585 | 2484.1138 | 13.7756 | 0.48724 | 0.51276 | 1.0633 | 12.955 | 2497.0689 | 1214.6675 | 1282.4014
2016-07-03 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.2194 | 1266.8721 | 2483.0915 | 10.4525 | 0.49041 | 0.50959 | 1.0638 | 9.8261 | 2492.9175 | 1221.0382 | 1271.8794
2016-07-03 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-03 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-03 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-03 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-04 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.24% | 1351.4296 | 1477.9986 | 2829.4282 | 46.8382 | 0.48122 | 0.51878 | 1.1925 | 39.2777 | 2868.7059 | 1370.3308 | 1498.3751
2016-07-04 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.77% | 1330.7962 | 1506.8853 | 2837.6815 | 36.3231 | 0.47387 | 0.52613 | 1.1895 | 30.5352 | 2868.2167 | 1345.266 | 1522.9507
2016-07-04 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.15% | 1322.0445 | 1519.1377 | 2841.1822 | 33.4764 | 0.47076 | 0.52924 | 1.1883 | 28.1716 | 2869.3538 | 1335.3065 | 1534.0473
2016-07-04 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.17% | 1322.3106 | 1518.7651 | 2841.0758 | 34.8903 | 0.47085 | 0.52915 | 1.1883 | 29.3605 | 2870.4363 | 1336.1351 | 1534.3012
2016-07-04 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.65% | 1343.1291 | 1489.6193 | 2832.7484 | 39.3367 | 0.47827 | 0.52173 | 1.1913 | 33.0198 | 2865.7682 | 1358.9214 | 1506.8468
2016-07-04 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.63% | 1384.9523 | 1431.0667 | 2816.0191 | 15.8691 | 0.49316 | 0.50684 | 1.1973 | 13.2545 | 2829.2736 | 1391.4889 | 1437.7846
2016-07-04 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6126 | 1431.5423 | 2816.1549 | 16.6772 | 0.49304 | 0.50696 | 1.1972 | 13.93 | 2830.085 | 1391.4806 | 1438.6043
2016-07-04 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5373 | 1430.2477 | 2815.7851 | 41.8394 | 0.49337 | 0.50663 | 1.1973 | 34.9435 | 2850.7285 | 1402.7773 | 1447.9512
2016-07-04 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.59% | 1384.361 | 1431.8946 | 2816.2556 | 43.7633 | 0.49295 | 0.50705 | 1.1972 | 36.5554 | 2852.811 | 1402.3809 | 1450.43
2016-07-04 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0976 | 1372.1731 | 2701.2707 | 33.4896 | 0.49305 | 0.50695 | 1.1479 | 29.1743 | 2730.445 | 1343.4821 | 1386.9629
2016-07-04 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.48% | 1330.5446 | 1376.8192 | 2707.3638 | 25.8152 | 0.49239 | 0.50761 | 1.1231 | 22.9857 | 2730.3496 | 1341.8625 | 1388.487
2016-07-04 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.34% | 1328.7459 | 1379.0676 | 2707.8135 | 24.195 | 0.49172 | 0.50828 | 1.1229 | 21.5463 | 2729.3598 | 1339.3407 | 1390.0191
2016-07-04 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.21% | 1217.7947 | 1265.092 | 2482.8867 | 11.9732 | 0.49105 | 0.50895 | 1.0638 | 11.2547 | 2494.1414 | 1223.3213 | 1270.8202
2016-07-04 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-04 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-04 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-04 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-04 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-04 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.45% | 1236.8401 | 1304.2127 | 2541.0528 | 8.4773 | 0.48724 | 0.51276 | 1.039 | 8.1593 | 2549.2121 | 1240.8156 | 1308.3965
2016-07-04 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-04 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-04 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-04 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-04 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-05 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-05 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-05 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-05 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-05 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-05 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-05 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-05 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-05 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.59% | 1328.8151 | 1372.5403 | 2701.3555 | 32.8225 | 0.49295 | 0.50705 | 1.1479 | 28.5939 | 2729.9494 | 1342.9104 | 1387.0389
2016-07-05 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-05 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-05 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-05 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-05 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-05 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-05 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-05 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-05 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-05 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-05 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-05 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-05 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-05 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-05 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.65% | 1252.0858 | 1287.7474 | 2539.8331 | 9.1789 | 0.49325 | 0.50675 | 1.0395 | 8.8305 | 2548.6636 | 1256.4414 | 1292.2223
2016-07-06 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-06 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-06 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-06 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-06 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-06 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-06 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-06 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.67% | 1223.5487 | 1258.59 | 2482.1387 | 13.5978 | 0.49337 | 0.50663 | 1.0641 | 12.7783 | 2494.9169 | 1229.8531 | 1265.0639
2016-07-06 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-06 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-06 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-06 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-06 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-06 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-06 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-06 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-06 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-06 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-06 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-06 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-06 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-06 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-06 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.39% | 1219.9835 | 1260.0165 | 2480 | 0 | 0.49193 | 0.50807 | 1 | 0 | 2480 | 1219.9835 | 1260.0165
2016-07-06 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-07 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-07 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-07 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-07 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-07 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-07 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-07 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-07 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-07 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-07 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-07 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-07 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-07 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-07 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-07 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-07 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-07 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-07 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-07 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-07 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-07 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-07 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-07 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-07 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-08 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-08 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-08 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-08 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-08 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-08 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-08 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-08 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-08 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-08 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-08 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-08 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.34% | 1219.4741 | 1263.1943 | 2482.6684 | 12.5814 | 0.49172 | 0.50828 | 1.0639 | 11.8255 | 2494.4938 | 1225.2889 | 1269.2049
2016-07-08 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.21% | 1217.7947 | 1265.092 | 2482.8867 | 11.9732 | 0.49105 | 0.50895 | 1.0638 | 11.2547 | 2494.1414 | 1223.3213 | 1270.8202
2016-07-08 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.81% | 1200.4377 | 1284.7054 | 2485.1431 | 14.0099 | 0.48405 | 0.51595 | 1.0629 | 13.1805 | 2498.3236 | 1206.8177 | 1291.5059
2016-07-08 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.7897 | 1301.2577 | 2487.0473 | 20.9867 | 0.47814 | 0.52186 | 1.0622 | 19.7586 | 2506.8059 | 1195.237 | 1311.5689
2016-07-08 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.63% | 1185.783 | 1301.2652 | 2487.0482 | 21.2371 | 0.47814 | 0.52186 | 1.0622 | 19.9943 | 2507.0425 | 1195.343 | 1311.6995
2016-07-08 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.64% | 1185.8819 | 1301.1534 | 2487.0353 | 21.9858 | 0.47818 | 0.52182 | 1.0622 | 20.6991 | 2507.7344 | 1195.7798 | 1311.9546
2016-07-08 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.83% | 1188.2969 | 1298.4245 | 2486.7214 | 18.2164 | 0.47915 | 0.52085 | 1.0623 | 17.1482 | 2503.8696 | 1196.5135 | 1307.3561
2016-07-08 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.45% | 1208.3553 | 1275.7585 | 2484.1138 | 13.7756 | 0.48724 | 0.51276 | 1.0633 | 12.955 | 2497.0689 | 1214.6675 | 1282.4014
2016-07-08 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.2194 | 1266.8721 | 2483.0915 | 10.4525 | 0.49041 | 0.50959 | 1.0638 | 9.8261 | 2492.9175 | 1221.0382 | 1271.8794
2016-07-08 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-08 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-08 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-08 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-09 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-09 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-09 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-09 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-09 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-09 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-09 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-09 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-09 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-09 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-09 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-09 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-09 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-09 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-09 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-09 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-09 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-09 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-09 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-09 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-09 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-09 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-09 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-09 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-10 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.24% | 1193.4286 | 1292.6257 | 2486.0543 | 15.2224 | 0.48122 | 0.51878 | 1.0626 | 14.3262 | 2500.3805 | 1200.3227 | 1300.0578
2016-07-10 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-10 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-10 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-10 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-10 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-10 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-10 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-10 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-10 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-10 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-10 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-10 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-10 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-10 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-10 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-10 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-10 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-10 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-10 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-10 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-10 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-10 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-10 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-11 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-11 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-11 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-11 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-11 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-11 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-11 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-11 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-11 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.59% | 1328.8151 | 1372.5403 | 2701.3555 | 32.8225 | 0.49295 | 0.50705 | 1.1479 | 28.5939 | 2729.9494 | 1342.9104 | 1387.0389
2016-07-11 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-11 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-11 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-11 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-11 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-11 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-11 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-11 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-11 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-11 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-11 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-11 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-11 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-11 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-11 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-12 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-12 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-12 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-12 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-12 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-12 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-12 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-12 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-12 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-12 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-12 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-12 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-12 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-12 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-12 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-12 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-12 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-12 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-12 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-12 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-12 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-12 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-12 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-12 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-13 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-13 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-13 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-13 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-13 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-13 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-13 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-13 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-13 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-13 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-13 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-13 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-13 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-13 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-13 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-13 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-13 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-13 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-13 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-13 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-13 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-13 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-13 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-13 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-14 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-14 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-14 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-14 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-14 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-14 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-14 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-14 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-14 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.59% | 1328.8151 | 1372.5403 | 2701.3555 | 32.8225 | 0.49295 | 0.50705 | 1.1479 | 28.5939 | 2729.9494 | 1342.9104 | 1387.0389
2016-07-14 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.337 | 1374.5787 | 2706.9157 | 27.908 | 0.49305 | 0.50695 | 1.1233 | 24.8455 | 2731.7612 | 1344.5871 | 1387.1741
2016-07-14 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-14 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-14 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.21% | 1246.502 | 1293.7779 | 2540.2798 | 7.3681 | 0.49105 | 0.50895 | 1.0393 | 7.0896 | 2547.3695 | 1249.9833 | 1297.3861
2016-07-14 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-14 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-14 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-14 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-14 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-14 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-14 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-14 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-14 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-14 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-14 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.65% | 1329.6194 | 1371.4948 | 2701.1142 | 34.4209 | 0.49325 | 0.50675 | 1.148 | 29.9841 | 2731.0983 | 1344.4089 | 1386.6893
2016-07-15 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-15 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-15 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-15 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-15 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-15 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-15 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-15 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-15 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-15 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-15 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-15 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-15 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-15 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-15 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-15 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-15 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-15 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-15 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-15 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-15 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-15 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-15 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-15 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-16 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-16 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-16 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-16 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-16 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-16 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-16 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-16 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-16 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-16 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-16 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-16 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-16 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-16 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-16 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-16 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-16 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-16 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-16 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-16 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-16 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-16 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-16 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-16 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-17 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-17 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-17 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-17 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-17 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-17 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-17 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-17 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-17 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-17 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-17 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-17 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-17 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-17 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-17 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-17 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-17 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-17 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-17 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-17 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-17 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-17 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-17 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-17 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-18 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-18 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-18 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-18 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-18 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-18 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-18 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-18 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-18 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-18 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-18 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-18 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-18 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-18 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-18 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-18 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-18 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-18 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-18 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-18 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-18 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-18 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-18 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-18 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-19 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-19 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-19 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-19 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-19 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-19 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-19 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-19 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-19 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-19 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-19 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-19 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-19 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-19 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-19 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-19 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-19 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-19 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-19 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-19 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-19 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-19 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-19 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-19 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-20 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-20 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-20 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-20 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-20 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-20 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-20 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-20 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-20 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-20 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-20 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-20 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-20 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-20 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-20 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-20 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-20 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-20 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-20 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-20 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-20 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-20 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-20 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-20 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-21 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-21 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-21 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-21 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-21 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-21 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-21 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-21 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-21 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-21 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-21 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-21 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-21 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-21 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-21 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-21 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-21 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-21 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-21 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.45% | 1236.8401 | 1304.2127 | 2541.0528 | 8.4773 | 0.48724 | 0.51276 | 1.039 | 8.1593 | 2549.2121 | 1240.8156 | 1308.3965
2016-07-21 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.2194 | 1266.8721 | 2483.0915 | 10.4525 | 0.49041 | 0.50959 | 1.0638 | 9.8261 | 2492.9175 | 1221.0382 | 1271.8794
2016-07-21 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-21 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-21 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-21 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.65% | 1329.6194 | 1371.4948 | 2701.1142 | 34.4209 | 0.49325 | 0.50675 | 1.148 | 29.9841 | 2731.0983 | 1344.4089 | 1386.6893
2016-07-22 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-22 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-22 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-22 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-22 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-22 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-22 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-22 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-22 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-22 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-22 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-22 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-22 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-22 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-22 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-22 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-22 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-22 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-22 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-22 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-22 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-22 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-22 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-22 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-23 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-23 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-23 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-23 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-23 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-23 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-23 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-23 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-23 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-23 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-23 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-23 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-23 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-23 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-23 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-23 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-23 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-23 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-23 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-23 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-23 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.16% | 1217.1583 | 1265.8111 | 2482.9694 | 11.1556 | 0.49079 | 0.50921 | 1.0638 | 10.4865 | 2493.4559 | 1222.305 | 1271.1509
2016-07-23 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-23 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-23 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-24 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-24 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-24 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-24 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-24 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-24 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-24 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-24 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-24 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-24 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-24 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-24 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-24 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-24 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-24 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-24 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-24 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-24 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-24 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-24 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-24 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-24 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-24 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7425 | 1291.3581 | 2540.1006 | 8.278 | 0.49193 | 0.50807 | 1.0394 | 7.9646 | 2548.0652 | 1252.6605 | 1295.4047
2016-07-24 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-25 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-25 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-25 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-25 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-25 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-25 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-25 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-25 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-25 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-25 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-25 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-25 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-25 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-25 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-25 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-25 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-25 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-25 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-25 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-25 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-25 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-25 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-25 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.39% | 1219.9835 | 1260.0165 | 2480 | 0 | 0.49193 | 0.50807 | 1 | 0 | 2480 | 1219.9835 | 1260.0165
2016-07-25 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.65% | 1223.2498 | 1258.9277 | 2482.1775 | 14.9157 | 0.49325 | 0.50675 | 1.0641 | 14.0169 | 2496.1945 | 1230.1636 | 1266.0308
2016-07-26 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-26 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-26 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-26 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-26 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-26 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-26 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-26 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-26 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-26 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.61% | 1251.5944 | 1288.278 | 2539.8724 | 8.9306 | 0.49305 | 0.50695 | 1.0394 | 8.5917 | 2548.4641 | 1255.8306 | 1292.6335
2016-07-26 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-26 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-26 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-26 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-26 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-26 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-26 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-26 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-26 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-26 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-26 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-26 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2817 | 1291.8558 | 2540.1375 | 5.9694 | 0.49175 | 0.50825 | 1.0393 | 5.7435 | 2545.8809 | 1251.106 | 1294.7749
2016-07-26 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-26 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-27 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.24% | 1300.3666 | 1414.5417 | 2714.9083 | 29.2739 | 0.48122 | 0.51878 | 1.1203 | 26.1303 | 2741.0386 | 1312.9411 | 1428.0975
2016-07-27 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.77% | 1280.5129 | 1439.3589 | 2719.8718 | 22.702 | 0.47387 | 0.52613 | 1.1185 | 20.2974 | 2740.1691 | 1290.1313 | 1450.0378
2016-07-27 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.15% | 1272.0919 | 1449.8852 | 2721.977 | 20.9228 | 0.47076 | 0.52924 | 1.1177 | 18.7197 | 2740.6967 | 1280.9043 | 1459.7924
2016-07-27 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 94.17% | 1272.3479 | 1449.5651 | 2721.913 | 21.8065 | 0.47085 | 0.52915 | 1.1177 | 19.5099 | 2741.4229 | 1281.5342 | 1459.8887
2016-07-27 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.65% | 1292.3798 | 1424.5252 | 2716.905 | 24.5855 | 0.47827 | 0.52173 | 1.1196 | 21.9598 | 2738.8649 | 1302.8824 | 1435.9824
2016-07-27 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.63% | 1332.6228 | 1374.2215 | 2706.8443 | 9.9182 | 0.49316 | 0.50684 | 1.1233 | 8.8296 | 2715.6739 | 1336.9772 | 1378.6967
2016-07-27 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.2959 | 1374.6301 | 2706.926 | 10.4233 | 0.49304 | 0.50696 | 1.1233 | 9.2795 | 2716.2055 | 1336.871 | 1379.3345
2016-07-27 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-27 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.59% | 1222.5099 | 1259.7638 | 2482.2737 | 14.2231 | 0.49295 | 0.50705 | 1.0641 | 13.3665 | 2495.6402 | 1229.0989 | 1266.5413
2016-07-27 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-27 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-27 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-27 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-27 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-27 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-27 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-27 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-27 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-27 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-27 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-27 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-27 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-27 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-27 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-28 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-28 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-28 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-28 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-28 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-28 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-28 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-28 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-28 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-28 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-28 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.48% | 1221.1248 | 1261.3289 | 2482.4538 | 13.4239 | 0.49239 | 0.50761 | 1.064 | 12.6163 | 2495.0701 | 1227.337 | 1267.7331
2016-07-28 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.34% | 1248.221 | 1291.9214 | 2540.1423 | 7.7424 | 0.49172 | 0.50828 | 1.0393 | 7.4494 | 2547.5917 | 1251.884 | 1295.7077
2016-07-28 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-28 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-28 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-28 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-28 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-28 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-28 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-28 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-28 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-28 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-28 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.3011 | 1378.3737 | 2707.6747 | 25.8688 | 0.49193 | 0.50807 | 1.123 | 23.0358 | 2730.7105 | 1340.633 | 1390.0775
2016-07-28 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.65% | 1329.6194 | 1371.4948 | 2701.1142 | 34.4209 | 0.49325 | 0.50675 | 1.148 | 29.9841 | 2731.0983 | 1344.4089 | 1386.6893
2016-07-29 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-29 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-29 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-29 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-29 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-29 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-29 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-29 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9442 | 1371.0725 | 2701.0167 | 31.3796 | 0.49337 | 0.50663 | 1.148 | 27.3339 | 2728.3506 | 1343.4299 | 1384.9207
2016-07-29 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-29 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-29 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.48% | 1249.9107 | 1290.0965 | 2540.0071 | 8.2609 | 0.49239 | 0.50761 | 1.0394 | 7.9478 | 2547.9549 | 1253.8241 | 1294.1309
2016-07-29 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-29 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-29 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-29 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-29 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-29 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-29 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-29 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-29 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8895 | 1295.5193 | 2540.4088 | 6.4323 | 0.49041 | 0.50959 | 1.0392 | 6.1895 | 2546.5983 | 1247.9249 | 1298.6734
2016-07-29 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.16% | 1245.8506 | 1294.4813 | 2540.3319 | 6.865 | 0.49079 | 0.50921 | 1.0393 | 6.6056 | 2546.9375 | 1249.0926 | 1297.845
2016-07-29 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5334 | 1263.1273 | 2482.6607 | 9.7003 | 0.49175 | 0.50825 | 1.0639 | 9.1174 | 2491.7781 | 1224.0169 | 1267.7612
2016-07-29 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-29 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.65% | 1332.86 | 1373.9249 | 2706.785 | 28.6841 | 0.49325 | 0.50675 | 1.1233 | 25.5353 | 2732.3203 | 1345.4552 | 1386.8651
2016-07-30 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.24% | 1297.205 | 1413.6335 | 2710.8385 | 35.1287 | 0.48122 | 0.51878 | 1.1444 | 30.697 | 2741.5355 | 1311.9771 | 1429.5585
2016-07-30 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.77% | 1277.3995 | 1439.3806 | 2716.7801 | 27.2424 | 0.47387 | 0.52613 | 1.1422 | 23.8516 | 2740.6317 | 1288.7022 | 1451.9295
2016-07-30 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.15% | 1268.999 | 1450.3014 | 2719.3003 | 25.1073 | 0.47076 | 0.52924 | 1.1412 | 22.0003 | 2741.3006 | 1279.3558 | 1461.9448
2016-07-30 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.17% | 1269.2544 | 1449.9693 | 2719.2237 | 26.1678 | 0.47085 | 0.52915 | 1.1413 | 22.9289 | 2742.1526 | 1280.0506 | 1462.102
2016-07-30 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.65% | 1289.2376 | 1423.9911 | 2713.2287 | 29.5026 | 0.47827 | 0.52173 | 1.1435 | 25.8007 | 2739.0294 | 1301.5772 | 1437.4522
2016-07-30 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.63% | 1329.3827 | 1371.8025 | 2701.1852 | 11.9018 | 0.49316 | 0.50684 | 1.1479 | 10.3679 | 2711.5531 | 1334.4958 | 1377.0574
2016-07-30 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.0566 | 1372.2264 | 2701.283 | 12.5079 | 0.49304 | 0.50696 | 1.1479 | 10.8962 | 2712.1792 | 1334.4289 | 1377.7504
2016-07-30 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1857 | 1373.5179 | 2706.7036 | 26.1496 | 0.49337 | 0.50663 | 1.1233 | 23.2784 | 2729.982 | 1344.6705 | 1385.3115
2016-07-30 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.59% | 1332.0538 | 1374.9327 | 2706.9865 | 27.3521 | 0.49295 | 0.50705 | 1.1232 | 24.3511 | 2731.3377 | 1344.0576 | 1387.28
2016-07-30 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.61% | 1222.7698 | 1259.4701 | 2482.2399 | 14.5122 | 0.49305 | 0.50695 | 1.0641 | 13.638 | 2495.8779 | 1229.4941 | 1266.3839
2016-07-30 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.48% | 1221.1248 | 1258.8752 | 2480 | 0 | 0.49239 | 0.50761 | 1 | 0 | 2480 | 1221.1248 | 1258.8752
2016-07-30 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.34% | 1219.4741 | 1260.5259 | 2480 | 0 | 0.49172 | 0.50828 | 1 | 0 | 2480 | 1219.4741 | 1260.5259
2016-07-30 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.21% | 1217.7947 | 1262.2053 | 2480 | 0 | 0.49105 | 0.50895 | 1 | 0 | 2480 | 1217.7947 | 1262.2053
2016-07-30 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.81% | 1200.4377 | 1279.5623 | 2480 | 0 | 0.48405 | 0.51595 | 1 | 0 | 2480 | 1200.4377 | 1279.5623
2016-07-30 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.7897 | 1294.2103 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.7897 | 1294.2103
2016-07-30 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.63% | 1185.783 | 1294.217 | 2480 | 0 | 0.47814 | 0.52186 | 1 | 0 | 2480 | 1185.783 | 1294.217
2016-07-30 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.64% | 1185.8819 | 1294.1181 | 2480 | 0 | 0.47818 | 0.52182 | 1 | 0 | 2480 | 1185.8819 | 1294.1181
2016-07-30 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.83% | 1188.2969 | 1291.7031 | 2480 | 0 | 0.47915 | 0.52085 | 1 | 0 | 2480 | 1188.2969 | 1291.7031
2016-07-30 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.45% | 1208.3553 | 1271.6447 | 2480 | 0 | 0.48724 | 0.51276 | 1 | 0 | 2480 | 1208.3553 | 1271.6447
2016-07-30 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.08% | 1216.2194 | 1263.7806 | 2480 | 0 | 0.49041 | 0.50959 | 1 | 0 | 2480 | 1216.2194 | 1263.7806
2016-07-30 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.16% | 1217.1583 | 1262.8417 | 2480 | 0 | 0.49079 | 0.50921 | 1 | 0 | 2480 | 1217.1583 | 1262.8417
2016-07-30 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5334 | 1260.4666 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5334 | 1260.4666
2016-07-30 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.39% | 1219.9835 | 1262.6186 | 2482.6021 | 13.4518 | 0.49193 | 0.50807 | 1.064 | 12.6432 | 2495.2454 | 1226.2031 | 1269.0423
2016-07-30 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.6841 | 0.48997 | 0.51003 | 1.1225 | 25.5539 | 2734.5511 | 1336.5322 | 1398.0189
2016-07-31 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-07-31 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-07-31 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-07-31 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-07-31 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-07-31 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-07-31 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-07-31 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-07-31 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-07-31 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-07-31 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-07-31 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-07-31 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-07-31 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-07-31 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-07-31 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-07-31 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-07-31 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-07-31 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-07-31 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-07-31 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-07-31 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-07-31 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-07-31 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-01 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-01 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-01 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-01 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-01 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-01 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-01 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-01 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-01 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-01 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-01 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-01 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-01 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-01 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-01 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-01 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-01 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-01 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-01 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-01 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-01 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-01 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-01 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-01 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-02 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-02 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-02 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-02 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-02 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-02 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-02 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-02 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-02 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-02 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-02 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-02 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-02 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-02 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-02 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-02 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-02 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-02 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-02 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-02 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-02 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-02 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-02 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-02 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-03 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-03 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-03 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-03 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-03 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-03 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-03 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-03 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-03 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-03 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-03 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-03 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-03 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-03 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-03 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-03 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-03 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-03 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-03 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-03 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-03 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-03 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-03 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-03 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-04 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-04 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-04 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-04 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-04 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-04 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-04 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-04 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-04 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-04 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-04 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-04 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-04 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-04 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-04 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-04 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-04 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-04 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-04 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-04 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-04 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-04 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-04 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-04 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-05 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-05 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-05 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-05 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-05 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-05 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-05 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-05 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-05 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-05 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-05 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-05 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-05 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-05 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-05 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-05 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-05 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-05 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-05 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-05 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-05 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-05 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-05 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-05 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-06 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 93.62% | 1188.2041 | 1356.7396 | 2544.9437 | 16.0348 | 0.46808 | 0.53192 | 1.0374 | 15.4561 | 2560.3997 | 1195.4388 | 1364.961
2016-08-06 01:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 92.51% | 1174.1229 | 1371.9473 | 2546.0702 | 15.4545 | 0.46253 | 0.53747 | 1.037 | 14.9031 | 2560.9732 | 1181.016 | 1379.9572
2016-08-06 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-06 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-06 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-06 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-06 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-06 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.42% | 1249.1828 | 1290.8826 | 2540.0654 | 10.4402 | 0.4921 | 0.5079 | 1.0394 | 10.0447 | 2550.1101 | 1254.1258 | 1295.9843
2016-08-06 08:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.35% | 1219.5393 | 1260.4607 | 2480 | 0 | 0.49175 | 0.50825 | 1 | 0 | 2480 | 1219.5393 | 1260.4607
2016-08-06 09:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-06 10:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-06 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-06 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-06 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-06 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-06 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-06 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-06 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-06 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-06 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-06 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-06 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-06 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-06 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-07 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-07 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-07 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-07 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-07 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-07 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-07 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-07 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-07 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-07 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-07 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-07 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-07 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-07 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-07 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-07 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-07 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-07 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-07 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-07 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-07 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-07 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-07 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-07 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-08 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-08 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-08 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-08 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-08 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-08 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-08 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-08 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-08 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-08 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-08 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-08 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-08 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-08 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-08 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-08 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-08 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-08 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-08 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-08 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-08 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-08 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-08 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-08 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-09 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-09 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-09 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-09 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-09 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-09 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-09 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-09 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-09 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2877 | 1291.8493 | 2540.137 | 10.3083 | 0.49175 | 0.50825 | 1.0393 | 9.9181 | 2550.0551 | 1253.1649 | 1296.8901
2016-08-09 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-09 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-09 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-09 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-09 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-09 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-09 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-09 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-09 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-09 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-09 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-09 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-09 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-09 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-09 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-10 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-10 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-10 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-10 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-10 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-10 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-10 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-10 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-10 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-10 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-10 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-10 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-10 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-10 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-10 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-10 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-10 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-10 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-10 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-10 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-10 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-10 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-10 22:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-10 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-11 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-11 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-11 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-11 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-11 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-11 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-11 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-11 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-11 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-11 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-11 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-11 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-11 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-11 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-11 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-11 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-11 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-11 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-11 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-11 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-11 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-11 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-11 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-11 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-12 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-12 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-12 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-12 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-12 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-12 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-12 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-12 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-12 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-12 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-12 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-12 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-12 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-12 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-12 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-12 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-12 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-12 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-12 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-12 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-12 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-12 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-12 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-12 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-13 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-13 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-13 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-13 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-13 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-13 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-13 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-13 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-13 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-13 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-13 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-13 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-13 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-13 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-13 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-13 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-13 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-13 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-13 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-13 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-13 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-13 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-13 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-13 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-14 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-14 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-14 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-14 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-14 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-14 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-14 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-14 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-14 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-14 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-14 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-14 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-14 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-14 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-14 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-14 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-14 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-14 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-14 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-14 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-14 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-14 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-14 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-14 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-15 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-15 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-15 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-15 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-15 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-15 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-15 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-15 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-15 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-15 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-15 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-15 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-15 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-15 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-15 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-15 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-15 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-15 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-15 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-15 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-15 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-15 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-15 22:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-15 23:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.129 | 1264.871 | 2480 | 0 | 0.48997 | 0.51003 | 1 | 0 | 2480 | 1215.129 | 1264.871
2016-08-16 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-16 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-16 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-16 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-16 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-16 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-16 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-16 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-16 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2877 | 1291.8493 | 2540.137 | 10.3083 | 0.49175 | 0.50825 | 1.0393 | 9.9181 | 2550.0551 | 1253.1649 | 1296.8901
2016-08-16 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-16 10:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-16 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-16 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-16 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-16 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-16 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-16 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-16 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-16 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-16 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-16 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-16 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-16 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-16 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-17 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-17 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-17 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-17 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-17 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-17 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-17 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-17 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-17 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-17 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-17 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-17 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-17 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-17 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-17 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-17 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-17 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-17 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-17 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-17 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-17 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-17 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-17 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-17 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-18 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-18 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-18 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-18 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-18 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-18 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-18 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-18 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-18 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-18 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-18 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-18 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-18 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-18 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-18 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-18 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-18 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-18 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-18 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-18 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-18 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-18 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-18 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.84% | 1241.8751 | 1298.7749 | 2540.65 | 12.1807 | 0.48922 | 0.51078 | 1.0391 | 11.722 | 2552.3719 | 1247.6097 | 1304.7622
2016-08-18 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.99% | 1215.129 | 1268.1043 | 2483.2332 | 14.9893 | 0.48997 | 0.51003 | 1.0637 | 14.0917 | 2497.3249 | 1222.0335 | 1275.2914
2016-08-19 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-19 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-19 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-19 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-19 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-19 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-19 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-19 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-19 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-19 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-19 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-19 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-19 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-19 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-19 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-19 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-19 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-19 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-19 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-19 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-19 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.8% | 1241.2944 | 1299.402 | 2540.6964 | 10.4612 | 0.48899 | 0.51101 | 1.0391 | 10.0673 | 2550.7638 | 1246.2173 | 1304.5465
2016-08-19 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5292 | 1271.042 | 2483.5712 | 17.7683 | 0.48892 | 0.51108 | 1.0636 | 16.7065 | 2500.2777 | 1220.6974 | 1279.5803
2016-08-19 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.9906 | 1387.5117 | 2709.5023 | 38.0648 | 0.48922 | 0.51078 | 1.1223 | 33.9166 | 2743.4189 | 1338.5834 | 1404.8355
2016-08-19 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-20 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.62% | 1261.7819 | 1459.6835 | 2721.4654 | 60.1306 | 0.46808 | 0.53192 | 1.1404 | 52.7265 | 2774.192 | 1286.4622 | 1487.7298
2016-08-20 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.51% | 1246.8288 | 1479.1226 | 2725.9514 | 57.9545 | 0.46253 | 0.53747 | 1.1388 | 50.8926 | 2776.844 | 1270.3683 | 1506.4757
2016-08-20 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.22% | 1242.947 | 1484.1689 | 2727.1159 | 57.8477 | 0.46109 | 0.53891 | 1.1383 | 50.8182 | 2777.9341 | 1266.3789 | 1511.5551
2016-08-20 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.11% | 1241.4595 | 1486.1027 | 2727.5622 | 56.3793 | 0.46054 | 0.53946 | 1.1382 | 49.5353 | 2777.0975 | 1264.2726 | 1512.8249
2016-08-20 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.73% | 1263.3058 | 1457.7024 | 2721.0083 | 60.4943 | 0.46865 | 0.53135 | 1.1406 | 53.0375 | 2774.0458 | 1288.1616 | 1485.8841
2016-08-20 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5596 | 1371.5725 | 2701.1321 | 48.2721 | 0.49322 | 0.50678 | 1.148 | 42.0501 | 2743.1822 | 1350.2997 | 1392.8824
2016-08-20 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.51% | 1327.7464 | 1373.9297 | 2701.6761 | 47.0471 | 0.49255 | 0.50745 | 1.1478 | 40.9902 | 2742.6663 | 1347.9361 | 1394.7301
2016-08-20 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5366 | 1375.5024 | 2702.039 | 39.1506 | 0.4921 | 0.5079 | 1.1476 | 34.1143 | 2736.1533 | 1343.3243 | 1392.829
2016-08-20 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.35% | 1325.5862 | 1376.738 | 2702.3241 | 38.656 | 0.49175 | 0.50825 | 1.1475 | 33.6864 | 2736.0106 | 1342.1515 | 1393.8591
2016-08-20 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-20 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.12% | 1245.3584 | 1295.0129 | 2540.3713 | 9.8186 | 0.4906 | 0.5094 | 1.0392 | 9.4478 | 2549.8191 | 1249.9935 | 1299.8257
2016-08-20 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-20 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-20 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-20 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-20 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-20 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-20 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-20 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-20 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-20 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-20 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-20 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-20 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-21 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-21 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-21 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-21 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-21 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-21 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-21 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-21 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-21 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-21 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-21 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-21 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-21 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-21 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-21 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-21 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-21 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-21 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-21 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-21 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-21 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-21 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-21 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-21 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-22 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-22 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-22 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-22 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-22 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-22 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-22 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-22 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-22 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-22 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-22 10:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-22 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-22 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-22 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-22 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-22 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-22 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-22 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-22 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-22 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-22 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-22 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-22 22:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-22 23:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.99% | 1215.129 | 1264.871 | 2480 | 0 | 0.48997 | 0.51003 | 1 | 0 | 2480 | 1215.129 | 1264.871
2016-08-23 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-23 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-23 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-23 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-23 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-23 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-23 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-23 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-23 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.35% | 1248.2877 | 1291.8493 | 2540.137 | 10.3083 | 0.49175 | 0.50825 | 1.0393 | 9.9181 | 2550.0551 | 1253.1649 | 1296.8901
2016-08-23 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-23 10:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-23 11:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-23 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-23 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-23 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-23 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-23 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-23 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-23 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-23 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-23 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-23 21:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.78% | 1212.5292 | 1267.4708 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5292 | 1267.4708
2016-08-23 22:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.84% | 1213.2743 | 1266.7257 | 2480 | 0 | 0.48922 | 0.51078 | 1 | 0 | 2480 | 1213.2743 | 1266.7257
2016-08-23 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.99% | 1243.7734 | 1296.7247 | 2540.4981 | 9.2242 | 0.48997 | 0.51003 | 1.0392 | 8.8762 | 2549.3744 | 1248.1225 | 1301.2518
2016-08-24 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.62% | 1160.8394 | 1329.4515 | 2490.2909 | 26.0566 | 0.46808 | 0.53192 | 1.0609 | 24.562 | 2514.8529 | 1172.3364 | 1342.5165
2016-08-24 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.51% | 1147.0825 | 1344.9968 | 2492.0793 | 25.1136 | 0.46253 | 0.53747 | 1.0601 | 23.6892 | 2515.7685 | 1158.0395 | 1357.729
2016-08-24 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.22% | 1143.5113 | 1349.0323 | 2492.5435 | 25.0674 | 0.46109 | 0.53891 | 1.0599 | 23.6497 | 2516.1933 | 1154.416 | 1361.7773
2016-08-24 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.11% | 1142.1427 | 1350.5787 | 2492.7214 | 24.431 | 0.46054 | 0.53946 | 1.0599 | 23.0509 | 2515.7724 | 1152.7587 | 1363.0137
2016-08-24 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 93.73% | 1162.2414 | 1327.8673 | 2490.1086 | 26.2142 | 0.46865 | 0.53135 | 1.0609 | 24.7088 | 2514.8175 | 1173.8211 | 1340.9964
2016-08-24 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1949 | 1258.9898 | 2482.1847 | 20.9179 | 0.49322 | 0.50678 | 1.0641 | 19.6575 | 2501.8421 | 1232.8904 | 1268.9517
2016-08-24 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-24 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-24 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-24 09:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.1% | 1216.5007 | 1263.4993 | 2480 | 0 | 0.49052 | 0.50948 | 1 | 0 | 2480 | 1216.5007 | 1263.4993
2016-08-24 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-24 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-24 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-24 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-24 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-24 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-24 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-24 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-24 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-24 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-24 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-24 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-24 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-24 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-25 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-25 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-25 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-25 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-25 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-25 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-25 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-25 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-25 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-25 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-25 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.12% | 1216.6774 | 1266.3545 | 2483.0319 | 15.9553 | 0.4906 | 0.5094 | 1.0638 | 14.9987 | 2498.0306 | 1224.0357 | 1273.9949
2016-08-25 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.2% | 1217.7081 | 1265.1898 | 2482.8979 | 16.283 | 0.49101 | 0.50899 | 1.0638 | 15.306 | 2498.2039 | 1225.2235 | 1272.9804
2016-08-25 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.44% | 1249.4739 | 1290.5681 | 2540.0421 | 10.1532 | 0.49222 | 0.50778 | 1.0394 | 9.7685 | 2549.8106 | 1254.2822 | 1295.5285
2016-08-25 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.05% | 1231.8076 | 1309.6478 | 2541.4554 | 9.5831 | 0.48526 | 0.51474 | 1.0388 | 9.225 | 2550.6804 | 1236.2841 | 1314.3963
2016-08-25 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-25 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-25 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-25 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-25 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-25 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-25 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-25 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-25 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-25 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-26 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-26 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-26 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-26 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-26 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-26 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-26 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-26 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-26 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-26 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.5062 | 1383.1173 | 2708.6235 | 32.0792 | 0.49052 | 0.50948 | 1.1226 | 28.575 | 2737.1984 | 1339.5229 | 1397.6755
2016-08-26 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.12% | 1216.6774 | 1266.3545 | 2483.0319 | 15.9553 | 0.4906 | 0.5094 | 1.0638 | 14.9987 | 2498.0306 | 1224.0357 | 1273.9949
2016-08-26 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.2% | 1246.4134 | 1293.8735 | 2540.2869 | 10.0203 | 0.49101 | 0.50899 | 1.0393 | 9.6416 | 2549.9285 | 1251.1475 | 1298.781
2016-08-26 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-26 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-26 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-26 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-26 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-26 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-26 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-26 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-26 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-26 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-26 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-26 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-27 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-27 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-27 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-27 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-27 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-27 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-27 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.51% | 1330.9824 | 1376.2719 | 2707.2544 | 39.2059 | 0.49255 | 0.50745 | 1.1231 | 34.9075 | 2742.1619 | 1348.1762 | 1393.9857
2016-08-27 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7698 | 1377.7878 | 2707.5576 | 32.6255 | 0.4921 | 0.5079 | 1.123 | 29.0514 | 2736.609 | 1344.066 | 1392.543
2016-08-27 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-27 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-27 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.12% | 1245.3584 | 1295.0129 | 2540.3713 | 9.8186 | 0.4906 | 0.5094 | 1.0392 | 9.4478 | 2549.8191 | 1249.9935 | 1299.8257
2016-08-27 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-27 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-27 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-27 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-27 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-27 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-27 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-27 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-27 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-27 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.8% | 1241.2944 | 1299.402 | 2540.6964 | 10.4612 | 0.48899 | 0.51101 | 1.0391 | 10.0673 | 2550.7638 | 1246.2173 | 1304.5465
2016-08-27 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5292 | 1271.042 | 2483.5712 | 17.7683 | 0.48892 | 0.51108 | 1.0636 | 16.7065 | 2500.2777 | 1220.6974 | 1279.5803
2016-08-27 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.9906 | 1387.5117 | 2709.5023 | 38.0648 | 0.48922 | 0.51078 | 1.1223 | 33.9166 | 2743.4189 | 1338.5834 | 1404.8355
2016-08-27 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.99% | 1320.7924 | 1382.9699 | 2703.7623 | 34.5906 | 0.48997 | 0.51003 | 1.147 | 30.1577 | 2733.92 | 1335.5688 | 1398.3512
2016-08-28 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.62% | 1314.5258 | 1529.6639 | 2844.1897 | 80.1742 | 0.46808 | 0.53192 | 1.1872 | 67.5303 | 2911.72 | 1346.1354 | 1565.5846
2016-08-28 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.51% | 1298.9475 | 1551.4734 | 2850.421 | 77.2726 | 0.46253 | 0.53747 | 1.185 | 65.2082 | 2915.6292 | 1329.1085 | 1586.5207
2016-08-28 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.22% | 1294.9035 | 1557.135 | 2852.0386 | 77.1303 | 0.46109 | 0.53891 | 1.1844 | 65.1198 | 2917.1584 | 1324.9298 | 1592.2285
2016-08-28 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.11% | 1293.3538 | 1559.3046 | 2852.6585 | 75.1724 | 0.46054 | 0.53946 | 1.1842 | 63.4786 | 2916.137 | 1322.5883 | 1593.5487
2016-08-28 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 93.73% | 1316.1134 | 1527.4413 | 2843.5547 | 80.659 | 0.46865 | 0.53135 | 1.1875 | 67.9258 | 2911.4804 | 1347.9465 | 1563.5339
2016-08-28 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.1367 | 1430.8087 | 2815.9453 | 64.3628 | 0.49322 | 0.50678 | 1.1973 | 53.7571 | 2869.7024 | 1411.6509 | 1458.0515
2016-08-28 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.51% | 1383.2476 | 1433.4534 | 2816.701 | 62.7295 | 0.49255 | 0.50745 | 1.197 | 52.4047 | 2869.1056 | 1409.0596 | 1460.0461
2016-08-28 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9873 | 1435.2178 | 2817.2051 | 52.2008 | 0.4921 | 0.5079 | 1.1968 | 43.6155 | 2860.8206 | 1403.4506 | 1457.37
2016-08-28 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.35% | 1325.5862 | 1376.738 | 2702.3241 | 38.656 | 0.49175 | 0.50825 | 1.1475 | 33.6864 | 2736.0106 | 1342.1515 | 1393.8591
2016-08-28 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.5062 | 1383.1173 | 2708.6235 | 32.0792 | 0.49052 | 0.50948 | 1.1226 | 28.575 | 2737.1984 | 1339.5229 | 1397.6755
2016-08-28 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.12% | 1216.6774 | 1266.3545 | 2483.0319 | 15.9553 | 0.4906 | 0.5094 | 1.0638 | 14.9987 | 2498.0306 | 1224.0357 | 1273.9949
2016-08-28 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.2% | 1246.4134 | 1293.8735 | 2540.2869 | 10.0203 | 0.49101 | 0.50899 | 1.0393 | 9.6416 | 2549.9285 | 1251.1475 | 1298.781
2016-08-28 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-28 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-28 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-28 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-28 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-28 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-28 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-28 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-28 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-28 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-28 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-28 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-29 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.62% | 1261.7819 | 1459.6835 | 2721.4654 | 60.1306 | 0.46808 | 0.53192 | 1.1404 | 52.7265 | 2774.192 | 1286.4622 | 1487.7298
2016-08-29 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.51% | 1246.8288 | 1479.1226 | 2725.9514 | 57.9545 | 0.46253 | 0.53747 | 1.1388 | 50.8926 | 2776.844 | 1270.3683 | 1506.4757
2016-08-29 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.22% | 1242.947 | 1484.1689 | 2727.1159 | 57.8477 | 0.46109 | 0.53891 | 1.1383 | 50.8182 | 2777.9341 | 1266.3789 | 1511.5551
2016-08-29 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.11% | 1241.4595 | 1486.1027 | 2727.5622 | 56.3793 | 0.46054 | 0.53946 | 1.1382 | 49.5353 | 2777.0975 | 1264.2726 | 1512.8249
2016-08-29 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 93.73% | 1263.3058 | 1457.7024 | 2721.0083 | 60.4943 | 0.46865 | 0.53135 | 1.1406 | 53.0375 | 2774.0458 | 1288.1616 | 1485.8841
2016-08-29 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5596 | 1371.5725 | 2701.1321 | 48.2721 | 0.49322 | 0.50678 | 1.148 | 42.0501 | 2743.1822 | 1350.2997 | 1392.8824
2016-08-29 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.51% | 1327.7464 | 1373.9297 | 2701.6761 | 47.0471 | 0.49255 | 0.50745 | 1.1478 | 40.9902 | 2742.6663 | 1347.9361 | 1394.7301
2016-08-29 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5366 | 1375.5024 | 2702.039 | 39.1506 | 0.4921 | 0.5079 | 1.1476 | 34.1143 | 2736.1533 | 1343.3243 | 1392.829
2016-08-29 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.35% | 1328.817 | 1378.9788 | 2707.7958 | 32.2133 | 0.49175 | 0.50825 | 1.1229 | 28.6867 | 2736.4824 | 1342.9237 | 1393.5588
2016-08-29 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.1% | 1216.5007 | 1266.5542 | 2483.0549 | 16.6812 | 0.49052 | 0.50948 | 1.0638 | 15.6812 | 2498.7361 | 1224.1928 | 1274.5433
2016-08-29 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.12% | 1245.3584 | 1295.0129 | 2540.3713 | 9.8186 | 0.4906 | 0.5094 | 1.0392 | 9.4478 | 2549.8191 | 1249.9935 | 1299.8257
2016-08-29 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-29 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-29 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-29 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-29 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-29 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-29 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-29 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-29 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-29 20:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-29 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-29 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-29 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.99% | 1324.0115 | 1384.9856 | 2708.9971 | 28.8255 | 0.48997 | 0.51003 | 1.1225 | 25.6799 | 2734.677 | 1336.5939 | 1398.0831
2016-08-30 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.62% | 1264.8572 | 1458.9284 | 2723.7857 | 50.1088 | 0.46808 | 0.53192 | 1.117 | 44.8594 | 2768.6451 | 1285.855 | 1482.79
2016-08-30 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.51% | 1249.8676 | 1477.6655 | 2727.5331 | 48.2954 | 0.46253 | 0.53747 | 1.1156 | 43.2897 | 2770.8228 | 1269.8905 | 1500.9322
2016-08-30 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.22% | 1245.9764 | 1482.5295 | 2728.5059 | 48.2065 | 0.46109 | 0.53891 | 1.1153 | 43.2239 | 2771.7298 | 1265.9067 | 1505.8231
2016-08-30 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.11% | 1244.4853 | 1484.3934 | 2728.8787 | 46.9827 | 0.46054 | 0.53946 | 1.1151 | 42.1319 | 2771.0105 | 1263.8887 | 1507.1218
2016-08-30 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 93.73% | 1266.3849 | 1457.0189 | 2723.4038 | 50.4119 | 0.46865 | 0.53135 | 1.1172 | 45.125 | 2768.5288 | 1287.5325 | 1480.9963
2016-08-30 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.8001 | 1373.9998 | 2706.8 | 40.2267 | 0.49322 | 0.50678 | 1.1233 | 35.811 | 2742.611 | 1350.463 | 1392.148
2016-08-30 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.51% | 1221.5267 | 1260.8749 | 2482.4015 | 20.3871 | 0.49255 | 0.50745 | 1.064 | 19.1602 | 2501.5617 | 1230.964 | 1270.5977
2016-08-30 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4137 | 1262.1325 | 2482.5462 | 16.9653 | 0.4921 | 0.5079 | 1.064 | 15.9452 | 2498.4914 | 1228.2604 | 1270.2311
2016-08-30 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.35% | 1219.5393 | 1263.1206 | 2482.6599 | 16.7509 | 0.49175 | 0.50825 | 1.0639 | 15.7444 | 2498.4043 | 1227.2816 | 1271.1227
2016-08-30 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1776 | 1295.2082 | 2540.3858 | 10.2653 | 0.49052 | 0.50948 | 1.0392 | 9.8777 | 2550.2635 | 1250.0228 | 1300.2407
2016-08-30 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.12% | 1216.6774 | 1263.3226 | 2480 | 0 | 0.4906 | 0.5094 | 1 | 0 | 2480 | 1216.6774 | 1263.3226
2016-08-30 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.2% | 1217.7081 | 1262.2919 | 2480 | 0 | 0.49101 | 0.50899 | 1 | 0 | 2480 | 1217.7081 | 1262.2919
2016-08-30 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.44% | 1220.6982 | 1259.3018 | 2480 | 0 | 0.49222 | 0.50778 | 1 | 0 | 2480 | 1220.6982 | 1259.3018
2016-08-30 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.05% | 1203.4387 | 1276.5613 | 2480 | 0 | 0.48526 | 0.51474 | 1 | 0 | 2480 | 1203.4387 | 1276.5613
2016-08-30 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.93% | 1189.4821 | 1290.5179 | 2480 | 0 | 0.47963 | 0.52037 | 1 | 0 | 2480 | 1189.4821 | 1290.5179
2016-08-30 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.86% | 1188.7013 | 1291.2987 | 2480 | 0 | 0.47932 | 0.52068 | 1 | 0 | 2480 | 1188.7013 | 1291.2987
2016-08-30 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.79% | 1187.8429 | 1292.1571 | 2480 | 0 | 0.47897 | 0.52103 | 1 | 0 | 2480 | 1187.8429 | 1292.1571
2016-08-30 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.23% | 1193.1905 | 1286.8095 | 2480 | 0 | 0.48113 | 0.51887 | 1 | 0 | 2480 | 1193.1905 | 1286.8095
2016-08-30 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.35% | 1207.0937 | 1272.9063 | 2480 | 0 | 0.48673 | 0.51327 | 1 | 0 | 2480 | 1207.0937 | 1272.9063
2016-08-30 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.86% | 1213.5224 | 1266.4776 | 2480 | 0 | 0.48932 | 0.51068 | 1 | 0 | 2480 | 1213.5224 | 1266.4776
2016-08-30 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.8% | 1212.707 | 1267.293 | 2480 | 0 | 0.48899 | 0.51101 | 1 | 0 | 2480 | 1212.707 | 1267.293
2016-08-30 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.1124 | 1299.5986 | 2540.711 | 10.9344 | 0.48892 | 0.51108 | 1.0391 | 10.5228 | 2551.2338 | 1246.2572 | 1304.9766
2016-08-30 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.2743 | 1270.2 | 2483.4743 | 19.7937 | 0.48922 | 0.51078 | 1.0636 | 18.6101 | 2502.0844 | 1222.3788 | 1279.7056
2016-08-30 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 28.8255 | 0.48208 | 0.51792 | 1.1205 | 25.7251 | 2740.0523 | 1315.0928 | 1424.9594
2016-08-31 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-08-31 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-08-31 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-08-31 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-08-31 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-08-31 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-08-31 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-08-31 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-08-31 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-08-31 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-08-31 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.05% | 1215.8476 | 1264.1524 | 2480 | 0 | 0.49026 | 0.50974 | 1 | 0 | 2480 | 1215.8476 | 1264.1524
2016-08-31 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-08-31 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-08-31 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-08-31 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-08-31 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-08-31 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-08-31 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-08-31 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-08-31 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-08-31 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-08-31 21:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.11% | 1204.2147 | 1275.7853 | 2480 | 0 | 0.48557 | 0.51443 | 1 | 0 | 2480 | 1204.2147 | 1275.7853
2016-08-31 22:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.78% | 1241.0982 | 1299.6139 | 2540.7121 | 13.5843 | 0.48892 | 0.51108 | 1.0391 | 13.0729 | 2553.7851 | 1247.4898 | 1306.2953
2016-08-31 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.42% | 1195.562 | 1290.2149 | 2485.7769 | 19.4757 | 0.48208 | 0.51792 | 1.0627 | 18.3271 | 2504.104 | 1204.3972 | 1299.7068
2016-09-01 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.06% | 1141.5219 | 1351.2803 | 2492.8022 | 14.1589 | 0.46029 | 0.53971 | 1.0598 | 13.3595 | 2506.1617 | 1147.6711 | 1358.4905
2016-09-01 01:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.44% | 1133.8495 | 1359.9501 | 2493.7996 | 15.8236 | 0.4572 | 0.5428 | 1.0594 | 14.9359 | 2508.7354 | 1140.6781 | 1368.0573
2016-09-01 02:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.01% | 1128.4707 | 1366.0282 | 2494.4988 | 14.9841 | 0.45503 | 0.54497 | 1.0592 | 14.1473 | 2508.6461 | 1134.9081 | 1373.738
2016-09-01 03:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 91.22% | 1131.0767 | 1363.0833 | 2494.16 | 15.8148 | 0.45608 | 0.54392 | 1.0593 | 14.9296 | 2509.0897 | 1137.8858 | 1371.2039
2016-09-01 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 92.75% | 1150.1147 | 1341.5704 | 2491.6851 | 16.9887 | 0.46376 | 0.53624 | 1.0603 | 16.0227 | 2507.7078 | 1157.5453 | 1350.1625
2016-09-01 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-01 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-01 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-01 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-01 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-01 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-01 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-01 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-01 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-01 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-01 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-01 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-01 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-01 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-01 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-01 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-01 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-01 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-01 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-02 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-02 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-02 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-02 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-02 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-02 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-02 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-02 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-02 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-02 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-02 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-02 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-02 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-02 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-02 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-02 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-02 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-02 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-02 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-02 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-02 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-02 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-02 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-02 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-03 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-03 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-03 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-03 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-03 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-03 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-03 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-03 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-03 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-03 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.05% | 1321.5735 | 1381.9545 | 2703.528 | 41.9797 | 0.49026 | 0.50974 | 1.1471 | 36.597 | 2740.125 | 1339.5156 | 1400.6094
2016-09-03 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.26% | 1324.4175 | 1378.2573 | 2702.6748 | 42.3005 | 0.49132 | 0.50868 | 1.1474 | 36.8665 | 2739.5413 | 1342.5306 | 1397.0107
2016-09-03 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7965 | 1387.7544 | 2709.5509 | 35.1358 | 0.48915 | 0.51085 | 1.1223 | 31.3073 | 2740.8581 | 1337.1105 | 1403.7477
2016-09-03 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3673 | 1413.2909 | 2714.6582 | 38.0385 | 0.48159 | 0.51841 | 1.1204 | 33.9509 | 2748.609 | 1317.7177 | 1430.8913
2016-09-03 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8637 | 1303.4341 | 2487.2977 | 19.9938 | 0.47736 | 0.52264 | 1.0621 | 18.8255 | 2506.1232 | 1192.8503 | 1313.273
2016-09-03 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8052 | 1303.5001 | 2487.3053 | 19.8276 | 0.47734 | 0.52266 | 1.0621 | 18.6691 | 2505.9745 | 1192.7168 | 1313.2577
2016-09-03 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.82% | 1188.1411 | 1298.6005 | 2486.7417 | 19.4055 | 0.47909 | 0.52091 | 1.0623 | 18.2677 | 2505.0094 | 1196.893 | 1308.1164
2016-09-03 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.39% | 1195.2167 | 1290.6052 | 2485.8218 | 21.2305 | 0.48194 | 0.51806 | 1.0627 | 19.9788 | 2505.8006 | 1204.8453 | 1300.9553
2016-09-03 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.08% | 1203.752 | 1280.9602 | 2484.7122 | 19.7809 | 0.48538 | 0.51462 | 1.0631 | 18.6068 | 2503.3191 | 1212.7835 | 1290.5356
2016-09-03 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.17% | 1217.2694 | 1265.6856 | 2482.955 | 19.8093 | 0.49083 | 0.50917 | 1.0638 | 18.6212 | 2501.5761 | 1226.4093 | 1275.1668
2016-09-03 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-03 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-03 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-03 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-04 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-04 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-04 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-04 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-04 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-04 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-04 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-04 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-04 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-04 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-04 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-04 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-04 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-04 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-04 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-04 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-04 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-04 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-04 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-04 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-04 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-04 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-04 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-04 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-05 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.06% | 1292.6508 | 1560.2889 | 2852.9397 | 43.5659 | 0.46029 | 0.53971 | 1.1841 | 36.7919 | 2889.7316 | 1309.5858 | 1580.1458
2016-09-05 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.44% | 1283.9627 | 1572.4523 | 2856.4149 | 48.688 | 0.4572 | 0.5428 | 1.1829 | 41.1606 | 2897.5755 | 1302.7812 | 1594.7943
2016-09-05 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-05 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-05 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-05 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-05 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.06% | 1376.9465 | 1442.2749 | 2819.2214 | 60.9441 | 0.49031 | 0.50969 | 1.1961 | 50.9514 | 2870.1728 | 1401.9283 | 1468.2445
2016-09-05 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.01% | 1376.2127 | 1443.3022 | 2819.5149 | 62.0913 | 0.49005 | 0.50995 | 1.196 | 51.915 | 2871.4299 | 1401.6534 | 1469.7764
2016-09-05 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.84% | 1373.7704 | 1446.7215 | 2820.4919 | 57.3008 | 0.48918 | 0.51082 | 1.1957 | 47.9235 | 2868.4154 | 1397.2134 | 1471.202
2016-09-05 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-05 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-05 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-05 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6927 | 1298.9719 | 2540.6646 | 11.2434 | 0.48915 | 0.51085 | 1.0391 | 10.82 | 2551.4846 | 1246.9853 | 1304.4993
2016-09-05 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-05 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-05 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-05 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-05 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-05 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-05 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-05 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-05 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-05 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-05 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-06 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.06% | 1292.6508 | 1560.2889 | 2852.9397 | 43.5659 | 0.46029 | 0.53971 | 1.1841 | 36.7919 | 2889.7316 | 1309.5858 | 1580.1458
2016-09-06 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.44% | 1283.9627 | 1572.4523 | 2856.4149 | 48.688 | 0.4572 | 0.5428 | 1.1829 | 41.1606 | 2897.5755 | 1302.7812 | 1594.7943
2016-09-06 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-06 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-06 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-06 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-06 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.06% | 1376.9465 | 1442.2749 | 2819.2214 | 60.9441 | 0.49031 | 0.50969 | 1.1961 | 50.9514 | 2870.1728 | 1401.9283 | 1468.2445
2016-09-06 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.01% | 1376.2127 | 1443.3022 | 2819.5149 | 62.0913 | 0.49005 | 0.50995 | 1.196 | 51.915 | 2871.4299 | 1401.6534 | 1469.7764
2016-09-06 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.84% | 1373.7704 | 1446.7215 | 2820.4919 | 57.3008 | 0.48918 | 0.51082 | 1.1957 | 47.9235 | 2868.4154 | 1397.2134 | 1471.202
2016-09-06 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-06 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-06 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-06 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6927 | 1298.9719 | 2540.6646 | 11.2434 | 0.48915 | 0.51085 | 1.0391 | 10.82 | 2551.4846 | 1246.9853 | 1304.4993
2016-09-06 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-06 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-06 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-06 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-06 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-06 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-06 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-06 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-06 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-06 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-06 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-07 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-07 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-07 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-07 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-07 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-07 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-07 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-07 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.01% | 1215.3143 | 1267.8949 | 2483.2091 | 20.1797 | 0.49005 | 0.50995 | 1.0637 | 18.9711 | 2502.1802 | 1224.611 | 1277.5693
2016-09-07 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.1574 | 1270.3321 | 2483.4895 | 18.6228 | 0.48918 | 0.51082 | 1.0636 | 17.5093 | 2500.9988 | 1221.7226 | 1279.2762
2016-09-07 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-07 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-07 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-07 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.0961 | 1270.4014 | 2483.4975 | 18.2706 | 0.48915 | 0.51085 | 1.0636 | 17.1782 | 2500.6757 | 1221.4989 | 1279.1769
2016-09-07 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3469 | 1291.5879 | 2485.9349 | 19.78 | 0.48159 | 0.51841 | 1.0626 | 18.6146 | 2504.5495 | 1203.3116 | 1301.2379
2016-09-07 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8637 | 1303.4341 | 2487.2977 | 19.9938 | 0.47736 | 0.52264 | 1.0621 | 18.8255 | 2506.1232 | 1192.8503 | 1313.273
2016-09-07 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8052 | 1303.5001 | 2487.3053 | 19.8276 | 0.47734 | 0.52266 | 1.0621 | 18.6691 | 2505.9745 | 1192.7168 | 1313.2577
2016-09-07 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.82% | 1294.6054 | 1421.7433 | 2716.3487 | 37.3182 | 0.47909 | 0.52091 | 1.1198 | 33.3266 | 2749.6753 | 1310.5718 | 1439.1035
2016-09-07 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.39% | 1302.3149 | 1412.1063 | 2714.4213 | 40.8279 | 0.48194 | 0.51806 | 1.1205 | 36.4377 | 2750.859 | 1319.8758 | 1430.9831
2016-09-07 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.08% | 1311.6151 | 1400.4811 | 2712.0962 | 38.0402 | 0.48538 | 0.51462 | 1.1213 | 33.9237 | 2746.02 | 1328.0812 | 1417.9388
2016-09-07 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.17% | 1326.3437 | 1382.0704 | 2708.4141 | 38.0949 | 0.49083 | 0.50917 | 1.1227 | 33.9312 | 2742.3453 | 1342.9983 | 1399.347
2016-09-07 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.03% | 1324.4377 | 1384.4528 | 2708.8906 | 40.4476 | 0.49013 | 0.50987 | 1.1225 | 36.0324 | 2744.923 | 1342.0983 | 1402.8247
2016-09-07 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-07 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-07 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-08 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-08 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-08 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-08 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-08 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-08 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-08 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-08 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-08 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-08 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-08 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-08 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-08 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.0961 | 1270.4014 | 2483.4975 | 18.2706 | 0.48915 | 0.51085 | 1.0636 | 17.1782 | 2500.6757 | 1221.4989 | 1279.1769
2016-09-08 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.32% | 1222.5015 | 1319.6983 | 2542.1999 | 12.1723 | 0.48159 | 0.51841 | 1.0385 | 11.7207 | 2553.9206 | 1228.1461 | 1325.7745
2016-09-08 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.47% | 1211.7711 | 1331.2872 | 2543.0583 | 12.3039 | 0.47736 | 0.52264 | 1.0382 | 11.8513 | 2554.9096 | 1217.4285 | 1337.4811
2016-09-08 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-08 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-08 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-08 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-08 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-08 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-08 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-08 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-08 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-09 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-09 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-09 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-09 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-09 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-09 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-09 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-09 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-09 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-09 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-09 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-09 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-09 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6927 | 1298.9719 | 2540.6646 | 11.2434 | 0.48915 | 0.51085 | 1.0391 | 10.82 | 2551.4846 | 1246.9853 | 1304.4993
2016-09-09 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-09 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-09 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-09 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-09 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-09 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-09 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-09 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-09 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-09 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-09 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-10 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-10 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-10 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-10 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-10 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-10 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-10 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-10 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-10 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-10 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-10 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-10 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-10 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-10 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-10 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-10 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-10 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-10 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-10 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-10 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-10 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-09-10 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-10 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-10 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.42% | 1195.562 | 1290.2149 | 2485.7769 | 19.4757 | 0.48208 | 0.51792 | 1.0627 | 18.3271 | 2504.104 | 1204.3972 | 1299.7068
2016-09-11 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-11 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-11 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-11 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-11 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-11 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-11 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-11 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-11 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-11 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-11 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-11 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-11 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-11 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-11 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-11 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-11 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-11 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-11 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-11 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-11 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-09-11 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-11 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-11 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.42% | 1195.562 | 1290.2149 | 2485.7769 | 19.4757 | 0.48208 | 0.51792 | 1.0627 | 18.3271 | 2504.104 | 1204.3972 | 1299.7068
2016-09-12 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-12 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-12 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-12 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-12 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-12 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-12 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-12 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-12 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-12 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-12 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.05% | 1215.8476 | 1264.1524 | 2480 | 0 | 0.49026 | 0.50974 | 1 | 0 | 2480 | 1215.8476 | 1264.1524
2016-09-12 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-12 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-12 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-12 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-12 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-12 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-12 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-12 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-12 19:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-12 20:00 | 1 | 2140 | 1240 | 1240 | 2140 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-09-12 21:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.11% | 1204.2147 | 1275.7853 | 2480 | 0 | 0.48557 | 0.51443 | 1 | 0 | 2480 | 1204.2147 | 1275.7853
2016-09-12 22:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.78% | 1212.5153 | 1267.4847 | 2480 | 0 | 0.48892 | 0.51108 | 1 | 0 | 2480 | 1212.5153 | 1267.4847
2016-09-12 23:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.42% | 1223.7453 | 1318.3551 | 2542.1004 | 11.985 | 0.48208 | 0.51792 | 1.0386 | 11.54 | 2553.6403 | 1229.3085 | 1324.3319
2016-09-13 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-13 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-13 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-13 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-13 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-13 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-13 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-13 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.01% | 1215.3143 | 1267.8949 | 2483.2091 | 20.1797 | 0.49005 | 0.50995 | 1.0637 | 18.9711 | 2502.1802 | 1224.611 | 1277.5693
2016-09-13 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.1574 | 1270.3321 | 2483.4895 | 18.6228 | 0.48918 | 0.51082 | 1.0636 | 17.5093 | 2500.9988 | 1221.7226 | 1279.2762
2016-09-13 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-13 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-13 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-13 12:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-13 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-13 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-13 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-13 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-13 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-13 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-13 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-13 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-09-13 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-13 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-13 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-14 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-14 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-14 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-14 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-14 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-14 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-14 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-14 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-14 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-14 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-14 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-14 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-14 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-14 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-14 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-14 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-14 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-14 17:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-14 18:00 | 1 | 2140 | 1240 | 1240 | 2140 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-14 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-14 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-14 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-14 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-14 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-15 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-15 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-15 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-15 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-15 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-15 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-15 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-15 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-15 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-15 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-15 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-15 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-15 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-15 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-15 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-15 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-15 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-15 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-15 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-15 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-15 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-15 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-15 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-15 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-16 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-16 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-16 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-16 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-16 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-16 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-16 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-16 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-16 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-16 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-16 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-16 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-16 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-16 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-16 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-16 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-16 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-16 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-16 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-16 19:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-16 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-16 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-16 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-16 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-17 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-17 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-17 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-17 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-17 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-17 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-17 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-17 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.01% | 1215.3143 | 1267.8949 | 2483.2091 | 20.1797 | 0.49005 | 0.50995 | 1.0637 | 18.9711 | 2502.1802 | 1224.611 | 1277.5693
2016-09-17 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.1574 | 1270.3321 | 2483.4895 | 18.6228 | 0.48918 | 0.51082 | 1.0636 | 17.5093 | 2500.9988 | 1221.7226 | 1279.2762
2016-09-17 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8156 | 1295.5991 | 2540.4147 | 11.4192 | 0.49038 | 0.50962 | 1.0392 | 10.9881 | 2551.4028 | 1250.204 | 1301.1989
2016-09-17 10:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.05% | 1215.8476 | 1264.1524 | 2480 | 0 | 0.49026 | 0.50974 | 1 | 0 | 2480 | 1215.8476 | 1264.1524
2016-09-17 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-17 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-17 13:00 | 1 | 2140 | 1240 | 1240 | 2140 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-17 14:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-17 15:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-17 16:00 | 1 | 2140 | 1240 | 1240 | 2140 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-17 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-17 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-17 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-17 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-17 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-17 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-17 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-18 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-18 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-18 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-18 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-18 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-18 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-18 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-18 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-18 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-18 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-18 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-18 11:00 | 1 | 2280 | 1240 | 1240 | 2280 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-18 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-18 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-18 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-18 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-18 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-18 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-18 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-18 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-18 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-18 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-18 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-18 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-19 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-19 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-19 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-19 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-19 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-19 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-19 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-19 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-19 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-19 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-19 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-19 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-19 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-19 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-19 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-19 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-19 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-19 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-19 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.08% | 1232.1283 | 1309.3014 | 2541.4297 | 12.1729 | 0.48538 | 0.51462 | 1.0388 | 11.7179 | 2553.1476 | 1237.816 | 1315.3316
2016-09-19 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-19 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-19 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-19 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-19 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-20 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-20 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-20 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-20 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-20 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-20 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-20 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-20 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-20 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-20 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-20 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.05% | 1215.8476 | 1267.2922 | 2483.1398 | 18.1912 | 0.49026 | 0.50974 | 1.0637 | 17.1013 | 2500.2411 | 1224.2317 | 1276.0094
2016-09-20 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-20 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6927 | 1298.9719 | 2540.6646 | 11.2434 | 0.48915 | 0.51085 | 1.0391 | 10.82 | 2551.4846 | 1246.9853 | 1304.4993
2016-09-20 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-20 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-20 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-20 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-20 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-20 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-20 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-20 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-20 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-20 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-20 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-21 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-21 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-21 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-21 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-21 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-21 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-21 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-21 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-21 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-21 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-21 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-21 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.26% | 1327.6455 | 1380.4432 | 2708.0886 | 35.2504 | 0.49132 | 0.50868 | 1.1228 | 31.3942 | 2739.4829 | 1343.07 | 1396.4129
2016-09-21 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.0961 | 1270.4014 | 2483.4975 | 18.2706 | 0.48915 | 0.51085 | 1.0636 | 17.1782 | 2500.6757 | 1221.4989 | 1279.1769
2016-09-21 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.32% | 1222.5015 | 1319.6983 | 2542.1999 | 12.1723 | 0.48159 | 0.51841 | 1.0385 | 11.7207 | 2553.9206 | 1228.1461 | 1325.7745
2016-09-21 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.47% | 1211.7711 | 1331.2872 | 2543.0583 | 12.3039 | 0.47736 | 0.52264 | 1.0382 | 11.8513 | 2554.9096 | 1217.4285 | 1337.4811
2016-09-21 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.47% | 1211.7113 | 1331.3518 | 2543.0631 | 12.2016 | 0.47734 | 0.52266 | 1.0382 | 11.7528 | 2554.8159 | 1217.3214 | 1337.4945
2016-09-21 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.82% | 1216.1494 | 1326.5586 | 2542.708 | 11.9418 | 0.47909 | 0.52091 | 1.0383 | 11.501 | 2554.2091 | 1221.6594 | 1332.5497
2016-09-21 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.39% | 1223.3918 | 1318.7369 | 2542.1287 | 13.0649 | 0.48194 | 0.51806 | 1.0386 | 12.5799 | 2554.7086 | 1229.4545 | 1325.254
2016-09-21 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.08% | 1203.752 | 1280.9602 | 2484.7122 | 19.7809 | 0.48538 | 0.51462 | 1.0631 | 18.6068 | 2503.3191 | 1212.7835 | 1290.5356
2016-09-21 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.17% | 1326.3437 | 1382.0704 | 2708.4141 | 38.0949 | 0.49083 | 0.50917 | 1.1227 | 33.9312 | 2742.3453 | 1342.9983 | 1399.347
2016-09-21 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.03% | 1324.4377 | 1384.4528 | 2708.8906 | 40.4476 | 0.49013 | 0.50987 | 1.1225 | 36.0324 | 2744.923 | 1342.0983 | 1402.8247
2016-09-21 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.929 | 1398.3923 | 2707.3213 | 45.9378 | 0.48557 | 0.51443 | 1.1457 | 40.0969 | 2747.4182 | 1328.3988 | 1419.0193
2016-09-21 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-21 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.42% | 1353.8455 | 1474.6164 | 2828.4618 | 59.9251 | 0.48208 | 0.51792 | 1.1928 | 50.2377 | 2878.6995 | 1378.0641 | 1500.6354
2016-09-22 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.06% | 1292.6508 | 1560.2889 | 2852.9397 | 43.5659 | 0.46029 | 0.53971 | 1.1841 | 36.7919 | 2889.7316 | 1309.5858 | 1580.1458
2016-09-22 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.44% | 1283.9627 | 1572.4523 | 2856.4149 | 48.688 | 0.4572 | 0.5428 | 1.1829 | 41.1606 | 2897.5755 | 1302.7812 | 1594.7943
2016-09-22 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-22 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-22 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-22 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-22 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-22 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-22 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-22 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-22 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.05% | 1321.5735 | 1381.9545 | 2703.528 | 41.9797 | 0.49026 | 0.50974 | 1.1471 | 36.597 | 2740.125 | 1339.5156 | 1400.6094
2016-09-22 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.26% | 1324.4175 | 1378.2573 | 2702.6748 | 42.3005 | 0.49132 | 0.50868 | 1.1474 | 36.8665 | 2739.5413 | 1342.5306 | 1397.0107
2016-09-22 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5827 | 1385.8424 | 2704.4252 | 42.1629 | 0.48915 | 0.51085 | 1.1467 | 36.7675 | 2741.1926 | 1336.5676 | 1404.625
2016-09-22 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.32% | 1298.2032 | 1412.3358 | 2710.539 | 45.6462 | 0.48159 | 0.51841 | 1.1445 | 39.8839 | 2750.4229 | 1317.4109 | 1433.012
2016-09-22 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.9446 | 1427.5692 | 2717.5138 | 38.4496 | 0.47736 | 0.52264 | 1.1193 | 34.3502 | 2751.864 | 1306.3422 | 1445.5218
2016-09-22 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.881 | 1427.6488 | 2717.5298 | 38.1301 | 0.47734 | 0.52266 | 1.1193 | 34.0649 | 2751.5947 | 1306.1416 | 1445.4531
2016-09-22 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.82% | 1294.6054 | 1421.7433 | 2716.3487 | 37.3182 | 0.47909 | 0.52091 | 1.1198 | 33.3266 | 2749.6753 | 1310.5718 | 1439.1035
2016-09-22 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.39% | 1302.3149 | 1412.1063 | 2714.4213 | 40.8279 | 0.48194 | 0.51806 | 1.1205 | 36.4377 | 2750.859 | 1319.8758 | 1430.9831
2016-09-22 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.08% | 1311.6151 | 1400.4811 | 2712.0962 | 38.0402 | 0.48538 | 0.51462 | 1.1213 | 33.9237 | 2746.02 | 1328.0812 | 1417.9388
2016-09-22 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.17% | 1326.3437 | 1382.0704 | 2708.4141 | 38.0949 | 0.49083 | 0.50917 | 1.1227 | 33.9312 | 2742.3453 | 1342.9983 | 1399.347
2016-09-22 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.03% | 1324.4377 | 1384.4528 | 2708.8906 | 40.4476 | 0.49013 | 0.50987 | 1.1225 | 36.0324 | 2744.923 | 1342.0983 | 1402.8247
2016-09-22 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.11% | 1308.929 | 1398.3923 | 2707.3213 | 45.9378 | 0.48557 | 0.51443 | 1.1457 | 40.0969 | 2747.4182 | 1328.3988 | 1419.0193
2016-09-22 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.78% | 1373.0432 | 1447.7395 | 2820.7827 | 67.9214 | 0.48892 | 0.51108 | 1.1956 | 56.811 | 2877.5937 | 1400.8191 | 1476.7746
2016-09-22 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.42% | 1353.8455 | 1474.6164 | 2828.4618 | 59.9251 | 0.48208 | 0.51792 | 1.1928 | 50.2377 | 2878.6995 | 1378.0641 | 1500.6354
2016-09-23 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.06% | 1380.8732 | 1678.6901 | 3059.5634 | 54.4573 | 0.46029 | 0.53971 | 1.2301 | 44.269 | 3103.8324 | 1401.2499 | 1702.5825
2016-09-23 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.44% | 1371.5922 | 1692.6118 | 3064.2039 | 60.8599 | 0.4572 | 0.5428 | 1.2286 | 49.5361 | 3113.74 | 1394.2399 | 1719.5001
2016-09-23 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.01% | 1365.0855 | 1702.3718 | 3067.4573 | 57.6313 | 0.45503 | 0.54497 | 1.2275 | 46.9496 | 3114.4068 | 1386.4489 | 1727.958
2016-09-23 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 91.22% | 1368.2379 | 1697.6431 | 3065.881 | 60.8263 | 0.45608 | 0.54392 | 1.228 | 49.5312 | 3115.4122 | 1390.8281 | 1724.5841
2016-09-23 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 92.75% | 1391.2678 | 1663.0984 | 3054.3661 | 65.3411 | 0.46376 | 0.53624 | 1.2319 | 53.0419 | 3107.408 | 1415.8662 | 1691.5418
2016-09-23 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.08% | 1471.2307 | 1543.1539 | 3014.3846 | 69.6356 | 0.49041 | 0.50959 | 1.2452 | 55.923 | 3070.3076 | 1498.6559 | 1571.6517
2016-09-23 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.06% | 1376.9465 | 1442.2749 | 2819.2214 | 60.9441 | 0.49031 | 0.50969 | 1.1961 | 50.9514 | 2870.1728 | 1401.9283 | 1468.2445
2016-09-23 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.01% | 1376.2127 | 1443.3022 | 2819.5149 | 62.0913 | 0.49005 | 0.50995 | 1.196 | 51.915 | 2871.4299 | 1401.6534 | 1469.7764
2016-09-23 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.84% | 1373.7704 | 1446.7215 | 2820.4919 | 57.3008 | 0.48918 | 0.51082 | 1.1957 | 47.9235 | 2868.4154 | 1397.2134 | 1471.202
2016-09-23 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.1559 | 1441.9818 | 2819.1377 | 57.0958 | 0.49038 | 0.50962 | 1.1962 | 47.7328 | 2866.8705 | 1400.5632 | 1466.3073
2016-09-23 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.05% | 1376.8167 | 1442.4566 | 2819.2733 | 55.9729 | 0.49026 | 0.50974 | 1.1961 | 46.796 | 2866.0693 | 1399.7589 | 1466.3104
2016-09-23 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.26% | 1324.4175 | 1378.2573 | 2702.6748 | 42.3005 | 0.49132 | 0.50868 | 1.1474 | 36.8665 | 2739.5413 | 1342.5306 | 1397.0107
2016-09-23 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.83% | 1318.5827 | 1385.8424 | 2704.4252 | 42.1629 | 0.48915 | 0.51085 | 1.1467 | 36.7675 | 2741.1926 | 1336.5676 | 1404.625
2016-09-23 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3673 | 1413.2909 | 2714.6582 | 38.0385 | 0.48159 | 0.51841 | 1.1204 | 33.9509 | 2748.609 | 1317.7177 | 1430.8913
2016-09-23 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.9446 | 1427.5692 | 2717.5138 | 38.4496 | 0.47736 | 0.52264 | 1.1193 | 34.3502 | 2751.864 | 1306.3422 | 1445.5218
2016-09-23 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8052 | 1303.5001 | 2487.3053 | 19.8276 | 0.47734 | 0.52266 | 1.0621 | 18.6691 | 2505.9745 | 1192.7168 | 1313.2577
2016-09-23 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.82% | 1216.1494 | 1326.5586 | 2542.708 | 11.9418 | 0.47909 | 0.52091 | 1.0383 | 11.501 | 2554.2091 | 1221.6594 | 1332.5497
2016-09-23 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.39% | 1223.3918 | 1318.7369 | 2542.1287 | 13.0649 | 0.48194 | 0.51806 | 1.0386 | 12.5799 | 2554.7086 | 1229.4545 | 1325.254
2016-09-23 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.08% | 1232.1283 | 1309.3014 | 2541.4297 | 12.1729 | 0.48538 | 0.51462 | 1.0388 | 11.7179 | 2553.1476 | 1237.816 | 1315.3316
2016-09-23 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.17% | 1217.2694 | 1265.6856 | 2482.955 | 19.8093 | 0.49083 | 0.50917 | 1.0638 | 18.6212 | 2501.5761 | 1226.4093 | 1275.1668
2016-09-23 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-23 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-23 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-23 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-24 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-24 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-24 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-24 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-24 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-24 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-24 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-24 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.01% | 1215.3143 | 1267.8949 | 2483.2091 | 20.1797 | 0.49005 | 0.50995 | 1.0637 | 18.9711 | 2502.1802 | 1224.611 | 1277.5693
2016-09-24 08:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.84% | 1213.1574 | 1270.3321 | 2483.4895 | 18.6228 | 0.48918 | 0.51082 | 1.0636 | 17.5093 | 2500.9988 | 1221.7226 | 1279.2762
2016-09-24 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.08% | 1244.8156 | 1295.5991 | 2540.4147 | 11.4192 | 0.49038 | 0.50962 | 1.0392 | 10.9881 | 2551.4028 | 1250.204 | 1301.1989
2016-09-24 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-24 11:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.26% | 1218.4641 | 1261.5359 | 2480 | 0 | 0.49132 | 0.50868 | 1 | 0 | 2480 | 1218.4641 | 1261.5359
2016-09-24 12:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-24 13:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-24 14:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-24 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-24 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-24 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-24 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-24 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-24 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-24 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-24 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-24 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.42% | 1302.6913 | 1411.6359 | 2714.3272 | 37.4532 | 0.48208 | 0.51792 | 1.1205 | 33.4248 | 2747.752 | 1318.8047 | 1428.9473
2016-09-25 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-25 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.44% | 1235.4489 | 1495.6888 | 2731.1378 | 30.43 | 0.4572 | 0.5428 | 1.1143 | 27.3086 | 2758.4464 | 1247.9344 | 1510.512
2016-09-25 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.01% | 1229.5881 | 1503.0149 | 2732.603 | 28.8156 | 0.45503 | 0.54497 | 1.1138 | 25.8725 | 2758.4754 | 1241.3608 | 1517.1146
2016-09-25 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 91.22% | 1232.4277 | 1499.4654 | 2731.8931 | 30.4131 | 0.45608 | 0.54392 | 1.114 | 27.3004 | 2759.1934 | 1244.8788 | 1514.3147
2016-09-25 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.75% | 1253.1715 | 1473.5356 | 2726.7071 | 32.6706 | 0.46376 | 0.53624 | 1.1159 | 29.2763 | 2755.9834 | 1266.7486 | 1489.2348
2016-09-25 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1975 | 1383.5032 | 2708.7006 | 34.8178 | 0.49041 | 0.50959 | 1.1226 | 31.0152 | 2739.7159 | 1340.4076 | 1399.3082
2016-09-25 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.06% | 1324.9194 | 1383.8507 | 2708.7701 | 38.0901 | 0.49031 | 0.50969 | 1.1226 | 33.9309 | 2742.7011 | 1341.556 | 1401.1451
2016-09-25 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.01% | 1324.2134 | 1384.7333 | 2708.9467 | 38.807 | 0.49005 | 0.50995 | 1.1225 | 34.5716 | 2743.5183 | 1341.1551 | 1402.3632
2016-09-25 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.84% | 1321.8633 | 1387.6709 | 2709.5342 | 35.813 | 0.48918 | 0.51082 | 1.1223 | 31.9105 | 2741.4447 | 1337.4732 | 1403.9715
2016-09-25 09:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.08% | 1216.1471 | 1266.9537 | 2483.1009 | 18.5561 | 0.49038 | 0.50962 | 1.0637 | 17.4441 | 2500.5449 | 1224.7014 | 1275.8435
2016-09-25 10:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.05% | 1244.509 | 1295.9302 | 2540.4393 | 11.1946 | 0.49026 | 0.50974 | 1.0392 | 10.7721 | 2551.2114 | 1249.7902 | 1301.4212
2016-09-25 11:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.26% | 1247.1872 | 1293.0378 | 2540.225 | 11.2801 | 0.49132 | 0.50868 | 1.0393 | 10.8535 | 2551.0785 | 1252.5197 | 1298.5589
2016-09-25 12:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.83% | 1213.0961 | 1266.9039 | 2480 | 0 | 0.48915 | 0.51085 | 1 | 0 | 2480 | 1213.0961 | 1266.9039
2016-09-25 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-25 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-25 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-25 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-25 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-25 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.08% | 1232.1283 | 1309.3014 | 2541.4297 | 12.1729 | 0.48538 | 0.51462 | 1.0388 | 11.7179 | 2553.1476 | 1237.816 | 1315.3316
2016-09-25 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.17% | 1245.9643 | 1294.3585 | 2540.3229 | 12.1904 | 0.49083 | 0.50917 | 1.0393 | 11.7298 | 2552.0526 | 1251.7217 | 1300.3309
2016-09-25 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-25 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-25 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.78% | 1212.5153 | 1271.0577 | 2483.573 | 22.0744 | 0.48892 | 0.51108 | 1.0636 | 20.7553 | 2504.3283 | 1222.6629 | 1281.6653
2016-09-25 23:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.42% | 1195.562 | 1290.2149 | 2485.7769 | 19.4757 | 0.48208 | 0.51792 | 1.0627 | 18.3271 | 2504.104 | 1204.3972 | 1299.7068
2016-09-26 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 92.06% | 1243.8088 | 1485.239 | 2729.0478 | 27.2287 | 0.46029 | 0.53971 | 1.1151 | 24.4187 | 2753.4665 | 1255.0485 | 1498.418
2016-09-26 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-26 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.01% | 1226.5985 | 1505.4219 | 2732.0204 | 34.5788 | 0.45503 | 0.54497 | 1.1365 | 30.4254 | 2762.4459 | 1240.443 | 1522.0029
2016-09-26 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.22% | 1229.4312 | 1501.7394 | 2731.1706 | 36.4958 | 0.45608 | 0.54392 | 1.1368 | 32.1033 | 2763.2739 | 1244.0728 | 1519.2011
2016-09-26 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.75% | 1250.1246 | 1474.838 | 2724.9626 | 39.2047 | 0.46376 | 0.53624 | 1.1391 | 34.4164 | 2759.379 | 1266.0855 | 1493.2936
2016-09-26 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.9754 | 1381.4319 | 2703.4074 | 41.7813 | 0.49041 | 0.50959 | 1.1471 | 36.4227 | 2739.8301 | 1339.8375 | 1399.9926
2016-09-26 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-26 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-26 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-26 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-26 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.05% | 1321.5735 | 1381.9545 | 2703.528 | 41.9797 | 0.49026 | 0.50974 | 1.1471 | 36.597 | 2740.125 | 1339.5156 | 1400.6094
2016-09-26 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.26% | 1324.4175 | 1378.2573 | 2702.6748 | 42.3005 | 0.49132 | 0.50868 | 1.1474 | 36.8665 | 2739.5413 | 1342.5306 | 1397.0107
2016-09-26 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7965 | 1387.7544 | 2709.5509 | 35.1358 | 0.48915 | 0.51085 | 1.1223 | 31.3073 | 2740.8581 | 1337.1105 | 1403.7477
2016-09-26 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.32% | 1301.3673 | 1413.2909 | 2714.6582 | 38.0385 | 0.48159 | 0.51841 | 1.1204 | 33.9509 | 2748.609 | 1317.7177 | 1430.8913
2016-09-26 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.9446 | 1427.5692 | 2717.5138 | 38.4496 | 0.47736 | 0.52264 | 1.1193 | 34.3502 | 2751.864 | 1306.3422 | 1445.5218
2016-09-26 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.881 | 1427.6488 | 2717.5298 | 38.1301 | 0.47734 | 0.52266 | 1.1193 | 34.0649 | 2751.5947 | 1306.1416 | 1445.4531
2016-09-26 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.82% | 1294.6054 | 1421.7433 | 2716.3487 | 37.3182 | 0.47909 | 0.52091 | 1.1198 | 33.3266 | 2749.6753 | 1310.5718 | 1439.1035
2016-09-26 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.39% | 1302.3149 | 1412.1063 | 2714.4213 | 40.8279 | 0.48194 | 0.51806 | 1.1205 | 36.4377 | 2750.859 | 1319.8758 | 1430.9831
2016-09-26 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.08% | 1203.752 | 1280.9602 | 2484.7122 | 19.7809 | 0.48538 | 0.51462 | 1.0631 | 18.6068 | 2503.3191 | 1212.7835 | 1290.5356
2016-09-26 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.17% | 1217.2694 | 1265.6856 | 2482.955 | 19.8093 | 0.49083 | 0.50917 | 1.0638 | 18.6212 | 2501.5761 | 1226.4093 | 1275.1668
2016-09-26 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-26 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-26 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-26 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-27 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 92.06% | 1240.7846 | 1486.98 | 2727.7646 | 32.6744 | 0.46029 | 0.53971 | 1.1381 | 28.7099 | 2756.4745 | 1253.9996 | 1502.475
2016-09-27 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 91.44% | 1232.4451 | 1497.8213 | 2730.2665 | 36.516 | 0.4572 | 0.5428 | 1.1372 | 32.1116 | 2762.378 | 1247.1264 | 1515.2516
2016-09-27 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-27 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-27 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-27 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-27 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.06% | 1376.9465 | 1442.2749 | 2819.2214 | 60.9441 | 0.49031 | 0.50969 | 1.1961 | 50.9514 | 2870.1728 | 1401.9283 | 1468.2445
2016-09-27 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-27 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-27 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-27 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-27 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.26% | 1327.6455 | 1380.4432 | 2708.0886 | 35.2504 | 0.49132 | 0.50868 | 1.1228 | 31.3942 | 2739.4829 | 1343.07 | 1396.4129
2016-09-27 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.83% | 1321.7965 | 1387.7544 | 2709.5509 | 35.1358 | 0.48915 | 0.51085 | 1.1223 | 31.3073 | 2740.8581 | 1337.1105 | 1403.7477
2016-09-27 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3469 | 1291.5879 | 2485.9349 | 19.78 | 0.48159 | 0.51841 | 1.0626 | 18.6146 | 2504.5495 | 1203.3116 | 1301.2379
2016-09-27 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8637 | 1303.4341 | 2487.2977 | 19.9938 | 0.47736 | 0.52264 | 1.0621 | 18.8255 | 2506.1232 | 1192.8503 | 1313.273
2016-09-27 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.47% | 1211.7113 | 1331.3518 | 2543.0631 | 12.2016 | 0.47734 | 0.52266 | 1.0382 | 11.7528 | 2554.8159 | 1217.3214 | 1337.4945
2016-09-27 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.82% | 1216.1494 | 1326.5586 | 2542.708 | 11.9418 | 0.47909 | 0.52091 | 1.0383 | 11.501 | 2554.2091 | 1221.6594 | 1332.5497
2016-09-27 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 96.39% | 1223.3918 | 1318.7369 | 2542.1287 | 13.0649 | 0.48194 | 0.51806 | 1.0386 | 12.5799 | 2554.7086 | 1229.4545 | 1325.254
2016-09-27 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.08% | 1232.1283 | 1309.3014 | 2541.4297 | 12.1729 | 0.48538 | 0.51462 | 1.0388 | 11.7179 | 2553.1476 | 1237.816 | 1315.3316
2016-09-27 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.17% | 1217.2694 | 1265.6856 | 2482.955 | 19.8093 | 0.49083 | 0.50917 | 1.0638 | 18.6212 | 2501.5761 | 1226.4093 | 1275.1668
2016-09-27 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.03% | 1215.5202 | 1267.6622 | 2483.1824 | 21.0327 | 0.49013 | 0.50987 | 1.0637 | 19.7729 | 2502.9553 | 1225.2114 | 1277.7438
2016-09-27 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.11% | 1312.1192 | 1399.851 | 2711.9702 | 38.2815 | 0.48557 | 0.51443 | 1.1214 | 34.1375 | 2746.1077 | 1328.6953 | 1417.4123
2016-09-27 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-27 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.42% | 1353.8455 | 1474.6164 | 2828.4618 | 59.9251 | 0.48208 | 0.51792 | 1.1928 | 50.2377 | 2878.6995 | 1378.0641 | 1500.6354
2016-09-28 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.06% | 1292.6508 | 1560.2889 | 2852.9397 | 43.5659 | 0.46029 | 0.53971 | 1.1841 | 36.7919 | 2889.7316 | 1309.5858 | 1580.1458
2016-09-28 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.44% | 1283.9627 | 1572.4523 | 2856.4149 | 48.688 | 0.4572 | 0.5428 | 1.1829 | 41.1606 | 2897.5755 | 1302.7812 | 1594.7943
2016-09-28 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-28 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-28 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-28 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-28 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.06% | 1376.9465 | 1442.2749 | 2819.2214 | 60.9441 | 0.49031 | 0.50969 | 1.1961 | 50.9514 | 2870.1728 | 1401.9283 | 1468.2445
2016-09-28 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.01% | 1376.2127 | 1443.3022 | 2819.5149 | 62.0913 | 0.49005 | 0.50995 | 1.196 | 51.915 | 2871.4299 | 1401.6534 | 1469.7764
2016-09-28 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.84% | 1373.7704 | 1446.7215 | 2820.4919 | 57.3008 | 0.48918 | 0.51082 | 1.1957 | 47.9235 | 2868.4154 | 1397.2134 | 1471.202
2016-09-28 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.08% | 1321.8991 | 1381.5312 | 2703.4303 | 42.8218 | 0.49038 | 0.50962 | 1.1471 | 37.33 | 2740.7603 | 1340.205 | 1400.5553
2016-09-28 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-28 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.26% | 1327.6455 | 1380.4432 | 2708.0886 | 35.2504 | 0.49132 | 0.50868 | 1.1228 | 31.3942 | 2739.4829 | 1343.07 | 1396.4129
2016-09-28 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.83% | 1213.0961 | 1270.4014 | 2483.4975 | 18.2706 | 0.48915 | 0.51085 | 1.0636 | 17.1782 | 2500.6757 | 1221.4989 | 1279.1769
2016-09-28 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.32% | 1194.3469 | 1291.5879 | 2485.9349 | 19.78 | 0.48159 | 0.51841 | 1.0626 | 18.6146 | 2504.5495 | 1203.3116 | 1301.2379
2016-09-28 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 95.47% | 1211.7711 | 1331.2872 | 2543.0583 | 12.3039 | 0.47736 | 0.52264 | 1.0382 | 11.8513 | 2554.9096 | 1217.4285 | 1337.4811
2016-09-28 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-28 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-28 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-28 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-28 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-28 20:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.03% | 1215.5202 | 1264.4798 | 2480 | 0 | 0.49013 | 0.50987 | 1 | 0 | 2480 | 1215.5202 | 1264.4798
2016-09-28 21:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.11% | 1232.6019 | 1308.79 | 2541.3919 | 12.2501 | 0.48557 | 0.51443 | 1.0388 | 11.792 | 2553.1839 | 1238.3277 | 1314.8562
2016-09-28 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.78% | 1321.1637 | 1388.5454 | 2709.7091 | 42.4509 | 0.48892 | 0.51108 | 1.1222 | 37.8273 | 2747.5363 | 1339.6581 | 1407.8783
2016-09-28 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.42% | 1299.524 | 1410.6189 | 2710.1428 | 44.9438 | 0.48208 | 0.51792 | 1.1446 | 39.2651 | 2749.408 | 1318.4529 | 1430.955
2016-09-29 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.06% | 1292.6508 | 1560.2889 | 2852.9397 | 43.5659 | 0.46029 | 0.53971 | 1.1841 | 36.7919 | 2889.7316 | 1309.5858 | 1580.1458
2016-09-29 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.44% | 1283.9627 | 1572.4523 | 2856.4149 | 48.688 | 0.4572 | 0.5428 | 1.1829 | 41.1606 | 2897.5755 | 1302.7812 | 1594.7943
2016-09-29 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.01% | 1277.8717 | 1580.9797 | 2858.8513 | 46.105 | 0.45503 | 0.54497 | 1.182 | 39.0056 | 2897.8569 | 1295.6203 | 1602.2366
2016-09-29 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 91.22% | 1280.8227 | 1576.8482 | 2857.6709 | 48.661 | 0.45608 | 0.54392 | 1.1824 | 41.1533 | 2898.8243 | 1299.5919 | 1599.2323
2016-09-29 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 92.75% | 1302.3812 | 1546.6663 | 2849.0475 | 52.2729 | 0.46376 | 0.53624 | 1.1855 | 44.0935 | 2893.141 | 1322.8298 | 1570.3112
2016-09-29 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.08% | 1377.2354 | 1441.8704 | 2819.1058 | 55.7084 | 0.49041 | 0.50959 | 1.1962 | 46.5726 | 2865.6784 | 1400.0751 | 1465.6033
2016-09-29 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.06% | 1321.6981 | 1381.7925 | 2703.4906 | 45.7081 | 0.49031 | 0.50969 | 1.1471 | 39.8469 | 2743.3375 | 1341.2353 | 1402.1022
2016-09-29 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.01% | 1320.9938 | 1382.7081 | 2703.7019 | 46.5684 | 0.49005 | 0.50995 | 1.147 | 40.5997 | 2744.3016 | 1340.8895 | 1403.4121
2016-09-29 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.84% | 1318.6494 | 1385.7558 | 2704.4052 | 42.9756 | 0.48918 | 0.51082 | 1.1468 | 37.4759 | 2741.8811 | 1336.9817 | 1404.8993
2016-09-29 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.08% | 1325.1209 | 1383.5989 | 2708.7198 | 35.6849 | 0.49038 | 0.50962 | 1.1226 | 31.7878 | 2740.5076 | 1340.7091 | 1399.7985
2016-09-29 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.05% | 1324.7945 | 1384.0068 | 2708.8014 | 34.9831 | 0.49026 | 0.50974 | 1.1226 | 31.1635 | 2739.9649 | 1340.0728 | 1399.8921
2016-09-29 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.26% | 1218.4641 | 1264.3356 | 2482.7997 | 18.3302 | 0.49132 | 0.50868 | 1.0639 | 17.2297 | 2500.0294 | 1226.9293 | 1273.1001
2016-09-29 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 97.83% | 1241.6927 | 1298.9719 | 2540.6646 | 11.2434 | 0.48915 | 0.51085 | 1.0391 | 10.82 | 2551.4846 | 1246.9853 | 1304.4993
2016-09-29 13:00 | 1 | 2240 | 1240 | 1240 | 2240 | 96.32% | 1194.3469 | 1285.6531 | 2480 | 0 | 0.48159 | 0.51841 | 1 | 0 | 2480 | 1194.3469 | 1285.6531
2016-09-29 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 95.47% | 1183.8637 | 1296.1363 | 2480 | 0 | 0.47736 | 0.52264 | 1 | 0 | 2480 | 1183.8637 | 1296.1363
2016-09-29 15:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.47% | 1183.8052 | 1296.1948 | 2480 | 0 | 0.47734 | 0.52266 | 1 | 0 | 2480 | 1183.8052 | 1296.1948
2016-09-29 16:00 | 1 | 2280 | 1240 | 1240 | 2280 | 95.82% | 1188.1411 | 1291.8589 | 2480 | 0 | 0.47909 | 0.52091 | 1 | 0 | 2480 | 1188.1411 | 1291.8589
2016-09-29 17:00 | 1 | 2280 | 1240 | 1240 | 2280 | 96.39% | 1195.2167 | 1284.7833 | 2480 | 0 | 0.48194 | 0.51806 | 1 | 0 | 2480 | 1195.2167 | 1284.7833
2016-09-29 18:00 | 1 | 2280 | 1240 | 1240 | 2280 | 97.08% | 1203.752 | 1276.248 | 2480 | 0 | 0.48538 | 0.51462 | 1 | 0 | 2480 | 1203.752 | 1276.248
2016-09-29 19:00 | 1 | 2240 | 1240 | 1240 | 2240 | 98.17% | 1217.2694 | 1262.7306 | 2480 | 0 | 0.49083 | 0.50917 | 1 | 0 | 2480 | 1217.2694 | 1262.7306
2016-09-29 20:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.03% | 1244.1739 | 1296.2922 | 2540.4661 | 12.9432 | 0.49013 | 0.50987 | 1.0392 | 12.4549 | 2552.921 | 1250.2783 | 1302.6426
2016-09-29 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 97.11% | 1204.2147 | 1280.4374 | 2484.6521 | 19.9064 | 0.48557 | 0.51443 | 1.0631 | 18.7244 | 2503.3765 | 1213.3067 | 1290.0698
2016-09-29 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.78% | 1317.9514 | 1386.6631 | 2704.6146 | 50.941 | 0.48892 | 0.51108 | 1.1467 | 44.425 | 2749.0395 | 1339.6716 | 1409.368
2016-09-29 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 59.9251 | 0.43552 | 0.56448 | 1.1742 | 51.0345 | 2931.8013 | 1245.3095 | 1686.4918
2016-09-30 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-09-30 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-09-30 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-09-30 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-09-30 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-09-30 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-09-30 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.12% | 1187.6564 | 1556.0466 | 2743.7031 | 42.9472 | 0.44058 | 0.55942 | 1.1322 | 37.9334 | 2781.6364 | 1204.3692 | 1577.2672
2016-09-30 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-09-30 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-09-30 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.78% | 1185.9436 | 1557.5705 | 2743.5141 | 35.2868 | 0.43888 | 0.56112 | 1.1097 | 31.7979 | 2775.312 | 1199.899 | 1575.413
2016-09-30 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-09-30 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-09-30 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-09-30 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.43% | 1109.6825 | 1441.5429 | 2551.2254 | 11.2823 | 0.43715 | 0.56285 | 1.035 | 10.901 | 2562.1264 | 1114.4479 | 1447.6786
2016-09-30 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.3% | 1108.006 | 1443.3536 | 2551.3595 | 11.3183 | 0.43649 | 0.56351 | 1.0349 | 10.9364 | 2562.2959 | 1112.7796 | 1449.5164
2016-09-30 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.56% | 1085.8 | 1394.2 | 2480 | 0 | 0.43782 | 0.56218 | 1 | 0 | 2480 | 1085.8 | 1394.2
2016-09-30 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.23% | 1081.6169 | 1398.3831 | 2480 | 0 | 0.43614 | 0.56386 | 1 | 0 | 2480 | 1081.6169 | 1398.3831
2016-09-30 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.34% | 1082.9844 | 1397.0156 | 2480 | 0 | 0.43669 | 0.56331 | 1 | 0 | 2480 | 1082.9844 | 1397.0156
2016-09-30 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.5% | 1085.0038 | 1394.9962 | 2480 | 0 | 0.4375 | 0.5625 | 1 | 0 | 2480 | 1085.0038 | 1394.9962
2016-09-30 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.51% | 1110.736 | 1440.4051 | 2551.1411 | 12.3602 | 0.43756 | 0.56244 | 1.035 | 11.9422 | 2563.0833 | 1115.9615 | 1447.1218
2016-09-30 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 85.87% | 1064.8301 | 1437.942 | 2502.7721 | 22.7383 | 0.42937 | 0.57063 | 1.0558 | 21.5362 | 2524.3082 | 1074.077 | 1450.2313
2016-09-30 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.02% | 1162.1819 | 1587.2726 | 2749.4545 | 43.5495 | 0.43008 | 0.56992 | 1.1075 | 39.3216 | 2788.7761 | 1179.0935 | 1609.6826
2016-09-30 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-09-30 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.1% | 1174.0082 | 1573.7894 | 2747.7975 | 44.1478 | 0.43552 | 0.56448 | 1.1307 | 39.0462 | 2786.8437 | 1191.0135 | 1595.8302
2016-10-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.08% | 1173.6786 | 1574.2179 | 2747.8964 | 36.0832 | 0.4354 | 0.5646 | 1.1306 | 31.9146 | 2779.811 | 1187.5741 | 1592.2369
2016-10-01 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-01 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-01 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-01 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-01 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.12% | 1187.6564 | 1556.0466 | 2743.7031 | 42.9472 | 0.44058 | 0.55942 | 1.1322 | 37.9334 | 2781.6364 | 1204.3692 | 1577.2672
2016-10-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-10-01 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-10-01 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.78% | 1185.9436 | 1557.5705 | 2743.5141 | 35.2868 | 0.43888 | 0.56112 | 1.1097 | 31.7979 | 2775.312 | 1199.899 | 1575.413
2016-10-01 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-01 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.53% | 1085.4226 | 1414.6725 | 2500.0951 | 18.8858 | 0.43767 | 0.56233 | 1.0569 | 17.8691 | 2517.9642 | 1093.2434 | 1424.7208
2016-10-01 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-01 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.43% | 1109.6825 | 1441.5429 | 2551.2254 | 11.2823 | 0.43715 | 0.56285 | 1.035 | 10.901 | 2562.1264 | 1114.4479 | 1447.6786
2016-10-01 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.3% | 1082.4882 | 1397.5118 | 2480 | 0 | 0.43649 | 0.56351 | 1 | 0 | 2480 | 1082.4882 | 1397.5118
2016-10-01 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.56% | 1085.8 | 1394.2 | 2480 | 0 | 0.43782 | 0.56218 | 1 | 0 | 2480 | 1085.8 | 1394.2
2016-10-01 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.23% | 1081.6169 | 1398.3831 | 2480 | 0 | 0.43614 | 0.56386 | 1 | 0 | 2480 | 1081.6169 | 1398.3831
2016-10-01 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.34% | 1082.9844 | 1397.0156 | 2480 | 0 | 0.43669 | 0.56331 | 1 | 0 | 2480 | 1082.9844 | 1397.0156
2016-10-01 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.5% | 1085.0038 | 1394.9962 | 2480 | 0 | 0.4375 | 0.5625 | 1 | 0 | 2480 | 1085.0038 | 1394.9962
2016-10-01 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.51% | 1110.736 | 1440.4051 | 2551.1411 | 12.3602 | 0.43756 | 0.56244 | 1.035 | 11.9422 | 2563.0833 | 1115.9615 | 1447.1218
2016-10-01 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 85.87% | 1064.8301 | 1437.942 | 2502.7721 | 22.7383 | 0.42937 | 0.57063 | 1.0558 | 21.5362 | 2524.3082 | 1074.077 | 1450.2313
2016-10-01 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.02% | 1162.1819 | 1587.2726 | 2749.4545 | 43.5495 | 0.43008 | 0.56992 | 1.1075 | 39.3216 | 2788.7761 | 1179.0935 | 1609.6826
2016-10-01 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-10-01 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.1% | 1174.0082 | 1573.7894 | 2747.7975 | 44.1478 | 0.43552 | 0.56448 | 1.1307 | 39.0462 | 2786.8437 | 1191.0135 | 1595.8302
2016-10-02 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.08% | 1173.6786 | 1574.2179 | 2747.8964 | 36.0832 | 0.4354 | 0.5646 | 1.1306 | 31.9146 | 2779.811 | 1187.5741 | 1592.2369
2016-10-02 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.91% | 1171.4427 | 1577.1245 | 2748.5672 | 36.6928 | 0.43457 | 0.56543 | 1.1304 | 32.4608 | 2781.028 | 1185.5491 | 1595.4789
2016-10-02 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.74% | 1169.0751 | 1580.2024 | 2749.2775 | 36.8657 | 0.43369 | 0.56631 | 1.1301 | 32.6214 | 2781.8989 | 1183.2227 | 1598.6762
2016-10-02 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.87% | 1170.9156 | 1577.8098 | 2748.7253 | 36.7472 | 0.43437 | 0.56563 | 1.1303 | 32.5107 | 2781.236 | 1185.0373 | 1596.1987
2016-10-02 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.27% | 1176.2441 | 1570.8826 | 2747.1268 | 39.2478 | 0.43635 | 0.56365 | 1.1309 | 34.7048 | 2781.8316 | 1191.3875 | 1590.444
2016-10-02 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.1% | 1187.4824 | 1556.2729 | 2743.7553 | 42.8107 | 0.44052 | 0.55948 | 1.1322 | 37.8134 | 2781.5687 | 1204.1399 | 1577.4288
2016-10-02 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.12% | 1187.6564 | 1556.0466 | 2743.7031 | 42.9472 | 0.44058 | 0.55942 | 1.1322 | 37.9334 | 2781.6364 | 1204.3692 | 1577.2672
2016-10-02 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-10-02 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-10-02 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-02 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-02 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-02 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-02 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.43% | 1084.1262 | 1416.1374 | 2500.2636 | 18.3337 | 0.43715 | 0.56285 | 1.0568 | 17.3478 | 2517.6114 | 1091.7097 | 1425.9017
2016-10-02 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-02 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-02 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-02 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-02 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-02 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-02 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-02 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.02% | 1162.1819 | 1587.2726 | 2749.4545 | 43.5495 | 0.43008 | 0.56992 | 1.1075 | 39.3216 | 2788.7761 | 1179.0935 | 1609.6826
2016-10-02 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-10-02 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-03 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-03 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-03 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-03 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-03 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-03 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-03 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-03 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-03 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-03 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-03 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-03 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-03 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-03 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-03 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-03 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-03 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-03 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-03 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-03 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-03 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-03 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-03 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-03 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-04 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-04 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-04 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-04 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-04 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-04 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-04 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-04 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-04 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-04 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-04 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-04 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-04 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-04 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-04 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-04 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-04 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-04 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-04 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-04 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-04 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-04 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-04 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-04 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-05 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-05 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-05 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-05 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-05 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-05 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-05 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-05 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-05 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-05 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-05 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-05 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-05 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-05 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-05 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-05 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-05 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-05 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-05 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-05 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-05 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-05 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-05 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-05 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-06 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-06 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-06 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-06 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-06 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-06 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-06 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-06 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-06 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-06 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-06 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-06 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-06 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-06 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-06 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-06 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-06 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-06 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-06 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-06 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-06 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-06 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-06 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-06 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-07 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-07 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-07 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-07 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-07 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-07 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-07 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-07 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-07 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-07 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-07 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-07 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-07 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-07 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-07 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-07 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-07 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-07 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-07 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-07 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-07 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-07 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-07 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-08 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-08 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-08 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-08 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-08 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-08 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-08 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-08 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-08 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-08 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-08 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-08 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-08 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-08 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.43% | 1084.1262 | 1416.1374 | 2500.2636 | 18.3337 | 0.43715 | 0.56285 | 1.0568 | 17.3478 | 2517.6114 | 1091.7097 | 1425.9017
2016-10-08 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.3% | 1108.006 | 1443.3536 | 2551.3595 | 11.3183 | 0.43649 | 0.56351 | 1.0349 | 10.9364 | 2562.2959 | 1112.7796 | 1449.5164
2016-10-08 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.56% | 1111.3957 | 1439.6926 | 2551.0883 | 11.6326 | 0.43782 | 0.56218 | 1.035 | 11.2389 | 2562.3272 | 1116.3164 | 1446.0109
2016-10-08 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.23% | 1107.1141 | 1444.3168 | 2551.4309 | 11.3428 | 0.43614 | 0.56386 | 1.0349 | 10.9604 | 2562.3913 | 1111.8943 | 1450.497
2016-10-08 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.34% | 1108.5138 | 1442.8051 | 2551.3189 | 11.2044 | 0.43669 | 0.56331 | 1.0349 | 10.8262 | 2562.1451 | 1113.2414 | 1448.9037
2016-10-08 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-08 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-08 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-08 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-08 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-08 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-09 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-09 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-09 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-09 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-09 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-09 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-09 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-09 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-09 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-09 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-09 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-09 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-09 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-09 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.43% | 1084.1262 | 1416.1374 | 2500.2636 | 18.3337 | 0.43715 | 0.56285 | 1.0568 | 17.3478 | 2517.6114 | 1091.7097 | 1425.9017
2016-10-09 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.3% | 1108.006 | 1443.3536 | 2551.3595 | 11.3183 | 0.43649 | 0.56351 | 1.0349 | 10.9364 | 2562.2959 | 1112.7796 | 1449.5164
2016-10-09 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.56% | 1111.3957 | 1439.6926 | 2551.0883 | 11.6326 | 0.43782 | 0.56218 | 1.035 | 11.2389 | 2562.3272 | 1116.3164 | 1446.0109
2016-10-09 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.23% | 1107.1141 | 1444.3168 | 2551.4309 | 11.3428 | 0.43614 | 0.56386 | 1.0349 | 10.9604 | 2562.3913 | 1111.8943 | 1450.497
2016-10-09 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.34% | 1108.5138 | 1442.8051 | 2551.3189 | 11.2044 | 0.43669 | 0.56331 | 1.0349 | 10.8262 | 2562.1451 | 1113.2414 | 1448.9037
2016-10-09 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.5% | 1110.5808 | 1440.5727 | 2551.1535 | 11.1249 | 0.4375 | 0.5625 | 1.035 | 10.7487 | 2561.9023 | 1115.2834 | 1446.6189
2016-10-09 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.51% | 1085.1555 | 1414.9743 | 2500.1298 | 20.0853 | 0.43756 | 0.56244 | 1.0569 | 19.0043 | 2519.1341 | 1093.471 | 1425.663
2016-10-09 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-09 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-09 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-09 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-10 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-10 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-10 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-10 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-10 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-10 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-10 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-10 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-10 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-10 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-10 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-10 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-10 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-10 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-10 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-10 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-10 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-10 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-10 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-10 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.51% | 1085.1555 | 1414.9743 | 2500.1298 | 20.0853 | 0.43756 | 0.56244 | 1.0569 | 19.0043 | 2519.1341 | 1093.471 | 1425.663
2016-10-10 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 85.87% | 1064.8301 | 1437.942 | 2502.7721 | 22.7383 | 0.42937 | 0.57063 | 1.0558 | 21.5362 | 2524.3082 | 1074.077 | 1450.2313
2016-10-10 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.02% | 1162.1819 | 1587.2726 | 2749.4545 | 43.5495 | 0.43008 | 0.56992 | 1.1075 | 39.3216 | 2788.7761 | 1179.0935 | 1609.6826
2016-10-10 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.19% | 1164.5617 | 1584.2979 | 2748.8596 | 43.5064 | 0.43096 | 0.56904 | 1.1077 | 39.2749 | 2788.1345 | 1181.4878 | 1606.6467
2016-10-10 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.1% | 1174.0082 | 1573.7894 | 2747.7975 | 44.1478 | 0.43552 | 0.56448 | 1.1307 | 39.0462 | 2786.8437 | 1191.0135 | 1595.8302
2016-10-11 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.08% | 1173.6786 | 1574.2179 | 2747.8964 | 36.0832 | 0.4354 | 0.5646 | 1.1306 | 31.9146 | 2779.811 | 1187.5741 | 1592.2369
2016-10-11 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-11 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-11 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-11 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-11 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-11 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-11 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-10-11 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-10-11 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.78% | 1185.9436 | 1557.5705 | 2743.5141 | 35.2868 | 0.43888 | 0.56112 | 1.1097 | 31.7979 | 2775.312 | 1199.899 | 1575.413
2016-10-11 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-11 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.53% | 1085.4226 | 1414.6725 | 2500.0951 | 18.8858 | 0.43767 | 0.56233 | 1.0569 | 17.8691 | 2517.9642 | 1093.2434 | 1424.7208
2016-10-11 12:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.48% | 1110.2885 | 1440.8884 | 2551.1769 | 11.6885 | 0.43739 | 0.56261 | 1.035 | 11.2933 | 2562.4702 | 1115.2281 | 1447.2422
2016-10-11 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.43% | 1109.6825 | 1441.5429 | 2551.2254 | 11.2823 | 0.43715 | 0.56285 | 1.035 | 10.901 | 2562.1264 | 1114.4479 | 1447.6786
2016-10-11 14:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.3% | 1082.4882 | 1397.5118 | 2480 | 0 | 0.43649 | 0.56351 | 1 | 0 | 2480 | 1082.4882 | 1397.5118
2016-10-11 15:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.56% | 1085.8 | 1394.2 | 2480 | 0 | 0.43782 | 0.56218 | 1 | 0 | 2480 | 1085.8 | 1394.2
2016-10-11 16:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.23% | 1081.6169 | 1398.3831 | 2480 | 0 | 0.43614 | 0.56386 | 1 | 0 | 2480 | 1081.6169 | 1398.3831
2016-10-11 17:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.34% | 1082.9844 | 1397.0156 | 2480 | 0 | 0.43669 | 0.56331 | 1 | 0 | 2480 | 1082.9844 | 1397.0156
2016-10-11 18:00 | 1 | 2240 | 1240 | 1240 | 2240 | 87.5% | 1085.0038 | 1394.9962 | 2480 | 0 | 0.4375 | 0.5625 | 1 | 0 | 2480 | 1085.0038 | 1394.9962
2016-10-11 19:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.51% | 1110.736 | 1440.4051 | 2551.1411 | 12.3602 | 0.43756 | 0.56244 | 1.035 | 11.9422 | 2563.0833 | 1115.9615 | 1447.1218
2016-10-11 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 85.87% | 1064.8301 | 1437.942 | 2502.7721 | 22.7383 | 0.42937 | 0.57063 | 1.0558 | 21.5362 | 2524.3082 | 1074.077 | 1450.2313
2016-10-11 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 86.02% | 1066.6077 | 1435.9333 | 2502.541 | 22.6457 | 0.43008 | 0.56992 | 1.0559 | 21.4466 | 2523.9876 | 1075.8316 | 1448.156
2016-10-11 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.19% | 1164.5617 | 1584.2979 | 2748.8596 | 43.5064 | 0.43096 | 0.56904 | 1.1077 | 39.2749 | 2788.1345 | 1181.4878 | 1606.6467
2016-10-11 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.1% | 1174.0082 | 1573.7894 | 2747.7975 | 44.1478 | 0.43552 | 0.56448 | 1.1307 | 39.0462 | 2786.8437 | 1191.0135 | 1595.8302
2016-10-12 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.08% | 1173.6786 | 1574.2179 | 2747.8964 | 36.0832 | 0.4354 | 0.5646 | 1.1306 | 31.9146 | 2779.811 | 1187.5741 | 1592.2369
2016-10-12 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.91% | 1171.4427 | 1577.1245 | 2748.5672 | 36.6928 | 0.43457 | 0.56543 | 1.1304 | 32.4608 | 2781.028 | 1185.5491 | 1595.4789
2016-10-12 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.74% | 1169.0751 | 1580.2024 | 2749.2775 | 36.8657 | 0.43369 | 0.56631 | 1.1301 | 32.6214 | 2781.8989 | 1183.2227 | 1598.6762
2016-10-12 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.87% | 1170.9156 | 1577.8098 | 2748.7253 | 36.7472 | 0.43437 | 0.56563 | 1.1303 | 32.5107 | 2781.236 | 1185.0373 | 1596.1987
2016-10-12 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.27% | 1176.2441 | 1570.8826 | 2747.1268 | 39.2478 | 0.43635 | 0.56365 | 1.1309 | 34.7048 | 2781.8316 | 1191.3875 | 1590.444
2016-10-12 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.1% | 1187.4824 | 1556.2729 | 2743.7553 | 42.8107 | 0.44052 | 0.55948 | 1.1322 | 37.8134 | 2781.5687 | 1204.1399 | 1577.4288
2016-10-12 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 88.12% | 1187.6564 | 1556.0466 | 2743.7031 | 42.9472 | 0.44058 | 0.55942 | 1.1322 | 37.9334 | 2781.6364 | 1204.3692 | 1577.2672
2016-10-12 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-10-12 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-10-12 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.78% | 1185.9436 | 1557.5705 | 2743.5141 | 35.2868 | 0.43888 | 0.56112 | 1.1097 | 31.7979 | 2775.312 | 1199.899 | 1575.413
2016-10-12 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-12 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.53% | 1085.4226 | 1414.6725 | 2500.0951 | 18.8858 | 0.43767 | 0.56233 | 1.0569 | 17.8691 | 2517.9642 | 1093.2434 | 1424.7208
2016-10-12 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-12 13:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.43% | 1109.6825 | 1441.5429 | 2551.2254 | 11.2823 | 0.43715 | 0.56285 | 1.035 | 10.901 | 2562.1264 | 1114.4479 | 1447.6786
2016-10-12 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.3% | 1108.006 | 1443.3536 | 2551.3595 | 11.3183 | 0.43649 | 0.56351 | 1.0349 | 10.9364 | 2562.2959 | 1112.7796 | 1449.5164
2016-10-12 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.56% | 1111.3957 | 1439.6926 | 2551.0883 | 11.6326 | 0.43782 | 0.56218 | 1.035 | 11.2389 | 2562.3272 | 1116.3164 | 1446.0109
2016-10-12 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.23% | 1107.1141 | 1444.3168 | 2551.4309 | 11.3428 | 0.43614 | 0.56386 | 1.0349 | 10.9604 | 2562.3913 | 1111.8943 | 1450.497
2016-10-12 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.34% | 1108.5138 | 1442.8051 | 2551.3189 | 11.2044 | 0.43669 | 0.56331 | 1.0349 | 10.8262 | 2562.1451 | 1113.2414 | 1448.9037
2016-10-12 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.5% | 1110.5808 | 1440.5727 | 2551.1535 | 11.1249 | 0.4375 | 0.5625 | 1.035 | 10.7487 | 2561.9023 | 1115.2834 | 1446.6189
2016-10-12 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.51% | 1085.1555 | 1414.9743 | 2500.1298 | 20.0853 | 0.43756 | 0.56244 | 1.0569 | 19.0043 | 2519.1341 | 1093.471 | 1425.663
2016-10-12 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 85.87% | 1064.8301 | 1437.942 | 2502.7721 | 22.7383 | 0.42937 | 0.57063 | 1.0558 | 21.5362 | 2524.3082 | 1074.077 | 1450.2313
2016-10-12 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 86.02% | 1162.1819 | 1587.2726 | 2749.4545 | 43.5495 | 0.43008 | 0.56992 | 1.1075 | 39.3216 | 2788.7761 | 1179.0935 | 1609.6826
2016-10-12 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-10-12 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-13 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-13 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-13 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-13 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-13 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-13 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-13 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-13 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-13 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-13 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-13 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-13 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-13 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-13 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-13 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-13 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-13 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-13 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-13 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-13 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-13 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-13 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-13 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-10-13 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-14 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-14 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-14 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-14 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-14 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-14 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-14 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-14 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.98% | 1185.8451 | 1558.4014 | 2744.2465 | 42.9907 | 0.43991 | 0.56009 | 1.132 | 37.9786 | 2782.225 | 1202.5523 | 1579.6728
2016-10-14 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.73% | 1182.4025 | 1562.8767 | 2745.2792 | 41.766 | 0.43863 | 0.56137 | 1.1316 | 36.9091 | 2782.1883 | 1198.5921 | 1583.5962
2016-10-14 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-14 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-14 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-14 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-14 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-14 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-14 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-14 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-14 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-14 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-14 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-14 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-14 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-14 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-14 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-15 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-15 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-15 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-15 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-15 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-15 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-15 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-15 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-15 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-15 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-15 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.65% | 1184.2712 | 1559.661 | 2743.9322 | 33.9629 | 0.43826 | 0.56174 | 1.1096 | 30.6092 | 2774.5414 | 1197.686 | 1576.8554
2016-10-15 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-15 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-15 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.43% | 1084.1262 | 1416.1374 | 2500.2636 | 18.3337 | 0.43715 | 0.56285 | 1.0568 | 17.3478 | 2517.6114 | 1091.7097 | 1425.9017
2016-10-15 14:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.3% | 1108.006 | 1443.3536 | 2551.3595 | 11.3183 | 0.43649 | 0.56351 | 1.0349 | 10.9364 | 2562.2959 | 1112.7796 | 1449.5164
2016-10-15 15:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.56% | 1111.3957 | 1439.6926 | 2551.0883 | 11.6326 | 0.43782 | 0.56218 | 1.035 | 11.2389 | 2562.3272 | 1116.3164 | 1446.0109
2016-10-15 16:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.23% | 1107.1141 | 1444.3168 | 2551.4309 | 11.3428 | 0.43614 | 0.56386 | 1.0349 | 10.9604 | 2562.3913 | 1111.8943 | 1450.497
2016-10-15 17:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.34% | 1108.5138 | 1442.8051 | 2551.3189 | 11.2044 | 0.43669 | 0.56331 | 1.0349 | 10.8262 | 2562.1451 | 1113.2414 | 1448.9037
2016-10-15 18:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 87.5% | 1110.5808 | 1440.5727 | 2551.1535 | 11.1249 | 0.4375 | 0.5625 | 1.035 | 10.7487 | 2561.9023 | 1115.2834 | 1446.6189
2016-10-15 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.51% | 1085.1555 | 1414.9743 | 2500.1298 | 20.0853 | 0.43756 | 0.56244 | 1.0569 | 19.0043 | 2519.1341 | 1093.471 | 1425.663
2016-10-15 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-15 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-15 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-15 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-16 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-16 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-16 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-16 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-16 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-16 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-16 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-16 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-16 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-16 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-16 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-16 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-16 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-16 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-16 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-16 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-16 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-16 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-16 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-16 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-16 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-16 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-16 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-16 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-17 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-17 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-17 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-17 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-17 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-17 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-17 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.12% | 1380.491 | 1939.018 | 3319.509 | 143.1574 | 0.44058 | 0.55942 | 1.4406 | 99.3747 | 3418.8837 | 1424.2737 | 1994.61
2016-10-17 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.98% | 1378.3855 | 1943.2289 | 3321.6145 | 143.3023 | 0.43991 | 0.56009 | 1.4399 | 99.5217 | 3421.1362 | 1422.1662 | 1998.97
2016-10-17 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-17 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-17 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-17 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-17 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-17 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-17 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-17 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-17 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-17 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-17 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-17 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-17 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-17 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-17 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-17 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.1% | 1364.6267 | 1970.7466 | 3335.3733 | 147.1594 | 0.43552 | 0.56448 | 1.4355 | 102.513 | 3437.8863 | 1409.2731 | 2028.6132
2016-10-18 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-18 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-18 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-18 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-18 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-18 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-18 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-18 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-18 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-18 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-18 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-18 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-18 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-18 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-18 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-18 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-18 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-18 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-18 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-18 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-18 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-18 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-18 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-18 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-19 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-19 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-19 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-19 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-19 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-19 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-19 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-19 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-19 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-19 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.78% | 1183.0602 | 1562.0218 | 2745.0819 | 42.3441 | 0.43888 | 0.56112 | 1.1317 | 37.4176 | 2782.4995 | 1199.4819 | 1583.0176
2016-10-19 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-19 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-19 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.48% | 1084.7183 | 1415.4684 | 2500.1866 | 18.9938 | 0.43739 | 0.56261 | 1.0569 | 17.9719 | 2518.1585 | 1092.5789 | 1425.5796
2016-10-19 13:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.43% | 1084.1262 | 1416.1374 | 2500.2636 | 18.3337 | 0.43715 | 0.56285 | 1.0568 | 17.3478 | 2517.6114 | 1091.7097 | 1425.9017
2016-10-19 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-19 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-19 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-19 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.34% | 1082.9844 | 1417.4277 | 2500.412 | 18.2072 | 0.43669 | 0.56331 | 1.0568 | 17.2291 | 2517.6412 | 1090.5081 | 1427.1331
2016-10-19 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.5% | 1085.0038 | 1415.1457 | 2500.1495 | 18.078 | 0.4375 | 0.5625 | 1.0569 | 17.1052 | 2517.2547 | 1092.4873 | 1424.7673
2016-10-19 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-19 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-19 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-19 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.19% | 1161.7302 | 1589.7507 | 2751.4809 | 52.2077 | 0.43096 | 0.56904 | 1.1293 | 46.2306 | 2797.7115 | 1181.654 | 1616.0576
2016-10-19 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.1% | 1223.083 | 1657.6838 | 2880.7668 | 58.8638 | 0.43552 | 0.56448 | 1.1742 | 50.1306 | 2930.8974 | 1244.9158 | 1685.9816
2016-10-20 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.08% | 1222.7396 | 1658.1646 | 2880.9042 | 48.1109 | 0.4354 | 0.5646 | 1.1742 | 40.9748 | 2921.879 | 1240.5799 | 1681.2991
2016-10-20 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.91% | 1220.4103 | 1661.4256 | 2881.8359 | 48.9237 | 0.43457 | 0.56543 | 1.1738 | 41.6788 | 2923.5147 | 1238.5225 | 1684.9921
2016-10-20 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.74% | 1217.9437 | 1664.8788 | 2882.8225 | 49.1542 | 0.43369 | 0.56631 | 1.1735 | 41.8877 | 2924.7103 | 1236.11 | 1688.6003
2016-10-20 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.87% | 1219.8611 | 1662.1945 | 2882.0556 | 48.9962 | 0.43437 | 0.56563 | 1.1737 | 41.7434 | 2923.7989 | 1237.9932 | 1685.8057
2016-10-20 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.27% | 1225.4124 | 1654.4226 | 2879.835 | 52.3304 | 0.43635 | 0.56365 | 1.1745 | 44.554 | 2924.389 | 1244.8535 | 1679.5356
2016-10-20 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.1% | 1237.1204 | 1638.0314 | 2875.1518 | 57.0809 | 0.44052 | 0.55948 | 1.1762 | 48.5296 | 2923.6814 | 1258.4986 | 1665.1829
2016-10-20 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-20 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-20 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-20 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-20 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-20 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-20 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-20 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-20 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.3% | 1082.4882 | 1417.9883 | 2500.4765 | 18.3922 | 0.43649 | 0.56351 | 1.0567 | 17.4046 | 2517.8811 | 1090.0851 | 1427.796
2016-10-20 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.56% | 1085.8 | 1414.246 | 2500.046 | 18.9029 | 0.43782 | 0.56218 | 1.0569 | 17.8849 | 2517.9309 | 1093.6304 | 1424.3006
2016-10-20 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 87.23% | 1081.6169 | 1418.9729 | 2500.5898 | 18.4321 | 0.43614 | 0.56386 | 1.0567 | 17.4431 | 2518.0329 | 1089.2245 | 1428.8085
2016-10-20 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-20 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-20 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-20 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-20 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-20 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-20 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-21 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-21 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-21 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-21 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-21 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-21 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-21 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-21 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-21 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-21 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-21 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-21 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-21 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-21 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.43% | 1178.398 | 1568.0826 | 2746.4806 | 42.3084 | 0.43715 | 0.56285 | 1.1311 | 37.4032 | 2783.8838 | 1194.7487 | 1589.1351
2016-10-21 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.3% | 1176.6177 | 1570.3971 | 2747.0147 | 42.4436 | 0.43649 | 0.56351 | 1.1309 | 37.5293 | 2784.544 | 1192.9987 | 1591.5453
2016-10-21 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.56% | 1180.2173 | 1565.7175 | 2745.9348 | 43.6221 | 0.43782 | 0.56218 | 1.1313 | 38.5576 | 2784.4924 | 1197.0988 | 1587.3937
2016-10-21 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.23% | 1175.6705 | 1571.6283 | 2747.2988 | 42.5357 | 0.43614 | 0.56386 | 1.1308 | 37.6142 | 2784.913 | 1192.0754 | 1592.8376
2016-10-21 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.34% | 1177.1569 | 1569.696 | 2746.8529 | 42.0166 | 0.43669 | 0.56331 | 1.131 | 37.1498 | 2784.0027 | 1193.3797 | 1590.623
2016-10-21 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.5% | 1179.352 | 1566.8425 | 2746.1944 | 41.7186 | 0.4375 | 0.5625 | 1.1313 | 36.8783 | 2783.0727 | 1195.4863 | 1587.5864
2016-10-21 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.51% | 1228.8219 | 1649.6494 | 2878.4712 | 61.801 | 0.43756 | 0.56244 | 1.175 | 52.5954 | 2931.0667 | 1251.8357 | 1679.231
2016-10-21 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 85.87% | 1205.8056 | 1681.8722 | 2887.6778 | 69.9639 | 0.42937 | 0.57063 | 1.1717 | 59.709 | 2947.3868 | 1231.4426 | 1715.9441
2016-10-21 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.02% | 1290.2513 | 1814.6231 | 3104.8744 | 87.0989 | 0.43008 | 0.56992 | 1.215 | 71.6839 | 3176.5582 | 1321.0814 | 1855.4769
2016-10-21 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-21 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-22 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-22 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-22 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-22 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-22 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-22 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-22 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 88.12% | 1237.3018 | 1637.7775 | 2875.0793 | 57.263 | 0.44058 | 0.55942 | 1.1762 | 48.6833 | 2923.7626 | 1258.7508 | 1665.0119
2016-10-22 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-22 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-22 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-22 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-22 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-22 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-22 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.43% | 1178.398 | 1568.0826 | 2746.4806 | 42.3084 | 0.43715 | 0.56285 | 1.1311 | 37.4032 | 2783.8838 | 1194.7487 | 1589.1351
2016-10-22 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.3% | 1176.6177 | 1570.3971 | 2747.0147 | 42.4436 | 0.43649 | 0.56351 | 1.1309 | 37.5293 | 2784.544 | 1192.9987 | 1591.5453
2016-10-22 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-22 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-22 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-22 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-22 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-22 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-22 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-22 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-22 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-23 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-23 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-23 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-23 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-23 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-23 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-23 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-23 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-23 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-23 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-23 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-23 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.53% | 1229.1244 | 1649.2259 | 2878.3502 | 58.1101 | 0.43767 | 0.56233 | 1.1751 | 49.4526 | 2927.8028 | 1250.7683 | 1677.0345
2016-10-23 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.48% | 1228.3268 | 1650.3425 | 2878.6693 | 58.4424 | 0.43739 | 0.56261 | 1.175 | 49.7402 | 2928.4095 | 1250.0825 | 1678.327
2016-10-23 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.43% | 1227.6563 | 1651.2812 | 2878.9375 | 56.4113 | 0.43715 | 0.56285 | 1.1749 | 48.0153 | 2926.9528 | 1248.6461 | 1678.3067
2016-10-23 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.3% | 1225.8015 | 1653.8779 | 2879.6794 | 56.5914 | 0.43649 | 0.56351 | 1.1746 | 48.1795 | 2927.8589 | 1246.8313 | 1681.0276
2016-10-23 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.56% | 1229.5517 | 1648.6276 | 2878.1793 | 58.1628 | 0.43782 | 0.56218 | 1.1751 | 49.4948 | 2927.6741 | 1251.2216 | 1676.4525
2016-10-23 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.23% | 1224.8148 | 1655.2592 | 2880.0741 | 56.7142 | 0.43614 | 0.56386 | 1.1745 | 48.2899 | 2928.3639 | 1245.8758 | 1682.4882
2016-10-23 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.34% | 1226.3633 | 1653.0913 | 2879.4547 | 56.0222 | 0.43669 | 0.56331 | 1.1747 | 47.6916 | 2927.1463 | 1247.1897 | 1679.9566
2016-10-23 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.5% | 1228.6501 | 1649.8898 | 2878.5399 | 55.6247 | 0.4375 | 0.5625 | 1.175 | 47.3402 | 2925.8801 | 1249.3615 | 1676.5186
2016-10-23 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.51% | 1228.8219 | 1649.6494 | 2878.4712 | 61.801 | 0.43756 | 0.56244 | 1.175 | 52.5954 | 2931.0667 | 1251.8357 | 1679.231
2016-10-23 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 85.87% | 1205.8056 | 1681.8722 | 2887.6778 | 69.9639 | 0.42937 | 0.57063 | 1.1717 | 59.709 | 2947.3868 | 1231.4426 | 1715.9441
2016-10-23 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.02% | 1290.2513 | 1814.6231 | 3104.8744 | 87.0989 | 0.43008 | 0.56992 | 1.215 | 71.6839 | 3176.5582 | 1321.0814 | 1855.4769
2016-10-23 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-23 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.1% | 1364.6267 | 1970.7466 | 3335.3733 | 147.1594 | 0.43552 | 0.56448 | 1.4355 | 102.513 | 3437.8863 | 1409.2731 | 2028.6132
2016-10-24 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-24 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-24 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-24 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-24 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-24 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-24 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.12% | 1380.491 | 1939.018 | 3319.509 | 143.1574 | 0.44058 | 0.55942 | 1.4406 | 99.3747 | 3418.8837 | 1424.2737 | 1994.61
2016-10-24 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.98% | 1378.3855 | 1943.2289 | 3321.6145 | 143.3023 | 0.43991 | 0.56009 | 1.4399 | 99.5217 | 3421.1362 | 1422.1662 | 1998.97
2016-10-24 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.73% | 1374.384 | 1951.2319 | 3325.616 | 139.2199 | 0.43863 | 0.56137 | 1.4386 | 96.7723 | 3422.3883 | 1416.8316 | 2005.5567
2016-10-24 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.78% | 1316.6315 | 1775.0528 | 3091.6843 | 70.5735 | 0.43888 | 0.56112 | 1.2194 | 57.8738 | 3149.558 | 1342.031 | 1807.5271
2016-10-24 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-24 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.53% | 1229.1244 | 1649.2259 | 2878.3502 | 58.1101 | 0.43767 | 0.56233 | 1.1751 | 49.4526 | 2927.8028 | 1250.7683 | 1677.0345
2016-10-24 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-24 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.43% | 1178.398 | 1568.0826 | 2746.4806 | 42.3084 | 0.43715 | 0.56285 | 1.1311 | 37.4032 | 2783.8838 | 1194.7487 | 1589.1351
2016-10-24 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.3% | 1176.6177 | 1570.3971 | 2747.0147 | 42.4436 | 0.43649 | 0.56351 | 1.1309 | 37.5293 | 2784.544 | 1192.9987 | 1591.5453
2016-10-24 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-24 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-24 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-24 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-24 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-24 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-24 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-24 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-24 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-25 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-25 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-25 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-25 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-25 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-25 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-25 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.12% | 1380.491 | 1939.018 | 3319.509 | 143.1574 | 0.44058 | 0.55942 | 1.4406 | 99.3747 | 3418.8837 | 1424.2737 | 1994.61
2016-10-25 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.98% | 1378.3855 | 1943.2289 | 3321.6145 | 143.3023 | 0.43991 | 0.56009 | 1.4399 | 99.5217 | 3421.1362 | 1422.1662 | 1998.97
2016-10-25 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.73% | 1374.384 | 1951.2319 | 3325.616 | 139.2199 | 0.43863 | 0.56137 | 1.4386 | 96.7723 | 3422.3883 | 1416.8316 | 2005.5567
2016-10-25 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.78% | 1316.6315 | 1775.0528 | 3091.6843 | 70.5735 | 0.43888 | 0.56112 | 1.2194 | 57.8738 | 3149.558 | 1342.031 | 1807.5271
2016-10-25 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.65% | 1314.7748 | 1777.8378 | 3092.6126 | 67.9258 | 0.43826 | 0.56174 | 1.2191 | 55.7167 | 3148.3293 | 1339.1931 | 1809.1362
2016-10-25 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.53% | 1313.0112 | 1780.4832 | 3093.4944 | 72.6377 | 0.43767 | 0.56233 | 1.2188 | 59.596 | 3153.0904 | 1339.0946 | 1813.9958
2016-10-25 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.48% | 1228.3268 | 1650.3425 | 2878.6693 | 58.4424 | 0.43739 | 0.56261 | 1.175 | 49.7402 | 2928.4095 | 1250.0825 | 1678.327
2016-10-25 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.43% | 1178.398 | 1568.0826 | 2746.4806 | 42.3084 | 0.43715 | 0.56285 | 1.1311 | 37.4032 | 2783.8838 | 1194.7487 | 1589.1351
2016-10-25 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.3% | 1176.6177 | 1570.3971 | 2747.0147 | 42.4436 | 0.43649 | 0.56351 | 1.1309 | 37.5293 | 2784.544 | 1192.9987 | 1591.5453
2016-10-25 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.56% | 1180.2173 | 1565.7175 | 2745.9348 | 43.6221 | 0.43782 | 0.56218 | 1.1313 | 38.5576 | 2784.4924 | 1197.0988 | 1587.3937
2016-10-25 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.23% | 1175.6705 | 1571.6283 | 2747.2988 | 42.5357 | 0.43614 | 0.56386 | 1.1308 | 37.6142 | 2784.913 | 1192.0754 | 1592.8376
2016-10-25 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.34% | 1177.1569 | 1569.696 | 2746.8529 | 42.0166 | 0.43669 | 0.56331 | 1.131 | 37.1498 | 2784.0027 | 1193.3797 | 1590.623
2016-10-25 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.5% | 1179.352 | 1566.8425 | 2746.1944 | 41.7186 | 0.4375 | 0.5625 | 1.1313 | 36.8783 | 2783.0727 | 1195.4863 | 1587.5864
2016-10-25 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-25 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 85.87% | 1205.8056 | 1681.8722 | 2887.6778 | 69.9639 | 0.42937 | 0.57063 | 1.1717 | 59.709 | 2947.3868 | 1231.4426 | 1715.9441
2016-10-25 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-25 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-25 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.1% | 1364.6267 | 1970.7466 | 3335.3733 | 147.1594 | 0.43552 | 0.56448 | 1.4355 | 102.513 | 3437.8863 | 1409.2731 | 2028.6132
2016-10-26 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-26 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-26 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-26 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-26 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-26 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-26 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-26 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-26 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-26 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-26 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.65% | 1181.3918 | 1564.1906 | 2745.5824 | 40.7555 | 0.43826 | 0.56174 | 1.1315 | 36.0197 | 2781.6021 | 1197.1778 | 1584.4244
2016-10-26 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.53% | 1182.6827 | 1561.6466 | 2744.3293 | 36.3188 | 0.43767 | 0.56233 | 1.1094 | 32.7368 | 2777.0662 | 1197.0106 | 1580.0555
2016-10-26 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-26 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-26 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-26 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-26 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-26 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-26 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-26 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-26 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 85.87% | 1160.245 | 1589.6938 | 2749.9388 | 43.7274 | 0.42937 | 0.57063 | 1.1073 | 39.4886 | 2789.4274 | 1177.2001 | 1612.2273
2016-10-26 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 86.02% | 1159.3562 | 1592.8369 | 2752.1931 | 52.2593 | 0.43008 | 0.56992 | 1.129 | 46.2871 | 2798.4803 | 1179.2636 | 1619.2167
2016-10-26 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.19% | 1210.2918 | 1675.5915 | 2885.8833 | 69.6103 | 0.43096 | 0.56904 | 1.1724 | 59.3749 | 2945.2582 | 1235.8803 | 1709.3779
2016-10-26 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.1% | 1364.6267 | 1970.7466 | 3335.3733 | 147.1594 | 0.43552 | 0.56448 | 1.4355 | 102.513 | 3437.8863 | 1409.2731 | 2028.6132
2016-10-27 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-27 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-27 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-27 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-27 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-27 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-27 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-27 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-27 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-27 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-27 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-27 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-27 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-27 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-27 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-27 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-27 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-27 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-27 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.5% | 1179.352 | 1566.8425 | 2746.1944 | 41.7186 | 0.4375 | 0.5625 | 1.1313 | 36.8783 | 2783.0727 | 1195.4863 | 1587.5864
2016-10-27 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.51% | 1179.5168 | 1566.6282 | 2746.145 | 46.3507 | 0.43756 | 0.56244 | 1.1313 | 40.9723 | 2787.1173 | 1197.4448 | 1589.6725
2016-10-27 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-27 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-27 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-27 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-28 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-28 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-28 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-28 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-28 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-28 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-28 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-28 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-28 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-28 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.78% | 1316.6315 | 1775.0528 | 3091.6843 | 70.5735 | 0.43888 | 0.56112 | 1.2194 | 57.8738 | 3149.558 | 1342.031 | 1807.5271
2016-10-28 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-28 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.53% | 1229.1244 | 1649.2259 | 2878.3502 | 58.1101 | 0.43767 | 0.56233 | 1.1751 | 49.4526 | 2927.8028 | 1250.7683 | 1677.0345
2016-10-28 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.48% | 1228.3268 | 1650.3425 | 2878.6693 | 58.4424 | 0.43739 | 0.56261 | 1.175 | 49.7402 | 2928.4095 | 1250.0825 | 1678.327
2016-10-28 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.43% | 1227.6563 | 1651.2812 | 2878.9375 | 56.4113 | 0.43715 | 0.56285 | 1.1749 | 48.0153 | 2926.9528 | 1248.6461 | 1678.3067
2016-10-28 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.3% | 1225.8015 | 1653.8779 | 2879.6794 | 56.5914 | 0.43649 | 0.56351 | 1.1746 | 48.1795 | 2927.8589 | 1246.8313 | 1681.0276
2016-10-28 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.56% | 1229.5517 | 1648.6276 | 2878.1793 | 58.1628 | 0.43782 | 0.56218 | 1.1751 | 49.4948 | 2927.6741 | 1251.2216 | 1676.4525
2016-10-28 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.23% | 1224.8148 | 1655.2592 | 2880.0741 | 56.7142 | 0.43614 | 0.56386 | 1.1745 | 48.2899 | 2928.3639 | 1245.8758 | 1682.4882
2016-10-28 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.34% | 1226.3633 | 1653.0913 | 2879.4547 | 56.0222 | 0.43669 | 0.56331 | 1.1747 | 47.6916 | 2927.1463 | 1247.1897 | 1679.9566
2016-10-28 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.5% | 1228.6501 | 1649.8898 | 2878.5399 | 55.6247 | 0.4375 | 0.5625 | 1.175 | 47.3402 | 2925.8801 | 1249.3615 | 1676.5186
2016-10-28 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.51% | 1228.8219 | 1649.6494 | 2878.4712 | 61.801 | 0.43756 | 0.56244 | 1.175 | 52.5954 | 2931.0667 | 1251.8357 | 1679.231
2016-10-28 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 85.87% | 1205.8056 | 1681.8722 | 2887.6778 | 69.9639 | 0.42937 | 0.57063 | 1.1717 | 59.709 | 2947.3868 | 1231.4426 | 1715.9441
2016-10-28 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-28 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-28 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.1% | 1306.5575 | 1790.1638 | 3096.7213 | 73.5797 | 0.43552 | 0.56448 | 1.2178 | 60.4222 | 3157.1434 | 1332.8725 | 1824.2709
2016-10-29 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.08% | 1306.1907 | 1790.714 | 3096.9047 | 60.1387 | 0.4354 | 0.5646 | 1.2177 | 49.3872 | 3146.2918 | 1327.6937 | 1818.5982
2016-10-29 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.91% | 1303.7024 | 1794.4464 | 3098.1488 | 61.1546 | 0.43457 | 0.56543 | 1.2173 | 50.2386 | 3148.3874 | 1325.5344 | 1822.853
2016-10-29 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.74% | 1301.0675 | 1798.3988 | 3099.4663 | 61.4428 | 0.43369 | 0.56631 | 1.2168 | 50.4935 | 3149.9598 | 1322.966 | 1826.9939
2016-10-29 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.87% | 1303.1157 | 1795.3264 | 3098.4421 | 61.2453 | 0.43437 | 0.56563 | 1.2172 | 50.3171 | 3148.7593 | 1324.972 | 1823.7872
2016-10-29 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.27% | 1309.0459 | 1786.4312 | 3095.4771 | 65.413 | 0.43635 | 0.56365 | 1.2182 | 53.6976 | 3149.1747 | 1332.4768 | 1816.6979
2016-10-29 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.1% | 1321.553 | 1767.6706 | 3089.2235 | 71.3511 | 0.44052 | 0.55948 | 1.2203 | 58.4721 | 3147.6956 | 1347.311 | 1800.3847
2016-10-29 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 88.12% | 1321.7467 | 1767.38 | 3089.1267 | 71.5787 | 0.44058 | 0.55942 | 1.2203 | 58.6571 | 3147.7837 | 1347.5899 | 1800.1938
2016-10-29 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.98% | 1235.4147 | 1640.4194 | 2875.8341 | 57.3209 | 0.43991 | 0.56009 | 1.176 | 48.7438 | 2924.5779 | 1256.8576 | 1667.7203
2016-10-29 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.73% | 1231.8282 | 1645.4405 | 2877.2687 | 55.6879 | 0.43863 | 0.56137 | 1.1755 | 47.3757 | 2924.6444 | 1252.6088 | 1672.0356
2016-10-29 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-29 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-29 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-29 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.48% | 1179.0416 | 1567.2459 | 2746.2875 | 43.8318 | 0.43739 | 0.56261 | 1.1312 | 38.7475 | 2785.0351 | 1195.9892 | 1589.0458
2016-10-29 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.43% | 1178.398 | 1568.0826 | 2746.4806 | 42.3084 | 0.43715 | 0.56285 | 1.1311 | 37.4032 | 2783.8838 | 1194.7487 | 1589.1351
2016-10-29 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.3% | 1176.6177 | 1570.3971 | 2747.0147 | 42.4436 | 0.43649 | 0.56351 | 1.1309 | 37.5293 | 2784.544 | 1192.9987 | 1591.5453
2016-10-29 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.56% | 1180.2173 | 1565.7175 | 2745.9348 | 43.6221 | 0.43782 | 0.56218 | 1.1313 | 38.5576 | 2784.4924 | 1197.0988 | 1587.3937
2016-10-29 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.23% | 1175.6705 | 1571.6283 | 2747.2988 | 42.5357 | 0.43614 | 0.56386 | 1.1308 | 37.6142 | 2784.913 | 1192.0754 | 1592.8376
2016-10-29 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.34% | 1177.1569 | 1569.696 | 2746.8529 | 42.0166 | 0.43669 | 0.56331 | 1.131 | 37.1498 | 2784.0027 | 1193.3797 | 1590.623
2016-10-29 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.5% | 1179.352 | 1566.8425 | 2746.1944 | 41.7186 | 0.4375 | 0.5625 | 1.1313 | 36.8783 | 2783.0727 | 1195.4863 | 1587.5864
2016-10-29 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.51% | 1228.8219 | 1649.6494 | 2878.4712 | 61.801 | 0.43756 | 0.56244 | 1.175 | 52.5954 | 2931.0667 | 1251.8357 | 1679.231
2016-10-29 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 85.87% | 1288.1009 | 1817.8486 | 3105.9495 | 87.4548 | 0.42937 | 0.57063 | 1.2147 | 71.998 | 3177.9476 | 1319.0145 | 1858.9331
2016-10-29 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.02% | 1347.5958 | 2004.8084 | 3352.4042 | 174.1978 | 0.43008 | 0.56992 | 1.4301 | 121.8095 | 3474.2137 | 1399.9841 | 2074.2296
2016-10-29 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.19% | 1350.3552 | 1999.2895 | 3349.6448 | 174.0258 | 0.43096 | 0.56904 | 1.431 | 121.6143 | 3471.2591 | 1402.7667 | 2068.4924
2016-10-29 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.1% | 1364.6267 | 1970.7466 | 3335.3733 | 147.1594 | 0.43552 | 0.56448 | 1.4355 | 102.513 | 3437.8863 | 1409.2731 | 2028.6132
2016-10-30 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.08% | 1364.2436 | 1971.5128 | 3335.7564 | 120.2774 | 0.4354 | 0.5646 | 1.4354 | 83.7938 | 3419.5502 | 1400.7271 | 2018.8231
2016-10-30 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.91% | 1361.6447 | 1976.7106 | 3338.3553 | 122.3092 | 0.43457 | 0.56543 | 1.4346 | 85.2586 | 3423.6139 | 1398.6953 | 2024.9186
2016-10-30 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.74% | 1358.8927 | 1982.2147 | 3341.1073 | 122.8856 | 0.43369 | 0.56631 | 1.4337 | 85.7129 | 3426.8202 | 1396.0654 | 2030.7548
2016-10-30 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 86.87% | 1361.032 | 1977.9361 | 3338.968 | 122.4906 | 0.43437 | 0.56563 | 1.4344 | 85.3966 | 3424.3647 | 1398.1259 | 2026.2388
2016-10-30 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 87.27% | 1367.2257 | 1965.5486 | 3332.7743 | 130.8261 | 0.43635 | 0.56365 | 1.4363 | 91.0824 | 3423.8567 | 1406.9694 | 2016.8873
2016-10-30 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.1% | 1380.2887 | 1939.4227 | 3319.7113 | 142.7022 | 0.44052 | 0.55948 | 1.4405 | 99.0631 | 3418.7745 | 1423.9277 | 1994.8468
2016-10-30 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 88.12% | 1380.491 | 1939.018 | 3319.509 | 143.1574 | 0.44058 | 0.55942 | 1.4406 | 99.3747 | 3418.8837 | 1424.2737 | 1994.61
2016-10-30 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.98% | 1319.7308 | 1770.4037 | 3090.1346 | 71.6512 | 0.43991 | 0.56009 | 1.22 | 58.7326 | 3148.8672 | 1345.5679 | 1803.2993
2016-10-30 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 87.73% | 1315.8996 | 1776.1506 | 3092.0502 | 69.6099 | 0.43863 | 0.56137 | 1.2193 | 57.0893 | 3149.1395 | 1340.9409 | 1808.1986
2016-10-30 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.78% | 1232.5134 | 1644.4813 | 2876.9947 | 56.4588 | 0.43888 | 0.56112 | 1.1756 | 48.0275 | 2925.0222 | 1253.5916 | 1671.4306
2016-10-30 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 87.65% | 1230.7753 | 1646.9146 | 2877.6899 | 54.3406 | 0.43826 | 0.56174 | 1.1753 | 46.2354 | 2923.9253 | 1251.0384 | 1672.8869
2016-10-30 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 87.53% | 1179.8072 | 1566.2507 | 2746.0578 | 43.5826 | 0.43767 | 0.56233 | 1.1313 | 38.5243 | 2784.5822 | 1196.6681 | 1587.914
2016-10-30 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.48% | 1181.9152 | 1562.606 | 2744.5212 | 36.5265 | 0.43739 | 0.56261 | 1.1093 | 32.9262 | 2777.4474 | 1196.3167 | 1581.1307
2016-10-30 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.43% | 1181.2701 | 1563.4124 | 2744.6825 | 35.257 | 0.43715 | 0.56285 | 1.1093 | 31.7835 | 2776.466 | 1195.1642 | 1581.3018
2016-10-30 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.3% | 1179.4854 | 1565.6433 | 2745.1287 | 35.3696 | 0.43649 | 0.56351 | 1.1091 | 31.8898 | 2777.0184 | 1193.4049 | 1583.6136
2016-10-30 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.56% | 1183.0939 | 1561.1327 | 2744.2265 | 36.3517 | 0.43782 | 0.56218 | 1.1095 | 32.7654 | 2776.9919 | 1197.4393 | 1579.5526
2016-10-30 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.23% | 1178.536 | 1566.83 | 2745.366 | 35.4464 | 0.43614 | 0.56386 | 1.109 | 31.9615 | 2777.3275 | 1192.4755 | 1584.852
2016-10-30 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.34% | 1180.026 | 1564.9675 | 2744.9935 | 35.0139 | 0.43669 | 0.56331 | 1.1092 | 31.5676 | 2776.5611 | 1193.8111 | 1582.75
2016-10-30 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.5% | 1182.2264 | 1562.217 | 2744.4434 | 34.7655 | 0.4375 | 0.5625 | 1.1094 | 31.3379 | 2775.7813 | 1195.9367 | 1579.8445
2016-10-30 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 87.51% | 1182.3916 | 1562.0105 | 2744.4021 | 38.6256 | 0.43756 | 0.56244 | 1.1094 | 34.8169 | 2779.219 | 1197.6262 | 1581.5928
2016-10-30 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 85.87% | 1157.424 | 1595.3488 | 2752.7728 | 52.4729 | 0.42937 | 0.57063 | 1.1288 | 46.4851 | 2799.2579 | 1177.3832 | 1621.8748
2016-10-30 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 86.02% | 1207.8186 | 1679.054 | 2886.8726 | 69.6791 | 0.43008 | 0.56992 | 1.172 | 59.4515 | 2946.324 | 1233.3877 | 1712.9364
2016-10-30 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 86.19% | 1292.8933 | 1810.66 | 3103.5533 | 87.0129 | 0.43096 | 0.56904 | 1.2155 | 71.5871 | 3175.1405 | 1323.7448 | 1851.3957
2016-10-30 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.2916 | 1606.0626 | 3035.3542 | 73.5797 | 0.47643 | 0.52357 | 1.2382 | 59.424 | 3094.7782 | 1457.603 | 1637.1752
2016-10-31 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.9641 | 0.47482 | 0.52518 | 1.4748 | 130.8389 | 3343.0642 | 1549.8998 | 1793.1644
2016-10-31 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 192.3912 | 0.47348 | 0.52652 | 1.4735 | 130.5696 | 3347.0119 | 1545.3793 | 1801.6325
2016-10-31 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 187.9245 | 0.47286 | 0.52714 | 1.4729 | 127.5914 | 3345.9558 | 1541.9687 | 1803.9872
2016-10-31 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 183.7118 | 0.47583 | 0.52417 | 1.4758 | 124.4802 | 3333.5417 | 1550.1701 | 1783.3716
2016-10-31 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 196.7273 | 0.47692 | 0.52308 | 1.4769 | 133.2009 | 3338.8468 | 1557.8806 | 1780.9662
2016-10-31 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 187.038 | 0.47816 | 0.52184 | 1.4782 | 126.5344 | 3328.3015 | 1558.7365 | 1769.5649
2016-10-31 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 189.1349 | 0.47882 | 0.52118 | 1.4788 | 127.8958 | 3327.5938 | 1561.541 | 1766.0528
2016-10-31 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 188.6753 | 0.47907 | 0.52093 | 1.4791 | 127.5636 | 3326.4823 | 1562.193 | 1764.2893
2016-10-31 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 99.1653 | 0.47793 | 0.52207 | 1.239 | 80.0389 | 3113.1476 | 1472.0354 | 1641.1122
2016-10-31 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 94.8025 | 0.48026 | 0.51974 | 1.2401 | 76.4457 | 3106.0577 | 1477.4896 | 1628.5681
2016-10-31 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 86.3887 | 0.47859 | 0.52141 | 1.1914 | 72.508 | 2904.8867 | 1378.755 | 1526.1317
2016-10-31 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 54.0137 | 0.47791 | 0.52209 | 1.1434 | 47.2407 | 2760.7583 | 1310.8515 | 1449.9068
2016-10-31 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.58% | 1291.4068 | 1425.7415 | 2717.1483 | 47.8225 | 0.47791 | 0.52209 | 1.1195 | 42.7186 | 2759.8669 | 1311.8223 | 1448.0447
2016-10-31 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.93% | 1296.1684 | 1419.7895 | 2715.9579 | 48.3676 | 0.47967 | 0.52033 | 1.1199 | 43.1886 | 2759.1465 | 1316.8846 | 1442.2619
2016-10-31 14:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.97% | 1190.0679 | 1296.4233 | 2486.4912 | 25.4032 | 0.47987 | 0.52013 | 1.0624 | 23.9115 | 2510.4027 | 1201.5422 | 1308.8605
2016-10-31 15:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.18% | 1192.5764 | 1293.5887 | 2486.1651 | 23.4762 | 0.48088 | 0.51912 | 1.0625 | 22.095 | 2508.2601 | 1203.2014 | 1305.0587
2016-10-31 16:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.35% | 1182.3093 | 1305.1905 | 2487.4998 | 24.8388 | 0.47674 | 0.52326 | 1.062 | 23.3892 | 2510.889 | 1193.4599 | 1317.4292
2016-10-31 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.33% | 1182.0905 | 1305.4378 | 2487.5282 | 23.7553 | 0.47665 | 0.52335 | 1.062 | 22.3692 | 2509.8975 | 1192.7528 | 1317.1447
2016-10-31 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8087 | 1303.4962 | 2487.3049 | 22.4127 | 0.47734 | 0.52266 | 1.0621 | 21.1031 | 2508.408 | 1193.8821 | 1314.5259
2016-10-31 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.75% | 1187.3138 | 1299.5354 | 2486.8492 | 22.4748 | 0.47876 | 0.52124 | 1.0622 | 21.1579 | 2508.0071 | 1197.4432 | 1310.5639
2016-10-31 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.07% | 1178.8482 | 1309.1016 | 2487.9497 | 23.5777 | 0.47534 | 0.52466 | 1.0618 | 22.2055 | 2510.1552 | 1189.4034 | 1320.7518
2016-10-31 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.29% | 1287.4298 | 1430.7127 | 2718.1425 | 50.4182 | 0.47643 | 0.52357 | 1.1191 | 45.0522 | 2763.1947 | 1308.8942 | 1454.3005
2016-10-31 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.3% | 1287.6749 | 1430.4064 | 2718.0813 | 46.6943 | 0.47652 | 0.52348 | 1.1191 | 41.7237 | 2759.805 | 1307.5572 | 1452.2478
2016-10-31 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.29% | 1284.291 | 1430.4217 | 2714.7127 | 63.9045 | 0.47643 | 0.52357 | 1.1429 | 55.9129 | 2770.6256 | 1310.9296 | 1459.696
2016-11-01 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.482 | 0.47482 | 0.52518 | 1.2374 | 77.9709 | 3115.7383 | 1461.4874 | 1654.251
2016-11-01 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.1956 | 0.47482 | 0.52518 | 1.2374 | 77.7394 | 3115.5069 | 1461.3775 | 1654.1294
2016-11-01 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.7% | 1420.4276 | 1619.3585 | 3039.7862 | 93.9623 | 0.47348 | 0.52652 | 1.2367 | 75.9759 | 3115.7621 | 1456.4004 | 1659.3617
2016-11-01 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.57% | 1418.5872 | 1622.1192 | 3040.7064 | 91.8559 | 0.47286 | 0.52714 | 1.2364 | 74.2911 | 3114.9975 | 1453.7167 | 1661.2808
2016-11-01 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.17% | 1427.4943 | 1608.7585 | 3036.2528 | 98.3637 | 0.47583 | 0.52417 | 1.2379 | 79.4591 | 3115.7119 | 1465.3034 | 1650.4085
2016-11-01 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.38% | 1430.7646 | 1603.853 | 3034.6177 | 93.519 | 0.47692 | 0.52308 | 1.2385 | 75.5123 | 3110.13 | 1466.7781 | 1643.3519
2016-11-01 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-01 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-01 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-01 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-01 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-01 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-01 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-01 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.58% | 1291.4068 | 1425.7415 | 2717.1483 | 48.3676 | 0.47791 | 0.52209 | 1.1195 | 43.2056 | 2760.3539 | 1312.055 | 1448.2989
2016-11-01 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.93% | 1296.1684 | 1419.7895 | 2715.9579 | 48.8523 | 0.47967 | 0.52033 | 1.1199 | 43.6214 | 2759.5793 | 1317.0922 | 1442.4871
2016-11-01 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.97% | 1296.7048 | 1419.119 | 2715.8238 | 45.1466 | 0.47987 | 0.52013 | 1.12 | 40.3107 | 2756.1345 | 1316.0485 | 1440.0859
2016-11-01 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.18% | 1299.4381 | 1415.7024 | 2715.1405 | 47.767 | 0.48088 | 0.51912 | 1.1202 | 42.6407 | 2757.7812 | 1319.943 | 1437.8382
2016-11-01 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.35% | 1285.1188 | 1429.3455 | 2714.4644 | 54.82 | 0.47674 | 0.52326 | 1.143 | 47.9606 | 2762.425 | 1307.9835 | 1454.4415
2016-11-01 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-01 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.47% | 1286.7486 | 1427.2269 | 2713.9754 | 51.8648 | 0.47734 | 0.52266 | 1.1432 | 45.368 | 2759.3434 | 1308.4046 | 1450.9388
2016-11-01 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.75% | 1290.5584 | 1422.274 | 2712.8325 | 54.41 | 0.47876 | 0.52124 | 1.1436 | 47.5767 | 2760.4092 | 1313.336 | 1447.0731
2016-11-01 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-01 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-01 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-02 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-02 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-02 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-02 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-02 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-02 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-02 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-02 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-02 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-02 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-02 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-02 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-02 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-02 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-02 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.93% | 1439.0028 | 1591.4959 | 3030.4986 | 97.7046 | 0.47967 | 0.52033 | 1.2398 | 78.8046 | 3109.3032 | 1476.8028 | 1632.5005
2016-11-02 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.97% | 1439.5983 | 1590.6026 | 3030.2009 | 90.2932 | 0.47987 | 0.52013 | 1.2399 | 72.821 | 3103.0219 | 1474.5426 | 1628.4793
2016-11-02 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-02 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-02 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-02 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-02 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-02 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-02 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-02 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.3% | 1429.5732 | 1605.6401 | 3035.2134 | 106.5076 | 0.47652 | 0.52348 | 1.2383 | 86.0137 | 3121.2271 | 1470.5609 | 1650.6662
2016-11-03 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.2916 | 1606.0626 | 3035.3542 | 96.482 | 0.47643 | 0.52357 | 1.2382 | 77.9202 | 3113.2744 | 1466.4152 | 1646.8593
2016-11-03 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.1956 | 0.47482 | 0.52518 | 1.2374 | 77.7394 | 3115.5069 | 1461.3775 | 1654.1294
2016-11-03 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-03 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-03 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-03 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-03 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-03 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-03 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-03 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-03 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.8104 | 1690.3791 | 3195.1896 | 215.9718 | 0.48026 | 0.51974 | 1.4803 | 145.9014 | 3341.091 | 1574.8808 | 1766.2101
2016-11-03 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.72% | 1499.5963 | 1700.8073 | 3200.4037 | 180.0458 | 0.47859 | 0.52141 | 1.4786 | 121.7682 | 3322.1719 | 1557.8739 | 1764.2979
2016-11-03 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4462 | 1705.1075 | 3202.5538 | 191.2901 | 0.47791 | 0.52209 | 1.4779 | 129.433 | 3331.9867 | 1559.3033 | 1772.6834
2016-11-03 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4371 | 1705.1257 | 3202.5629 | 193.4705 | 0.47791 | 0.52209 | 1.4779 | 130.9086 | 3333.4714 | 1559.9991 | 1773.4724
2016-11-03 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.93% | 1502.9584 | 1694.0831 | 3197.0416 | 195.4092 | 0.47967 | 0.52033 | 1.4797 | 132.0629 | 3329.1045 | 1566.3047 | 1762.7997
2016-11-03 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.97% | 1503.5804 | 1692.8391 | 3196.4196 | 180.5864 | 0.47987 | 0.52013 | 1.4799 | 122.0289 | 3318.4485 | 1562.138 | 1756.3105
2016-11-03 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.18% | 1506.7497 | 1686.5005 | 3193.2503 | 191.0678 | 0.48088 | 0.51912 | 1.4809 | 129.0234 | 3322.2737 | 1568.7942 | 1753.4795
2016-11-03 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.35% | 1493.7779 | 1712.4442 | 3206.2221 | 182.7334 | 0.47674 | 0.52326 | 1.4767 | 123.7413 | 3329.9634 | 1552.77 | 1777.1933
2016-11-03 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.33% | 1493.5014 | 1712.9972 | 3206.4986 | 172.4052 | 0.47665 | 0.52335 | 1.4766 | 116.7544 | 3323.2529 | 1549.1523 | 1774.1006
2016-11-03 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.47% | 1495.6722 | 1708.6555 | 3204.3278 | 172.8827 | 0.47734 | 0.52266 | 1.4773 | 117.0228 | 3321.3505 | 1551.5322 | 1769.8184
2016-11-03 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.75% | 1500.1007 | 1699.7986 | 3199.8993 | 181.3666 | 0.47876 | 0.52124 | 1.4788 | 122.6481 | 3322.5474 | 1558.8192 | 1763.7282
2016-11-03 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-03 22:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 95.29% | 1548.4096 | 1793.4988 | 3341.9084 | 224.1327 | 0.47643 | 0.52357 | 1.5717 | 142.6034 | 3484.5118 | 1616.3507 | 1868.1611
2016-11-03 23:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 95.3% | 1548.7043 | 1792.8505 | 3341.5548 | 255.6181 | 0.47652 | 0.52348 | 1.5718 | 162.6246 | 3504.1794 | 1626.1989 | 1877.9805
2016-11-04 | 2.2 | 5200 | 1240 | 1625 | 3250 | 95.29% | 1548.3992 | 1793.5217 | 3341.9209 | 231.5569 | 0.47643 | 0.52357 | 1.5717 | 147.3274 | 3489.2483 | 1618.5905 | 1870.6578
2016-11-04 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 94.96% | 1543.1705 | 1805.0248 | 3348.1954 | 230.8694 | 0.47482 | 0.52518 | 1.5698 | 147.0706 | 3495.266 | 1613.0029 | 1882.2632
2016-11-04 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 94.7% | 1538.7966 | 1814.6475 | 3353.4441 | 225.5094 | 0.47348 | 0.52652 | 1.5682 | 143.8041 | 3497.2482 | 1606.8844 | 1890.3638
2016-11-04 03:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 94.57% | 1536.8028 | 1819.0338 | 3355.8366 | 220.4541 | 0.47286 | 0.52714 | 1.5674 | 140.6464 | 3496.4831 | 1603.3092 | 1893.1738
2016-11-04 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-04 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-04 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-04 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-04 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-04 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-04 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-04 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-04 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-04 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-04 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.93% | 1439.0028 | 1591.4959 | 3030.4986 | 97.7046 | 0.47967 | 0.52033 | 1.2398 | 78.8046 | 3109.3032 | 1476.8028 | 1632.5005
2016-11-04 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.97% | 1439.5983 | 1590.6026 | 3030.2009 | 90.2932 | 0.47987 | 0.52013 | 1.2399 | 72.821 | 3103.0219 | 1474.5426 | 1628.4793
2016-11-04 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-04 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-04 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-04 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-04 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-04 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-04 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9847 | 1496.8214 | 2834.8061 | 74.7109 | 0.47643 | 0.52357 | 1.1906 | 62.752 | 2897.5581 | 1367.8819 | 1529.6762
2016-11-04 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.3% | 1338.2394 | 1496.4649 | 2834.7042 | 85.206 | 0.47652 | 0.52348 | 1.1906 | 71.565 | 2906.2693 | 1372.3419 | 1533.9274
2016-11-05 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9758 | 1496.8339 | 2834.8097 | 77.1856 | 0.47643 | 0.52357 | 1.1906 | 64.8307 | 2899.6404 | 1368.8631 | 1530.7773
2016-11-05 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.96% | 1333.4576 | 1503.1593 | 2836.617 | 76.9565 | 0.47482 | 0.52518 | 1.1899 | 64.6732 | 2901.2901 | 1364.1658 | 1537.1243
2016-11-05 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.7% | 1329.6781 | 1508.4507 | 2838.1288 | 75.1698 | 0.47348 | 0.52652 | 1.1894 | 63.2003 | 2901.3291 | 1359.6019 | 1541.7271
2016-11-05 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.57% | 1327.9552 | 1510.8627 | 2838.8179 | 73.4847 | 0.47286 | 0.52714 | 1.1891 | 61.7963 | 2900.6142 | 1357.1764 | 1543.4378
2016-11-05 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.17% | 1336.2933 | 1499.1894 | 2835.4827 | 78.6909 | 0.47583 | 0.52417 | 1.1903 | 66.1084 | 2901.591 | 1367.7497 | 1533.8413
2016-11-05 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.38% | 1285.6146 | 1428.701 | 2714.3156 | 56.1114 | 0.47692 | 0.52308 | 1.1431 | 49.0881 | 2763.4037 | 1309.0258 | 1454.3779
2016-11-05 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.63% | 1288.9515 | 1424.363 | 2713.3145 | 56.7405 | 0.47816 | 0.52184 | 1.1434 | 49.6223 | 2762.9368 | 1312.6789 | 1450.2579
2016-11-05 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.76% | 1293.8775 | 1422.6532 | 2716.5306 | 47.1688 | 0.47882 | 0.52118 | 1.1197 | 42.1261 | 2758.6568 | 1314.0483 | 1444.6085
2016-11-05 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.81% | 1291.402 | 1421.1774 | 2712.5794 | 59.4992 | 0.47907 | 0.52093 | 1.1437 | 52.0225 | 2764.6019 | 1316.3244 | 1448.2775
2016-11-05 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.59% | 1288.3264 | 1425.1757 | 2713.5021 | 56.8815 | 0.47793 | 0.52207 | 1.1434 | 49.7486 | 2763.2507 | 1312.1027 | 1451.1481
2016-11-05 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-05 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-05 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-05 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2669 | 1425.253 | 2713.5199 | 58.0411 | 0.47791 | 0.52209 | 1.1434 | 50.7631 | 2764.2831 | 1312.5269 | 1451.7562
2016-11-05 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.93% | 1293.017 | 1419.0779 | 2712.0949 | 58.6228 | 0.47967 | 0.52033 | 1.1439 | 51.2481 | 2763.3431 | 1317.599 | 1445.744
2016-11-05 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.97% | 1293.5521 | 1418.3823 | 2711.9344 | 54.1759 | 0.47987 | 0.52013 | 1.144 | 47.3582 | 2759.2926 | 1316.2777 | 1443.0149
2016-11-05 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.18% | 1296.2787 | 1414.8377 | 2711.1164 | 57.3204 | 0.48088 | 0.51912 | 1.1443 | 50.0937 | 2761.2101 | 1320.3676 | 1440.8425
2016-11-05 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.35% | 1285.1188 | 1429.3455 | 2714.4644 | 54.82 | 0.47674 | 0.52326 | 1.143 | 47.9606 | 2762.425 | 1307.9835 | 1454.4415
2016-11-05 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-05 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.47% | 1286.7486 | 1427.2269 | 2713.9754 | 51.8648 | 0.47734 | 0.52266 | 1.1432 | 45.368 | 2759.3434 | 1308.4046 | 1450.9388
2016-11-05 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-05 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-05 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-05 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-06 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-06 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-06 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-06 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-06 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-06 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-06 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-06 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-06 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-06 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-06 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-06 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-06 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-06 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-06 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-06 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-06 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-06 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-06 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-06 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-06 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-06 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-06 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-06 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-07 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-07 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-07 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-07 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-07 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-07 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-07 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-07 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-07 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-07 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-07 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-07 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-07 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-07 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-07 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.93% | 1439.0028 | 1591.4959 | 3030.4986 | 97.7046 | 0.47967 | 0.52033 | 1.2398 | 78.8046 | 3109.3032 | 1476.8028 | 1632.5005
2016-11-07 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.97% | 1439.5983 | 1590.6026 | 3030.2009 | 90.2932 | 0.47987 | 0.52013 | 1.2399 | 72.821 | 3103.0219 | 1474.5426 | 1628.4793
2016-11-07 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-07 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-07 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-07 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-07 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-07 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-07 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-07 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-08 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-08 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-08 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-08 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-08 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-08 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-08 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-08 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-08 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-08 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-08 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-08 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-08 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-08 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-08 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-08 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-08 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-08 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-08 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-08 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-08 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-08 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-08 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-08 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-09 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-09 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-09 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-09 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-09 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-09 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-09 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-09 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-09 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-09 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-09 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-09 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-09 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-09 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-09 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.93% | 1439.0028 | 1591.4959 | 3030.4986 | 97.7046 | 0.47967 | 0.52033 | 1.2398 | 78.8046 | 3109.3032 | 1476.8028 | 1632.5005
2016-11-09 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.97% | 1439.5983 | 1590.6026 | 3030.2009 | 90.2932 | 0.47987 | 0.52013 | 1.2399 | 72.821 | 3103.0219 | 1474.5426 | 1628.4793
2016-11-09 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-09 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-09 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-09 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-09 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-09 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-09 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-09 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-10 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-10 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-10 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-10 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-10 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-10 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-10 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-10 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-10 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-10 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-10 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-10 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-10 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-10 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2669 | 1425.253 | 2713.5199 | 58.0411 | 0.47791 | 0.52209 | 1.1434 | 50.7631 | 2764.2831 | 1312.5269 | 1451.7562
2016-11-10 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.93% | 1296.1684 | 1419.7895 | 2715.9579 | 48.8523 | 0.47967 | 0.52033 | 1.1199 | 43.6214 | 2759.5793 | 1317.0922 | 1442.4871
2016-11-10 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.97% | 1296.7048 | 1419.119 | 2715.8238 | 45.1466 | 0.47987 | 0.52013 | 1.12 | 40.3107 | 2756.1345 | 1316.0485 | 1440.0859
2016-11-10 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.18% | 1299.4381 | 1415.7024 | 2715.1405 | 47.767 | 0.48088 | 0.51912 | 1.1202 | 42.6407 | 2757.7812 | 1319.943 | 1437.8382
2016-11-10 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.35% | 1288.251 | 1429.6862 | 2717.9372 | 45.6833 | 0.47674 | 0.52326 | 1.1192 | 40.8184 | 2758.7557 | 1307.7107 | 1451.045
2016-11-10 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-10 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.47% | 1286.7486 | 1427.2269 | 2713.9754 | 51.8648 | 0.47734 | 0.52266 | 1.1432 | 45.368 | 2759.3434 | 1308.4046 | 1450.9388
2016-11-10 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.75% | 1290.5584 | 1422.274 | 2712.8325 | 54.41 | 0.47876 | 0.52124 | 1.1436 | 47.5767 | 2760.4092 | 1313.336 | 1447.0731
2016-11-10 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-10 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-10 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-11 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-11 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-11 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-11 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-11 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-11 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-11 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-11 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-11 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-11 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-11 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-11 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-11 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-11 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-11 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-11 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-11 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-11 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-11 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-11 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-11 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-11 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-11 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-11 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-12 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-12 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-12 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-12 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-12 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-12 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-12 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-12 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-12 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-12 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-12 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-12 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-12 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-12 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-12 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.93% | 1439.0028 | 1591.4959 | 3030.4986 | 97.7046 | 0.47967 | 0.52033 | 1.2398 | 78.8046 | 3109.3032 | 1476.8028 | 1632.5005
2016-11-12 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.97% | 1439.5983 | 1590.6026 | 3030.2009 | 90.2932 | 0.47987 | 0.52013 | 1.2399 | 72.821 | 3103.0219 | 1474.5426 | 1628.4793
2016-11-12 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-12 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-12 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-12 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-12 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-12 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-12 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-12 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.3% | 1429.5732 | 1605.6401 | 3035.2134 | 106.5076 | 0.47652 | 0.52348 | 1.2383 | 86.0137 | 3121.2271 | 1470.5609 | 1650.6662
2016-11-13 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.2916 | 1606.0626 | 3035.3542 | 96.482 | 0.47643 | 0.52357 | 1.2382 | 77.9202 | 3113.2744 | 1466.4152 | 1646.8593
2016-11-13 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.1956 | 0.47482 | 0.52518 | 1.2374 | 77.7394 | 3115.5069 | 1461.3775 | 1654.1294
2016-11-13 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.7% | 1420.4276 | 1619.3585 | 3039.7862 | 93.9623 | 0.47348 | 0.52652 | 1.2367 | 75.9759 | 3115.7621 | 1456.4004 | 1659.3617
2016-11-13 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.57% | 1418.5872 | 1622.1192 | 3040.7064 | 91.8559 | 0.47286 | 0.52714 | 1.2364 | 74.2911 | 3114.9975 | 1453.7167 | 1661.2808
2016-11-13 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.17% | 1427.4943 | 1608.7585 | 3036.2528 | 98.3637 | 0.47583 | 0.52417 | 1.2379 | 79.4591 | 3115.7119 | 1465.3034 | 1650.4085
2016-11-13 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.38% | 1430.7646 | 1603.853 | 3034.6177 | 93.519 | 0.47692 | 0.52308 | 1.2385 | 75.5123 | 3110.13 | 1466.7781 | 1643.3519
2016-11-13 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.63% | 1342.8311 | 1490.0365 | 2832.8676 | 75.654 | 0.47816 | 0.52184 | 1.1913 | 63.5073 | 2896.3749 | 1373.1977 | 1523.1771
2016-11-13 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-13 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.81% | 1291.402 | 1421.1774 | 2712.5794 | 59.4992 | 0.47907 | 0.52093 | 1.1437 | 52.0225 | 2764.6019 | 1316.3244 | 1448.2775
2016-11-13 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.59% | 1288.3264 | 1425.1757 | 2713.5021 | 56.8815 | 0.47793 | 0.52207 | 1.1434 | 49.7486 | 2763.2507 | 1312.1027 | 1451.1481
2016-11-13 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-13 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-13 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-13 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2669 | 1425.253 | 2713.5199 | 58.0411 | 0.47791 | 0.52209 | 1.1434 | 50.7631 | 2764.2831 | 1312.5269 | 1451.7562
2016-11-13 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.93% | 1293.017 | 1419.0779 | 2712.0949 | 58.6228 | 0.47967 | 0.52033 | 1.1439 | 51.2481 | 2763.3431 | 1317.599 | 1445.744
2016-11-13 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.97% | 1296.7048 | 1419.119 | 2715.8238 | 45.1466 | 0.47987 | 0.52013 | 1.12 | 40.3107 | 2756.1345 | 1316.0485 | 1440.0859
2016-11-13 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.18% | 1299.4381 | 1415.7024 | 2715.1405 | 47.767 | 0.48088 | 0.51912 | 1.1202 | 42.6407 | 2757.7812 | 1319.943 | 1437.8382
2016-11-13 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.35% | 1288.251 | 1429.6862 | 2717.9372 | 45.6833 | 0.47674 | 0.52326 | 1.1192 | 40.8184 | 2758.7557 | 1307.7107 | 1451.045
2016-11-13 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.33% | 1288.0126 | 1429.9843 | 2717.9969 | 43.1013 | 0.47665 | 0.52335 | 1.1192 | 38.5121 | 2756.509 | 1306.3693 | 1450.1396
2016-11-13 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.47% | 1289.8847 | 1427.6441 | 2717.5288 | 43.2207 | 0.47734 | 0.52266 | 1.1193 | 38.6128 | 2756.1416 | 1308.3162 | 1447.8254
2016-11-13 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.75% | 1293.7039 | 1422.8701 | 2716.574 | 45.3416 | 0.47876 | 0.52124 | 1.1197 | 40.4949 | 2757.0689 | 1313.091 | 1443.9779
2016-11-13 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.07% | 1281.3567 | 1434.2363 | 2715.593 | 60.5019 | 0.47534 | 0.52466 | 1.1426 | 52.951 | 2768.5439 | 1306.5265 | 1462.0174
2016-11-13 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.29% | 1284.2996 | 1430.4105 | 2714.7101 | 56.0332 | 0.47643 | 0.52357 | 1.1429 | 49.0259 | 2763.736 | 1307.6572 | 1456.0788
2016-11-13 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.3% | 1338.2394 | 1496.4649 | 2834.7042 | 85.206 | 0.47652 | 0.52348 | 1.1906 | 71.565 | 2906.2693 | 1372.3419 | 1533.9274
2016-11-14 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9758 | 1496.8339 | 2834.8097 | 77.1856 | 0.47643 | 0.52357 | 1.1906 | 64.8307 | 2899.6404 | 1368.8631 | 1530.7773
2016-11-14 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.96% | 1333.4576 | 1503.1593 | 2836.617 | 76.9565 | 0.47482 | 0.52518 | 1.1899 | 64.6732 | 2901.2901 | 1364.1658 | 1537.1243
2016-11-14 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.7% | 1420.4276 | 1619.3585 | 3039.7862 | 93.9623 | 0.47348 | 0.52652 | 1.2367 | 75.9759 | 3115.7621 | 1456.4004 | 1659.3617
2016-11-14 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.57% | 1418.5872 | 1622.1192 | 3040.7064 | 91.8559 | 0.47286 | 0.52714 | 1.2364 | 74.2911 | 3114.9975 | 1453.7167 | 1661.2808
2016-11-14 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.17% | 1427.4943 | 1608.7585 | 3036.2528 | 98.3637 | 0.47583 | 0.52417 | 1.2379 | 79.4591 | 3115.7119 | 1465.3034 | 1650.4085
2016-11-14 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.38% | 1430.7646 | 1603.853 | 3034.6177 | 93.519 | 0.47692 | 0.52308 | 1.2385 | 75.5123 | 3110.13 | 1466.7781 | 1643.3519
2016-11-14 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-14 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-14 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-14 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-14 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-14 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-14 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-14 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-14 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-14 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.97% | 1293.5521 | 1418.3823 | 2711.9344 | 54.1759 | 0.47987 | 0.52013 | 1.144 | 47.3582 | 2759.2926 | 1316.2777 | 1443.0149
2016-11-14 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.18% | 1296.2787 | 1414.8377 | 2711.1164 | 57.3204 | 0.48088 | 0.51912 | 1.1443 | 50.0937 | 2761.2101 | 1320.3676 | 1440.8425
2016-11-14 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.35% | 1285.1188 | 1429.3455 | 2714.4644 | 54.82 | 0.47674 | 0.52326 | 1.143 | 47.9606 | 2762.425 | 1307.9835 | 1454.4415
2016-11-14 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-14 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.47% | 1286.7486 | 1427.2269 | 2713.9754 | 51.8648 | 0.47734 | 0.52266 | 1.1432 | 45.368 | 2759.3434 | 1308.4046 | 1450.9388
2016-11-14 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.75% | 1290.5584 | 1422.274 | 2712.8325 | 54.41 | 0.47876 | 0.52124 | 1.1436 | 47.5767 | 2760.4092 | 1313.336 | 1447.0731
2016-11-14 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.07% | 1281.3567 | 1434.2363 | 2715.593 | 60.5019 | 0.47534 | 0.52466 | 1.1426 | 52.951 | 2768.5439 | 1306.5265 | 1462.0174
2016-11-14 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9847 | 1496.8214 | 2834.8061 | 74.7109 | 0.47643 | 0.52357 | 1.1906 | 62.752 | 2897.5581 | 1367.8819 | 1529.6762
2016-11-14 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.3% | 1429.5732 | 1605.6401 | 3035.2134 | 106.5076 | 0.47652 | 0.52348 | 1.2383 | 86.0137 | 3121.2271 | 1470.5609 | 1650.6662
2016-11-15 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.2916 | 1606.0626 | 3035.3542 | 96.482 | 0.47643 | 0.52357 | 1.2382 | 77.9202 | 3113.2744 | 1466.4152 | 1646.8593
2016-11-15 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.1956 | 0.47482 | 0.52518 | 1.2374 | 77.7394 | 3115.5069 | 1461.3775 | 1654.1294
2016-11-15 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.7% | 1420.4276 | 1619.3585 | 3039.7862 | 93.9623 | 0.47348 | 0.52652 | 1.2367 | 75.9759 | 3115.7621 | 1456.4004 | 1659.3617
2016-11-15 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.57% | 1418.5872 | 1622.1192 | 3040.7064 | 91.8559 | 0.47286 | 0.52714 | 1.2364 | 74.2911 | 3114.9975 | 1453.7167 | 1661.2808
2016-11-15 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.17% | 1427.4943 | 1608.7585 | 3036.2528 | 98.3637 | 0.47583 | 0.52417 | 1.2379 | 79.4591 | 3115.7119 | 1465.3034 | 1650.4085
2016-11-15 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.38% | 1430.7646 | 1603.853 | 3034.6177 | 93.519 | 0.47692 | 0.52308 | 1.2385 | 75.5123 | 3110.13 | 1466.7781 | 1643.3519
2016-11-15 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.63% | 1342.8311 | 1490.0365 | 2832.8676 | 75.654 | 0.47816 | 0.52184 | 1.1913 | 63.5073 | 2896.3749 | 1373.1977 | 1523.1771
2016-11-15 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-15 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-15 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-15 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-15 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-15 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-15 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-15 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-15 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-15 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-15 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-15 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-15 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.47% | 1286.7486 | 1427.2269 | 2713.9754 | 51.8648 | 0.47734 | 0.52266 | 1.1432 | 45.368 | 2759.3434 | 1308.4046 | 1450.9388
2016-11-15 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.75% | 1290.5584 | 1422.274 | 2712.8325 | 54.41 | 0.47876 | 0.52124 | 1.1436 | 47.5767 | 2760.4092 | 1313.336 | 1447.0731
2016-11-15 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.07% | 1281.3567 | 1434.2363 | 2715.593 | 60.5019 | 0.47534 | 0.52466 | 1.1426 | 52.951 | 2768.5439 | 1306.5265 | 1462.0174
2016-11-15 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9847 | 1496.8214 | 2834.8061 | 74.7109 | 0.47643 | 0.52357 | 1.1906 | 62.752 | 2897.5581 | 1367.8819 | 1529.6762
2016-11-15 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.3% | 1338.2394 | 1496.4649 | 2834.7042 | 85.206 | 0.47652 | 0.52348 | 1.1906 | 71.565 | 2906.2693 | 1372.3419 | 1533.9274
2016-11-16 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9758 | 1496.8339 | 2834.8097 | 77.1856 | 0.47643 | 0.52357 | 1.1906 | 64.8307 | 2899.6404 | 1368.8631 | 1530.7773
2016-11-16 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.96% | 1424.4651 | 1613.3024 | 3037.7675 | 96.1956 | 0.47482 | 0.52518 | 1.2374 | 77.7394 | 3115.5069 | 1461.3775 | 1654.1294
2016-11-16 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.7% | 1420.4276 | 1619.3585 | 3039.7862 | 93.9623 | 0.47348 | 0.52652 | 1.2367 | 75.9759 | 3115.7621 | 1456.4004 | 1659.3617
2016-11-16 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 94.57% | 1418.5872 | 1622.1192 | 3040.7064 | 91.8559 | 0.47286 | 0.52714 | 1.2364 | 74.2911 | 3114.9975 | 1453.7167 | 1661.2808
2016-11-16 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.17% | 1427.4943 | 1608.7585 | 3036.2528 | 98.3637 | 0.47583 | 0.52417 | 1.2379 | 79.4591 | 3115.7119 | 1465.3034 | 1650.4085
2016-11-16 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.38% | 1339.3547 | 1494.9034 | 2834.2581 | 74.8152 | 0.47692 | 0.52308 | 1.1908 | 62.8293 | 2897.0875 | 1369.3194 | 1527.7681
2016-11-16 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.63% | 1342.8311 | 1490.0365 | 2832.8676 | 75.654 | 0.47816 | 0.52184 | 1.1913 | 63.5073 | 2896.3749 | 1373.1977 | 1523.1771
2016-11-16 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-16 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-16 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-16 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-16 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-16 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-16 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-16 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-16 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-16 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-16 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-16 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-16 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-16 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-16 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-16 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-16 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-17 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-17 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-17 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-17 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-17 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-17 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-17 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-17 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-17 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-17 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-17 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.8104 | 1690.3791 | 3195.1896 | 215.9718 | 0.48026 | 0.51974 | 1.4803 | 145.9014 | 3341.091 | 1574.8808 | 1766.2101
2016-11-17 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.72% | 1499.5963 | 1700.8073 | 3200.4037 | 180.0458 | 0.47859 | 0.52141 | 1.4786 | 121.7682 | 3322.1719 | 1557.8739 | 1764.2979
2016-11-17 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4462 | 1705.1075 | 3202.5538 | 191.2901 | 0.47791 | 0.52209 | 1.4779 | 129.433 | 3331.9867 | 1559.3033 | 1772.6834
2016-11-17 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4371 | 1705.1257 | 3202.5629 | 193.4705 | 0.47791 | 0.52209 | 1.4779 | 130.9086 | 3333.4714 | 1559.9991 | 1773.4724
2016-11-17 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.93% | 1502.9584 | 1694.0831 | 3197.0416 | 195.4092 | 0.47967 | 0.52033 | 1.4797 | 132.0629 | 3329.1045 | 1566.3047 | 1762.7997
2016-11-17 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.97% | 1503.5804 | 1692.8391 | 3196.4196 | 180.5864 | 0.47987 | 0.52013 | 1.4799 | 122.0289 | 3318.4485 | 1562.138 | 1756.3105
2016-11-17 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.18% | 1506.7497 | 1686.5005 | 3193.2503 | 191.0678 | 0.48088 | 0.51912 | 1.4809 | 129.0234 | 3322.2737 | 1568.7942 | 1753.4795
2016-11-17 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.35% | 1493.7779 | 1712.4442 | 3206.2221 | 182.7334 | 0.47674 | 0.52326 | 1.4767 | 123.7413 | 3329.9634 | 1552.77 | 1777.1933
2016-11-17 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.33% | 1493.5014 | 1712.9972 | 3206.4986 | 172.4052 | 0.47665 | 0.52335 | 1.4766 | 116.7544 | 3323.2529 | 1549.1523 | 1774.1006
2016-11-17 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.47% | 1495.6722 | 1708.6555 | 3204.3278 | 172.8827 | 0.47734 | 0.52266 | 1.4773 | 117.0228 | 3321.3505 | 1551.5322 | 1769.8184
2016-11-17 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.75% | 1500.1007 | 1699.7986 | 3199.8993 | 181.3666 | 0.47876 | 0.52124 | 1.4788 | 122.6481 | 3322.5474 | 1558.8192 | 1763.7282
2016-11-17 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-17 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-17 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-18 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-18 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-18 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-18 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-18 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-18 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.38% | 1430.7646 | 1603.853 | 3034.6177 | 93.519 | 0.47692 | 0.52308 | 1.2385 | 75.5123 | 3110.13 | 1466.7781 | 1643.3519
2016-11-18 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.63% | 1342.8311 | 1490.0365 | 2832.8676 | 75.654 | 0.47816 | 0.52184 | 1.1913 | 63.5073 | 2896.3749 | 1373.1977 | 1523.1771
2016-11-18 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-18 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-18 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-18 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-18 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-18 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-18 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-18 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-18 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-18 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-18 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-18 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-18 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-18 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-18 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-18 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-18 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-19 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-19 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-19 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-19 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-19 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-19 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-19 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-19 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-19 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-19 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.59% | 1342.1798 | 1490.9482 | 2833.1281 | 75.842 | 0.47793 | 0.52207 | 1.1912 | 63.6701 | 2896.7982 | 1372.6096 | 1524.1886
2016-11-19 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-19 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-19 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-19 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-19 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-19 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-19 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.18% | 1442.6327 | 1586.0509 | 3028.6836 | 95.5339 | 0.48088 | 0.51912 | 1.2404 | 77.0162 | 3105.6999 | 1479.6681 | 1626.0318
2016-11-19 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-19 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-19 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-19 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-19 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-19 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-19 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-20 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-20 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-20 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-20 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-20 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-20 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-20 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-20 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-20 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-20 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-20 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-20 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-20 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-20 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-20 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-20 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-20 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-20 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-20 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-20 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-20 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.75% | 1500.1007 | 1699.7986 | 3199.8993 | 181.3666 | 0.47876 | 0.52124 | 1.4788 | 122.6481 | 3322.5474 | 1558.8192 | 1763.7282
2016-11-20 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-20 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-20 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-21 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-21 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-21 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-21 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-21 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-21 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-21 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-21 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-21 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-21 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-21 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.8104 | 1690.3791 | 3195.1896 | 215.9718 | 0.48026 | 0.51974 | 1.4803 | 145.9014 | 3341.091 | 1574.8808 | 1766.2101
2016-11-21 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-21 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-21 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-21 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-21 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-21 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-21 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-21 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-21 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-21 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-21 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-21 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-21 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.3% | 1429.5732 | 1605.6401 | 3035.2134 | 106.5076 | 0.47652 | 0.52348 | 1.2383 | 86.0137 | 3121.2271 | 1470.5609 | 1650.6662
2016-11-22 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-22 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-22 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-22 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-22 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-22 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-22 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-22 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-22 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-22 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-22 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-22 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-22 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-22 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-22 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-22 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-22 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-22 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-22 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-22 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-22 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-22 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-22 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-22 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-23 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-23 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-23 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-23 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-23 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-23 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-23 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.63% | 1434.4783 | 1598.2825 | 3032.7608 | 94.5674 | 0.47816 | 0.52184 | 1.2391 | 76.3207 | 3109.0815 | 1470.9718 | 1638.1097
2016-11-23 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.76% | 1344.6856 | 1487.4402 | 2832.1258 | 75.4701 | 0.47882 | 0.52118 | 1.1915 | 63.339 | 2895.4647 | 1375.0135 | 1520.4512
2016-11-23 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.81% | 1345.384 | 1486.4624 | 2831.8464 | 79.3323 | 0.47907 | 0.52093 | 1.1916 | 66.5747 | 2898.4211 | 1377.2779 | 1521.1432
2016-11-23 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.59% | 1288.3264 | 1425.1757 | 2713.5021 | 56.8815 | 0.47793 | 0.52207 | 1.1434 | 49.7486 | 2763.2507 | 1312.1027 | 1451.1481
2016-11-23 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-23 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-23 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-23 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2669 | 1425.253 | 2713.5199 | 58.0411 | 0.47791 | 0.52209 | 1.1434 | 50.7631 | 2764.2831 | 1312.5269 | 1451.7562
2016-11-23 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.93% | 1293.017 | 1419.0779 | 2712.0949 | 58.6228 | 0.47967 | 0.52033 | 1.1439 | 51.2481 | 2763.3431 | 1317.599 | 1445.744
2016-11-23 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.97% | 1293.5521 | 1418.3823 | 2711.9344 | 54.1759 | 0.47987 | 0.52013 | 1.144 | 47.3582 | 2759.2926 | 1316.2777 | 1443.0149
2016-11-23 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.18% | 1296.2787 | 1414.8377 | 2711.1164 | 57.3204 | 0.48088 | 0.51912 | 1.1443 | 50.0937 | 2761.2101 | 1320.3676 | 1440.8425
2016-11-23 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.35% | 1285.1188 | 1429.3455 | 2714.4644 | 54.82 | 0.47674 | 0.52326 | 1.143 | 47.9606 | 2762.425 | 1307.9835 | 1454.4415
2016-11-23 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.33% | 1284.881 | 1429.6548 | 2714.5357 | 51.7216 | 0.47665 | 0.52335 | 1.143 | 45.2509 | 2759.7866 | 1306.4498 | 1453.3369
2016-11-23 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-23 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-23 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-23 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-23 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-24 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-24 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-24 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-24 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-24 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-24 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-24 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-24 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-24 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-24 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-24 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.05% | 1440.7759 | 1588.8361 | 3029.612 | 107.9859 | 0.48026 | 0.51974 | 1.2401 | 87.0763 | 3116.6884 | 1482.5951 | 1634.0933
2016-11-24 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.72% | 1435.7837 | 1596.3244 | 3032.1081 | 90.0229 | 0.47859 | 0.52141 | 1.2393 | 72.6403 | 3104.7484 | 1470.549 | 1634.1994
2016-11-24 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7251 | 1599.4123 | 3033.1374 | 95.645 | 0.47791 | 0.52209 | 1.239 | 77.1982 | 3110.3356 | 1470.6188 | 1639.7168
2016-11-24 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.58% | 1433.7164 | 1599.4254 | 3033.1418 | 96.7352 | 0.47791 | 0.52209 | 1.239 | 78.0782 | 3111.22 | 1471.0304 | 1640.1896
2016-11-24 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-24 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-24 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-24 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-24 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-24 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-24 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-24 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-24 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-24 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-25 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-25 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-25 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-25 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-25 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-25 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-25 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-25 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-25 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-25 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-25 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-25 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-25 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-25 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-25 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-25 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-25 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-25 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-25 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-25 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-25 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-25 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-25 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9847 | 1496.8214 | 2834.8061 | 74.7109 | 0.47643 | 0.52357 | 1.1906 | 62.752 | 2897.5581 | 1367.8819 | 1529.6762
2016-11-25 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.3% | 1338.2394 | 1496.4649 | 2834.7042 | 85.206 | 0.47652 | 0.52348 | 1.1906 | 71.565 | 2906.2693 | 1372.3419 | 1533.9274
2016-11-26 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.29% | 1337.9758 | 1496.8339 | 2834.8097 | 77.1856 | 0.47643 | 0.52357 | 1.1906 | 64.8307 | 2899.6404 | 1368.8631 | 1530.7773
2016-11-26 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.96% | 1333.4576 | 1503.1593 | 2836.617 | 76.9565 | 0.47482 | 0.52518 | 1.1899 | 64.6732 | 2901.2901 | 1364.1658 | 1537.1243
2016-11-26 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.7% | 1329.6781 | 1508.4507 | 2838.1288 | 75.1698 | 0.47348 | 0.52652 | 1.1894 | 63.2003 | 2901.3291 | 1359.6019 | 1541.7271
2016-11-26 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 94.57% | 1327.9552 | 1510.8627 | 2838.8179 | 73.4847 | 0.47286 | 0.52714 | 1.1891 | 61.7963 | 2900.6142 | 1357.1764 | 1543.4378
2016-11-26 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.17% | 1336.2933 | 1499.1894 | 2835.4827 | 78.6909 | 0.47583 | 0.52417 | 1.1903 | 66.1084 | 2901.591 | 1367.7497 | 1533.8413
2016-11-26 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.38% | 1285.6146 | 1428.701 | 2714.3156 | 56.1114 | 0.47692 | 0.52308 | 1.1431 | 49.0881 | 2763.4037 | 1309.0258 | 1454.3779
2016-11-26 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.63% | 1288.9515 | 1424.363 | 2713.3145 | 56.7405 | 0.47816 | 0.52184 | 1.1434 | 49.6223 | 2762.9368 | 1312.6789 | 1450.2579
2016-11-26 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.76% | 1293.8775 | 1422.6532 | 2716.5306 | 47.1688 | 0.47882 | 0.52118 | 1.1197 | 42.1261 | 2758.6568 | 1314.0483 | 1444.6085
2016-11-26 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.81% | 1294.5495 | 1421.8131 | 2716.3626 | 49.5827 | 0.47907 | 0.52093 | 1.1198 | 44.2794 | 2760.6421 | 1315.7624 | 1444.8796
2016-11-26 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.59% | 1291.4664 | 1425.667 | 2717.1334 | 47.4013 | 0.47793 | 0.52207 | 1.1195 | 42.3421 | 2759.4755 | 1311.7029 | 1447.7726
2016-11-26 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.05% | 1297.7656 | 1417.793 | 2715.5586 | 53.993 | 0.48026 | 0.51974 | 1.1201 | 48.2052 | 2763.7638 | 1320.9166 | 1442.8473
2016-11-26 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.72% | 1293.2689 | 1423.4139 | 2716.6828 | 45.0114 | 0.47859 | 0.52141 | 1.1196 | 40.2014 | 2756.8842 | 1312.5091 | 1444.3751
2016-11-26 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.58% | 1291.4146 | 1425.7317 | 2717.1463 | 47.8225 | 0.47791 | 0.52209 | 1.1195 | 42.7186 | 2759.865 | 1311.8302 | 1448.0347
2016-11-26 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.58% | 1291.4068 | 1425.7415 | 2717.1483 | 48.3676 | 0.47791 | 0.52209 | 1.1195 | 43.2056 | 2760.3539 | 1312.055 | 1448.2989
2016-11-26 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.93% | 1296.1684 | 1419.7895 | 2715.9579 | 48.8523 | 0.47967 | 0.52033 | 1.1199 | 43.6214 | 2759.5793 | 1317.0922 | 1442.4871
2016-11-26 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.97% | 1296.7048 | 1419.119 | 2715.8238 | 45.1466 | 0.47987 | 0.52013 | 1.12 | 40.3107 | 2756.1345 | 1316.0485 | 1440.0859
2016-11-26 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.18% | 1299.4381 | 1415.7024 | 2715.1405 | 47.767 | 0.48088 | 0.51912 | 1.1202 | 42.6407 | 2757.7812 | 1319.943 | 1437.8382
2016-11-26 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.35% | 1288.251 | 1429.6862 | 2717.9372 | 45.6833 | 0.47674 | 0.52326 | 1.1192 | 40.8184 | 2758.7557 | 1307.7107 | 1451.045
2016-11-26 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.33% | 1182.0905 | 1305.4378 | 2487.5282 | 22.4127 | 0.47665 | 0.52335 | 1.062 | 21.1049 | 2508.6332 | 1192.1501 | 1316.483
2016-11-26 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.47% | 1183.8087 | 1303.4962 | 2487.3049 | 22.4748 | 0.47734 | 0.52266 | 1.0621 | 21.1616 | 2508.4665 | 1193.91 | 1314.5565
2016-11-26 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.75% | 1187.3138 | 1299.5354 | 2486.8492 | 23.5777 | 0.47876 | 0.52124 | 1.0622 | 22.1962 | 2509.0454 | 1197.9403 | 1311.1051
2016-11-26 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 95.07% | 1178.8482 | 1309.1016 | 2487.9497 | 26.2175 | 0.47534 | 0.52466 | 1.0618 | 24.6917 | 2512.6414 | 1190.5852 | 1322.0562
2016-11-26 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.29% | 1287.4298 | 1430.7127 | 2718.1425 | 46.6943 | 0.47643 | 0.52357 | 1.1191 | 41.7246 | 2759.8671 | 1307.3088 | 1452.5583
2016-11-26 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.3% | 1287.6749 | 1430.4064 | 2718.0813 | 53.2538 | 0.47652 | 0.52348 | 1.1191 | 47.5849 | 2765.6662 | 1310.3502 | 1455.316
2016-11-27 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.29% | 1287.4212 | 1430.7235 | 2718.1447 | 48.241 | 0.47643 | 0.52357 | 1.1191 | 43.1067 | 2761.2514 | 1307.9585 | 1453.2929
2016-11-27 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.96% | 1279.9541 | 1436.0596 | 2716.0138 | 57.7174 | 0.47482 | 0.52518 | 1.1424 | 50.5208 | 2766.5346 | 1303.9425 | 1462.5921
2016-11-27 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.7% | 1276.3263 | 1440.7758 | 2717.1021 | 56.3774 | 0.47348 | 0.52652 | 1.142 | 49.3654 | 2766.4675 | 1299.6996 | 1466.7679
2016-11-27 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 94.57% | 1274.6726 | 1442.9257 | 2717.5982 | 55.1135 | 0.47286 | 0.52714 | 1.1419 | 48.2665 | 2765.8647 | 1297.496 | 1468.3688
2016-11-27 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.17% | 1282.676 | 1432.5211 | 2715.1972 | 59.0182 | 0.47583 | 0.52417 | 1.1427 | 51.6458 | 2766.843 | 1307.2507 | 1459.5922
2016-11-27 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.38% | 1285.6146 | 1428.701 | 2714.3156 | 56.1114 | 0.47692 | 0.52308 | 1.1431 | 49.0881 | 2763.4037 | 1309.0258 | 1454.3779
2016-11-27 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.63% | 1288.9515 | 1424.363 | 2713.3145 | 56.7405 | 0.47816 | 0.52184 | 1.1434 | 49.6223 | 2762.9368 | 1312.6789 | 1450.2579
2016-11-27 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.76% | 1290.7316 | 1422.0489 | 2712.7805 | 56.6026 | 0.47882 | 0.52118 | 1.1436 | 49.4931 | 2762.2736 | 1314.4299 | 1447.8438
2016-11-27 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.81% | 1291.402 | 1421.1774 | 2712.5794 | 59.4992 | 0.47907 | 0.52093 | 1.1437 | 52.0225 | 2764.6019 | 1316.3244 | 1448.2775
2016-11-27 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.59% | 1288.3264 | 1425.1757 | 2713.5021 | 56.8815 | 0.47793 | 0.52207 | 1.1434 | 49.7486 | 2763.2507 | 1312.1027 | 1451.1481
2016-11-27 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.05% | 1294.6103 | 1417.0067 | 2711.6169 | 64.7915 | 0.48026 | 0.51974 | 1.1441 | 56.6321 | 2768.249 | 1321.8083 | 1446.4407
2016-11-27 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.72% | 1290.1245 | 1422.8381 | 2712.9626 | 54.0137 | 0.47859 | 0.52141 | 1.1436 | 47.2322 | 2760.1949 | 1312.7296 | 1447.4653
2016-11-27 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2747 | 1425.2428 | 2713.5176 | 57.387 | 0.47791 | 0.52209 | 1.1434 | 50.191 | 2763.7086 | 1312.2615 | 1451.4471
2016-11-27 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.58% | 1288.2669 | 1425.253 | 2713.5199 | 58.0411 | 0.47791 | 0.52209 | 1.1434 | 50.7631 | 2764.2831 | 1312.5269 | 1451.7562
2016-11-27 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-27 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-27 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-27 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-27 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-27 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-27 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.75% | 1436.2666 | 1595.6 | 3031.8667 | 90.6833 | 0.47876 | 0.52124 | 1.2394 | 73.1684 | 3105.0351 | 1471.2964 | 1633.7386
2016-11-27 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.07% | 1426.026 | 1610.961 | 3036.987 | 100.8365 | 0.47534 | 0.52466 | 1.2377 | 81.4728 | 3118.4598 | 1464.7535 | 1653.7063
2016-11-27 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-27 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-28 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-28 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-28 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-28 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-28 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-28 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-28 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-28 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.76% | 1500.302 | 1699.396 | 3199.698 | 188.6753 | 0.47882 | 0.52118 | 1.4788 | 127.5851 | 3327.2831 | 1561.3923 | 1765.8908
2016-11-28 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.81% | 1501.0813 | 1697.8374 | 3198.9187 | 198.3306 | 0.47907 | 0.52093 | 1.4791 | 134.0916 | 3333.0103 | 1565.3203 | 1767.69
2016-11-28 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.59% | 1497.5063 | 1704.9874 | 3202.4937 | 189.605 | 0.47793 | 0.52207 | 1.4779 | 128.2911 | 3330.7849 | 1558.8202 | 1771.9647
2016-11-28 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.05% | 1504.8104 | 1690.3791 | 3195.1896 | 215.9718 | 0.48026 | 0.51974 | 1.4803 | 145.9014 | 3341.091 | 1574.8808 | 1766.2101
2016-11-28 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.72% | 1499.5963 | 1700.8073 | 3200.4037 | 180.0458 | 0.47859 | 0.52141 | 1.4786 | 121.7682 | 3322.1719 | 1557.8739 | 1764.2979
2016-11-28 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4462 | 1705.1075 | 3202.5538 | 191.2901 | 0.47791 | 0.52209 | 1.4779 | 129.433 | 3331.9867 | 1559.3033 | 1772.6834
2016-11-28 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.58% | 1497.4371 | 1705.1257 | 3202.5629 | 193.4705 | 0.47791 | 0.52209 | 1.4779 | 130.9086 | 3333.4714 | 1559.9991 | 1773.4724
2016-11-28 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.93% | 1502.9584 | 1694.0831 | 3197.0416 | 195.4092 | 0.47967 | 0.52033 | 1.4797 | 132.0629 | 3329.1045 | 1566.3047 | 1762.7997
2016-11-28 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.97% | 1503.5804 | 1692.8391 | 3196.4196 | 180.5864 | 0.47987 | 0.52013 | 1.4799 | 122.0289 | 3318.4485 | 1562.138 | 1756.3105
2016-11-28 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.18% | 1506.7497 | 1686.5005 | 3193.2503 | 191.0678 | 0.48088 | 0.51912 | 1.4809 | 129.0234 | 3322.2737 | 1568.7942 | 1753.4795
2016-11-28 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.35% | 1430.2129 | 1604.6807 | 3034.8936 | 91.3667 | 0.47674 | 0.52326 | 1.2384 | 73.7799 | 3108.6734 | 1465.3865 | 1643.2869
2016-11-28 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.33% | 1429.9482 | 1605.0778 | 3035.0259 | 86.2026 | 0.47665 | 0.52335 | 1.2383 | 69.6123 | 3104.6382 | 1463.1288 | 1641.5094
2016-11-28 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.47% | 1432.0266 | 1601.9601 | 3033.9867 | 86.4414 | 0.47734 | 0.52266 | 1.2387 | 69.7856 | 3103.7723 | 1465.3382 | 1638.434
2016-11-28 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.75% | 1500.1007 | 1699.7986 | 3199.8993 | 181.3666 | 0.47876 | 0.52124 | 1.4788 | 122.6481 | 3322.5474 | 1558.8192 | 1763.7282
2016-11-28 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.07% | 1489.405 | 1721.1901 | 3210.595 | 201.673 | 0.47534 | 0.52466 | 1.4753 | 136.6958 | 3347.2908 | 1554.3822 | 1792.9086
2016-11-28 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8257 | 1714.3486 | 3207.1743 | 186.7772 | 0.47643 | 0.52357 | 1.4764 | 126.5057 | 3333.68 | 1553.0973 | 1780.5827
2016-11-28 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.3% | 1493.1098 | 1713.7804 | 3206.8902 | 213.0151 | 0.47652 | 0.52348 | 1.4765 | 144.2679 | 3351.1581 | 1561.857 | 1789.3011
2016-11-29 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.29% | 1492.8157 | 1714.3686 | 3207.1843 | 192.9641 | 0.47643 | 0.52357 | 1.4764 | 130.6963 | 3337.8807 | 1555.0834 | 1782.7973
2016-11-29 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.96% | 1487.7747 | 1724.4507 | 3212.2253 | 192.3912 | 0.47482 | 0.52518 | 1.4748 | 130.4505 | 3342.6758 | 1549.7154 | 1792.9604
2016-11-29 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.7% | 1483.5578 | 1732.8845 | 3216.4422 | 187.9245 | 0.47348 | 0.52652 | 1.4735 | 127.5382 | 3343.9805 | 1543.944 | 1800.0365
2016-11-29 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 94.57% | 1481.6355 | 1736.7289 | 3218.3645 | 183.7118 | 0.47286 | 0.52714 | 1.4729 | 124.7311 | 3343.0956 | 1540.6162 | 1802.4794
2016-11-29 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.17% | 1490.9385 | 1718.123 | 3209.0615 | 196.7273 | 0.47583 | 0.52417 | 1.4758 | 133.2993 | 3342.3608 | 1554.3665 | 1787.9943
2016-11-29 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.38% | 1494.3542 | 1711.2916 | 3205.6458 | 187.038 | 0.47692 | 0.52308 | 1.4769 | 126.6405 | 3332.2863 | 1554.7518 | 1777.5345
2016-11-29 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.63% | 1498.2329 | 1703.5342 | 3201.7671 | 189.1349 | 0.47816 | 0.52184 | 1.4782 | 127.953 | 3329.72 | 1559.4148 | 1770.3052
2016-11-29 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.76% | 1436.4594 | 1595.311 | 3031.7703 | 94.3377 | 0.47882 | 0.52118 | 1.2394 | 76.115 | 3107.8853 | 1472.9047 | 1634.9806
2016-11-29 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.81% | 1437.2055 | 1594.1918 | 3031.3973 | 99.1653 | 0.47907 | 0.52093 | 1.2395 | 80.0021 | 3111.3993 | 1475.532 | 1635.8674
2016-11-29 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.59% | 1433.7826 | 1599.3261 | 3033.1087 | 94.8025 | 0.47793 | 0.52207 | 1.239 | 76.5176 | 3109.6263 | 1470.3525 | 1639.2738
2016-11-29 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.05% | 1348.7264 | 1481.7831 | 2830.5095 | 86.3887 | 0.48026 | 0.51974 | 1.1921 | 72.4675 | 2902.9769 | 1383.5295 | 1519.4474
2016-11-29 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.72% | 1344.0531 | 1488.3257 | 2832.3788 | 72.0183 | 0.47859 | 0.52141 | 1.1914 | 60.4466 | 2892.8253 | 1372.9825 | 1519.8428
2016-11-29 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.126 | 1491.0236 | 2833.1496 | 76.516 | 0.47791 | 0.52209 | 1.1912 | 64.2364 | 2897.386 | 1372.8251 | 1524.5608
2016-11-29 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.58% | 1342.1179 | 1491.035 | 2833.1529 | 77.3882 | 0.47791 | 0.52209 | 1.1912 | 64.9686 | 2898.1215 | 1373.1667 | 1524.9548
2016-11-29 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.93% | 1347.0665 | 1484.1069 | 2831.1734 | 78.1637 | 0.47967 | 0.52033 | 1.1919 | 65.5809 | 2896.7543 | 1378.5235 | 1518.2308
2016-11-29 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.97% | 1347.6239 | 1483.3265 | 2830.9504 | 72.2346 | 0.47987 | 0.52013 | 1.1919 | 60.6022 | 2891.5526 | 1376.7049 | 1514.8477
2016-11-29 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.18% | 1350.4645 | 1479.3497 | 2829.8142 | 76.4271 | 0.48088 | 0.51912 | 1.1924 | 64.0978 | 2893.912 | 1381.2877 | 1512.6243
2016-11-29 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.35% | 1338.8382 | 1495.6265 | 2834.4647 | 73.0934 | 0.47674 | 0.52326 | 1.1907 | 61.3871 | 2895.8519 | 1368.1037 | 1527.7481
2016-11-29 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.33% | 1338.5904 | 1495.9735 | 2834.5639 | 68.9621 | 0.47665 | 0.52335 | 1.1907 | 57.9192 | 2892.4831 | 1366.1975 | 1526.2856
2016-11-29 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.47% | 1340.536 | 1493.2496 | 2833.7856 | 69.1531 | 0.47734 | 0.52266 | 1.1909 | 58.0661 | 2891.8517 | 1368.2534 | 1523.5983
2016-11-29 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.75% | 1344.5052 | 1487.6928 | 2832.1979 | 72.5466 | 0.47876 | 0.52124 | 1.1915 | 60.8867 | 2893.0846 | 1373.655 | 1519.4296
2016-11-29 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.07% | 1334.9188 | 1501.1137 | 2836.0325 | 80.6692 | 0.47534 | 0.52466 | 1.1901 | 67.7814 | 2903.8139 | 1367.1382 | 1536.6757
2016-11-29 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.29% | 1429.3012 | 1606.0482 | 3035.3494 | 93.3886 | 0.47643 | 0.52357 | 1.2382 | 75.4219 | 3110.7713 | 1465.2347 | 1645.5365
2016-11-29 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.3% | 1429.5732 | 1605.6401 | 3035.2134 | 106.5076 | 0.47652 | 0.52348 | 1.2383 | 86.0137 | 3121.2271 | 1470.5609 | 1650.6662
2016-11-30 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-11-30 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-11-30 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-11-30 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-11-30 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-11-30 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-11-30 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.73% | 1480.9484 | 1528.5774 | 3009.5258 | 106.7995 | 0.49365 | 0.50635 | 1.2468 | 85.6572 | 3095.183 | 1523.233 | 1571.95
2016-11-30 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.83% | 1482.4242 | 1526.3636 | 3008.7879 | 106.4664 | 0.49414 | 0.50586 | 1.2471 | 85.3732 | 3094.1611 | 1524.6107 | 1569.5504
2016-11-30 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.39% | 1475.781 | 1536.3285 | 3012.1095 | 105.1751 | 0.49193 | 0.50807 | 1.246 | 84.4127 | 3096.5221 | 1517.3059 | 1579.2162
2016-11-30 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.1% | 1471.5236 | 1542.7147 | 3014.2382 | 102.8258 | 0.49051 | 0.50949 | 1.2453 | 82.5742 | 3096.8124 | 1512.0269 | 1584.7856
2016-11-30 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-11-30 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-11-30 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-11-30 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-11-30 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-11-30 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-11-30 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-11-30 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-11-30 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-11-30 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-11-30 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-11-30 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-11-30 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4458 | 1374.3205 | 2701.7663 | 54.0187 | 0.49244 | 0.50756 | 1.1477 | 47.0656 | 2748.8319 | 1350.6228 | 1398.2091
2016-11-30 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.4506 | 1375.6143 | 2702.0648 | 53.6952 | 0.49207 | 0.50793 | 1.1476 | 46.7883 | 2748.8531 | 1349.4737 | 1399.3794
2016-12-01 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.8146 | 1386.841 | 2704.6556 | 59.9793 | 0.48887 | 0.51113 | 1.1467 | 52.3078 | 2756.9634 | 1343.3861 | 1413.5773
2016-12-01 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-01 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-01 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-01 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-01 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-01 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-01 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-01 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-01 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-01 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-01 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-01 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-01 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-01 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-01 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-01 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-01 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-01 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-01 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-01 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-01 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-01 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.49% | 1477.3187 | 1534.022 | 3011.3407 | 90.0312 | 0.49244 | 0.50756 | 1.2462 | 72.2434 | 3083.5841 | 1512.8942 | 1570.6899
2016-12-01 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-02 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.6001 | 1550.0998 | 3016.6999 | 99.9654 | 0.48887 | 0.51113 | 1.2444 | 80.3301 | 3097.03 | 1505.8708 | 1591.1592
2016-12-02 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8618 | 1588.7073 | 3029.5691 | 94.9364 | 0.48029 | 0.51971 | 1.2401 | 76.5527 | 3106.1218 | 1477.6291 | 1628.4927
2016-12-02 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.54% | 1433.1356 | 1600.2966 | 3033.4322 | 93.0661 | 0.47771 | 0.52229 | 1.2389 | 75.1226 | 3108.5548 | 1469.0226 | 1639.5322
2016-12-02 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.89% | 1438.3363 | 1592.4955 | 3030.8318 | 92.2133 | 0.47945 | 0.52055 | 1.2397 | 74.3822 | 3105.214 | 1473.9985 | 1631.2155
2016-12-02 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.88% | 1453.1488 | 1570.2768 | 3023.4256 | 98.7086 | 0.48438 | 0.51562 | 1.2422 | 79.4633 | 3102.8889 | 1491.6394 | 1611.2495
2016-12-02 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-02 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-02 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-02 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-02 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-02 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-02 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-02 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-02 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-02 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-02 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-02 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-02 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-02 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-02 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-02 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-02 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.43% | 1326.6607 | 1375.341 | 2702.0018 | 51.8268 | 0.49215 | 0.50785 | 1.1476 | 45.1593 | 2747.161 | 1348.8858 | 1398.2752
2016-12-02 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-02 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-03 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-03 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-03 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-03 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-03 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-03 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-03 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-03 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-03 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-03 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-03 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-03 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-03 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-03 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-03 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-03 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-03 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-03 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-03 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.53% | 1478.0186 | 1532.9721 | 3010.9907 | 84.7611 | 0.49267 | 0.50733 | 1.2463 | 68.0082 | 3078.9989 | 1511.5244 | 1567.4745
2016-12-03 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.64% | 1479.6417 | 1530.5375 | 3010.1792 | 89.2806 | 0.49321 | 0.50679 | 1.2466 | 71.6189 | 3081.798 | 1514.9651 | 1566.833
2016-12-03 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.62% | 1479.3252 | 1531.0122 | 3010.3374 | 90.683 | 0.49311 | 0.50689 | 1.2466 | 72.747 | 3083.0844 | 1515.1974 | 1567.887
2016-12-03 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.43% | 1542.0648 | 1615.8704 | 3157.9352 | 172.7559 | 0.49215 | 0.50785 | 1.4921 | 115.7766 | 3273.7118 | 1599.0441 | 1674.6678
2016-12-03 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-03 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886
2016-12-04 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-04 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-04 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-04 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-04 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-04 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-04 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-04 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-04 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.39% | 1541.3713 | 1617.2574 | 3158.6287 | 210.3502 | 0.49193 | 0.50807 | 1.4919 | 140.9923 | 3299.621 | 1610.7292 | 1688.8918
2016-12-04 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.1% | 1536.9246 | 1626.1508 | 3163.0754 | 205.6517 | 0.49051 | 0.50949 | 1.4905 | 137.9742 | 3301.0496 | 1604.6021 | 1696.4476
2016-12-04 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.7699 | 1616.4603 | 3158.2301 | 170.041 | 0.49205 | 0.50795 | 1.4921 | 113.9644 | 3272.1945 | 1597.8465 | 1674.348
2016-12-04 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.45% | 1476.7869 | 1534.8197 | 3011.6066 | 85.7606 | 0.49226 | 0.50774 | 1.2461 | 68.8215 | 3080.428 | 1510.6651 | 1569.763
2016-12-04 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.42% | 1476.318 | 1535.523 | 3011.841 | 89.4564 | 0.49211 | 0.50789 | 1.2461 | 71.7918 | 3083.6328 | 1511.6472 | 1571.9856
2016-12-04 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.61% | 1479.1661 | 1531.2509 | 3010.417 | 94.2773 | 0.49306 | 0.50694 | 1.2465 | 75.6319 | 3086.0489 | 1516.4568 | 1569.5921
2016-12-04 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.67% | 1480.0961 | 1529.8559 | 3009.952 | 92.6176 | 0.49337 | 0.50663 | 1.2467 | 74.2913 | 3084.2432 | 1516.7488 | 1567.4944
2016-12-04 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.74% | 1481.1589 | 1528.2616 | 3009.4205 | 93.2654 | 0.49372 | 0.50628 | 1.2469 | 74.8002 | 3084.2208 | 1518.0893 | 1566.1315
2016-12-04 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-04 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-04 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-04 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-04 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-04 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-04 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-04 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-05 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-05 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-05 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-05 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-05 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-05 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-05 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-05 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-05 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-05 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-05 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-05 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-05 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-05 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-05 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-05 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-05 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-05 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-05 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.53% | 1221.8287 | 1260.5335 | 2482.3623 | 22.0379 | 0.49267 | 0.50733 | 1.064 | 20.7114 | 2503.0736 | 1232.0327 | 1271.041
2016-12-05 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1704 | 1259.0174 | 2482.1878 | 23.2129 | 0.49321 | 0.50679 | 1.0641 | 21.8143 | 2504.0021 | 1233.9295 | 1270.0726
2016-12-05 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-12-05 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-12-05 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4458 | 1374.3205 | 2701.7663 | 54.0187 | 0.49244 | 0.50756 | 1.1477 | 47.0656 | 2748.8319 | 1350.6228 | 1398.2091
2016-12-05 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.4506 | 1375.6143 | 2702.0648 | 53.6952 | 0.49207 | 0.50793 | 1.1476 | 46.7883 | 2748.8531 | 1349.4737 | 1399.3794
2016-12-06 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.77% | 1321.0265 | 1388.7169 | 2709.7434 | 49.9827 | 0.48887 | 0.51113 | 1.1222 | 44.5393 | 2754.2827 | 1342.8003 | 1411.4824
2016-12-06 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8429 | 1417.6963 | 2715.5393 | 47.4682 | 0.48029 | 0.51971 | 1.1201 | 42.3796 | 2757.9189 | 1318.1973 | 1439.7216
2016-12-06 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.54% | 1290.8836 | 1426.3954 | 2717.2791 | 46.533 | 0.47771 | 0.52229 | 1.1194 | 41.5686 | 2758.8477 | 1310.7415 | 1448.1062
2016-12-06 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.89% | 1295.5681 | 1420.5398 | 2716.108 | 46.1067 | 0.47945 | 0.52055 | 1.1199 | 41.1718 | 2757.2797 | 1315.3077 | 1441.972
2016-12-06 04:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.88% | 1308.9103 | 1403.8621 | 2712.7724 | 49.3543 | 0.48438 | 0.51562 | 1.1211 | 44.0233 | 2756.7957 | 1330.2344 | 1426.5613
2016-12-06 05:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.3% | 1328.1016 | 1379.8729 | 2707.9746 | 51.2164 | 0.49148 | 0.50852 | 1.1229 | 45.612 | 2753.5866 | 1350.5192 | 1403.0673
2016-12-06 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.73% | 1224.2507 | 1257.7967 | 2482.0474 | 27.7679 | 0.49365 | 0.50635 | 1.0642 | 26.0934 | 2508.1408 | 1237.1316 | 1271.0091
2016-12-06 07:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.83% | 1225.4707 | 1256.4181 | 2481.8888 | 27.6813 | 0.49414 | 0.50586 | 1.0642 | 26.0104 | 2507.8992 | 1238.3235 | 1269.5757
2016-12-06 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.2961 | 1378.3799 | 2707.676 | 52.5875 | 0.49193 | 0.50807 | 1.123 | 46.8285 | 2754.5045 | 1352.3323 | 1402.1722
2016-12-06 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.4612 | 1383.1735 | 2708.6347 | 51.4129 | 0.49051 | 0.50949 | 1.1226 | 45.797 | 2754.4317 | 1347.925 | 1406.5067
2016-12-06 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6398 | 1377.9502 | 2707.59 | 42.5102 | 0.49205 | 0.50795 | 1.123 | 37.8537 | 2745.4438 | 1348.2659 | 1397.1779
2016-12-06 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.45% | 1330.2021 | 1377.2474 | 2707.4495 | 42.8803 | 0.49226 | 0.50774 | 1.1231 | 38.1815 | 2745.6309 | 1348.9974 | 1396.6336
2016-12-06 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7798 | 1377.7753 | 2707.5551 | 44.7282 | 0.49211 | 0.50789 | 1.123 | 39.8283 | 2747.3833 | 1349.3795 | 1398.0038
2016-12-06 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.3451 | 1374.5686 | 2706.9137 | 47.1386 | 0.49306 | 0.50694 | 1.1233 | 41.9658 | 2748.8795 | 1353.0366 | 1395.8429
2016-12-06 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1829 | 1373.5214 | 2706.7043 | 46.3088 | 0.49337 | 0.50663 | 1.1233 | 41.2242 | 2747.9285 | 1353.5214 | 1394.407
2016-12-06 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.74% | 1334.1402 | 1372.3248 | 2706.465 | 46.6327 | 0.49372 | 0.50628 | 1.1234 | 41.5092 | 2747.9742 | 1354.6341 | 1393.3401
2016-12-06 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-06 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-06 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-06 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-06 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-12-06 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-12-06 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4458 | 1374.3205 | 2701.7663 | 54.0187 | 0.49244 | 0.50756 | 1.1477 | 47.0656 | 2748.8319 | 1350.6228 | 1398.2091
2016-12-06 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-07 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-07 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-07 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-07 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-07 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-07 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-07 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-07 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-07 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-07 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-07 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-07 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-07 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-07 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-07 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-07 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-07 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-07 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-07 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-07 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-07 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-07 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-07 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-07 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-08 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-08 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-08 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-08 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-08 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-08 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-08 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-08 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-08 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-08 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-08 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-08 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-08 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-08 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-08 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-08 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-08 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-08 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-08 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-08 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-08 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-08 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-08 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-08 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-09 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.6001 | 1550.0998 | 3016.6999 | 99.9654 | 0.48887 | 0.51113 | 1.2444 | 80.3301 | 3097.03 | 1505.8708 | 1591.1592
2016-12-09 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8618 | 1588.7073 | 3029.5691 | 94.9364 | 0.48029 | 0.51971 | 1.2401 | 76.5527 | 3106.1218 | 1477.6291 | 1628.4927
2016-12-09 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.54% | 1433.1356 | 1600.2966 | 3033.4322 | 93.0661 | 0.47771 | 0.52229 | 1.2389 | 75.1226 | 3108.5548 | 1469.0226 | 1639.5322
2016-12-09 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.89% | 1438.3363 | 1592.4955 | 3030.8318 | 92.2133 | 0.47945 | 0.52055 | 1.2397 | 74.3822 | 3105.214 | 1473.9985 | 1631.2155
2016-12-09 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.88% | 1453.1488 | 1570.2768 | 3023.4256 | 98.7086 | 0.48438 | 0.51562 | 1.2422 | 79.4633 | 3102.8889 | 1491.6394 | 1611.2495
2016-12-09 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.3% | 1474.4549 | 1538.3176 | 3012.7725 | 102.4328 | 0.49148 | 0.50852 | 1.2457 | 82.2263 | 3094.9988 | 1514.8679 | 1580.1309
2016-12-09 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-09 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-09 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-09 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-09 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-09 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-09 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-09 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-09 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-09 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-09 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-09 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-09 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-09 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-09 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-09 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-09 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-09 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-10 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-10 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-10 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-10 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-10 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-10 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-10 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.73% | 1333.9505 | 1372.5618 | 2706.5124 | 53.3998 | 0.49365 | 0.50635 | 1.1234 | 47.5335 | 2754.0459 | 1357.4155 | 1396.6305
2016-12-10 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.83% | 1335.2799 | 1370.9001 | 2706.18 | 53.2332 | 0.49414 | 0.50586 | 1.1235 | 47.3801 | 2753.5601 | 1358.6924 | 1394.8677
2016-12-10 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.2961 | 1378.3799 | 2707.676 | 52.5875 | 0.49193 | 0.50807 | 1.123 | 46.8285 | 2754.5045 | 1352.3323 | 1402.1722
2016-12-10 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-10 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-10 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-10 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-10 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-10 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-10 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-10 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-10 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-10 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-10 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-10 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.62% | 1479.3252 | 1531.0122 | 3010.3374 | 90.683 | 0.49311 | 0.50689 | 1.2466 | 72.747 | 3083.0844 | 1515.1974 | 1567.887
2016-12-10 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.43% | 1476.445 | 1535.3325 | 3011.7775 | 86.3779 | 0.49215 | 0.50785 | 1.2461 | 69.3201 | 3081.0976 | 1510.5608 | 1570.5368
2016-12-10 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-10 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886
2016-12-11 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-11 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-11 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-11 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-11 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-11 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-11 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-11 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-11 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.39% | 1475.781 | 1536.3285 | 3012.1095 | 105.1751 | 0.49193 | 0.50807 | 1.246 | 84.4127 | 3096.5221 | 1517.3059 | 1579.2162
2016-12-11 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.1% | 1471.5236 | 1542.7147 | 3014.2382 | 102.8258 | 0.49051 | 0.50949 | 1.2453 | 82.5742 | 3096.8124 | 1512.0269 | 1584.7856
2016-12-11 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-11 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-11 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-11 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-11 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-11 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-11 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-11 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-11 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-11 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-11 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-11 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-11 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-11 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-12 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-12 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-12 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-12 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-12 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-12 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-12 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-12 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-12 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-12 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-12 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-12 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-12 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-12 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-12 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-12 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-12 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-12 17:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.75% | 1224.4564 | 1257.5643 | 2482.0207 | 22.1742 | 0.49373 | 0.50627 | 1.0642 | 20.8368 | 2502.8574 | 1234.7442 | 1268.1133
2016-12-12 18:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.53% | 1221.8287 | 1260.5335 | 2482.3623 | 22.0379 | 0.49267 | 0.50733 | 1.064 | 20.7114 | 2503.0736 | 1232.0327 | 1271.041
2016-12-12 19:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.64% | 1223.1704 | 1259.0174 | 2482.1878 | 23.2129 | 0.49321 | 0.50679 | 1.0641 | 21.8143 | 2504.0021 | 1233.9295 | 1270.0726
2016-12-12 20:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.62% | 1222.9088 | 1259.313 | 2482.2218 | 23.5776 | 0.49311 | 0.50689 | 1.0641 | 22.1572 | 2504.3791 | 1233.8348 | 1270.5443
2016-12-12 21:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.43% | 1220.5279 | 1262.0035 | 2482.5314 | 22.4583 | 0.49215 | 0.50785 | 1.064 | 21.1078 | 2503.6392 | 1230.916 | 1272.7231
2016-12-12 22:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.49% | 1221.2501 | 1261.1874 | 2482.4375 | 23.4081 | 0.49244 | 0.50756 | 1.064 | 21.9997 | 2504.4372 | 1232.0837 | 1272.3536
2016-12-12 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6835 | 1377.8956 | 2707.5791 | 44.746 | 0.49207 | 0.50793 | 1.123 | 39.8444 | 2747.4236 | 1349.2898 | 1398.1338
2016-12-13 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.77% | 1321.0265 | 1388.7169 | 2709.7434 | 49.9827 | 0.48887 | 0.51113 | 1.1222 | 44.5393 | 2754.2827 | 1342.8003 | 1411.4824
2016-12-13 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6874 | 1416.9064 | 2711.5938 | 56.9618 | 0.48029 | 0.51971 | 1.1441 | 49.788 | 2761.3818 | 1318.6 | 1442.7818
2016-12-13 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.54% | 1287.7451 | 1425.9314 | 2713.6765 | 55.8396 | 0.47771 | 0.52229 | 1.1433 | 48.8402 | 2762.5167 | 1311.0766 | 1451.4401
2016-12-13 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.89% | 1292.4182 | 1419.8564 | 2712.2746 | 55.328 | 0.47945 | 0.52055 | 1.1438 | 48.3707 | 2760.6452 | 1315.6092 | 1445.036
2016-12-13 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.88% | 1305.7279 | 1402.5537 | 2708.2816 | 59.2252 | 0.48438 | 0.51562 | 1.1453 | 51.7108 | 2759.9924 | 1330.7757 | 1429.2167
2016-12-13 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-13 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.73% | 1333.9505 | 1372.5618 | 2706.5124 | 53.3998 | 0.49365 | 0.50635 | 1.1234 | 47.5335 | 2754.0459 | 1357.4155 | 1396.6305
2016-12-13 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.83% | 1335.2799 | 1370.9001 | 2706.18 | 53.2332 | 0.49414 | 0.50586 | 1.1235 | 47.3801 | 2753.5601 | 1358.6924 | 1394.8677
2016-12-13 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.2961 | 1378.3799 | 2707.676 | 52.5875 | 0.49193 | 0.50807 | 1.123 | 46.8285 | 2754.5045 | 1352.3323 | 1402.1722
2016-12-13 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-13 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-13 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-13 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-13 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-13 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-13 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-13 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-13 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-13 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-13 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-13 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-13 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-13 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-13 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-14 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-14 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8618 | 1588.7073 | 3029.5691 | 94.9364 | 0.48029 | 0.51971 | 1.2401 | 76.5527 | 3106.1218 | 1477.6291 | 1628.4927
2016-12-14 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-14 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-14 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-14 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-14 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-14 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-14 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-14 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.1% | 1471.5236 | 1542.7147 | 3014.2382 | 102.8258 | 0.49051 | 0.50949 | 1.2453 | 82.5742 | 3096.8124 | 1512.0269 | 1584.7856
2016-12-14 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.1626 | 1535.756 | 3011.9187 | 85.0205 | 0.49205 | 0.50795 | 1.246 | 68.2333 | 3080.1519 | 1509.7371 | 1570.4148
2016-12-14 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.45% | 1476.7869 | 1534.8197 | 3011.6066 | 85.7606 | 0.49226 | 0.50774 | 1.2461 | 68.8215 | 3080.428 | 1510.6651 | 1569.763
2016-12-14 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.42% | 1476.318 | 1535.523 | 3011.841 | 89.4564 | 0.49211 | 0.50789 | 1.2461 | 71.7918 | 3083.6328 | 1511.6472 | 1571.9856
2016-12-14 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.61% | 1479.1661 | 1531.2509 | 3010.417 | 94.2773 | 0.49306 | 0.50694 | 1.2465 | 75.6319 | 3086.0489 | 1516.4568 | 1569.5921
2016-12-14 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.67% | 1480.0961 | 1529.8559 | 3009.952 | 92.6176 | 0.49337 | 0.50663 | 1.2467 | 74.2913 | 3084.2432 | 1516.7488 | 1567.4944
2016-12-14 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.74% | 1481.1589 | 1528.2616 | 3009.4205 | 93.2654 | 0.49372 | 0.50628 | 1.2469 | 74.8002 | 3084.2208 | 1518.0893 | 1566.1315
2016-12-14 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.7% | 1480.4974 | 1529.2539 | 3009.7513 | 85.6355 | 0.4935 | 0.5065 | 1.2467 | 68.687 | 3078.4383 | 1514.3944 | 1564.0439
2016-12-14 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.75% | 1481.1972 | 1528.2042 | 3009.4014 | 85.2852 | 0.49373 | 0.50627 | 1.2469 | 68.3997 | 3077.8011 | 1514.9684 | 1562.8327
2016-12-14 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.53% | 1478.0186 | 1532.9721 | 3010.9907 | 84.7611 | 0.49267 | 0.50733 | 1.2463 | 68.0082 | 3078.9989 | 1511.5244 | 1567.4745
2016-12-14 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.64% | 1479.6417 | 1530.5375 | 3010.1792 | 89.2806 | 0.49321 | 0.50679 | 1.2466 | 71.6189 | 3081.798 | 1514.9651 | 1566.833
2016-12-14 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.62% | 1479.3252 | 1531.0122 | 3010.3374 | 90.683 | 0.49311 | 0.50689 | 1.2466 | 72.747 | 3083.0844 | 1515.1974 | 1567.887
2016-12-14 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.43% | 1542.0648 | 1615.8704 | 3157.9352 | 172.7559 | 0.49215 | 0.50785 | 1.4921 | 115.7766 | 3273.7118 | 1599.0441 | 1674.6678
2016-12-14 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-14 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886
2016-12-15 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-15 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-15 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-15 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-15 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-15 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-15 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-15 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-15 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.39% | 1541.3713 | 1617.2574 | 3158.6287 | 210.3502 | 0.49193 | 0.50807 | 1.4919 | 140.9923 | 3299.621 | 1610.7292 | 1688.8918
2016-12-15 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.1% | 1536.9246 | 1626.1508 | 3163.0754 | 205.6517 | 0.49051 | 0.50949 | 1.4905 | 137.9742 | 3301.0496 | 1604.6021 | 1696.4476
2016-12-15 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.7699 | 1616.4603 | 3158.2301 | 170.041 | 0.49205 | 0.50795 | 1.4921 | 113.9644 | 3272.1945 | 1597.8465 | 1674.348
2016-12-15 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.45% | 1542.4218 | 1615.1563 | 3157.5782 | 171.5211 | 0.49226 | 0.50774 | 1.4923 | 114.9403 | 3272.5185 | 1599.0026 | 1673.5159
2016-12-15 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.42% | 1541.9321 | 1616.1357 | 3158.0679 | 178.9128 | 0.49211 | 0.50789 | 1.4921 | 119.9062 | 3277.9741 | 1600.9387 | 1677.0354
2016-12-15 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.61% | 1544.9068 | 1610.1865 | 3155.0932 | 188.5546 | 0.49306 | 0.50694 | 1.4931 | 126.2877 | 3281.381 | 1607.1736 | 1674.2074
2016-12-15 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.67% | 1545.8781 | 1608.2437 | 3154.1219 | 185.2353 | 0.49337 | 0.50663 | 1.4934 | 124.0388 | 3278.1607 | 1607.0746 | 1671.0861
2016-12-15 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.74% | 1546.9882 | 1606.0236 | 3153.0118 | 186.5308 | 0.49372 | 0.50628 | 1.4937 | 124.8767 | 3277.8885 | 1608.6423 | 1669.2462
2016-12-15 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.7% | 1546.2973 | 1607.4054 | 3153.7027 | 171.271 | 0.4935 | 0.5065 | 1.4935 | 114.6777 | 3268.3804 | 1602.8907 | 1665.4897
2016-12-15 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.75% | 1547.0282 | 1605.9436 | 3152.9718 | 170.5705 | 0.49373 | 0.50627 | 1.4937 | 114.1908 | 3267.1626 | 1603.4079 | 1663.7547
2016-12-15 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.53% | 1543.7083 | 1612.5833 | 3156.2917 | 169.5222 | 0.49267 | 0.50733 | 1.4927 | 113.5695 | 3269.8612 | 1599.661 | 1670.2002
2016-12-15 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.64% | 1545.4035 | 1609.193 | 3154.5965 | 178.5611 | 0.49321 | 0.50679 | 1.4932 | 119.5817 | 3274.1782 | 1604.3829 | 1669.7953
2016-12-15 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.62% | 1545.073 | 1609.854 | 3154.927 | 181.3661 | 0.49311 | 0.50689 | 1.4931 | 121.4688 | 3276.3958 | 1604.9703 | 1671.4255
2016-12-15 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.43% | 1542.0648 | 1615.8704 | 3157.9352 | 172.7559 | 0.49215 | 0.50785 | 1.4921 | 115.7766 | 3273.7118 | 1599.0441 | 1674.6678
2016-12-15 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-15 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886
2016-12-16 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-16 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-16 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-16 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-16 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-16 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-16 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-16 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.83% | 1482.4242 | 1526.3636 | 3008.7879 | 106.4664 | 0.49414 | 0.50586 | 1.2471 | 85.3732 | 3094.1611 | 1524.6107 | 1569.5504
2016-12-16 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.39% | 1475.781 | 1536.3285 | 3012.1095 | 105.1751 | 0.49193 | 0.50807 | 1.246 | 84.4127 | 3096.5221 | 1517.3059 | 1579.2162
2016-12-16 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-16 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-16 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-16 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-16 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-16 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-16 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-16 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-16 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-16 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-16 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-16 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-16 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-16 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-16 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-17 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-17 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-17 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-17 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-17 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-17 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-17 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.73% | 1333.9505 | 1372.5618 | 2706.5124 | 53.3998 | 0.49365 | 0.50635 | 1.1234 | 47.5335 | 2754.0459 | 1357.4155 | 1396.6305
2016-12-17 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.83% | 1335.2799 | 1370.9001 | 2706.18 | 53.2332 | 0.49414 | 0.50586 | 1.1235 | 47.3801 | 2753.5601 | 1358.6924 | 1394.8677
2016-12-17 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.2961 | 1378.3799 | 2707.676 | 52.5875 | 0.49193 | 0.50807 | 1.123 | 46.8285 | 2754.5045 | 1352.3323 | 1402.1722
2016-12-17 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.4612 | 1383.1735 | 2708.6347 | 51.4129 | 0.49051 | 0.50949 | 1.1226 | 45.797 | 2754.4317 | 1347.925 | 1406.5067
2016-12-17 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6398 | 1377.9502 | 2707.59 | 42.5102 | 0.49205 | 0.50795 | 1.123 | 37.8537 | 2745.4438 | 1348.2659 | 1397.1779
2016-12-17 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.45% | 1330.2021 | 1377.2474 | 2707.4495 | 42.8803 | 0.49226 | 0.50774 | 1.1231 | 38.1815 | 2745.6309 | 1348.9974 | 1396.6336
2016-12-17 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7798 | 1377.7753 | 2707.5551 | 44.7282 | 0.49211 | 0.50789 | 1.123 | 39.8283 | 2747.3833 | 1349.3795 | 1398.0038
2016-12-17 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.3451 | 1374.5686 | 2706.9137 | 47.1386 | 0.49306 | 0.50694 | 1.1233 | 41.9658 | 2748.8795 | 1353.0366 | 1395.8429
2016-12-17 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1829 | 1373.5214 | 2706.7043 | 46.3088 | 0.49337 | 0.50663 | 1.1233 | 41.2242 | 2747.9285 | 1353.5214 | 1394.407
2016-12-17 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.74% | 1334.1402 | 1372.3248 | 2706.465 | 46.6327 | 0.49372 | 0.50628 | 1.1234 | 41.5092 | 2747.9742 | 1354.6341 | 1393.3401
2016-12-17 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-17 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-17 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-17 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-17 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-12-17 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-12-17 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4458 | 1374.3205 | 2701.7663 | 54.0187 | 0.49244 | 0.50756 | 1.1477 | 47.0656 | 2748.8319 | 1350.6228 | 1398.2091
2016-12-17 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.4506 | 1375.6143 | 2702.0648 | 53.6952 | 0.49207 | 0.50793 | 1.1476 | 46.7883 | 2748.8531 | 1349.4737 | 1399.3794
2016-12-18 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.8146 | 1386.841 | 2704.6556 | 59.9793 | 0.48887 | 0.51113 | 1.1467 | 52.3078 | 2756.9634 | 1343.3861 | 1413.5773
2016-12-18 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6874 | 1416.9064 | 2711.5938 | 56.9618 | 0.48029 | 0.51971 | 1.1441 | 49.788 | 2761.3818 | 1318.6 | 1442.7818
2016-12-18 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.54% | 1287.7451 | 1425.9314 | 2713.6765 | 55.8396 | 0.47771 | 0.52229 | 1.1433 | 48.8402 | 2762.5167 | 1311.0766 | 1451.4401
2016-12-18 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.89% | 1292.4182 | 1419.8564 | 2712.2746 | 55.328 | 0.47945 | 0.52055 | 1.1438 | 48.3707 | 2760.6452 | 1315.6092 | 1445.036
2016-12-18 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.88% | 1305.7279 | 1402.5537 | 2708.2816 | 59.2252 | 0.48438 | 0.51562 | 1.1453 | 51.7108 | 2759.9924 | 1330.7757 | 1429.2167
2016-12-18 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-18 06:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.73% | 1333.9505 | 1372.5618 | 2706.5124 | 53.3998 | 0.49365 | 0.50635 | 1.1234 | 47.5335 | 2754.0459 | 1357.4155 | 1396.6305
2016-12-18 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.83% | 1335.2799 | 1370.9001 | 2706.18 | 53.2332 | 0.49414 | 0.50586 | 1.1235 | 47.3801 | 2753.5601 | 1358.6924 | 1394.8677
2016-12-18 08:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.39% | 1329.2961 | 1378.3799 | 2707.676 | 52.5875 | 0.49193 | 0.50807 | 1.123 | 46.8285 | 2754.5045 | 1352.3323 | 1402.1722
2016-12-18 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.4612 | 1383.1735 | 2708.6347 | 51.4129 | 0.49051 | 0.50949 | 1.1226 | 45.797 | 2754.4317 | 1347.925 | 1406.5067
2016-12-18 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6398 | 1377.9502 | 2707.59 | 42.5102 | 0.49205 | 0.50795 | 1.123 | 37.8537 | 2745.4438 | 1348.2659 | 1397.1779
2016-12-18 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.45% | 1330.2021 | 1377.2474 | 2707.4495 | 42.8803 | 0.49226 | 0.50774 | 1.1231 | 38.1815 | 2745.6309 | 1348.9974 | 1396.6336
2016-12-18 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7798 | 1377.7753 | 2707.5551 | 44.7282 | 0.49211 | 0.50789 | 1.123 | 39.8283 | 2747.3833 | 1349.3795 | 1398.0038
2016-12-18 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.3451 | 1374.5686 | 2706.9137 | 47.1386 | 0.49306 | 0.50694 | 1.1233 | 41.9658 | 2748.8795 | 1353.0366 | 1395.8429
2016-12-18 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1829 | 1373.5214 | 2706.7043 | 46.3088 | 0.49337 | 0.50663 | 1.1233 | 41.2242 | 2747.9285 | 1353.5214 | 1394.407
2016-12-18 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.74% | 1334.1402 | 1372.3248 | 2706.465 | 46.6327 | 0.49372 | 0.50628 | 1.1234 | 41.5092 | 2747.9742 | 1354.6341 | 1393.3401
2016-12-18 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-18 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-18 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-18 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-18 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-18 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.43% | 1326.6607 | 1375.341 | 2702.0018 | 51.8268 | 0.49215 | 0.50785 | 1.1476 | 45.1593 | 2747.161 | 1348.8858 | 1398.2752
2016-12-18 22:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.49% | 1327.4458 | 1374.3205 | 2701.7663 | 54.0187 | 0.49244 | 0.50756 | 1.1477 | 47.0656 | 2748.8319 | 1350.6228 | 1398.2091
2016-12-18 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.4506 | 1375.6143 | 2702.0648 | 53.6952 | 0.49207 | 0.50793 | 1.1476 | 46.7883 | 2748.8531 | 1349.4737 | 1399.3794
2016-12-19 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.8146 | 1386.841 | 2704.6556 | 59.9793 | 0.48887 | 0.51113 | 1.1467 | 52.3078 | 2756.9634 | 1343.3861 | 1413.5773
2016-12-19 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6874 | 1416.9064 | 2711.5938 | 56.9618 | 0.48029 | 0.51971 | 1.1441 | 49.788 | 2761.3818 | 1318.6 | 1442.7818
2016-12-19 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.54% | 1287.7451 | 1425.9314 | 2713.6765 | 55.8396 | 0.47771 | 0.52229 | 1.1433 | 48.8402 | 2762.5167 | 1311.0766 | 1451.4401
2016-12-19 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.89% | 1292.4182 | 1419.8564 | 2712.2746 | 55.328 | 0.47945 | 0.52055 | 1.1438 | 48.3707 | 2760.6452 | 1315.6092 | 1445.036
2016-12-19 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.88% | 1305.7279 | 1402.5537 | 2708.2816 | 59.2252 | 0.48438 | 0.51562 | 1.1453 | 51.7108 | 2759.9924 | 1330.7757 | 1429.2167
2016-12-19 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-19 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-19 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-19 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-19 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-19 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-19 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-19 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-19 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-19 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-19 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-19 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-19 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-19 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-19 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-19 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-19 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-19 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-19 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-20 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-20 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-20 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-20 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-20 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-20 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.3% | 1474.4549 | 1538.3176 | 3012.7725 | 102.4328 | 0.49148 | 0.50852 | 1.2457 | 82.2263 | 3094.9988 | 1514.8679 | 1580.1309
2016-12-20 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.73% | 1480.9484 | 1528.5774 | 3009.5258 | 106.7995 | 0.49365 | 0.50635 | 1.2468 | 85.6572 | 3095.183 | 1523.233 | 1571.95
2016-12-20 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.83% | 1482.4242 | 1526.3636 | 3008.7879 | 106.4664 | 0.49414 | 0.50586 | 1.2471 | 85.3732 | 3094.1611 | 1524.6107 | 1569.5504
2016-12-20 08:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.39% | 1475.781 | 1536.3285 | 3012.1095 | 105.1751 | 0.49193 | 0.50807 | 1.246 | 84.4127 | 3096.5221 | 1517.3059 | 1579.2162
2016-12-20 09:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.1% | 1471.5236 | 1542.7147 | 3014.2382 | 102.8258 | 0.49051 | 0.50949 | 1.2453 | 82.5742 | 3096.8124 | 1512.0269 | 1584.7856
2016-12-20 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.1626 | 1535.756 | 3011.9187 | 85.0205 | 0.49205 | 0.50795 | 1.246 | 68.2333 | 3080.1519 | 1509.7371 | 1570.4148
2016-12-20 11:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.45% | 1476.7869 | 1534.8197 | 3011.6066 | 85.7606 | 0.49226 | 0.50774 | 1.2461 | 68.8215 | 3080.428 | 1510.6651 | 1569.763
2016-12-20 12:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.42% | 1476.318 | 1535.523 | 3011.841 | 89.4564 | 0.49211 | 0.50789 | 1.2461 | 71.7918 | 3083.6328 | 1511.6472 | 1571.9856
2016-12-20 13:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.61% | 1479.1661 | 1531.2509 | 3010.417 | 94.2773 | 0.49306 | 0.50694 | 1.2465 | 75.6319 | 3086.0489 | 1516.4568 | 1569.5921
2016-12-20 14:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.67% | 1480.0961 | 1529.8559 | 3009.952 | 92.6176 | 0.49337 | 0.50663 | 1.2467 | 74.2913 | 3084.2432 | 1516.7488 | 1567.4944
2016-12-20 15:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.74% | 1481.1589 | 1528.2616 | 3009.4205 | 93.2654 | 0.49372 | 0.50628 | 1.2469 | 74.8002 | 3084.2208 | 1518.0893 | 1566.1315
2016-12-20 16:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.7% | 1480.4974 | 1529.2539 | 3009.7513 | 85.6355 | 0.4935 | 0.5065 | 1.2467 | 68.687 | 3078.4383 | 1514.3944 | 1564.0439
2016-12-20 17:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.75% | 1481.1972 | 1528.2042 | 3009.4014 | 85.2852 | 0.49373 | 0.50627 | 1.2469 | 68.3997 | 3077.8011 | 1514.9684 | 1562.8327
2016-12-20 18:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.53% | 1478.0186 | 1532.9721 | 3010.9907 | 84.7611 | 0.49267 | 0.50733 | 1.2463 | 68.0082 | 3078.9989 | 1511.5244 | 1567.4745
2016-12-20 19:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.64% | 1479.6417 | 1530.5375 | 3010.1792 | 89.2806 | 0.49321 | 0.50679 | 1.2466 | 71.6189 | 3081.798 | 1514.9651 | 1566.833
2016-12-20 20:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.62% | 1479.3252 | 1531.0122 | 3010.3374 | 90.683 | 0.49311 | 0.50689 | 1.2466 | 72.747 | 3083.0844 | 1515.1974 | 1567.887
2016-12-20 21:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.43% | 1476.445 | 1535.3325 | 3011.7775 | 86.3779 | 0.49215 | 0.50785 | 1.2461 | 69.3201 | 3081.0976 | 1510.5608 | 1570.5368
2016-12-20 22:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.49% | 1477.3187 | 1534.022 | 3011.3407 | 90.0312 | 0.49244 | 0.50756 | 1.2462 | 72.2434 | 3083.5841 | 1512.8942 | 1570.6899
2016-12-20 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-21 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 97.77% | 1531.7824 | 1636.4353 | 3168.2176 | 199.9309 | 0.48887 | 0.51113 | 1.4889 | 134.2839 | 3302.5016 | 1597.4293 | 1705.0723
2016-12-21 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-21 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-21 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-21 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-21 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-21 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-21 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-21 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.39% | 1541.3713 | 1617.2574 | 3158.6287 | 210.3502 | 0.49193 | 0.50807 | 1.4919 | 140.9923 | 3299.621 | 1610.7292 | 1688.8918
2016-12-21 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.1% | 1536.9246 | 1626.1508 | 3163.0754 | 205.6517 | 0.49051 | 0.50949 | 1.4905 | 137.9742 | 3301.0496 | 1604.6021 | 1696.4476
2016-12-21 10:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.1626 | 1535.756 | 3011.9187 | 85.0205 | 0.49205 | 0.50795 | 1.246 | 68.2333 | 3080.1519 | 1509.7371 | 1570.4148
2016-12-21 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-21 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-21 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-21 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-21 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-21 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-21 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-21 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-21 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-21 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-21 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.43% | 1326.6607 | 1375.341 | 2702.0018 | 51.8268 | 0.49215 | 0.50785 | 1.1476 | 45.1593 | 2747.161 | 1348.8858 | 1398.2752
2016-12-21 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-21 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-22 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.6001 | 1550.0998 | 3016.6999 | 99.9654 | 0.48887 | 0.51113 | 1.2444 | 80.3301 | 3097.03 | 1505.8708 | 1591.1592
2016-12-22 01:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.06% | 1440.8618 | 1588.7073 | 3029.5691 | 94.9364 | 0.48029 | 0.51971 | 1.2401 | 76.5527 | 3106.1218 | 1477.6291 | 1628.4927
2016-12-22 02:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.54% | 1433.1356 | 1600.2966 | 3033.4322 | 93.0661 | 0.47771 | 0.52229 | 1.2389 | 75.1226 | 3108.5548 | 1469.0226 | 1639.5322
2016-12-22 03:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 95.89% | 1438.3363 | 1592.4955 | 3030.8318 | 92.2133 | 0.47945 | 0.52055 | 1.2397 | 74.3822 | 3105.214 | 1473.9985 | 1631.2155
2016-12-22 04:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 96.88% | 1453.1488 | 1570.2768 | 3023.4256 | 98.7086 | 0.48438 | 0.51562 | 1.2422 | 79.4633 | 3102.8889 | 1491.6394 | 1611.2495
2016-12-22 05:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.3% | 1474.4549 | 1538.3176 | 3012.7725 | 102.4328 | 0.49148 | 0.50852 | 1.2457 | 82.2263 | 3094.9988 | 1514.8679 | 1580.1309
2016-12-22 06:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.73% | 1480.9484 | 1528.5774 | 3009.5258 | 106.7995 | 0.49365 | 0.50635 | 1.2468 | 85.6572 | 3095.183 | 1523.233 | 1571.95
2016-12-22 07:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.83% | 1482.4242 | 1526.3636 | 3008.7879 | 106.4664 | 0.49414 | 0.50586 | 1.2471 | 85.3732 | 3094.1611 | 1524.6107 | 1569.5504
2016-12-22 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-22 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-22 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-22 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-22 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-22 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-22 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-22 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-22 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-22 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-22 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-22 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-22 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-22 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-22 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-22 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-23 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-23 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-23 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-23 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-23 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-23 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-23 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-23 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-23 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-23 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-23 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-23 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-23 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-23 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-23 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-23 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-23 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-23 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-23 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-23 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-23 20:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.62% | 1384.8128 | 1431.2621 | 2816.0749 | 72.5464 | 0.49311 | 0.50689 | 1.1972 | 60.5946 | 2876.6694 | 1414.6925 | 1461.977
2016-12-23 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-23 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-23 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-24 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-24 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-24 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-24 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-24 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-24 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-24 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-24 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-24 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-24 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-24 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-24 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-24 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-24 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-24 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-24 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-24 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-24 17:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.75% | 1386.5652 | 1428.8087 | 2815.3739 | 68.2282 | 0.49373 | 0.50627 | 1.1975 | 56.9759 | 2872.3498 | 1414.696 | 1457.6538
2016-12-24 18:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.53% | 1383.5896 | 1432.9745 | 2816.5641 | 67.8089 | 0.49267 | 0.50733 | 1.1971 | 56.6457 | 2873.2099 | 1411.4975 | 1461.7124
2016-12-24 19:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.64% | 1385.109 | 1430.8474 | 2815.9564 | 71.4245 | 0.49321 | 0.50679 | 1.1973 | 59.6553 | 2875.6117 | 1414.5318 | 1461.0799
2016-12-24 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-24 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.43% | 1326.6607 | 1375.341 | 2702.0018 | 51.8268 | 0.49215 | 0.50785 | 1.1476 | 45.1593 | 2747.161 | 1348.8858 | 1398.2752
2016-12-24 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-24 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-25 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-25 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-25 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-25 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-25 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-25 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-25 06:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.73% | 1386.3322 | 1429.1349 | 2815.4671 | 85.4396 | 0.49365 | 0.50635 | 1.1975 | 71.3507 | 2886.8178 | 1421.5545 | 1465.2633
2016-12-25 07:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.83% | 1387.7138 | 1427.2007 | 2814.9145 | 85.1732 | 0.49414 | 0.50586 | 1.1977 | 71.1165 | 2886.031 | 1422.8554 | 1463.1756
2016-12-25 08:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.39% | 1381.495 | 1435.907 | 2817.402 | 84.1401 | 0.49193 | 0.50807 | 1.1968 | 70.3059 | 2887.7079 | 1416.0804 | 1471.6275
2016-12-25 09:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.1% | 1377.5096 | 1441.4866 | 2818.9962 | 82.2607 | 0.49051 | 0.50949 | 1.1962 | 68.7681 | 2887.7643 | 1411.2409 | 1476.5234
2016-12-25 10:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8523 | 1435.4068 | 2817.2591 | 68.0164 | 0.49205 | 0.50795 | 1.1968 | 56.8309 | 2874.09 | 1409.8161 | 1464.2738
2016-12-25 11:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.45% | 1382.4366 | 1434.5888 | 2817.0254 | 68.6085 | 0.49226 | 0.50774 | 1.1969 | 57.3216 | 2874.3469 | 1410.6538 | 1463.6931
2016-12-25 12:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.42% | 1381.9977 | 1435.2032 | 2817.2009 | 71.5651 | 0.49211 | 0.50789 | 1.1968 | 59.7949 | 2876.9959 | 1411.4231 | 1465.5727
2016-12-25 13:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.61% | 1384.6638 | 1431.4707 | 2816.1345 | 75.4218 | 0.49306 | 0.50694 | 1.1972 | 62.9974 | 2879.1319 | 1415.725 | 1463.4069
2016-12-25 14:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.67% | 1385.5344 | 1430.2518 | 2815.7862 | 74.0941 | 0.49337 | 0.50663 | 1.1973 | 61.8819 | 2877.6682 | 1416.0648 | 1461.6034
2016-12-25 15:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.74% | 1386.5293 | 1428.8589 | 2815.3883 | 74.6123 | 0.49372 | 0.50628 | 1.1975 | 62.3074 | 2877.6956 | 1417.2917 | 1460.4039
2016-12-25 16:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.7% | 1385.9101 | 1429.7259 | 2815.636 | 68.5084 | 0.4935 | 0.5065 | 1.1974 | 57.2143 | 2872.8503 | 1414.1453 | 1458.705
2016-12-25 17:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.75% | 1330.9308 | 1369.7899 | 2700.7207 | 51.1711 | 0.49373 | 0.50627 | 1.1481 | 44.5695 | 2745.2903 | 1352.9363 | 1392.354
2016-12-25 18:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.53% | 1328.0747 | 1373.5029 | 2701.5776 | 50.8566 | 0.49267 | 0.50733 | 1.1478 | 44.3079 | 2745.8855 | 1349.904 | 1395.9815
2016-12-25 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-25 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-12-25 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-12-25 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.6811 | 1376.6486 | 2707.3297 | 45.0156 | 0.49244 | 0.50756 | 1.1231 | 40.0812 | 2747.4109 | 1350.4187 | 1396.9922
2016-12-25 23:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6835 | 1377.8956 | 2707.5791 | 44.746 | 0.49207 | 0.50793 | 1.123 | 39.8444 | 2747.4236 | 1349.2898 | 1398.1338
2016-12-26 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 97.77% | 1321.0265 | 1388.7169 | 2709.7434 | 49.9827 | 0.48887 | 0.51113 | 1.1222 | 44.5393 | 2754.2827 | 1342.8003 | 1411.4824
2016-12-26 01:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 96.06% | 1297.8429 | 1417.6963 | 2715.5393 | 47.4682 | 0.48029 | 0.51971 | 1.1201 | 42.3796 | 2757.9189 | 1318.1973 | 1439.7216
2016-12-26 02:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.54% | 1290.8836 | 1426.3954 | 2717.2791 | 46.533 | 0.47771 | 0.52229 | 1.1194 | 41.5686 | 2758.8477 | 1310.7415 | 1448.1062
2016-12-26 03:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 95.89% | 1295.5681 | 1420.5398 | 2716.108 | 46.1067 | 0.47945 | 0.52055 | 1.1199 | 41.1718 | 2757.2797 | 1315.3077 | 1441.972
2016-12-26 04:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 96.88% | 1201.2697 | 1283.7653 | 2485.0349 | 25.6642 | 0.48438 | 0.51562 | 1.063 | 24.1439 | 2509.1788 | 1212.9646 | 1296.2143
2016-12-26 05:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.3% | 1218.8828 | 1263.8625 | 2482.7452 | 26.6325 | 0.49148 | 0.50852 | 1.0639 | 25.0331 | 2507.7783 | 1231.1861 | 1276.5922
2016-12-26 06:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.73% | 1224.2507 | 1257.7967 | 2482.0474 | 27.7679 | 0.49365 | 0.50635 | 1.0642 | 26.0934 | 2508.1408 | 1237.1316 | 1271.0091
2016-12-26 07:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.83% | 1254.359 | 1285.2923 | 2539.6513 | 17.0346 | 0.49414 | 0.50586 | 1.0395 | 16.3868 | 2556.0381 | 1262.4564 | 1293.5817
2016-12-26 08:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.39% | 1248.7378 | 1291.3632 | 2540.101 | 16.828 | 0.49193 | 0.50807 | 1.0394 | 16.1908 | 2556.2918 | 1256.7025 | 1299.5893
2016-12-26 09:00 | 1.08 | 2640 | 1240 | 1269.2308 | 2538.4615 | 98.1% | 1245.1353 | 1295.2539 | 2540.3892 | 16.4521 | 0.49051 | 0.50949 | 1.0392 | 15.8309 | 2556.2201 | 1252.9005 | 1303.3196
2016-12-26 10:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.41% | 1220.2945 | 1262.2673 | 2482.5617 | 22.1053 | 0.49205 | 0.50795 | 1.064 | 20.7763 | 2503.338 | 1230.5175 | 1272.8205
2016-12-26 11:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.45% | 1220.8105 | 1261.6842 | 2482.4946 | 22.2977 | 0.49226 | 0.50774 | 1.064 | 20.9566 | 2503.4513 | 1231.1266 | 1272.3247
2016-12-26 12:00 | 1.13 | 2640 | 1240 | 1240 | 2478.8 | 98.42% | 1220.4229 | 1262.1221 | 2482.545 | 23.2587 | 0.49211 | 0.50789 | 1.064 | 21.8602 | 2504.4052 | 1231.1804 | 1273.2248
2016-12-26 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.3451 | 1374.5686 | 2706.9137 | 47.1386 | 0.49306 | 0.50694 | 1.1233 | 41.9658 | 2748.8795 | 1353.0366 | 1395.8429
2016-12-26 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1829 | 1373.5214 | 2706.7043 | 46.3088 | 0.49337 | 0.50663 | 1.1233 | 41.2242 | 2747.9285 | 1353.5214 | 1394.407
2016-12-26 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.74% | 1334.1402 | 1372.3248 | 2706.465 | 46.6327 | 0.49372 | 0.50628 | 1.1234 | 41.5092 | 2747.9742 | 1354.6341 | 1393.3401
2016-12-26 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-26 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-26 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-26 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-26 20:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.62% | 1332.4885 | 1374.3894 | 2706.8779 | 45.3415 | 0.49311 | 0.50689 | 1.1233 | 40.3654 | 2747.2433 | 1352.393 | 1394.8503
2016-12-26 21:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.43% | 1329.8942 | 1377.6323 | 2707.5265 | 43.189 | 0.49215 | 0.50785 | 1.123 | 38.4573 | 2745.9838 | 1348.8209 | 1397.1629
2016-12-26 22:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.49% | 1330.6811 | 1376.6486 | 2707.3297 | 45.0156 | 0.49244 | 0.50756 | 1.1231 | 40.0812 | 2747.4109 | 1350.4187 | 1396.9922
2016-12-26 23:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.4506 | 1375.6143 | 2702.0648 | 53.6952 | 0.49207 | 0.50793 | 1.1476 | 46.7883 | 2748.8531 | 1349.4737 | 1399.3794
2016-12-27 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 97.77% | 1317.8146 | 1386.841 | 2704.6556 | 59.9793 | 0.48887 | 0.51113 | 1.1467 | 52.3078 | 2756.9634 | 1343.3861 | 1413.5773
2016-12-27 01:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.06% | 1294.6874 | 1416.9064 | 2711.5938 | 56.9618 | 0.48029 | 0.51971 | 1.1441 | 49.788 | 2761.3818 | 1318.6 | 1442.7818
2016-12-27 02:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.54% | 1287.7451 | 1425.9314 | 2713.6765 | 55.8396 | 0.47771 | 0.52229 | 1.1433 | 48.8402 | 2762.5167 | 1311.0766 | 1451.4401
2016-12-27 03:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 95.89% | 1292.4182 | 1419.8564 | 2712.2746 | 55.328 | 0.47945 | 0.52055 | 1.1438 | 48.3707 | 2760.6452 | 1315.6092 | 1445.036
2016-12-27 04:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 96.88% | 1305.7279 | 1402.5537 | 2708.2816 | 59.2252 | 0.48438 | 0.51562 | 1.1453 | 51.7108 | 2759.9924 | 1330.7757 | 1429.2167
2016-12-27 05:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.3% | 1324.8726 | 1377.6657 | 2702.5382 | 61.4597 | 0.49148 | 0.50852 | 1.1474 | 53.5622 | 2756.1004 | 1351.1976 | 1404.9028
2016-12-27 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-27 07:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.83% | 1335.2799 | 1370.9001 | 2706.18 | 53.2332 | 0.49414 | 0.50586 | 1.1235 | 47.3801 | 2753.5601 | 1358.6924 | 1394.8677
2016-12-27 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-27 09:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.1% | 1322.2386 | 1381.0899 | 2703.3284 | 61.6955 | 0.49051 | 0.50949 | 1.1472 | 53.7814 | 2757.1099 | 1348.6188 | 1408.4911
2016-12-27 10:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.41% | 1326.407 | 1375.6709 | 2702.0779 | 51.0123 | 0.49205 | 0.50795 | 1.1476 | 44.4507 | 2746.5286 | 1348.2791 | 1398.2494
2016-12-27 11:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.45% | 1326.9679 | 1374.9417 | 2701.9096 | 51.4563 | 0.49226 | 0.50774 | 1.1477 | 44.8351 | 2746.7448 | 1349.0386 | 1397.7062
2016-12-27 12:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.42% | 1326.5466 | 1375.4894 | 2702.036 | 53.6738 | 0.49211 | 0.50789 | 1.1476 | 46.7692 | 2748.8052 | 1349.562 | 1399.2432
2016-12-27 13:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.61% | 1329.1057 | 1372.1625 | 2701.2683 | 56.5664 | 0.49306 | 0.50694 | 1.1479 | 49.2774 | 2750.5457 | 1353.4022 | 1397.1435
2016-12-27 14:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.67% | 1329.9414 | 1371.0762 | 2701.0176 | 55.5706 | 0.49337 | 0.50663 | 1.148 | 48.406 | 2749.4236 | 1353.8233 | 1395.6003
2016-12-27 15:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.74% | 1330.8964 | 1369.8347 | 2700.7311 | 55.9592 | 0.49372 | 0.50628 | 1.1481 | 48.7401 | 2749.4711 | 1354.9603 | 1394.5108
2016-12-27 16:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.7% | 1330.302 | 1370.6074 | 2700.9094 | 51.3813 | 0.4935 | 0.5065 | 1.148 | 44.7553 | 2745.6647 | 1352.3887 | 1393.276
2016-12-27 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-27 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-27 19:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.64% | 1329.5331 | 1371.607 | 2701.1401 | 53.5683 | 0.49321 | 0.50679 | 1.148 | 46.6638 | 2747.8038 | 1352.5483 | 1395.2555
2016-12-27 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-27 21:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.43% | 1382.1166 | 1435.0368 | 2817.1534 | 69.1024 | 0.49215 | 0.50785 | 1.1969 | 57.7364 | 2874.8898 | 1410.5315 | 1464.3583
2016-12-27 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-27 23:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.41% | 1381.8976 | 1435.3433 | 2817.241 | 71.5936 | 0.49207 | 0.50793 | 1.1968 | 59.8195 | 2877.0604 | 1411.333 | 1465.7274
2016-12-28 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 97.77% | 1372.9007 | 1447.9391 | 2820.8397 | 79.9723 | 0.48887 | 0.51113 | 1.1955 | 66.8919 | 2887.7316 | 1405.6019 | 1482.1297
2016-12-28 01:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.06% | 1348.8067 | 1481.6706 | 2830.4773 | 75.9491 | 0.48029 | 0.51971 | 1.1921 | 63.7095 | 2894.1868 | 1379.4056 | 1514.7812
2016-12-28 02:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.54% | 1341.5742 | 1491.7961 | 2833.3703 | 74.4528 | 0.47771 | 0.52229 | 1.1911 | 62.5084 | 2895.8788 | 1371.4352 | 1524.4436
2016-12-28 03:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 95.89% | 1346.4426 | 1484.9803 | 2831.423 | 73.7706 | 0.47945 | 0.52055 | 1.1918 | 61.8996 | 2893.3226 | 1376.1201 | 1517.2025
2016-12-28 04:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 96.88% | 1360.3087 | 1465.5678 | 2825.8765 | 78.9669 | 0.48438 | 0.51562 | 1.1938 | 66.1501 | 2892.0266 | 1392.3507 | 1499.6759
2016-12-28 05:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.3% | 1380.2537 | 1437.6449 | 2817.8985 | 81.9462 | 0.49148 | 0.50852 | 1.1966 | 68.4829 | 2886.3814 | 1413.912 | 1472.4695
2016-12-28 06:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.73% | 1330.7072 | 1370.0806 | 2700.7878 | 64.0797 | 0.49365 | 0.50635 | 1.1481 | 55.814 | 2756.6018 | 1358.2598 | 1398.342
2016-12-28 07:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.83% | 1332.0334 | 1368.3566 | 2700.39 | 63.8799 | 0.49414 | 0.50586 | 1.1482 | 55.6327 | 2756.0227 | 1359.5238 | 1396.4989
2016-12-28 08:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.39% | 1326.0641 | 1376.1167 | 2702.1808 | 63.105 | 0.49193 | 0.50807 | 1.1476 | 54.9898 | 2757.1705 | 1353.1151 | 1404.0555
2016-12-28 09:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.1% | 1325.4612 | 1383.1735 | 2708.6347 | 51.4129 | 0.49051 | 0.50949 | 1.1226 | 45.797 | 2754.4317 | 1347.925 | 1406.5067
2016-12-28 10:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.41% | 1329.6398 | 1377.9502 | 2707.59 | 42.5102 | 0.49205 | 0.50795 | 1.123 | 37.8537 | 2745.4438 | 1348.2659 | 1397.1779
2016-12-28 11:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.45% | 1330.2021 | 1377.2474 | 2707.4495 | 42.8803 | 0.49226 | 0.50774 | 1.1231 | 38.1815 | 2745.6309 | 1348.9974 | 1396.6336
2016-12-28 12:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.42% | 1329.7798 | 1377.7753 | 2707.5551 | 44.7282 | 0.49211 | 0.50789 | 1.123 | 39.8283 | 2747.3833 | 1349.3795 | 1398.0038
2016-12-28 13:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.61% | 1332.3451 | 1374.5686 | 2706.9137 | 47.1386 | 0.49306 | 0.50694 | 1.1233 | 41.9658 | 2748.8795 | 1353.0366 | 1395.8429
2016-12-28 14:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.67% | 1333.1829 | 1373.5214 | 2706.7043 | 46.3088 | 0.49337 | 0.50663 | 1.1233 | 41.2242 | 2747.9285 | 1353.5214 | 1394.407
2016-12-28 15:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.74% | 1334.1402 | 1372.3248 | 2706.465 | 46.6327 | 0.49372 | 0.50628 | 1.1234 | 41.5092 | 2747.9742 | 1354.6341 | 1393.3401
2016-12-28 16:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.7% | 1333.5443 | 1373.0696 | 2706.6139 | 42.8178 | 0.4935 | 0.5065 | 1.1234 | 38.1153 | 2744.7292 | 1352.3542 | 1392.375
2016-12-28 17:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.75% | 1334.1747 | 1372.2816 | 2706.4563 | 42.6426 | 0.49373 | 0.50627 | 1.1234 | 37.9574 | 2744.4137 | 1352.9155 | 1391.4982
2016-12-28 18:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.53% | 1331.3116 | 1375.8605 | 2707.1721 | 42.3805 | 0.49267 | 0.50733 | 1.1232 | 37.733 | 2744.9051 | 1349.9016 | 1395.0035
2016-12-28 19:00 | 1.25 | 3040 | 1240 | 1351.1111 | 2702.2222 | 98.64% | 1332.7735 | 1374.0331 | 2706.8066 | 44.6403 | 0.49321 | 0.50679 | 1.1233 | 39.7402 | 2746.5468 | 1352.3739 | 1394.1729
2016-12-28 20:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.62% | 1329.2487 | 1371.9766 | 2701.2254 | 54.4098 | 0.49311 | 0.50689 | 1.1479 | 47.3981 | 2748.6235 | 1352.6212 | 1396.0023
2016-12-28 21:00 | 1.3 | 3100 | 1240 | 1347.8261 | 2695.6522 | 98.43% | 1326.6607 | 1375.341 | 2702.0018 | 51.8268 | 0.49215 | 0.50785 | 1.1476 | 45.1593 | 2747.161 | 1348.8858 | 1398.2752
2016-12-28 22:00 | 1.4 | 3370 | 1240 | 1404.1667 | 2808.3333 | 98.49% | 1382.9344 | 1433.8918 | 2816.8262 | 72.025 | 0.49244 | 0.50756 | 1.197 | 60.1724 | 2876.9987 | 1412.5657 | 1464.4329
2016-12-28 23:00 | 1.5 | 3750 | 1240 | 1500 | 3000 | 98.41% | 1476.2111 | 1535.6833 | 3011.8944 | 89.492 | 0.49207 | 0.50793 | 1.246 | 71.8214 | 3083.7159 | 1511.5523 | 1572.1636
2016-12-29 | 1.5 | 3750 | 1240 | 1500 | 3000 | 97.77% | 1466.6001 | 1550.0998 | 3016.6999 | 99.9654 | 0.48887 | 0.51113 | 1.2444 | 80.3301 | 3097.03 | 1505.8708 | 1591.1592
2016-12-29 01:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.06% | 1504.9001 | 1690.1998 | 3195.0999 | 189.8727 | 0.48029 | 0.51971 | 1.4803 | 128.2675 | 3323.3674 | 1566.5053 | 1756.862
2016-12-29 02:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.54% | 1496.8305 | 1706.3389 | 3203.1695 | 186.1321 | 0.47771 | 0.52229 | 1.4777 | 125.9597 | 3329.1291 | 1557.003 | 1772.1261
2016-12-29 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-29 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-29 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-29 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-29 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-29 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.39% | 1541.3713 | 1617.2574 | 3158.6287 | 210.3502 | 0.49193 | 0.50807 | 1.4919 | 140.9923 | 3299.621 | 1610.7292 | 1688.8918
2016-12-29 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.1% | 1536.9246 | 1626.1508 | 3163.0754 | 205.6517 | 0.49051 | 0.50949 | 1.4905 | 137.9742 | 3301.0496 | 1604.6021 | 1696.4476
2016-12-29 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.7699 | 1616.4603 | 3158.2301 | 170.041 | 0.49205 | 0.50795 | 1.4921 | 113.9644 | 3272.1945 | 1597.8465 | 1674.348
2016-12-29 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.45% | 1542.4218 | 1615.1563 | 3157.5782 | 171.5211 | 0.49226 | 0.50774 | 1.4923 | 114.9403 | 3272.5185 | 1599.0026 | 1673.5159
2016-12-29 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.42% | 1541.9321 | 1616.1357 | 3158.0679 | 178.9128 | 0.49211 | 0.50789 | 1.4921 | 119.9062 | 3277.9741 | 1600.9387 | 1677.0354
2016-12-29 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.61% | 1544.9068 | 1610.1865 | 3155.0932 | 188.5546 | 0.49306 | 0.50694 | 1.4931 | 126.2877 | 3281.381 | 1607.1736 | 1674.2074
2016-12-29 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.67% | 1545.8781 | 1608.2437 | 3154.1219 | 185.2353 | 0.49337 | 0.50663 | 1.4934 | 124.0388 | 3278.1607 | 1607.0746 | 1671.0861
2016-12-29 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.74% | 1546.9882 | 1606.0236 | 3153.0118 | 186.5308 | 0.49372 | 0.50628 | 1.4937 | 124.8767 | 3277.8885 | 1608.6423 | 1669.2462
2016-12-29 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.7% | 1546.2973 | 1607.4054 | 3153.7027 | 171.271 | 0.4935 | 0.5065 | 1.4935 | 114.6777 | 3268.3804 | 1602.8907 | 1665.4897
2016-12-29 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.75% | 1547.0282 | 1605.9436 | 3152.9718 | 170.5705 | 0.49373 | 0.50627 | 1.4937 | 114.1908 | 3267.1626 | 1603.4079 | 1663.7547
2016-12-29 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.53% | 1543.7083 | 1612.5833 | 3156.2917 | 169.5222 | 0.49267 | 0.50733 | 1.4927 | 113.5695 | 3269.8612 | 1599.661 | 1670.2002
2016-12-29 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.64% | 1545.4035 | 1609.193 | 3154.5965 | 178.5611 | 0.49321 | 0.50679 | 1.4932 | 119.5817 | 3274.1782 | 1604.3829 | 1669.7953
2016-12-29 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.62% | 1545.073 | 1609.854 | 3154.927 | 181.3661 | 0.49311 | 0.50689 | 1.4931 | 121.4688 | 3276.3958 | 1604.9703 | 1671.4255
2016-12-29 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.43% | 1542.0648 | 1615.8704 | 3157.9352 | 172.7559 | 0.49215 | 0.50785 | 1.4921 | 115.7766 | 3273.7118 | 1599.0441 | 1674.6678
2016-12-29 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-29 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886
2016-12-30 | 2.2 | 5200 | 1240 | 1625 | 3250 | 97.77% | 1588.8168 | 1704.603 | 3293.4198 | 239.917 | 0.48887 | 0.51113 | 1.5866 | 151.2107 | 3444.6306 | 1662.7387 | 1781.8919
2016-12-30 01:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 96.06% | 1560.9336 | 1765.946 | 3326.8797 | 227.8472 | 0.48029 | 0.51971 | 1.5763 | 144.5415 | 3471.4212 | 1630.3551 | 1841.0661
2016-12-30 02:00 | 2.2 | 5200 | 1240 | 1625 | 3250 | 95.54% | 1552.5636 | 1784.3601 | 3336.9237 | 223.3585 | 0.47771 | 0.52229 | 1.5733 | 141.9723 | 3478.896 | 1620.3855 | 1858.5105
2016-12-30 03:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 95.89% | 1502.2624 | 1695.4752 | 3197.7376 | 184.4266 | 0.47945 | 0.52055 | 1.4794 | 124.6593 | 3322.3969 | 1562.0297 | 1760.3672
2016-12-30 04:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 96.88% | 1517.7332 | 1664.5337 | 3182.2668 | 197.4172 | 0.48438 | 0.51562 | 1.4844 | 132.9961 | 3315.263 | 1582.1542 | 1733.1087
2016-12-30 05:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.3% | 1539.9863 | 1620.0274 | 3160.0137 | 204.8655 | 0.49148 | 0.50852 | 1.4915 | 137.3567 | 3297.3705 | 1607.4951 | 1689.8754
2016-12-30 06:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.73% | 1546.7683 | 1606.4634 | 3153.2317 | 213.5991 | 0.49365 | 0.50635 | 1.4936 | 143.0048 | 3296.2365 | 1617.3626 | 1678.8739
2016-12-30 07:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.83% | 1548.3098 | 1603.3805 | 3151.6902 | 212.9329 | 0.49414 | 0.50586 | 1.4941 | 142.5119 | 3294.2021 | 1618.7308 | 1675.4713
2016-12-30 08:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.39% | 1541.3713 | 1617.2574 | 3158.6287 | 210.3502 | 0.49193 | 0.50807 | 1.4919 | 140.9923 | 3299.621 | 1610.7292 | 1688.8918
2016-12-30 09:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.1% | 1536.9246 | 1626.1508 | 3163.0754 | 205.6517 | 0.49051 | 0.50949 | 1.4905 | 137.9742 | 3301.0496 | 1604.6021 | 1696.4476
2016-12-30 10:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.7699 | 1616.4603 | 3158.2301 | 170.041 | 0.49205 | 0.50795 | 1.4921 | 113.9644 | 3272.1945 | 1597.8465 | 1674.348
2016-12-30 11:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.45% | 1542.4218 | 1615.1563 | 3157.5782 | 171.5211 | 0.49226 | 0.50774 | 1.4923 | 114.9403 | 3272.5185 | 1599.0026 | 1673.5159
2016-12-30 12:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.42% | 1541.9321 | 1616.1357 | 3158.0679 | 178.9128 | 0.49211 | 0.50789 | 1.4921 | 119.9062 | 3277.9741 | 1600.9387 | 1677.0354
2016-12-30 13:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.61% | 1544.9068 | 1610.1865 | 3155.0932 | 188.5546 | 0.49306 | 0.50694 | 1.4931 | 126.2877 | 3281.381 | 1607.1736 | 1674.2074
2016-12-30 14:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.67% | 1545.8781 | 1608.2437 | 3154.1219 | 185.2353 | 0.49337 | 0.50663 | 1.4934 | 124.0388 | 3278.1607 | 1607.0746 | 1671.0861
2016-12-30 15:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.74% | 1546.9882 | 1606.0236 | 3153.0118 | 186.5308 | 0.49372 | 0.50628 | 1.4937 | 124.8767 | 3277.8885 | 1608.6423 | 1669.2462
2016-12-30 16:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.7% | 1546.2973 | 1607.4054 | 3153.7027 | 171.271 | 0.4935 | 0.5065 | 1.4935 | 114.6777 | 3268.3804 | 1602.8907 | 1665.4897
2016-12-30 17:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.75% | 1547.0282 | 1605.9436 | 3152.9718 | 170.5705 | 0.49373 | 0.50627 | 1.4937 | 114.1908 | 3267.1626 | 1603.4079 | 1663.7547
2016-12-30 18:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.53% | 1543.7083 | 1612.5833 | 3156.2917 | 169.5222 | 0.49267 | 0.50733 | 1.4927 | 113.5695 | 3269.8612 | 1599.661 | 1670.2002
2016-12-30 19:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.64% | 1545.4035 | 1609.193 | 3154.5965 | 178.5611 | 0.49321 | 0.50679 | 1.4932 | 119.5817 | 3274.1782 | 1604.3829 | 1669.7953
2016-12-30 20:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.62% | 1545.073 | 1609.854 | 3154.927 | 181.3661 | 0.49311 | 0.50689 | 1.4931 | 121.4688 | 3276.3958 | 1604.9703 | 1671.4255
2016-12-30 21:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.43% | 1542.0648 | 1615.8704 | 3157.9352 | 172.7559 | 0.49215 | 0.50785 | 1.4921 | 115.7766 | 3273.7118 | 1599.0441 | 1674.6678
2016-12-30 22:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.49% | 1542.9773 | 1614.0454 | 3157.0227 | 180.0624 | 0.49244 | 0.50756 | 1.4924 | 120.6497 | 3277.6724 | 1602.39 | 1675.2824
2016-12-30 23:00 | 2 | 4700 | 1240 | 1566.6667 | 3133.3333 | 98.41% | 1541.8205 | 1616.359 | 3158.1795 | 178.984 | 0.49207 | 0.50793 | 1.4921 | 119.9568 | 3278.1363 | 1600.8477 | 1677.2886

## FAS_2016_PFR_FFR
Requirement in Plexos, (PFR+Ratio*FFR) ≥ Requirement
Assumed Load Participation in Plexos
Date | Equivalency Ratio | PFR (no FFR), MW | Min PFR, based on BAL-003 IFRO, MW | Max FFR | 2014 Avg. Participation for Month&Hour | Expected FFR, MW
2016-01-01 | 1.3 | 3100 | 1240 | 1430.7692 | 90.58% | 1295.936
2016-01-01 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.86% | 1299.9361
2016-01-01 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.88% | 1300.26
2016-01-01 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.79% | 1298.9871
2016-01-01 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.21% | 1290.6698
2016-01-01 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.3% | 1292.014
2016-01-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-01 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-01 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-01 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-01 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-01 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-01 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-01 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.23% | 1333.9161
2016-01-01 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.02% | 1330.8613
2016-01-01 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.88% | 1328.9636
2016-01-01 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.07% | 1331.593
2016-01-01 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5015
2016-01-01 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-01 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-01 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-01 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-01 23:00 | 1.25 | 3040 | 1240 | 1440 | 91.32% | 1314.9612
2016-01-02 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-02 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-02 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-02 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-02 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-02 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-02 06:00 | 1.25 | 3040 | 1240 | 1440 | 90.56% | 1304.0683
2016-01-02 07:00 | 1.25 | 3040 | 1240 | 1440 | 88.02% | 1267.5556
2016-01-02 08:00 | 1.25 | 3040 | 1240 | 1440 | 88.59% | 1275.6749
2016-01-02 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-02 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-02 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-02 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-02 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-02 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.23% | 1333.9161
2016-01-02 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.02% | 1330.8613
2016-01-02 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.88% | 1328.9636
2016-01-02 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.07% | 1331.593
2016-01-02 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5015
2016-01-02 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.42% | 1322.3514
2016-01-02 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.91% | 1315.0398
2016-01-02 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.36% | 1307.1013
2016-01-02 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.19% | 1290.4608
2016-01-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.32% | 1306.5319
2016-01-03 | 1.3 | 3100 | 1240 | 1430.7692 | 90.58% | 1295.936
2016-01-03 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.86% | 1299.9361
2016-01-03 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.88% | 1300.26
2016-01-03 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.79% | 1298.9871
2016-01-03 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.21% | 1290.6698
2016-01-03 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.3% | 1292.014
2016-01-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-03 07:00 | 1.25 | 3040 | 1240 | 1440 | 88.02% | 1267.5556
2016-01-03 08:00 | 1.25 | 3040 | 1240 | 1440 | 88.59% | 1275.6749
2016-01-03 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-03 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-03 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-03 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-03 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-03 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-03 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-03 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.88% | 1150.7821
2016-01-03 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.07% | 1153.059
2016-01-03 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9797
2016-01-03 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-03 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-03 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-03 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.19% | 1117.4415
2016-01-03 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.32% | 1131.358
2016-01-04 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-04 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-04 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-04 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-04 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-04 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-04 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-04 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.02% | 1141.0608
2016-01-04 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.59% | 1148.3699
2016-01-04 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.93% | 1139.7876
2016-01-04 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.67% | 1149.4256
2016-01-04 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 90.5% | 1173.1084
2016-01-04 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 92.72% | 1201.9162
2016-01-04 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 93.06% | 1206.3701
2016-01-04 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 93.23% | 1208.546
2016-01-04 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 93.02% | 1205.7783
2016-01-04 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 92.88% | 1204.059
2016-01-04 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 93.07% | 1206.4413
2016-01-04 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 93.06% | 1206.3584
2016-01-04 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 92.42% | 1198.0682
2016-01-04 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 91.91% | 1191.4439
2016-01-04 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-04 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-04 23:00 | 1.25 | 3040 | 1240 | 1440 | 91.32% | 1314.9612
2016-01-05 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-05 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-05 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-05 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-05 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-05 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-05 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-05 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-05 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-05 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-05 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-05 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-05 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-05 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-05 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-05 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-05 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-05 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-05 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-05 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-05 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-05 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.36% | 1307.1013
2016-01-05 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.19% | 1290.4608
2016-01-05 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.32% | 1306.5319
2016-01-06 | 1.4 | 3370 | 1240 | 1521.4286 | 90.58% | 1378.0518
2016-01-06 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.86% | 1382.3053
2016-01-06 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.88% | 1382.6498
2016-01-06 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.79% | 1381.2962
2016-01-06 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.21% | 1372.4519
2016-01-06 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.3% | 1373.8812
2016-01-06 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-06 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-06 08:00 | 1.25 | 3040 | 1240 | 1440 | 88.59% | 1275.6749
2016-01-06 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-06 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-06 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-06 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-06 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-06 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-06 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-06 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-06 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-06 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-06 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.42% | 1322.3514
2016-01-06 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.91% | 1315.0398
2016-01-06 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.36% | 1389.9246
2016-01-06 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.19% | 1509.2378
2016-01-06 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-07 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-07 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-07 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-07 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-07 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-07 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.3% | 1511.0543
2016-01-07 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.56% | 1377.8103
2016-01-07 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-07 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-07 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-07 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-07 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-07 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-07 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-07 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.23% | 1333.9161
2016-01-07 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.02% | 1330.8613
2016-01-07 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.88% | 1328.9636
2016-01-07 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-07 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-07 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-07 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-07 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-07 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.19% | 1117.4415
2016-01-07 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.32% | 1131.358
2016-01-08 | 1.13 | 2640 | 1240 | 1238.9381 | 90.58% | 1122.1827
2016-01-08 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.86% | 1125.6464
2016-01-08 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.88% | 1125.9269
2016-01-08 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.79% | 1124.8247
2016-01-08 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.21% | 1117.6226
2016-01-08 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.3% | 1118.7865
2016-01-08 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-08 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-08 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.59% | 1148.3699
2016-01-08 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.93% | 1139.7876
2016-01-08 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.67% | 1149.4256
2016-01-08 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.5% | 1121.2009
2016-01-08 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.72% | 1148.7341
2016-01-08 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9909
2016-01-08 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.23% | 1155.0705
2016-01-08 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.02% | 1152.4253
2016-01-08 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.88% | 1150.7821
2016-01-08 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.07% | 1153.059
2016-01-08 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9797
2016-01-08 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-08 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-08 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-08 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.19% | 1117.4415
2016-01-08 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.32% | 1131.358
2016-01-09 | 1.13 | 2640 | 1240 | 1238.9381 | 90.58% | 1122.1827
2016-01-09 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.86% | 1125.6464
2016-01-09 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.88% | 1125.9269
2016-01-09 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.79% | 1124.8247
2016-01-09 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.21% | 1117.6226
2016-01-09 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.3% | 1118.7865
2016-01-09 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-09 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-09 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-09 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.93% | 1089.3545
2016-01-09 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.67% | 1098.5661
2016-01-09 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.5% | 1121.2009
2016-01-09 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.72% | 1148.7341
2016-01-09 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9909
2016-01-09 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.23% | 1155.0705
2016-01-09 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.02% | 1152.4253
2016-01-09 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.88% | 1150.7821
2016-01-09 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.07% | 1153.059
2016-01-09 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9797
2016-01-09 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-09 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-09 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-09 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.19% | 1117.4415
2016-01-09 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.32% | 1131.358
2016-01-10 | 1.13 | 2640 | 1240 | 1238.9381 | 90.58% | 1122.1827
2016-01-10 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.86% | 1125.6464
2016-01-10 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.88% | 1125.9269
2016-01-10 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.79% | 1124.8247
2016-01-10 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.21% | 1117.6226
2016-01-10 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.3% | 1118.7865
2016-01-10 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-10 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-10 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-10 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-10 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-10 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-10 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-10 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-10 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-10 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-10 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-10 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-10 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-10 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-10 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-10 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-10 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-10 23:00 | 1.25 | 3040 | 1240 | 1440 | 91.32% | 1314.9612
2016-01-11 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-11 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-11 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-11 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-11 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-11 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-11 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.56% | 1121.986
2016-01-11 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-11 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-11 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.93% | 1089.3545
2016-01-11 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.67% | 1098.5661
2016-01-11 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.5% | 1121.2009
2016-01-11 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-11 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-11 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-11 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-11 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-11 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-11 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-11 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-11 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-11 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-11 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.19% | 1117.4415
2016-01-11 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.32% | 1131.358
2016-01-12 | 1.13 | 2640 | 1240 | 1238.9381 | 90.58% | 1122.1827
2016-01-12 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.86% | 1125.6464
2016-01-12 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.88% | 1125.9269
2016-01-12 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.79% | 1124.8247
2016-01-12 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.21% | 1117.6226
2016-01-12 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.3% | 1118.7865
2016-01-12 06:00 | 1.08 | 2640 | 1240 | 1296.2963 | 90.56% | 1173.9298
2016-01-12 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.02% | 1141.0608
2016-01-12 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 88.59% | 1148.3699
2016-01-12 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.93% | 1089.3545
2016-01-12 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.67% | 1098.5661
2016-01-12 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-12 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-12 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-12 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-12 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-12 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-12 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-12 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5015
2016-01-12 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.42% | 1322.3514
2016-01-12 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.91% | 1315.0398
2016-01-12 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.36% | 1307.1013
2016-01-12 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.19% | 1372.2296
2016-01-12 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.32% | 1389.3191
2016-01-13 | 1.4 | 3370 | 1240 | 1521.4286 | 90.58% | 1378.0518
2016-01-13 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.86% | 1382.3053
2016-01-13 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.88% | 1382.6498
2016-01-13 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.79% | 1381.2962
2016-01-13 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.21% | 1372.4519
2016-01-13 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.3% | 1373.8812
2016-01-13 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-13 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-13 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-13 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-13 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.67% | 1349.0504
2016-01-13 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.5% | 1376.8462
2016-01-13 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.72% | 1410.6572
2016-01-13 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2515
2016-01-13 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.23% | 1560.0603
2016-01-13 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.02% | 1556.4876
2016-01-13 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.88% | 1554.2682
2016-01-13 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.07% | 1557.3434
2016-01-13 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2363
2016-01-13 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.42% | 1546.5349
2016-01-13 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-13 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-13 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.19% | 1509.2378
2016-01-13 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.32% | 1528.0336
2016-01-14 | 1.5 | 3750 | 1240 | 1673.3333 | 90.58% | 1515.6413
2016-01-14 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.86% | 1520.3195
2016-01-14 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.88% | 1520.6984
2016-01-14 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.79% | 1519.2097
2016-01-14 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.21% | 1509.4823
2016-01-14 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.3% | 1511.0543
2016-01-14 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.56% | 1377.8103
2016-01-14 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.02% | 1339.2328
2016-01-14 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.59% | 1347.8113
2016-01-14 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-14 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.67% | 1349.0504
2016-01-14 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.5% | 1376.8462
2016-01-14 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.72% | 1410.6572
2016-01-14 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-14 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-14 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-14 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-14 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.07% | 1415.9682
2016-01-14 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-14 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.42% | 1322.3514
2016-01-14 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.91% | 1315.0398
2016-01-14 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.36% | 1389.9246
2016-01-14 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.19% | 1372.2296
2016-01-14 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.32% | 1389.3191
2016-01-15 | 1.4 | 3370 | 1240 | 1521.4286 | 90.58% | 1378.0518
2016-01-15 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.86% | 1382.3053
2016-01-15 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.88% | 1382.6498
2016-01-15 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.79% | 1381.2962
2016-01-15 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.21% | 1372.4519
2016-01-15 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.3% | 1373.8812
2016-01-15 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-15 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-15 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-15 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-15 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-15 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-15 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-15 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-15 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.23% | 1333.9161
2016-01-15 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.02% | 1330.8613
2016-01-15 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.88% | 1328.9636
2016-01-15 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.07% | 1331.593
2016-01-15 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5015
2016-01-15 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.42% | 1322.3514
2016-01-15 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.91% | 1315.0398
2016-01-15 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.36% | 1307.1013
2016-01-15 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.19% | 1372.2296
2016-01-15 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.32% | 1389.3191
2016-01-16 | 1.4 | 3370 | 1240 | 1521.4286 | 90.58% | 1378.0518
2016-01-16 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.86% | 1382.3053
2016-01-16 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.88% | 1382.6498
2016-01-16 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.79% | 1381.2962
2016-01-16 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.21% | 1372.4519
2016-01-16 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.3% | 1373.8812
2016-01-16 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.56% | 1377.8103
2016-01-16 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-16 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-16 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-16 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-16 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-16 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-16 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-16 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-16 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-16 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-16 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-16 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-16 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-16 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-16 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-16 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-16 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.32% | 1306.5319
2016-01-17 | 1.3 | 3100 | 1240 | 1430.7692 | 90.58% | 1295.936
2016-01-17 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.86% | 1299.9361
2016-01-17 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.88% | 1300.26
2016-01-17 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.79% | 1298.9871
2016-01-17 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.21% | 1290.6698
2016-01-17 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.3% | 1292.014
2016-01-17 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.56% | 1295.7089
2016-01-17 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-17 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-17 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-17 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-17 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-17 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-17 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-17 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-17 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-17 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-17 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.07% | 1415.9682
2016-01-17 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-17 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-17 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.91% | 1398.3661
2016-01-17 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-17 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-17 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-18 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-18 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-18 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-18 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-18 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-18 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-18 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.56% | 1515.3757
2016-01-18 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.02% | 1339.2328
2016-01-18 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.59% | 1347.8113
2016-01-18 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-18 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.67% | 1349.0504
2016-01-18 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-18 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-18 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-18 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-18 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-18 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-18 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.07% | 1331.593
2016-01-18 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-18 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-18 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.91% | 1398.3661
2016-01-18 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.36% | 1389.9246
2016-01-18 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.19% | 1509.2378
2016-01-18 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-19 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-19 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-19 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-19 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-19 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-19 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-19 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.56% | 1515.3757
2016-01-19 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.02% | 1339.2328
2016-01-19 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.59% | 1347.8113
2016-01-19 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-19 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.67% | 1349.0504
2016-01-19 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.5% | 1376.8462
2016-01-19 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.72% | 1410.6572
2016-01-19 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-19 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-19 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.02% | 1556.4876
2016-01-19 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.88% | 1554.2682
2016-01-19 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.07% | 1557.3434
2016-01-19 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2363
2016-01-19 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.42% | 1546.5349
2016-01-19 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-19 21:00 | 2 | 4700 | 1240 | 1730 | 91.36% | 1580.4682
2016-01-19 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-19 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-20 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-20 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-20 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-20 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-20 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-20 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-20 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.56% | 1377.8103
2016-01-20 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.02% | 1339.2328
2016-01-20 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.59% | 1347.8113
2016-01-20 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-20 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.67% | 1349.0504
2016-01-20 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.5% | 1376.8462
2016-01-20 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.72% | 1410.6572
2016-01-20 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-20 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.23% | 1560.0603
2016-01-20 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.02% | 1556.4876
2016-01-20 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.88% | 1554.2682
2016-01-20 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.07% | 1557.3434
2016-01-20 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2363
2016-01-20 19:00 | 2 | 4700 | 1240 | 1730 | 92.42% | 1598.9076
2016-01-20 20:00 | 2 | 4700 | 1240 | 1730 | 91.91% | 1590.067
2016-01-20 21:00 | 2 | 4700 | 1240 | 1730 | 91.36% | 1580.4682
2016-01-20 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-20 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-21 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-21 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-21 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-21 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-21 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-21 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-21 06:00 | 2 | 4700 | 1240 | 1730 | 90.56% | 1566.6932
2016-01-21 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.02% | 1472.9465
2016-01-21 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.59% | 1482.3815
2016-01-21 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.93% | 1471.3029
2016-01-21 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.67% | 1483.7443
2016-01-21 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.5% | 1376.8462
2016-01-21 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.72% | 1410.6572
2016-01-21 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8846
2016-01-21 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-21 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-21 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-21 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.07% | 1415.9682
2016-01-21 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-21 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-21 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-21 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-21 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-21 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-22 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-22 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-22 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-22 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-22 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-22 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-22 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.56% | 1515.3757
2016-01-22 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.02% | 1472.9465
2016-01-22 08:00 | 2 | 4700 | 1240 | 1730 | 88.59% | 1532.5817
2016-01-22 09:00 | 2 | 4700 | 1240 | 1730 | 87.93% | 1521.1279
2016-01-22 10:00 | 2 | 4700 | 1240 | 1730 | 88.67% | 1533.9906
2016-01-22 11:00 | 2 | 4700 | 1240 | 1730 | 90.5% | 1565.5969
2016-01-22 12:00 | 2 | 4700 | 1240 | 1730 | 92.72% | 1604.043
2016-01-22 13:00 | 2 | 4700 | 1240 | 1730 | 93.06% | 1609.9871
2016-01-22 14:00 | 2 | 4700 | 1240 | 1730 | 93.23% | 1612.891
2016-01-22 15:00 | 2 | 4700 | 1240 | 1730 | 93.02% | 1609.1973
2016-01-22 16:00 | 2 | 4700 | 1240 | 1730 | 92.88% | 1606.9028
2016-01-22 17:00 | 2 | 4700 | 1240 | 1730 | 93.07% | 1610.0821
2016-01-22 18:00 | 2 | 4700 | 1240 | 1730 | 93.06% | 1609.9714
2016-01-22 19:00 | 2 | 4700 | 1240 | 1730 | 92.42% | 1598.9076
2016-01-22 20:00 | 2 | 4700 | 1240 | 1730 | 91.91% | 1590.067
2016-01-22 21:00 | 2.2 | 5200 | 1240 | 1800 | 91.36% | 1644.4178
2016-01-22 22:00 | 2.2 | 5200 | 1240 | 1800 | 90.19% | 1623.4829
2016-01-22 23:00 | 2.2 | 5200 | 1240 | 1800 | 91.32% | 1643.7015
2016-01-23 | 2.2 | 5200 | 1240 | 1800 | 90.58% | 1630.3711
2016-01-23 01:00 | 2.2 | 5200 | 1240 | 1800 | 90.86% | 1635.4034
2016-01-23 02:00 | 2.2 | 5200 | 1240 | 1800 | 90.88% | 1635.811
2016-01-23 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-23 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-23 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-23 06:00 | 2 | 4700 | 1240 | 1730 | 90.56% | 1566.6932
2016-01-23 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.02% | 1472.9465
2016-01-23 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.59% | 1482.3815
2016-01-23 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.93% | 1471.3029
2016-01-23 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.67% | 1483.7443
2016-01-23 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.5% | 1514.3153
2016-01-23 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.72% | 1551.5021
2016-01-23 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2515
2016-01-23 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.23% | 1560.0603
2016-01-23 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.02% | 1556.4876
2016-01-23 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.88% | 1554.2682
2016-01-23 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.07% | 1557.3434
2016-01-23 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2363
2016-01-23 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.42% | 1546.5349
2016-01-23 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-23 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-23 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-23 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-24 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-24 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-24 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-24 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-24 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-24 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-24 06:00 | 2 | 4700 | 1240 | 1730 | 90.56% | 1566.6932
2016-01-24 07:00 | 2 | 4700 | 1240 | 1730 | 88.02% | 1522.8272
2016-01-24 08:00 | 2 | 4700 | 1240 | 1730 | 88.59% | 1532.5817
2016-01-24 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.93% | 1471.3029
2016-01-24 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.67% | 1483.7443
2016-01-24 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.5% | 1514.3153
2016-01-24 12:00 | 2 | 4700 | 1240 | 1730 | 92.72% | 1604.043
2016-01-24 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2515
2016-01-24 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.23% | 1560.0603
2016-01-24 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.02% | 1556.4876
2016-01-24 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.88% | 1554.2682
2016-01-24 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.07% | 1557.3434
2016-01-24 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2363
2016-01-24 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-24 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.91% | 1398.3661
2016-01-24 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.36% | 1389.9246
2016-01-24 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.19% | 1372.2296
2016-01-24 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.32% | 1389.3191
2016-01-25 | 1.4 | 3370 | 1240 | 1521.4286 | 90.58% | 1378.0518
2016-01-25 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.86% | 1382.3053
2016-01-25 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.88% | 1382.6498
2016-01-25 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.79% | 1381.2962
2016-01-25 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.21% | 1372.4519
2016-01-25 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.3% | 1292.014
2016-01-25 06:00 | 1.25 | 3040 | 1240 | 1440 | 90.56% | 1304.0683
2016-01-25 07:00 | 1.25 | 3040 | 1240 | 1440 | 88.02% | 1267.5556
2016-01-25 08:00 | 1.25 | 3040 | 1240 | 1440 | 88.59% | 1275.6749
2016-01-25 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.93% | 1266.1411
2016-01-25 10:00 | 1.25 | 3040 | 1240 | 1440 | 88.67% | 1276.8477
2016-01-25 11:00 | 1.25 | 3040 | 1240 | 1440 | 90.5% | 1303.1558
2016-01-25 12:00 | 1.25 | 3040 | 1240 | 1440 | 92.72% | 1335.1572
2016-01-25 13:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.1049
2016-01-25 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-25 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-25 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-25 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-25 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-25 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-25 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-25 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-25 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.19% | 1290.4608
2016-01-25 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.32% | 1306.5319
2016-01-26 | 1.3 | 3100 | 1240 | 1430.7692 | 90.58% | 1295.936
2016-01-26 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.86% | 1299.9361
2016-01-26 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.88% | 1300.26
2016-01-26 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.79% | 1298.9871
2016-01-26 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.21% | 1290.6698
2016-01-26 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.3% | 1292.014
2016-01-26 06:00 | 1.25 | 3040 | 1240 | 1440 | 90.56% | 1304.0683
2016-01-26 07:00 | 1.25 | 3040 | 1240 | 1440 | 88.02% | 1267.5556
2016-01-26 08:00 | 1.25 | 3040 | 1240 | 1440 | 88.59% | 1275.6749
2016-01-26 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-26 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-26 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-26 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-26 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-26 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-26 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-26 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-26 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.07% | 1415.9682
2016-01-26 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-26 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-26 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-26 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-26 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-26 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-27 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-27 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-27 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-27 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-27 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-27 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-27 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.56% | 1515.3757
2016-01-27 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.02% | 1339.2328
2016-01-27 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.59% | 1347.8113
2016-01-27 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.93% | 1337.7384
2016-01-27 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.67% | 1483.7443
2016-01-27 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.5% | 1514.3153
2016-01-27 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.72% | 1551.5021
2016-01-27 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 93.06% | 1557.2515
2016-01-27 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-27 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-27 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-27 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.07% | 1415.9682
2016-01-27 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.06% | 1415.8708
2016-01-27 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.42% | 1406.1409
2016-01-27 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.91% | 1537.9839
2016-01-27 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.36% | 1528.6995
2016-01-27 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 90.19% | 1509.2378
2016-01-27 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-28 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-28 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-28 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-28 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-28 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-28 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-28 06:00 | 2 | 4700 | 1240 | 1730 | 90.56% | 1566.6932
2016-01-28 07:00 | 2 | 4700 | 1240 | 1730 | 88.02% | 1522.8272
2016-01-28 08:00 | 2 | 4700 | 1240 | 1730 | 88.59% | 1532.5817
2016-01-28 09:00 | 2 | 4700 | 1240 | 1730 | 87.93% | 1521.1279
2016-01-28 10:00 | 2 | 4700 | 1240 | 1730 | 88.67% | 1533.9906
2016-01-28 11:00 | 2 | 4700 | 1240 | 1730 | 90.5% | 1565.5969
2016-01-28 12:00 | 2.2 | 5200 | 1240 | 1800 | 92.72% | 1668.9465
2016-01-28 13:00 | 2.2 | 5200 | 1240 | 1800 | 93.06% | 1675.1311
2016-01-28 14:00 | 2.2 | 5200 | 1240 | 1800 | 93.23% | 1678.1525
2016-01-28 15:00 | 2.2 | 5200 | 1240 | 1800 | 93.02% | 1674.3093
2016-01-28 16:00 | 2 | 4700 | 1240 | 1730 | 92.88% | 1606.9028
2016-01-28 17:00 | 2 | 4700 | 1240 | 1730 | 93.07% | 1610.0821
2016-01-28 18:00 | 2 | 4700 | 1240 | 1730 | 93.06% | 1609.9714
2016-01-28 19:00 | 2 | 4700 | 1240 | 1730 | 92.42% | 1598.9076
2016-01-28 20:00 | 2 | 4700 | 1240 | 1730 | 91.91% | 1590.067
2016-01-28 21:00 | 2 | 4700 | 1240 | 1730 | 91.36% | 1580.4682
2016-01-28 22:00 | 2 | 4700 | 1240 | 1730 | 90.19% | 1560.3475
2016-01-28 23:00 | 2 | 4700 | 1240 | 1730 | 91.32% | 1579.7798
2016-01-29 | 2 | 4700 | 1240 | 1730 | 90.58% | 1566.9678
2016-01-29 01:00 | 2 | 4700 | 1240 | 1730 | 90.86% | 1571.8044
2016-01-29 02:00 | 2 | 4700 | 1240 | 1730 | 90.88% | 1572.1961
2016-01-29 03:00 | 2 | 4700 | 1240 | 1730 | 90.79% | 1570.657
2016-01-29 04:00 | 2 | 4700 | 1240 | 1730 | 90.21% | 1560.6003
2016-01-29 05:00 | 2 | 4700 | 1240 | 1730 | 90.3% | 1562.2255
2016-01-29 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 90.56% | 1377.8103
2016-01-29 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.02% | 1259.4302
2016-01-29 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.59% | 1267.4975
2016-01-29 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.93% | 1258.0249
2016-01-29 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.67% | 1268.6628
2016-01-29 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.5% | 1294.8022
2016-01-29 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.72% | 1326.5985
2016-01-29 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5145
2016-01-29 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.23% | 1418.4384
2016-01-29 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.02% | 1415.19
2016-01-29 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.88% | 1413.1721
2016-01-29 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.07% | 1331.593
2016-01-29 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.06% | 1331.5015
2016-01-29 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-29 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-29 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-29 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-29 23:00 | 1.25 | 3040 | 1240 | 1440 | 91.32% | 1314.9612
2016-01-30 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-30 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-30 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-30 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-30 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-30 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-30 06:00 | 1.25 | 3040 | 1240 | 1440 | 90.56% | 1304.0683
2016-01-30 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.02% | 1090.5714
2016-01-30 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-30 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.93% | 1089.3545
2016-01-30 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.67% | 1098.5661
2016-01-30 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.5% | 1121.2009
2016-01-30 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.72% | 1148.7341
2016-01-30 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9909
2016-01-30 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.23% | 1155.0705
2016-01-30 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.02% | 1152.4253
2016-01-30 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.88% | 1150.7821
2016-01-30 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.07% | 1153.059
2016-01-30 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9797
2016-01-30 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.42% | 1145.0564
2016-01-30 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.91% | 1138.7251
2016-01-30 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.36% | 1131.851
2016-01-30 22:00 | 1.25 | 3040 | 1240 | 1440 | 90.19% | 1298.7863
2016-01-30 23:00 | 1.25 | 3040 | 1240 | 1440 | 91.32% | 1314.9612
2016-01-31 | 1.25 | 3040 | 1240 | 1440 | 90.58% | 1304.2969
2016-01-31 01:00 | 1.25 | 3040 | 1240 | 1440 | 90.86% | 1308.3228
2016-01-31 02:00 | 1.25 | 3040 | 1240 | 1440 | 90.88% | 1308.6488
2016-01-31 03:00 | 1.25 | 3040 | 1240 | 1440 | 90.79% | 1307.3677
2016-01-31 04:00 | 1.25 | 3040 | 1240 | 1440 | 90.21% | 1298.9968
2016-01-31 05:00 | 1.25 | 3040 | 1240 | 1440 | 90.3% | 1300.3495
2016-01-31 06:00 | 1.25 | 3040 | 1240 | 1440 | 90.56% | 1304.0683
2016-01-31 07:00 | 1.25 | 3040 | 1240 | 1440 | 88.02% | 1267.5556
2016-01-31 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.59% | 1097.5571
2016-01-31 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.93% | 1089.3545
2016-01-31 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 88.67% | 1098.5661
2016-01-31 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 90.5% | 1121.2009
2016-01-31 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.72% | 1148.7341
2016-01-31 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.06% | 1152.9909
2016-01-31 14:00 | 1.25 | 3040 | 1240 | 1440 | 93.23% | 1342.522
2016-01-31 15:00 | 1.25 | 3040 | 1240 | 1440 | 93.02% | 1339.4475
2016-01-31 16:00 | 1.25 | 3040 | 1240 | 1440 | 92.88% | 1337.5376
2016-01-31 17:00 | 1.25 | 3040 | 1240 | 1440 | 93.07% | 1340.184
2016-01-31 18:00 | 1.25 | 3040 | 1240 | 1440 | 93.06% | 1340.0918
2016-01-31 19:00 | 1.25 | 3040 | 1240 | 1440 | 92.42% | 1330.8827
2016-01-31 20:00 | 1.25 | 3040 | 1240 | 1440 | 91.91% | 1323.524
2016-01-31 21:00 | 1.25 | 3040 | 1240 | 1440 | 91.36% | 1315.5342
2016-01-31 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 90.19% | 1290.4608
2016-01-31 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.32% | 1306.5319
2016-02-01 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-01 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-01 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-01 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-01 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-01 05:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9072
2016-02-01 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.8614
2016-02-01 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.95% | 1188.783
2016-02-01 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-01 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-01 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.15% | 1178.8573
2016-02-01 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1314
2016-02-01 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.25% | 1192.5048
2016-02-01 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5896
2016-02-01 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5606
2016-02-01 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.34% | 1193.5822
2016-02-01 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.37% | 1194.0078
2016-02-01 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.9309
2016-02-01 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3061
2016-02-01 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-01 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-01 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1644
2016-02-01 22:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1247
2016-02-01 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.1% | 1383.8924
2016-02-02 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.3186
2016-02-02 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.09% | 1383.754
2016-02-02 02:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2368
2016-02-02 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-02 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-02 05:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9072
2016-02-02 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.8614
2016-02-02 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.95% | 1188.783
2016-02-02 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-02 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-02 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.15% | 1178.8573
2016-02-02 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1314
2016-02-02 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.25% | 1192.5048
2016-02-02 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-02 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-02 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-02 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-02 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-02 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-02 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-02 20:00 | 1.25 | 3040 | 1240 | 1440 | 96.43% | 1388.5736
2016-02-02 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1644
2016-02-02 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-03 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-03 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-03 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-03 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-03 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-03 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-03 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-03 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.7% | 1369.2756
2016-02-03 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5374
2016-02-03 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.15% | 1447.6488
2016-02-03 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.2654
2016-02-03 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.25% | 1464.4081
2016-02-03 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6523
2016-02-03 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4482
2016-02-03 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.34% | 1612.0749
2016-02-03 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.37% | 1612.6497
2016-02-03 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.96% | 1605.7927
2016-02-03 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.32% | 1611.7019
2016-02-03 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.47% | 1467.6795
2016-02-03 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.43% | 1467.0942
2016-02-03 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-03 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3371
2016-02-03 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.1% | 1462.1482
2016-02-04 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-04 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-04 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-04 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-04 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-04 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-04 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-04 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-04 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-04 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-04 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-04 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-04 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-04 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-04 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-04 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-04 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-04 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-04 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-04 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-04 20:00 | 1.25 | 3040 | 1240 | 1440 | 96.43% | 1388.5736
2016-02-04 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-04 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-04 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.1% | 1462.1482
2016-02-05 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.542
2016-02-05 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.09% | 1462.002
2016-02-05 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4555
2016-02-05 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.8% | 1457.4944
2016-02-05 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-05 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-05 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1459.9339
2016-02-05 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.95% | 1459.8377
2016-02-05 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.7% | 1456.0385
2016-02-05 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.65% | 1455.2535
2016-02-05 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.15% | 1447.6488
2016-02-05 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-05 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-05 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-05 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-05 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.34% | 1378.3907
2016-02-05 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.37% | 1378.8822
2016-02-05 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1373.0192
2016-02-05 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0718
2016-02-05 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-05 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-05 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-05 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-05 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-06 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-06 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-06 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-06 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-06 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-06 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-06 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-06 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-06 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-06 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-06 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.15% | 1178.8573
2016-02-06 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-06 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-06 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-06 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-06 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-06 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-06 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-06 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-06 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-06 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-06 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-06 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3371
2016-02-06 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.1% | 1462.1482
2016-02-07 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.542
2016-02-07 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.09% | 1462.002
2016-02-07 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4555
2016-02-07 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.8% | 1457.4944
2016-02-07 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-07 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-07 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-07 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-07 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.7% | 1369.2756
2016-02-07 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5374
2016-02-07 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.15% | 1361.3858
2016-02-07 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-07 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-07 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-07 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6167
2016-02-07 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.34% | 1465.7311
2016-02-07 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.37% | 1466.2538
2016-02-07 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1460.0192
2016-02-07 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.32% | 1465.392
2016-02-07 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.47% | 1467.6795
2016-02-07 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.43% | 1467.0942
2016-02-07 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-07 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3371
2016-02-07 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-08 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-08 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-08 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-08 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-08 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.61% | 1599.9523
2016-02-08 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-08 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1459.9339
2016-02-08 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-08 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.7% | 1369.2756
2016-02-08 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5374
2016-02-08 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.15% | 1361.3858
2016-02-08 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-08 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-08 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-08 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-08 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.34% | 1378.3907
2016-02-08 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.37% | 1378.8822
2016-02-08 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1373.0192
2016-02-08 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0718
2016-02-08 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-08 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-08 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-08 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-08 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-09 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-09 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-09 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-09 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-09 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-09 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-09 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.8614
2016-02-09 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.95% | 1188.783
2016-02-09 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-09 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-09 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.15% | 1178.8573
2016-02-09 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1314
2016-02-09 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.25% | 1192.5048
2016-02-09 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5896
2016-02-09 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5606
2016-02-09 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.34% | 1193.5822
2016-02-09 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.37% | 1194.0078
2016-02-09 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.9309
2016-02-09 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3061
2016-02-09 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-09 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-09 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1644
2016-02-09 22:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1247
2016-02-09 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-10 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-10 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-10 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-10 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-10 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-10 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-10 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-10 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-10 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-10 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-10 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.15% | 1361.3858
2016-02-10 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-10 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-10 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-10 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-10 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-10 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-10 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-10 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-10 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-10 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-10 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-10 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-10 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-11 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-11 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-11 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-11 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-11 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-11 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-11 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-11 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.95% | 1188.783
2016-02-11 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-11 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-11 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-11 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-11 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-11 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5896
2016-02-11 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.66% | 1197.5606
2016-02-11 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.34% | 1193.5822
2016-02-11 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.37% | 1194.0078
2016-02-11 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.96% | 1188.9309
2016-02-11 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3061
2016-02-11 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-11 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-11 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1778
2016-02-11 22:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1247
2016-02-11 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.1% | 1383.8924
2016-02-12 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.3186
2016-02-12 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.09% | 1383.754
2016-02-12 02:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2368
2016-02-12 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.8% | 1379.4877
2016-02-12 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.61% | 1376.8514
2016-02-12 05:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9072
2016-02-12 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-12 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-12 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-12 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-12 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-12 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-12 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-12 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-12 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-12 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-12 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-12 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-12 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-12 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-12 20:00 | 1.25 | 3040 | 1240 | 1440 | 96.43% | 1388.5736
2016-02-12 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-12 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3371
2016-02-12 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.1% | 1462.1482
2016-02-13 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.542
2016-02-13 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.09% | 1462.002
2016-02-13 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4555
2016-02-13 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.8% | 1457.4944
2016-02-13 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-13 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-13 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-13 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-13 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-13 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-13 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-13 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-13 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-13 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-13 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-13 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-13 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-13 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-13 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-13 19:00 | 1.25 | 3040 | 1240 | 1440 | 96.47% | 1389.1276
2016-02-13 20:00 | 1.25 | 3040 | 1240 | 1440 | 96.43% | 1388.5736
2016-02-13 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1644
2016-02-13 22:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1247
2016-02-13 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-14 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-14 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-14 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-14 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-14 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-14 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-14 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-14 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-14 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.7% | 1369.2756
2016-02-14 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5374
2016-02-14 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.15% | 1361.3858
2016-02-14 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.2654
2016-02-14 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.25% | 1464.4081
2016-02-14 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6523
2016-02-14 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6167
2016-02-14 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.34% | 1465.7311
2016-02-14 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.37% | 1466.2538
2016-02-14 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1460.0192
2016-02-14 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.32% | 1465.392
2016-02-14 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-14 20:00 | 1.25 | 3040 | 1240 | 1440 | 96.43% | 1388.5736
2016-02-14 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1644
2016-02-14 22:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1247
2016-02-14 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.1% | 1383.8924
2016-02-15 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.3186
2016-02-15 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.09% | 1383.754
2016-02-15 02:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2368
2016-02-15 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.8% | 1379.4877
2016-02-15 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.61% | 1376.8514
2016-02-15 05:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9072
2016-02-15 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-15 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-15 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-15 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5374
2016-02-15 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-15 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-15 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-15 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-15 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-15 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.34% | 1378.3907
2016-02-15 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.37% | 1378.8822
2016-02-15 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1373.0192
2016-02-15 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-15 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-15 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-15 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1778
2016-02-15 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.05% | 1190.004
2016-02-15 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.1% | 1190.6645
2016-02-16 | 1.13 | 2640 | 1240 | 1238.9381 | 96.06% | 1190.1709
2016-02-16 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.09% | 1190.5455
2016-02-16 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.06% | 1190.1005
2016-02-16 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.8% | 1186.8748
2016-02-16 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.61% | 1184.6067
2016-02-16 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2358
2016-02-16 06:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.96% | 1243.9013
2016-02-16 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.95% | 1243.8193
2016-02-16 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.7% | 1240.5822
2016-02-16 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-16 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.15% | 1178.8573
2016-02-16 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1314
2016-02-16 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-16 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-16 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-16 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-16 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-16 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-16 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-16 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-16 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-16 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1778
2016-02-16 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.05% | 1190.004
2016-02-16 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.1% | 1383.8924
2016-02-17 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.3186
2016-02-17 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.09% | 1383.754
2016-02-17 02:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2368
2016-02-17 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.8% | 1379.4877
2016-02-17 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.61% | 1184.6067
2016-02-17 05:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.83% | 1242.2004
2016-02-17 06:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.96% | 1243.9013
2016-02-17 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.95% | 1243.8193
2016-02-17 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-17 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-17 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-17 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-17 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-17 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-17 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-17 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.34% | 1378.3907
2016-02-17 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.37% | 1378.8822
2016-02-17 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1373.0192
2016-02-17 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0718
2016-02-17 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-17 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-17 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-17 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3371
2016-02-17 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.1% | 1462.1482
2016-02-18 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.542
2016-02-18 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.09% | 1462.002
2016-02-18 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4555
2016-02-18 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.8% | 1457.4944
2016-02-18 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-18 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-18 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1372.939
2016-02-18 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.95% | 1372.8485
2016-02-18 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.7% | 1456.0385
2016-02-18 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.65% | 1600.5511
2016-02-18 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.15% | 1592.1871
2016-02-18 11:00 | 2 | 4700 | 1240 | 1730 | 95.98% | 1660.4521
2016-02-18 12:00 | 2 | 4700 | 1240 | 1730 | 96.25% | 1665.1627
2016-02-18 13:00 | 2 | 4700 | 1240 | 1730 | 96.66% | 1672.2628
2016-02-18 14:00 | 2 | 4700 | 1240 | 1730 | 96.66% | 1672.2223
2016-02-18 15:00 | 2 | 4700 | 1240 | 1730 | 96.34% | 1666.667
2016-02-18 16:00 | 2 | 4700 | 1240 | 1730 | 96.37% | 1667.2613
2016-02-18 17:00 | 2 | 4700 | 1240 | 1730 | 95.96% | 1660.1721
2016-02-18 18:00 | 2 | 4700 | 1240 | 1730 | 96.32% | 1666.2815
2016-02-18 19:00 | 2 | 4700 | 1240 | 1730 | 96.47% | 1668.8825
2016-02-18 20:00 | 2 | 4700 | 1240 | 1730 | 96.43% | 1668.2169
2016-02-18 21:00 | 2 | 4700 | 1240 | 1730 | 95.98% | 1660.5169
2016-02-18 22:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6706
2016-02-18 23:00 | 2 | 4700 | 1240 | 1730 | 96.1% | 1662.5929
2016-02-19 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.9036
2016-02-19 01:00 | 2 | 4700 | 1240 | 1730 | 96.09% | 1662.4266
2016-02-19 02:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.8053
2016-02-19 03:00 | 2 | 4700 | 1240 | 1730 | 95.8% | 1657.3012
2016-02-19 04:00 | 2 | 4700 | 1240 | 1730 | 95.61% | 1654.134
2016-02-19 05:00 | 2 | 4700 | 1240 | 1730 | 95.83% | 1657.8052
2016-02-19 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1459.9339
2016-02-19 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.95% | 1459.8377
2016-02-19 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.7% | 1456.0385
2016-02-19 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.65% | 1455.2535
2016-02-19 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.15% | 1447.6488
2016-02-19 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.2654
2016-02-19 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.25% | 1464.4081
2016-02-19 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6523
2016-02-19 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6167
2016-02-19 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.34% | 1465.7311
2016-02-19 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.37% | 1466.2538
2016-02-19 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1460.0192
2016-02-19 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.32% | 1465.392
2016-02-19 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.47% | 1467.6795
2016-02-19 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.43% | 1467.0942
2016-02-19 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-19 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2421
2016-02-19 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-20 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-20 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-20 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-20 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-20 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.61% | 1599.9523
2016-02-20 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.83% | 1603.5033
2016-02-20 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.96% | 1605.6989
2016-02-20 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.95% | 1605.593
2016-02-20 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.7% | 1601.4145
2016-02-20 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.65% | 1600.5511
2016-02-20 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.15% | 1592.1871
2016-02-20 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.0635
2016-02-20 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.25% | 1610.6198
2016-02-20 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4873
2016-02-20 14:00 | 2 | 4700 | 1240 | 1730 | 96.66% | 1672.2223
2016-02-20 15:00 | 2 | 4700 | 1240 | 1730 | 96.34% | 1666.667
2016-02-20 16:00 | 2 | 4700 | 1240 | 1730 | 96.37% | 1667.2613
2016-02-20 17:00 | 2 | 4700 | 1240 | 1730 | 95.96% | 1660.1721
2016-02-20 18:00 | 2 | 4700 | 1240 | 1730 | 96.32% | 1666.2815
2016-02-20 19:00 | 2 | 4700 | 1240 | 1730 | 96.47% | 1668.8825
2016-02-20 20:00 | 2 | 4700 | 1240 | 1730 | 96.43% | 1668.2169
2016-02-20 21:00 | 2 | 4700 | 1240 | 1730 | 95.98% | 1660.5169
2016-02-20 22:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6706
2016-02-20 23:00 | 2 | 4700 | 1240 | 1730 | 96.1% | 1662.5929
2016-02-21 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.9036
2016-02-21 01:00 | 2 | 4700 | 1240 | 1730 | 96.09% | 1662.4266
2016-02-21 02:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.8053
2016-02-21 03:00 | 2 | 4700 | 1240 | 1730 | 95.8% | 1657.3012
2016-02-21 04:00 | 2 | 4700 | 1240 | 1730 | 95.61% | 1654.134
2016-02-21 05:00 | 2 | 4700 | 1240 | 1730 | 95.83% | 1657.8052
2016-02-21 06:00 | 2 | 4700 | 1240 | 1730 | 95.96% | 1660.0751
2016-02-21 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.95% | 1605.593
2016-02-21 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.7% | 1601.4145
2016-02-21 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.65% | 1455.2535
2016-02-21 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.15% | 1447.6488
2016-02-21 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.2654
2016-02-21 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.25% | 1464.4081
2016-02-21 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6523
2016-02-21 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6167
2016-02-21 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.34% | 1465.7311
2016-02-21 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.37% | 1466.2538
2016-02-21 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1460.0192
2016-02-21 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0718
2016-02-21 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-21 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-21 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-21 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-21 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-22 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-22 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-22 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-22 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-22 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-22 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-22 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-22 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-22 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-22 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-22 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-22 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-22 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-22 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-22 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-22 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-22 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-22 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-22 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-22 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-22 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-22 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-22 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-22 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-23 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.542
2016-02-23 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.09% | 1462.002
2016-02-23 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4555
2016-02-23 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.8% | 1457.4944
2016-02-23 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.61% | 1454.7091
2016-02-23 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.83% | 1371.0617
2016-02-23 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-23 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-23 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-23 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-23 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-23 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.98% | 1382.1104
2016-02-23 12:00 | 1.25 | 3040 | 1240 | 1440 | 96.25% | 1386.0313
2016-02-23 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9413
2016-02-23 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.66% | 1391.9076
2016-02-23 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.34% | 1387.2836
2016-02-23 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.37% | 1387.7782
2016-02-23 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.8773
2016-02-23 18:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9626
2016-02-23 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.47% | 1195.1688
2016-02-23 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.43% | 1194.6922
2016-02-23 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.98% | 1189.1778
2016-02-23 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.05% | 1190.004
2016-02-23 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.1% | 1190.6645
2016-02-24 | 1.13 | 2640 | 1240 | 1238.9381 | 96.06% | 1190.1709
2016-02-24 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.09% | 1190.5455
2016-02-24 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.06% | 1190.1005
2016-02-24 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.8% | 1186.8748
2016-02-24 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.61% | 1184.6067
2016-02-24 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2358
2016-02-24 06:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.96% | 1243.9013
2016-02-24 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.95% | 1243.8193
2016-02-24 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.7% | 1185.6892
2016-02-24 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.65% | 1185.05
2016-02-24 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-24 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-24 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-24 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1383.0186
2016-02-24 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.66% | 1382.9851
2016-02-24 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.34% | 1378.3907
2016-02-24 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.37% | 1378.8822
2016-02-24 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.96% | 1373.0192
2016-02-24 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0718
2016-02-24 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.47% | 1380.223
2016-02-24 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-24 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.98% | 1460.3225
2016-02-24 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2421
2016-02-24 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-25 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-25 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-25 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-25 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-25 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.61% | 1599.9523
2016-02-25 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.83% | 1457.9377
2016-02-25 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1459.9339
2016-02-25 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.95% | 1459.8377
2016-02-25 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.7% | 1456.0385
2016-02-25 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.65% | 1600.5511
2016-02-25 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.15% | 1592.1871
2016-02-25 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.0635
2016-02-25 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.25% | 1610.6198
2016-02-25 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4873
2016-02-25 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4482
2016-02-25 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.34% | 1612.0749
2016-02-25 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.37% | 1612.6497
2016-02-25 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.96% | 1605.7927
2016-02-25 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.32% | 1611.7019
2016-02-25 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.47% | 1614.2178
2016-02-25 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.43% | 1613.574
2016-02-25 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.1262
2016-02-25 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2421
2016-02-25 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-26 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-26 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-26 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-26 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-26 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.61% | 1599.9523
2016-02-26 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.83% | 1603.5033
2016-02-26 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1459.9339
2016-02-26 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.95% | 1459.8377
2016-02-26 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.7% | 1456.0385
2016-02-26 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.65% | 1600.5511
2016-02-26 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.15% | 1592.1871
2016-02-26 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.0635
2016-02-26 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.25% | 1610.6198
2016-02-26 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4873
2016-02-26 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.66% | 1617.4482
2016-02-26 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.34% | 1612.0749
2016-02-26 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.37% | 1612.6497
2016-02-26 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.96% | 1605.7927
2016-02-26 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.32% | 1611.7019
2016-02-26 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.47% | 1467.6795
2016-02-26 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.43% | 1379.6725
2016-02-26 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.3043
2016-02-26 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2585
2016-02-26 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.1% | 1375.0213
2016-02-27 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.4512
2016-02-27 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.09% | 1374.8838
2016-02-27 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3699
2016-02-27 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.8% | 1370.6448
2016-02-27 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.61% | 1368.0254
2016-02-27 05:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9072
2016-02-27 06:00 | 1.25 | 3040 | 1240 | 1440 | 95.96% | 1381.7966
2016-02-27 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.95% | 1381.7056
2016-02-27 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.7% | 1378.1097
2016-02-27 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.3667
2016-02-27 10:00 | 1.25 | 3040 | 1240 | 1440 | 95.15% | 1370.169
2016-02-27 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.98% | 1373.2507
2016-02-27 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.25% | 1377.1465
2016-02-27 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6523
2016-02-27 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.66% | 1470.6167
2016-02-27 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.34% | 1465.7311
2016-02-27 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.37% | 1466.2538
2016-02-27 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.96% | 1460.0192
2016-02-27 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.32% | 1465.392
2016-02-27 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.47% | 1467.6795
2016-02-27 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.43% | 1613.574
2016-02-27 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.1262
2016-02-27 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2421
2016-02-27 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-28 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.4675
2016-02-28 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.09% | 1607.9734
2016-02-28 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3724
2016-02-28 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.8% | 1603.0158
2016-02-28 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.61% | 1599.9523
2016-02-28 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.83% | 1603.5033
2016-02-28 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.96% | 1605.6989
2016-02-28 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.95% | 1605.593
2016-02-28 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.7% | 1601.4145
2016-02-28 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.65% | 1600.5511
2016-02-28 10:00 | 2 | 4700 | 1240 | 1730 | 95.15% | 1646.1058
2016-02-28 11:00 | 2 | 4700 | 1240 | 1730 | 95.98% | 1660.4521
2016-02-28 12:00 | 2 | 4700 | 1240 | 1730 | 96.25% | 1665.1627
2016-02-28 13:00 | 2 | 4700 | 1240 | 1730 | 96.66% | 1672.2628
2016-02-28 14:00 | 2 | 4700 | 1240 | 1730 | 96.66% | 1672.2223
2016-02-28 15:00 | 2 | 4700 | 1240 | 1730 | 96.34% | 1666.667
2016-02-28 16:00 | 2 | 4700 | 1240 | 1730 | 96.37% | 1667.2613
2016-02-28 17:00 | 2 | 4700 | 1240 | 1730 | 95.96% | 1660.1721
2016-02-28 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.32% | 1611.7019
2016-02-28 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.47% | 1614.2178
2016-02-28 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.43% | 1613.574
2016-02-28 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.98% | 1606.1262
2016-02-28 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2421
2016-02-28 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.1% | 1608.1342
2016-02-29 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-02-29 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-02-29 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-02-29 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-02-29 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-02-29 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-02-29 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-02-29 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-02-29 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-02-29 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-02-29 10:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-02-29 11:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-02-29 12:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-02-29 13:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-02-29 14:00 | 2 | 4700 | 1240 | 1730 | 96.95% | 1677.244
2016-02-29 15:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-02-29 16:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-02-29 17:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-02-29 18:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-02-29 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-02-29 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-02-29 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-02-29 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-02-29 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-01 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-01 01:00 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-01 02:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-01 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-01 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-01 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.68% | 1486.1389
2016-03-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.55% | 1395.7782
2016-03-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.14% | 1389.8156
2016-03-01 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0832
2016-03-01 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.23% | 1391.1511
2016-03-01 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.41% | 1481.9983
2016-03-01 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-01 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-01 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-01 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-01 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-01 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-01 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-01 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-01 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.21% | 1390.7817
2016-03-01 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1109
2016-03-01 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.43% | 1393.995
2016-03-01 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.39% | 1393.3818
2016-03-01 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4417
2016-03-02 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1048
2016-03-02 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.7% | 1397.8043
2016-03-02 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9809
2016-03-02 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2873
2016-03-02 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1417
2016-03-02 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.68% | 1397.5824
2016-03-02 06:00 | 1.25 | 3040 | 1240 | 1440 | 97.55% | 1404.7832
2016-03-02 07:00 | 1.25 | 3040 | 1240 | 1440 | 97.14% | 1398.7822
2016-03-02 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.3% | 1401.0644
2016-03-02 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.23% | 1400.1263
2016-03-02 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.41% | 1402.6801
2016-03-02 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.51% | 1404.1794
2016-03-02 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.46% | 1403.441
2016-03-02 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.71% | 1392.6094
2016-03-02 14:00 | 1.25 | 3040 | 1240 | 1440 | 96.95% | 1396.0875
2016-03-02 15:00 | 1.25 | 3040 | 1240 | 1440 | 96.97% | 1396.3376
2016-03-02 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.4% | 1402.6194
2016-03-02 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9812
2016-03-02 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7329
2016-03-02 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.21% | 1399.7545
2016-03-02 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.79% | 1408.1374
2016-03-02 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.43% | 1402.9885
2016-03-02 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.39% | 1393.3818
2016-03-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4417
2016-03-03 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1048
2016-03-03 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.7% | 1397.8043
2016-03-03 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9809
2016-03-03 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2873
2016-03-03 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1417
2016-03-03 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.68% | 1397.5824
2016-03-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.55% | 1395.7782
2016-03-03 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.14% | 1389.8156
2016-03-03 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0832
2016-03-03 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.23% | 1391.1511
2016-03-03 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-03 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-03 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-03 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-03 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-03 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-03 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-03 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-03 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-03 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-03 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-03 21:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-03 22:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-03 23:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-04 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-04 01:00 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-04 02:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-04 03:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-04 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-04 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-04 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-04 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-04 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-04 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-04 10:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-04 11:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-03-04 12:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-04 13:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-04 14:00 | 2.2 | 5200 | 1240 | 1800 | 96.95% | 1745.1094
2016-03-04 15:00 | 2.2 | 5200 | 1240 | 1800 | 96.97% | 1745.422
2016-03-04 16:00 | 2.2 | 5200 | 1240 | 1800 | 97.4% | 1753.2743
2016-03-04 17:00 | 2.2 | 5200 | 1240 | 1800 | 97.57% | 1756.2265
2016-03-04 18:00 | 2.2 | 5200 | 1240 | 1800 | 97.69% | 1758.4161
2016-03-04 19:00 | 2.2 | 5200 | 1240 | 1800 | 97.21% | 1749.6931
2016-03-04 20:00 | 2.2 | 5200 | 1240 | 1800 | 97.79% | 1760.1718
2016-03-04 21:00 | 2.2 | 5200 | 1240 | 1800 | 97.43% | 1753.7357
2016-03-04 22:00 | 2.2 | 5200 | 1240 | 1800 | 97.39% | 1752.9642
2016-03-04 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.46% | 1754.2976
2016-03-05 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1758.906
2016-03-05 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.7% | 1758.528
2016-03-05 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.57% | 1756.2341
2016-03-05 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.45% | 1754.1034
2016-03-05 04:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-05 05:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-05 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-05 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-05 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-05 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-05 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-05 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-05 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-05 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-05 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-05 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-05 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-05 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-05 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-05 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-05 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-05 21:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-05 22:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-05 23:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-06 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-06 01:00 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-06 02:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-06 03:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-06 04:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-06 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-06 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-06 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-06 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-06 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-06 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-06 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-06 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-06 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-06 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-06 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-06 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-06 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-06 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-06 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-06 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-06 21:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-06 22:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-06 23:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-07 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-07 01:00 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-07 02:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-07 03:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-07 04:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-07 05:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-07 06:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-07 07:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-07 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-07 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-07 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-07 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-07 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-07 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-07 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-07 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-07 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-07 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-07 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-07 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-07 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-07 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-07 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-07 23:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-08 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-08 01:00 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-08 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-08 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-08 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-08 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-08 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-08 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-08 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-08 09:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-08 10:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-03-08 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-08 12:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-08 13:00 | 2 | 4700 | 1240 | 1730 | 96.95% | 1677.244
2016-03-08 14:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-03-08 15:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-03-08 16:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-03-08 17:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-03-08 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-08 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-08 20:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-08 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-08 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-08 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-09 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-09 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-09 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-09 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-09 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-09 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-09 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-09 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-09 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-09 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-09 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-09 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-09 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-09 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-09 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-09 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-09 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-09 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-09 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-09 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.7642
2016-03-09 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-09 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.39% | 1481.6721
2016-03-09 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-09 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-10 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-10 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-10 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.45% | 1754.1034
2016-03-10 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.79% | 1760.2105
2016-03-10 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.68% | 1758.2488
2016-03-10 05:00 | 2.2 | 5200 | 1240 | 1800 | 97.55% | 1755.979
2016-03-10 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-10 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-10 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-10 09:00 | 2.2 | 5200 | 1240 | 1800 | 97.41% | 1753.3501
2016-03-10 10:00 | 2.2 | 5200 | 1240 | 1800 | 97.51% | 1755.2243
2016-03-10 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-10 12:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-10 13:00 | 2 | 4700 | 1240 | 1730 | 96.95% | 1677.244
2016-03-10 14:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-03-10 15:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-03-10 16:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-03-10 17:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-03-10 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-10 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-10 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-10 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.39% | 1481.6721
2016-03-10 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-10 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-11 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-11 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-11 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-11 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-11 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-11 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-11 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-11 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-11 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-11 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-11 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-11 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-11 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-11 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-11 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-11 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-11 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-11 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-11 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-11 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-11 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-11 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-11 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-11 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-12 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-12 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-12 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-12 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-12 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-12 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-12 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-12 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-12 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.23% | 1479.3001
2016-03-12 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.41% | 1481.9983
2016-03-12 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-12 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-12 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-12 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-12 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-12 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-12 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-12 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-12 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-12 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-12 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-12 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-12 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-12 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-13 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-13 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4359
2016-03-13 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.635
2016-03-13 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-13 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-13 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.55% | 1484.2203
2016-03-13 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.14% | 1477.88
2016-03-13 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0832
2016-03-13 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.23% | 1391.1511
2016-03-13 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-13 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-13 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4446
2016-03-13 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.71% | 1383.6824
2016-03-13 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.95% | 1387.1382
2016-03-13 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.97% | 1387.3867
2016-03-13 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.4% | 1393.6283
2016-03-13 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9749
2016-03-13 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7154
2016-03-13 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.21% | 1390.7817
2016-03-13 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1109
2016-03-13 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-13 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-13 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-13 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-14 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-14 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-14 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-14 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-14 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-14 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-14 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-14 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.2912
2016-03-14 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.23% | 1479.3001
2016-03-14 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.41% | 1481.9983
2016-03-14 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-14 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-14 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-14 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-14 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-14 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-14 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-14 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-14 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-14 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-14 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-14 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-14 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-14 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-15 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-15 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-15 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-15 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-15 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-15 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-15 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-15 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-15 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-15 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-15 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-15 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-15 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-15 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-15 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-15 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-15 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-15 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-15 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-15 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-15 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-15 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-15 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-15 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-16 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-16 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-16 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-16 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-16 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-16 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-16 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.14% | 1477.88
2016-03-16 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.2912
2016-03-16 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.23% | 1479.3001
2016-03-16 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.41% | 1481.9983
2016-03-16 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-16 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4446
2016-03-16 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.71% | 1383.6824
2016-03-16 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.95% | 1387.1382
2016-03-16 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.97% | 1387.3867
2016-03-16 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.4% | 1393.6283
2016-03-16 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9749
2016-03-16 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7154
2016-03-16 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.21% | 1399.7545
2016-03-16 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.79% | 1408.1374
2016-03-16 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.43% | 1402.9885
2016-03-16 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.39% | 1402.3713
2016-03-16 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4417
2016-03-16 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1048
2016-03-17 | 1.3 | 3100 | 1240 | 1430.7692 | 97.7% | 1397.8043
2016-03-17 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9809
2016-03-17 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.635
2016-03-17 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.797
2016-03-17 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.68% | 1486.1389
2016-03-17 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.55% | 1484.2203
2016-03-17 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.14% | 1477.88
2016-03-17 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.2912
2016-03-17 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.23% | 1479.3001
2016-03-17 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-17 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-17 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4446
2016-03-17 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.71% | 1383.6824
2016-03-17 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-17 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-17 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-17 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-17 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-17 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-17 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.7642
2016-03-17 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-17 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-17 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-17 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-18 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-18 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-18 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-18 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-18 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-18 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-18 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.14% | 1477.88
2016-03-18 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0832
2016-03-18 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.23% | 1391.1511
2016-03-18 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-18 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-18 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-18 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-18 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-18 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-18 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-18 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-18 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-18 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-18 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-18 20:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-18 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-18 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-18 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-19 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-19 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-19 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-19 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-19 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-19 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-19 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-19 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-19 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-19 09:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-19 10:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-03-19 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-19 12:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-19 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-19 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-19 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-19 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-19 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-19 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-19 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-19 20:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-19 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-19 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-19 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-20 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-20 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-20 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-20 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-20 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-20 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-20 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-20 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-20 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-20 09:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-20 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-20 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-20 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-20 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-20 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-20 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-20 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-20 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-20 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.21% | 1390.7817
2016-03-20 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1109
2016-03-20 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.43% | 1402.9885
2016-03-20 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.39% | 1402.3713
2016-03-20 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.46% | 1403.4381
2016-03-20 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1248
2016-03-21 | 1.25 | 3040 | 1240 | 1440 | 97.7% | 1406.8224
2016-03-21 01:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9873
2016-03-21 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2873
2016-03-21 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1417
2016-03-21 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.68% | 1397.5824
2016-03-21 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.55% | 1395.7782
2016-03-21 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.14% | 1389.8156
2016-03-21 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0832
2016-03-21 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.23% | 1391.1511
2016-03-21 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-21 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-21 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-21 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-21 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-21 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-21 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-21 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-21 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-21 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-21 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1109
2016-03-21 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.43% | 1402.9885
2016-03-21 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.39% | 1402.3713
2016-03-21 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4417
2016-03-21 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1048
2016-03-22 | 1.25 | 3040 | 1240 | 1440 | 97.7% | 1406.8224
2016-03-22 01:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9873
2016-03-22 02:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2827
2016-03-22 03:00 | 1.25 | 3040 | 1240 | 1440 | 97.79% | 1408.1684
2016-03-22 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.68% | 1406.5991
2016-03-22 05:00 | 1.25 | 3040 | 1240 | 1440 | 97.55% | 1404.7832
2016-03-22 06:00 | 1.25 | 3040 | 1240 | 1440 | 97.14% | 1398.7822
2016-03-22 07:00 | 1.25 | 3040 | 1240 | 1440 | 97.3% | 1401.0644
2016-03-22 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.23% | 1400.1263
2016-03-22 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.41% | 1402.6801
2016-03-22 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-22 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4446
2016-03-22 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-22 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-22 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-22 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-22 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-22 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-22 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-22 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-22 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-22 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-22 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-22 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-23 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-23 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-23 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-23 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-23 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-23 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-23 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-23 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-23 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-23 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-23 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-23 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-23 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-23 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-23 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-23 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-23 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-23 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-23 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-23 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-23 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-23 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-23 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-23 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-24 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-24 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-24 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-24 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-24 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-24 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-24 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-24 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-24 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-24 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-24 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-24 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-24 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-24 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-24 14:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-03-24 15:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-03-24 16:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-03-24 17:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-03-24 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-24 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-24 20:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-24 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-24 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-24 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-25 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-25 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-25 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-25 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-25 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-25 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-25 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-25 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-25 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-25 09:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-25 10:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-03-25 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-25 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-25 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-25 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-25 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.4% | 1481.9342
2016-03-25 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4295
2016-03-25 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2803
2016-03-25 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-25 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.7642
2016-03-25 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-25 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.39% | 1481.6721
2016-03-25 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7992
2016-03-25 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-26 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-26 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-26 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-26 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-26 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-26 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-26 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-26 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-26 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-26 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-26 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-26 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-26 12:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-26 13:00 | 2 | 4700 | 1240 | 1730 | 96.95% | 1677.244
2016-03-26 14:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-03-26 15:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-03-26 16:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-03-26 17:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-03-26 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-26 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-26 20:00 | 2 | 4700 | 1240 | 1730 | 97.43% | 1685.5348
2016-03-26 21:00 | 2 | 4700 | 1240 | 1730 | 97.39% | 1684.7933
2016-03-26 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-26 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-27 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-27 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-27 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-27 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-27 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-27 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-27 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-27 07:00 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2232
2016-03-27 08:00 | 2 | 4700 | 1240 | 1730 | 97.23% | 1682.0962
2016-03-27 09:00 | 2 | 4700 | 1240 | 1730 | 97.41% | 1685.1643
2016-03-27 10:00 | 2 | 4700 | 1240 | 1730 | 97.51% | 1686.9656
2016-03-27 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0785
2016-03-27 12:00 | 2 | 4700 | 1240 | 1730 | 96.71% | 1673.0654
2016-03-27 13:00 | 2 | 4700 | 1240 | 1730 | 96.95% | 1677.244
2016-03-27 14:00 | 2 | 4700 | 1240 | 1730 | 96.97% | 1677.5444
2016-03-27 15:00 | 2 | 4700 | 1240 | 1730 | 97.4% | 1685.0914
2016-03-27 16:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9288
2016-03-27 17:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0333
2016-03-27 18:00 | 2 | 4700 | 1240 | 1730 | 97.21% | 1681.6495
2016-03-27 19:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7206
2016-03-27 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-27 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-27 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8471
2016-03-27 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.1311
2016-03-28 | 1.5 | 3750 | 1240 | 1673.3333 | 97.7% | 1634.7798
2016-03-28 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6472
2016-03-28 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.6665
2016-03-28 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3438
2016-03-28 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.68% | 1634.5202
2016-03-28 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.55% | 1632.4101
2016-03-28 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.14% | 1625.4367
2016-03-28 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-28 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-28 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.41% | 1629.9662
2016-03-28 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.7085
2016-03-28 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8505
2016-03-28 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.71% | 1618.2637
2016-03-28 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.95% | 1622.3054
2016-03-28 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.97% | 1622.596
2016-03-28 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-28 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-28 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-28 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.21% | 1478.9072
2016-03-28 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.79% | 1399.1109
2016-03-28 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.43% | 1402.9885
2016-03-28 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.39% | 1402.3713
2016-03-28 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4417
2016-03-28 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1048
2016-03-29 | 1.3 | 3100 | 1240 | 1430.7692 | 97.7% | 1397.8043
2016-03-29 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9809
2016-03-29 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.635
2016-03-29 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.797
2016-03-29 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.68% | 1486.1389
2016-03-29 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.55% | 1484.2203
2016-03-29 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.14% | 1477.88
2016-03-29 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.2912
2016-03-29 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.23% | 1479.3001
2016-03-29 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.41% | 1393.6886
2016-03-29 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1783
2016-03-29 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4446
2016-03-29 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.71% | 1383.6824
2016-03-29 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.95% | 1387.1382
2016-03-29 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.97% | 1387.3867
2016-03-29 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.4% | 1393.6283
2016-03-29 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9749
2016-03-29 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7154
2016-03-29 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.21% | 1390.7817
2016-03-29 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.79% | 1487.7642
2016-03-29 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.43% | 1482.3242
2016-03-29 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-29 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-29 23:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.5041
2016-03-30 | 2 | 4700 | 1240 | 1730 | 97.7% | 1690.1408
2016-03-30 01:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9361
2016-03-30 02:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8882
2016-03-30 03:00 | 2 | 4700 | 1240 | 1730 | 97.79% | 1691.7579
2016-03-30 04:00 | 2 | 4700 | 1240 | 1730 | 97.68% | 1689.8725
2016-03-30 05:00 | 2 | 4700 | 1240 | 1730 | 97.55% | 1687.6909
2016-03-30 06:00 | 2 | 4700 | 1240 | 1730 | 97.14% | 1680.4814
2016-03-30 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.0887
2016-03-30 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.23% | 1626.9986
2016-03-30 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.41% | 1481.9983
2016-03-30 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5824
2016-03-30 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.8023
2016-03-30 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.71% | 1471.3581
2016-03-30 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.95% | 1475.0329
2016-03-30 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.97% | 1475.2971
2016-03-30 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.4% | 1629.8957
2016-03-30 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6401
2016-03-30 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.69% | 1634.6757
2016-03-30 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.21% | 1626.5665
2016-03-30 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.79% | 1636.3078
2016-03-30 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.43% | 1630.3246
2016-03-30 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.39% | 1629.6074
2016-03-30 22:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.075
2016-03-30 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-03-31 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-03-31 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-03-31 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-03-31 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-03-31 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-03-31 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-03-31 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-03-31 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-03-31 08:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0528
2016-03-31 09:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0698
2016-03-31 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-03-31 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-03-31 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.6109
2016-03-31 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-03-31 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-03-31 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-03-31 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-03-31 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.11% | 1641.7771
2016-03-31 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0328
2016-03-31 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-03-31 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-03-31 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-03-31 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-03-31 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-01 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-01 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-01 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-01 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-01 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-01 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-01 06:00 | 2.2 | 5200 | 1240 | 1800 | 98% | 1764.0199
2016-04-01 07:00 | 2.2 | 5200 | 1240 | 1800 | 97.92% | 1762.6053
2016-04-01 08:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6388
2016-04-01 09:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6565
2016-04-01 10:00 | 2.2 | 5200 | 1240 | 1800 | 97.42% | 1753.4728
2016-04-01 11:00 | 2.2 | 5200 | 1240 | 1800 | 97.46% | 1754.2853
2016-04-01 12:00 | 2.2 | 5200 | 1240 | 1800 | 97.45% | 1754.0749
2016-04-01 13:00 | 2.2 | 5200 | 1240 | 1800 | 97.54% | 1755.7978
2016-04-01 14:00 | 2.2 | 5200 | 1240 | 1800 | 97.51% | 1755.1797
2016-04-01 15:00 | 2.2 | 5200 | 1240 | 1800 | 97.76% | 1759.6876
2016-04-01 16:00 | 2.2 | 5200 | 1240 | 1800 | 97.95% | 1763.0721
2016-04-01 17:00 | 2.2 | 5200 | 1240 | 1800 | 98.11% | 1766.0551
2016-04-01 18:00 | 2.2 | 5200 | 1240 | 1800 | 98.19% | 1767.4058
2016-04-01 19:00 | 2.2 | 5200 | 1240 | 1800 | 98.19% | 1767.4475
2016-04-01 20:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.6483
2016-04-01 21:00 | 2.2 | 5200 | 1240 | 1800 | 97.77% | 1759.8997
2016-04-01 22:00 | 2.2 | 5200 | 1240 | 1800 | 97.77% | 1759.8806
2016-04-01 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-04-02 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-02 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-02 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-02 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-02 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-02 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-02 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-02 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-02 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-02 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-02 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-02 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-02 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-02 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-02 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-02 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8577
2016-04-02 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.95% | 1639.004
2016-04-02 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.11% | 1641.7771
2016-04-02 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0328
2016-04-02 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-04-02 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-04-02 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-02 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-02 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-03 | 1.5 | 3750 | 1240 | 1673.3333 | 97.75% | 1635.7376
2016-04-03 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.62% | 1633.4893
2016-04-03 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.6086
2016-04-03 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.2275
2016-04-03 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.78% | 1636.1063
2016-04-03 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.14% | 1493.103
2016-04-03 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98% | 1491.0168
2016-04-03 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.92% | 1489.8211
2016-04-03 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-03 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-03 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-03 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-03 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-03 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-03 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-03 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-03 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-03 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-03 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-03 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-03 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-03 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-03 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-03 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-04 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-04 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-04 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-04 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-04 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-04 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-04 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-04 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-04 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-04 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-04 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-04 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-04 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-04 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-04 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-04 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-04 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-04 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-04 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-04 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-04 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-04 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-04 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-04 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-05 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-05 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-05 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-05 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-05 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-05 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-05 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98% | 1639.8852
2016-04-05 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-05 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-05 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-05 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-05 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-05 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-05 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-05 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-05 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-05 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-05 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-05 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-05 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-05 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-05 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-05 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-05 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-04-06 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-06 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-06 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-06 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-06 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-06 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-06 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-06 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-06 08:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0528
2016-04-06 09:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0698
2016-04-06 10:00 | 2 | 4700 | 1240 | 1730 | 97.42% | 1685.2822
2016-04-06 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-06 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-06 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-06 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-06 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-06 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-06 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-06 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-06 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-06 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-06 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-06 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-06 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-07 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-07 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-07 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-07 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-07 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-07 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-07 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-07 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-07 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-07 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-07 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-07 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-07 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-07 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-07 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-07 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8577
2016-04-07 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.95% | 1639.004
2016-04-07 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.11% | 1641.7771
2016-04-07 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0328
2016-04-07 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-04-07 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-04-07 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-07 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-07 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-08 | 1.5 | 3750 | 1240 | 1673.3333 | 97.75% | 1635.7376
2016-04-08 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.62% | 1633.4893
2016-04-08 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.6086
2016-04-08 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.2275
2016-04-08 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.78% | 1636.1063
2016-04-08 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.14% | 1642.1797
2016-04-08 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98% | 1491.0168
2016-04-08 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.92% | 1401.0452
2016-04-08 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-08 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-08 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-08 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-08 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-08 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-08 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-08 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-08 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-08 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-08 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-08 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-08 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-08 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-08 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-08 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-09 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-09 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-09 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-09 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-09 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-09 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-09 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98% | 1639.8852
2016-04-09 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.92% | 1489.8211
2016-04-09 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-09 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-09 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-09 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-09 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-09 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-09 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-09 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-09 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-09 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-09 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-09 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-04-09 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-04-09 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-09 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-09 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-10 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-10 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-10 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-10 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-10 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-10 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-10 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-10 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-10 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-10 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-10 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-10 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-10 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-10 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-10 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-10 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-10 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-10 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-10 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-10 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-10 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-10 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-10 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-10 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-11 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-11 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-11 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-11 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-11 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-11 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-11 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-11 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-11 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-11 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-11 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-11 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-11 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-11 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-11 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-11 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-11 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-11 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-11 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-11 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-11 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-11 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-11 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-11 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-12 | 1.5 | 3750 | 1240 | 1673.3333 | 97.75% | 1635.7376
2016-04-12 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.62% | 1633.4893
2016-04-12 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.6086
2016-04-12 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.2275
2016-04-12 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.78% | 1636.1063
2016-04-12 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.14% | 1642.1797
2016-04-12 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98% | 1491.0168
2016-04-12 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.92% | 1489.8211
2016-04-12 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-12 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-12 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-12 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-12 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.6109
2016-04-12 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-12 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-12 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-12 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-12 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-12 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-12 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-12 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-12 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-12 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-12 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-13 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-13 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-13 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-13 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-13 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-13 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-13 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98% | 1639.8852
2016-04-13 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-13 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-13 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-13 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-13 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-13 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-13 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-13 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-13 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8577
2016-04-13 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.95% | 1639.004
2016-04-13 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.11% | 1641.7771
2016-04-13 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-13 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-13 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-13 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-13 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-13 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-14 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-14 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-14 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-14 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-14 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-14 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-14 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-14 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-14 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-14 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-14 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-14 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-14 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-14 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-14 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-14 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-14 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-14 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-14 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-14 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-14 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-14 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-14 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-14 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.63% | 1485.3533
2016-04-15 | 1.4 | 3370 | 1240 | 1521.4286 | 97.75% | 1487.2457
2016-04-15 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.62% | 1485.2016
2016-04-15 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.0377
2016-04-15 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.72% | 1486.7819
2016-04-15 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.78% | 1487.581
2016-04-15 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.14% | 1493.103
2016-04-15 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98% | 1491.0168
2016-04-15 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.92% | 1489.8211
2016-04-15 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-15 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-15 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-15 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-15 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.6109
2016-04-15 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-15 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-15 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-15 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-15 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-15 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-15 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-15 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-15 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-15 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-15 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.63% | 1485.3533
2016-04-16 | 1.4 | 3370 | 1240 | 1521.4286 | 97.75% | 1487.2457
2016-04-16 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.62% | 1485.2016
2016-04-16 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.0377
2016-04-16 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.72% | 1486.7819
2016-04-16 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.78% | 1487.581
2016-04-16 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.14% | 1493.103
2016-04-16 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98% | 1402.1697
2016-04-16 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.92% | 1401.0452
2016-04-16 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-16 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-16 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.42% | 1402.7782
2016-04-16 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.46% | 1403.4282
2016-04-16 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2599
2016-04-16 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.54% | 1404.6382
2016-04-16 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.51% | 1404.1438
2016-04-16 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.76% | 1407.7501
2016-04-16 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.95% | 1410.4577
2016-04-16 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.11% | 1412.8441
2016-04-16 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-16 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-16 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.81% | 1408.5186
2016-04-16 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-16 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8794
2016-04-16 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.63% | 1396.8436
2016-04-17 | 1.3 | 3100 | 1240 | 1430.7692 | 97.75% | 1398.6233
2016-04-17 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.62% | 1396.701
2016-04-17 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.3681
2016-04-17 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1871
2016-04-17 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1398.9386
2016-04-17 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.14% | 1404.1315
2016-04-17 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98% | 1402.1697
2016-04-17 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.92% | 1401.0452
2016-04-17 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-17 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-17 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-17 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-17 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-17 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-17 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-17 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-17 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-17 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-17 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-17 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-17 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-17 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-17 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8794
2016-04-17 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.63% | 1396.8436
2016-04-18 | 1.3 | 3100 | 1240 | 1430.7692 | 97.75% | 1398.6233
2016-04-18 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.62% | 1396.701
2016-04-18 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.3681
2016-04-18 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1871
2016-04-18 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1398.9386
2016-04-18 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.14% | 1404.1315
2016-04-18 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98% | 1402.1697
2016-04-18 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.92% | 1401.0452
2016-04-18 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-18 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-18 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-18 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-18 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-18 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-18 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-18 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-18 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-18 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.11% | 1412.8441
2016-04-18 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.9246
2016-04-18 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.958
2016-04-18 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.81% | 1408.5186
2016-04-18 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.77% | 1407.9198
2016-04-18 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8794
2016-04-18 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.63% | 1396.8436
2016-04-19 | 1.3 | 3100 | 1240 | 1430.7692 | 97.75% | 1398.6233
2016-04-19 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.62% | 1396.701
2016-04-19 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.3681
2016-04-19 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1871
2016-04-19 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1398.9386
2016-04-19 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.14% | 1404.1315
2016-04-19 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98% | 1402.1697
2016-04-19 07:00 | 1.25 | 3040 | 1240 | 1440 | 97.92% | 1410.0842
2016-04-19 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.98% | 1410.911
2016-04-19 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.98% | 1410.9252
2016-04-19 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.42% | 1402.7782
2016-04-19 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.46% | 1403.4282
2016-04-19 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2599
2016-04-19 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.54% | 1404.6382
2016-04-19 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.51% | 1404.1438
2016-04-19 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.76% | 1407.7501
2016-04-19 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.95% | 1410.4577
2016-04-19 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-19 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-19 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-19 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-19 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-19 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-19 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.63% | 1485.3533
2016-04-20 | 1.5 | 3750 | 1240 | 1673.3333 | 97.75% | 1635.7376
2016-04-20 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.62% | 1633.4893
2016-04-20 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.6086
2016-04-20 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.2275
2016-04-20 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.78% | 1636.1063
2016-04-20 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.14% | 1642.1797
2016-04-20 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98% | 1491.0168
2016-04-20 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.92% | 1489.8211
2016-04-20 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-20 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-20 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.42% | 1393.7861
2016-04-20 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-20 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-20 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-20 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-20 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.726
2016-04-20 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-20 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-20 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-20 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-20 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-20 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-20 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-20 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-04-21 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-21 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-21 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-21 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-21 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-21 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-21 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-21 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-21 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-21 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-21 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-21 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-21 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.6109
2016-04-21 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-21 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-21 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-21 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-21 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-21 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-21 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-21 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-21 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-21 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-21 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-04-22 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-22 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-22 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-22 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-22 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-22 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-22 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-22 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-22 08:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0528
2016-04-22 09:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0698
2016-04-22 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-22 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-22 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-22 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-22 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-22 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-22 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-22 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-22 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-22 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-22 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-22 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-22 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0371
2016-04-22 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-23 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-23 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-23 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-23 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-23 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-23 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-23 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-23 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-23 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-23 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-23 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-23 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-23 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.45% | 1482.6109
2016-04-23 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.54% | 1484.0672
2016-04-23 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-23 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-23 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.95% | 1401.4163
2016-04-23 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.11% | 1403.7874
2016-04-23 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.8787
2016-04-23 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.19% | 1493.9139
2016-04-23 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.167
2016-04-23 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5343
2016-04-23 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-23 23:00 | 2 | 4700 | 1240 | 1730 | 97.63% | 1688.9792
2016-04-24 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-24 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-24 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-24 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-24 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-24 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-24 06:00 | 2.2 | 5200 | 1240 | 1800 | 98% | 1764.0199
2016-04-24 07:00 | 2.2 | 5200 | 1240 | 1800 | 97.92% | 1762.6053
2016-04-24 08:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6388
2016-04-24 09:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6565
2016-04-24 10:00 | 2 | 4700 | 1240 | 1730 | 97.42% | 1685.2822
2016-04-24 11:00 | 2 | 4700 | 1240 | 1730 | 97.46% | 1686.0631
2016-04-24 12:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8608
2016-04-24 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-24 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-24 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8577
2016-04-24 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-24 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-24 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-24 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-24 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-24 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-24 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8794
2016-04-24 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.63% | 1396.8436
2016-04-25 | 1.4 | 3370 | 1240 | 1521.4286 | 97.75% | 1487.2457
2016-04-25 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.62% | 1485.2016
2016-04-25 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.6086
2016-04-25 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.72% | 1635.2275
2016-04-25 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.78% | 1636.1063
2016-04-25 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.14% | 1642.1797
2016-04-25 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98% | 1639.8852
2016-04-25 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-25 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5309
2016-04-25 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-25 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-25 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.46% | 1482.7888
2016-04-25 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.45% | 1394.2646
2016-04-25 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.54% | 1395.6341
2016-04-25 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.51% | 1395.1428
2016-04-25 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.76% | 1407.7501
2016-04-25 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.95% | 1410.4577
2016-04-25 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.11% | 1412.8441
2016-04-25 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.9246
2016-04-25 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.958
2016-04-25 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.81% | 1408.5186
2016-04-25 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.77% | 1407.9198
2016-04-25 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8794
2016-04-25 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-26 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-26 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-26 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-26 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-26 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-26 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-26 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98% | 1639.8852
2016-04-26 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.92% | 1638.5701
2016-04-26 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.6947
2016-04-26 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.98% | 1490.7096
2016-04-26 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.42% | 1482.102
2016-04-26 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.46% | 1394.4319
2016-04-26 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2599
2016-04-26 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.54% | 1404.6382
2016-04-26 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.51% | 1404.1438
2016-04-26 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.76% | 1407.7501
2016-04-26 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.95% | 1410.4577
2016-04-26 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.11% | 1412.8441
2016-04-26 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.861
2016-04-26 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.19% | 1404.8941
2016-04-26 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.81% | 1399.4897
2016-04-26 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-26 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-26 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.63% | 1485.3533
2016-04-27 | 1.4 | 3370 | 1240 | 1521.4286 | 97.75% | 1487.2457
2016-04-27 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.62% | 1485.2016
2016-04-27 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.81% | 1488.0377
2016-04-27 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.72% | 1486.7819
2016-04-27 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.78% | 1487.581
2016-04-27 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.14% | 1493.103
2016-04-27 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98% | 1402.1697
2016-04-27 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.92% | 1401.0452
2016-04-27 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8667
2016-04-27 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.98% | 1401.8808
2016-04-27 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.42% | 1402.7782
2016-04-27 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.46% | 1403.4282
2016-04-27 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2599
2016-04-27 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.54% | 1404.6382
2016-04-27 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.51% | 1404.1438
2016-04-27 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.76% | 1407.7501
2016-04-27 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.95% | 1410.4577
2016-04-27 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.11% | 1412.8441
2016-04-27 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.9246
2016-04-27 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.19% | 1413.958
2016-04-27 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.81% | 1408.5186
2016-04-27 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.8946
2016-04-27 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5181
2016-04-27 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.63% | 1633.6562
2016-04-28 | 2 | 4700 | 1240 | 1730 | 97.75% | 1691.1311
2016-04-28 01:00 | 2 | 4700 | 1240 | 1730 | 97.62% | 1688.8067
2016-04-28 02:00 | 2 | 4700 | 1240 | 1730 | 97.81% | 1692.0316
2016-04-28 03:00 | 2 | 4700 | 1240 | 1730 | 97.72% | 1690.6037
2016-04-28 04:00 | 2 | 4700 | 1240 | 1730 | 97.78% | 1691.5123
2016-04-28 05:00 | 2 | 4700 | 1240 | 1730 | 98.14% | 1697.7913
2016-04-28 06:00 | 2 | 4700 | 1240 | 1730 | 98% | 1695.4191
2016-04-28 07:00 | 2 | 4700 | 1240 | 1730 | 97.92% | 1694.0595
2016-04-28 08:00 | 2 | 4700 | 1240 | 1730 | 97.98% | 1695.0528
2016-04-28 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.98% | 1639.5473
2016-04-28 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.42% | 1630.0803
2016-04-28 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.46% | 1630.8356
2016-04-28 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.45% | 1630.64
2016-04-28 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.54% | 1632.2416
2016-04-28 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.51% | 1483.5447
2016-04-28 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.355
2016-04-28 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.95% | 1490.2157
2016-04-28 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.11% | 1492.737
2016-04-28 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0328
2016-04-28 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-04-28 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-04-28 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-28 22:00 | 2.2 | 5200 | 1240 | 1800 | 97.77% | 1759.8806
2016-04-28 23:00 | 2.2 | 5200 | 1240 | 1800 | 97.63% | 1757.3194
2016-04-29 | 2.2 | 5200 | 1240 | 1800 | 97.75% | 1759.5583
2016-04-29 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.62% | 1757.1399
2016-04-29 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.81% | 1760.4954
2016-04-29 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.72% | 1759.0096
2016-04-29 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.78% | 1759.955
2016-04-29 05:00 | 2.2 | 5200 | 1240 | 1800 | 98.14% | 1766.4881
2016-04-29 06:00 | 2.2 | 5200 | 1240 | 1800 | 98% | 1764.0199
2016-04-29 07:00 | 2.2 | 5200 | 1240 | 1800 | 97.92% | 1762.6053
2016-04-29 08:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6388
2016-04-29 09:00 | 2.2 | 5200 | 1240 | 1800 | 97.98% | 1763.6565
2016-04-29 10:00 | 2.2 | 5200 | 1240 | 1800 | 97.42% | 1753.4728
2016-04-29 11:00 | 2.2 | 5200 | 1240 | 1800 | 97.46% | 1754.2853
2016-04-29 12:00 | 2 | 4700 | 1240 | 1730 | 97.45% | 1685.8608
2016-04-29 13:00 | 2 | 4700 | 1240 | 1730 | 97.54% | 1687.5168
2016-04-29 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.51% | 1631.667
2016-04-29 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8577
2016-04-29 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.95% | 1639.004
2016-04-29 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.11% | 1641.7771
2016-04-29 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0328
2016-04-29 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.19% | 1643.0715
2016-04-29 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.81% | 1636.7508
2016-04-29 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0549
2016-04-29 22:00 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4408
2016-04-29 23:00 | 2 | 4700 | 1240 | 1730 | 97.11% | 1680.0128
2016-04-30 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-04-30 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-04-30 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-04-30 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-04-30 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-04-30 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-04-30 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-04-30 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-04-30 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-04-30 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-04-30 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-04-30 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-04-30 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2475
2016-04-30 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4364
2016-04-30 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-04-30 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-04-30 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-04-30 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-04-30 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-04-30 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-04-30 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-04-30 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-04-30 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-04-30 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-01 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-01 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-01 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-01 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-01 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-01 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-01 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-01 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-01 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-01 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-01 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-01 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-01 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-01 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-01 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-01 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-01 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-01 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.87% | 1409.2573
2016-05-01 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-01 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-01 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-01 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-02 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.1077
2016-05-02 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.34% | 1628.783
2016-05-02 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.33% | 1628.6881
2016-05-02 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.56% | 1632.4204
2016-05-02 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.49% | 1631.3435
2016-05-02 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.09% | 1641.4108
2016-05-02 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-02 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-02 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.74% | 1635.4578
2016-05-02 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-02 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-02 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-02 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2475
2016-05-02 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4364
2016-05-02 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.61% | 1485.0517
2016-05-02 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-02 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-02 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-05-02 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-02 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.87% | 1409.2573
2016-05-02 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-02 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-02 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-03 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-03 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-03 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.33% | 1628.6881
2016-05-03 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.56% | 1632.4204
2016-05-03 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.49% | 1631.3435
2016-05-03 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.09% | 1641.4108
2016-05-03 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-03 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-03 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-03 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-03 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-03 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-03 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-03 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-03 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-03 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-03 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-03 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-03 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-03 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.87% | 1409.2573
2016-05-03 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-03 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-03 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-03 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-04 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.1077
2016-05-04 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.34% | 1628.783
2016-05-04 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.33% | 1628.6881
2016-05-04 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.56% | 1632.4204
2016-05-04 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.49% | 1631.3435
2016-05-04 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.09% | 1641.4108
2016-05-04 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-04 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-04 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-04 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-04 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-04 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-04 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-04 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-04 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-05-04 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-04 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-04 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-04 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-04 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-04 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-04 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-04 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-04 23:00 | 2 | 4700 | 1240 | 1730 | 97.11% | 1680.0128
2016-05-05 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-05 01:00 | 2.2 | 5200 | 1240 | 1800 | 97.34% | 1752.0773
2016-05-05 02:00 | 2.2 | 5200 | 1240 | 1800 | 97.33% | 1751.9752
2016-05-05 03:00 | 2.2 | 5200 | 1240 | 1800 | 97.56% | 1755.9901
2016-05-05 04:00 | 2.2 | 5200 | 1240 | 1800 | 97.49% | 1754.8317
2016-05-05 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-05 06:00 | 2 | 4700 | 1240 | 1730 | 97.82% | 1692.2786
2016-05-05 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-05 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-05 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-05 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-05 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-05 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-05 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.57% | 1208.8144
2016-05-05 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-05 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-05 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-05 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-05 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.1615
2016-05-05 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-05 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-05 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-05 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-05 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.11% | 1624.9834
2016-05-06 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-06 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-05-06 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-05-06 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-05-06 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-05-06 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-06 06:00 | 2 | 4700 | 1240 | 1730 | 97.82% | 1692.2786
2016-05-06 07:00 | 2 | 4700 | 1240 | 1730 | 97.76% | 1691.2589
2016-05-06 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.74% | 1635.4578
2016-05-06 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.57% | 1632.6536
2016-05-06 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-06 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-06 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-06 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-06 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-05-06 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-06 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-06 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-05-06 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-05-06 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.87% | 1488.9474
2016-05-06 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.25% | 1479.5242
2016-05-06 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.36% | 1481.2563
2016-05-06 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.34% | 1628.7835
2016-05-06 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.11% | 1624.9834
2016-05-07 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-07 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-05-07 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-05-07 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-05-07 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-05-07 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-07 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-07 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-07 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-07 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-07 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-07 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-07 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-07 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-07 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3155
2016-05-07 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3287
2016-05-07 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.72% | 1210.7016
2016-05-07 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.66% | 1210.0056
2016-05-07 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-07 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-07 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-07 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-07 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-07 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-08 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-08 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-08 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-08 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-08 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-08 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-08 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-08 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-08 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-08 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-08 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-08 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-08 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-08 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-08 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-05-08 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-08 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-08 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-05-08 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-05-08 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-08 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-08 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-08 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-08 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-09 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-09 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-09 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-09 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-09 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-09 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-09 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-09 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-09 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-09 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-09 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-09 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-09 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2475
2016-05-09 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4364
2016-05-09 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.61% | 1485.0517
2016-05-09 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.61% | 1485.068
2016-05-09 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.72% | 1486.754
2016-05-09 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.66% | 1485.8993
2016-05-09 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.83% | 1488.4075
2016-05-09 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.87% | 1637.6091
2016-05-09 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.25% | 1627.2451
2016-05-09 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.36% | 1629.1502
2016-05-09 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.34% | 1628.7835
2016-05-09 23:00 | 2 | 4700 | 1240 | 1730 | 97.11% | 1680.0128
2016-05-10 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-10 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-05-10 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-05-10 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-05-10 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-05-10 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-10 06:00 | 2 | 4700 | 1240 | 1730 | 97.82% | 1692.2786
2016-05-10 07:00 | 2 | 4700 | 1240 | 1730 | 97.76% | 1691.2589
2016-05-10 08:00 | 2 | 4700 | 1240 | 1730 | 97.74% | 1690.8419
2016-05-10 09:00 | 2 | 4700 | 1240 | 1730 | 97.57% | 1687.9427
2016-05-10 10:00 | 2 | 4700 | 1240 | 1730 | 97.69% | 1690.0174
2016-05-10 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.58% | 1632.7599
2016-05-10 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2475
2016-05-10 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4364
2016-05-10 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.61% | 1485.0517
2016-05-10 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-10 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-10 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-05-10 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-05-10 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-10 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-10 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-10 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-10 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-11 | 1.5 | 3750 | 1240 | 1673.3333 | 97.3% | 1628.1077
2016-05-11 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.34% | 1628.783
2016-05-11 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.33% | 1628.6881
2016-05-11 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.56% | 1632.4204
2016-05-11 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.49% | 1631.3435
2016-05-11 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.09% | 1641.4108
2016-05-11 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-11 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-11 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-11 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-11 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-11 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-11 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-11 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-11 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-11 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-11 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-11 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-11 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-05-11 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-11 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-11 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-11 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-11 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.11% | 1624.9834
2016-05-12 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-12 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-05-12 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-05-12 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-05-12 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-05-12 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-12 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-12 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-12 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.74% | 1635.4578
2016-05-12 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-12 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-12 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-12 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-12 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-12 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-05-12 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-12 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-12 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.66% | 1397.3571
2016-05-12 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7158
2016-05-12 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-12 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-12 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-12 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-12 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-13 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-13 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-13 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-13 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-13 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-13 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-13 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-13 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-13 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-13 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-13 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-13 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-13 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-13 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-13 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-13 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-13 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-13 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-13 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-13 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-13 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-13 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-13 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-13 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-14 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-14 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-14 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-14 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-14 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-14 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-14 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-14 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-14 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-14 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-14 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-14 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-14 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-14 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9814
2016-05-14 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.56
2016-05-14 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.61% | 1396.5753
2016-05-14 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.72% | 1398.1608
2016-05-14 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.66% | 1485.8993
2016-05-14 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.83% | 1488.4075
2016-05-14 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.87% | 1488.9474
2016-05-14 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.25% | 1479.5242
2016-05-14 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.36% | 1481.2563
2016-05-14 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-14 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-15 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-15 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-15 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-15 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-15 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-15 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-15 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-15 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-15 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-15 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-15 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-15 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-15 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-15 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-15 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-15 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-15 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-15 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-15 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-15 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.87% | 1409.2573
2016-05-15 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-15 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-15 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-15 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-16 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-16 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-16 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-16 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-16 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-16 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-16 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-16 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-16 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-16 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-16 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-16 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-16 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.2892
2016-05-16 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.57% | 1208.8144
2016-05-16 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-16 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-16 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-16 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-16 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.1615
2016-05-16 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.87% | 1268.6215
2016-05-16 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.25% | 1260.5927
2016-05-16 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-16 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.34% | 1205.9533
2016-05-16 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.3921
2016-05-17 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-17 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-17 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-17 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-17 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-17 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-17 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-17 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-17 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.74% | 1407.4059
2016-05-17 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-17 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.3045
2016-05-17 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.58% | 1264.8649
2016-05-17 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.69% | 1266.3211
2016-05-17 13:00 | 1 | 2240 | 1240 | 1000 | 97.57% | 975.6859
2016-05-17 14:00 | 1 | 2240 | 1240 | 1000 | 97.61% | 976.0903
2016-05-17 15:00 | 1 | 2240 | 1240 | 1000 | 97.61% | 976.101
2016-05-17 16:00 | 1 | 2240 | 1240 | 1000 | 97.72% | 977.2092
2016-05-17 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-17 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.1615
2016-05-17 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-17 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-17 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-17 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-17 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-18 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-18 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-18 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-18 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-18 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-18 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-18 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-18 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-18 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-18 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-18 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-18 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-18 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-18 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-18 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3155
2016-05-18 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3287
2016-05-18 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.72% | 1210.7016
2016-05-18 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.66% | 1210.0056
2016-05-18 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-18 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.87% | 1400.2236
2016-05-18 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-18 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-18 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9229
2016-05-18 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.11% | 1624.9834
2016-05-19 | 2 | 4700 | 1240 | 1730 | 97.3% | 1683.2429
2016-05-19 01:00 | 2 | 4700 | 1240 | 1730 | 97.34% | 1683.941
2016-05-19 02:00 | 2 | 4700 | 1240 | 1730 | 97.33% | 1683.8429
2016-05-19 03:00 | 2 | 4700 | 1240 | 1730 | 97.56% | 1687.7016
2016-05-19 04:00 | 2 | 4700 | 1240 | 1730 | 97.49% | 1686.5883
2016-05-19 05:00 | 2 | 4700 | 1240 | 1730 | 98.09% | 1696.9964
2016-05-19 06:00 | 2 | 4700 | 1240 | 1730 | 97.82% | 1692.2786
2016-05-19 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-19 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.74% | 1635.4578
2016-05-19 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-19 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-19 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-19 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-19 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-19 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-19 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-19 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-19 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-19 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0481
2016-05-19 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-19 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-19 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-19 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-19 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-20 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-20 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-20 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-20 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-20 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-20 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-20 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-20 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-20 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-20 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.57% | 1395.9864
2016-05-20 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-20 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-20 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.2892
2016-05-20 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.57% | 1208.8144
2016-05-20 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3155
2016-05-20 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-20 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-20 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-20 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0481
2016-05-20 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-20 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-20 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-20 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-20 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-21 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-21 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-21 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-21 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-21 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-21 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-21 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-21 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-21 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-21 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-21 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-21 11:00 | 1.25 | 3040 | 1240 | 1440 | 97.58% | 1405.0842
2016-05-21 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.2892
2016-05-21 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.57% | 1264.778
2016-05-21 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-21 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-21 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-21 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-21 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.1615
2016-05-21 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-21 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-21 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-21 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-21 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-22 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-22 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-22 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-22 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-22 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-22 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-22 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-22 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-22 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-22 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-22 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-22 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.58% | 1484.5383
2016-05-22 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-22 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-22 14:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5701
2016-05-22 15:00 | 1.25 | 3040 | 1240 | 1440 | 97.61% | 1405.5855
2016-05-22 16:00 | 1.25 | 3040 | 1240 | 1440 | 97.72% | 1407.1812
2016-05-22 17:00 | 1.25 | 3040 | 1240 | 1440 | 97.66% | 1406.3723
2016-05-22 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7462
2016-05-22 19:00 | 1.25 | 3040 | 1240 | 1440 | 97.87% | 1409.2573
2016-05-22 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.25% | 1391.3619
2016-05-22 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.36% | 1392.9908
2016-05-22 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-22 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-23 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-23 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-23 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.33% | 1628.6881
2016-05-23 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.56% | 1632.4204
2016-05-23 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.49% | 1631.3435
2016-05-23 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.09% | 1641.4108
2016-05-23 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.82% | 1636.8475
2016-05-23 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.76% | 1635.8612
2016-05-23 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 97.74% | 1635.4578
2016-05-23 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-23 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.69% | 1486.2663
2016-05-23 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-23 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.6845
2016-05-23 13:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9877
2016-05-23 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3155
2016-05-23 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.61% | 1209.3287
2016-05-23 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.72% | 1210.7016
2016-05-23 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.66% | 1210.0056
2016-05-23 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0481
2016-05-23 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-23 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-23 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-23 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-23 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-24 | 1.4 | 3370 | 1240 | 1521.4286 | 97.3% | 1480.3085
2016-05-24 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.34% | 1480.9225
2016-05-24 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.33% | 1480.8362
2016-05-24 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.56% | 1484.2297
2016-05-24 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.49% | 1483.2506
2016-05-24 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-24 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-24 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-24 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.74% | 1486.9914
2016-05-24 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.57% | 1484.4418
2016-05-24 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.69% | 1397.7022
2016-05-24 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.58% | 1396.0772
2016-05-24 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7018
2016-05-24 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.57% | 1208.8144
2016-05-24 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-24 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-24 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-24 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.66% | 1210.0056
2016-05-24 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0481
2016-05-24 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-24 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-24 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-24 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-24 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-25 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-25 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-25 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-25 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-25 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-25 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-25 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-25 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-25 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-25 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-25 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-25 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.58% | 1208.8974
2016-05-25 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.2892
2016-05-25 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.57% | 1264.778
2016-05-25 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-25 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-25 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.72% | 1266.7526
2016-05-25 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.66% | 1266.0244
2016-05-25 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0481
2016-05-25 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.87% | 1212.4878
2016-05-25 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.25% | 1400.3384
2016-05-25 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-25 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-25 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-26 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-26 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-26 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-26 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-26 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-26 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-26 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-26 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-26 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-26 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-26 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-26 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.58% | 1208.8974
2016-05-26 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.2892
2016-05-26 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.57% | 1264.778
2016-05-26 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3023
2016-05-26 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.61% | 1265.3162
2016-05-26 16:00 | 1 | 2240 | 1240 | 1000 | 97.72% | 977.2092
2016-05-26 17:00 | 1 | 2240 | 1240 | 1000 | 97.66% | 976.6474
2016-05-26 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.1615
2016-05-26 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.87% | 1268.6215
2016-05-26 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-26 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-26 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-26 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.11% | 1477.4679
2016-05-27 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-27 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-27 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-27 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-27 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-27 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.09% | 1492.404
2016-05-27 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.82% | 1488.2549
2016-05-27 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.76% | 1487.3582
2016-05-27 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-27 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-27 10:00 | 1.25 | 3040 | 1240 | 1440 | 97.69% | 1406.7196
2016-05-27 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.58% | 1208.8974
2016-05-27 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.69% | 1266.3211
2016-05-27 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.57% | 1264.778
2016-05-27 14:00 | 1 | 2240 | 1240 | 1000 | 97.61% | 976.0903
2016-05-27 15:00 | 1 | 2240 | 1240 | 1000 | 97.61% | 976.101
2016-05-27 16:00 | 1 | 2240 | 1240 | 1000 | 97.72% | 977.2092
2016-05-27 17:00 | 1 | 2240 | 1240 | 1000 | 97.66% | 976.6474
2016-05-27 18:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.296
2016-05-27 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.87% | 1268.6215
2016-05-27 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-27 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.36% | 1401.9778
2016-05-27 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6773
2016-05-27 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-28 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-28 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-28 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-28 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-28 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-28 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-28 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-28 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-28 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.74% | 1407.4059
2016-05-28 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-28 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.3045
2016-05-28 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.58% | 1264.8649
2016-05-28 12:00 | 1 | 2240 | 1240 | 1000 | 97.69% | 976.8763
2016-05-28 13:00 | 1 | 2280 | 1240 | 1040 | 97.57% | 1014.7133
2016-05-28 14:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.134
2016-05-28 15:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.1451
2016-05-28 16:00 | 1 | 2280 | 1240 | 1040 | 97.72% | 1016.2976
2016-05-28 17:00 | 1 | 2280 | 1240 | 1040 | 97.66% | 1015.7133
2016-05-28 18:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4278
2016-05-28 19:00 | 1 | 2240 | 1240 | 1000 | 97.87% | 978.6509
2016-05-28 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.25% | 1260.5927
2016-05-28 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-28 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-28 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-29 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-29 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-29 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-29 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-29 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-29 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-29 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-29 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-29 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-29 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-29 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.3045
2016-05-29 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.58% | 1264.8649
2016-05-29 12:00 | 1 | 2280 | 1240 | 1040 | 97.69% | 1015.9513
2016-05-29 13:00 | 1 | 2280 | 1240 | 1040 | 97.57% | 1014.7133
2016-05-29 14:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.134
2016-05-29 15:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.1451
2016-05-29 16:00 | 1 | 2280 | 1240 | 1040 | 97.72% | 1016.2976
2016-05-29 17:00 | 1 | 2280 | 1240 | 1040 | 97.66% | 1015.7133
2016-05-29 18:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4278
2016-05-29 19:00 | 1 | 2240 | 1240 | 1000 | 97.87% | 978.6509
2016-05-29 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.25% | 1204.8143
2016-05-29 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-29 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-29 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4281
2016-05-30 | 1.3 | 3100 | 1240 | 1430.7692 | 97.3% | 1392.0995
2016-05-30 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.34% | 1392.6769
2016-05-30 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.33% | 1392.5957
2016-05-30 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.56% | 1395.787
2016-05-30 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8662
2016-05-30 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.09% | 1403.4742
2016-05-30 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.82% | 1399.5723
2016-05-30 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.76% | 1398.729
2016-05-30 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.74% | 1398.3841
2016-05-30 09:00 | 1.25 | 3040 | 1240 | 1440 | 97.57% | 1404.9928
2016-05-30 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.69% | 1210.3045
2016-05-30 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.58% | 1264.8649
2016-05-30 12:00 | 1 | 2240 | 1240 | 1000 | 97.69% | 976.8763
2016-05-30 13:00 | 1 | 2280 | 1240 | 1040 | 97.57% | 1014.7133
2016-05-30 14:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.134
2016-05-30 15:00 | 1 | 2280 | 1240 | 1040 | 97.61% | 1015.1451
2016-05-30 16:00 | 1 | 2280 | 1240 | 1040 | 97.72% | 1016.2976
2016-05-30 17:00 | 1 | 2280 | 1240 | 1040 | 97.66% | 1015.7133
2016-05-30 18:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4278
2016-05-30 19:00 | 1 | 2280 | 1240 | 1040 | 97.87% | 1017.7969
2016-05-30 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.25% | 1260.5927
2016-05-30 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.36% | 1206.2248
2016-05-30 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.34% | 1401.6623
2016-05-30 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-05-31 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-05-31 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-05-31 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-05-31 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-05-31 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-05-31 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-05-31 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-05-31 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-05-31 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-05-31 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-05-31 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-05-31 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7412
2016-05-31 12:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9404
2016-05-31 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-05-31 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-05-31 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-05-31 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-05-31 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-05-31 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-05-31 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-05-31 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-05-31 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-05-31 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-05-31 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-01 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-01 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-01 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-01 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-01 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-01 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-01 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-01 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-01 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-01 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2482
2016-06-01 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-01 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-01 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-01 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-01 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-01 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-01 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-01 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-01 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-01 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-01 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-01 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-02 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-02 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-02 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.52% | 1453.2473
2016-06-02 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.73% | 1456.3988
2016-06-02 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.64% | 1485.4576
2016-06-02 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.66% | 1501.0615
2016-06-02 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2077
2016-06-02 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.58% | 1499.8004
2016-06-02 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-02 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-02 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2777
2016-06-02 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7412
2016-06-02 12:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9404
2016-06-02 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-02 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-02 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-02 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-02 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-02 18:00 | 1 | 2240 | 1240 | 1000 | 97.29% | 972.857
2016-06-02 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-02 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-02 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-02 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8491
2016-06-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-03 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-03 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-03 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-03 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-03 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-03 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-03 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-03 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-03 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-03 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-03 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2482
2016-06-03 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-03 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-03 14:00 | 1 | 2240 | 1240 | 1000 | 97.67% | 976.6651
2016-06-03 15:00 | 1 | 2240 | 1240 | 1000 | 97.31% | 973.1202
2016-06-03 16:00 | 1 | 2240 | 1240 | 1000 | 97.38% | 973.7964
2016-06-03 17:00 | 1 | 2240 | 1240 | 1000 | 96.71% | 967.0986
2016-06-03 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.29% | 1261.1109
2016-06-03 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-03 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-03 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-03 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-03 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-04 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-04 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-04 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-04 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-04 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-04 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-04 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-04 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-04 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-04 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-04 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-04 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-04 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-04 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-04 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-04 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-04 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-04 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-04 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-04 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-04 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-04 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.0205
2016-06-04 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-04 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-05 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-05 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-05 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-05 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-05 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-05 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-05 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-05 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-05 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-05 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-05 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-05 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-05 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-05 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-05 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-05 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-05 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-05 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-05 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-05 19:00 | 1 | 2140 | 1240 | 900 | 97.5% | 877.5315
2016-06-05 20:00 | 1 | 2280 | 1240 | 1040 | 97.41% | 1013.0345
2016-06-05 21:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.0451
2016-06-05 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.49% | 1263.7521
2016-06-05 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-06 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-06 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-06 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-06 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-06 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-06 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-06 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-06 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-06 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-06 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-06 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-06 11:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.3112
2016-06-06 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-06 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-06 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-06 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-06 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-06 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-06 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-06 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-06 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-06 21:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.0451
2016-06-06 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-06 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-07 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-07 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-07 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-07 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-07 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-07 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-07 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-07 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.58% | 1221.3257
2016-06-07 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-07 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.6273
2016-06-07 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-07 11:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.3112
2016-06-07 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-07 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-07 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-07 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-07 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-07 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-07 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-07 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-07 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-07 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.0205
2016-06-07 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-07 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-08 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-08 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-08 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-08 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-08 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-08 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-08 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-08 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-08 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-08 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-08 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-08 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7412
2016-06-08 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-08 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-08 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-08 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-08 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-08 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-08 18:00 | 1 | 2240 | 1240 | 1000 | 97.29% | 972.857
2016-06-08 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-08 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-08 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.0205
2016-06-08 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-08 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-09 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-09 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-09 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-09 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-09 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-09 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-09 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-09 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-09 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-09 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-09 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2777
2016-06-09 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2482
2016-06-09 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2802
2016-06-09 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2752
2016-06-09 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.67% | 1266.0474
2016-06-09 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.31% | 1261.4521
2016-06-09 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.38% | 1262.3287
2016-06-09 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.71% | 1253.6464
2016-06-09 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.29% | 1261.1109
2016-06-09 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.008
2016-06-09 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-09 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-09 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8491
2016-06-09 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-10 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-10 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-10 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-10 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-10 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-10 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-10 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-10 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-10 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-10 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.48% | 1409.0598
2016-06-10 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1862
2016-06-10 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2771
2016-06-10 12:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.3142
2016-06-10 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0684
2016-06-10 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.67% | 1266.0474
2016-06-10 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.31% | 1261.4521
2016-06-10 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.38% | 1262.3287
2016-06-10 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.71% | 1253.6464
2016-06-10 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.29% | 1261.1109
2016-06-10 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.008
2016-06-10 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-10 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-10 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8491
2016-06-10 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-11 | 1.4 | 3370 | 1240 | 1521.4286 | 96.41% | 1466.8367
2016-06-11 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.3% | 1465.1589
2016-06-11 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.52% | 1453.2473
2016-06-11 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.73% | 1456.3988
2016-06-11 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.64% | 1485.4576
2016-06-11 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.66% | 1501.0615
2016-06-11 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2077
2016-06-11 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-11 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-11 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.48% | 1409.0598
2016-06-11 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2777
2016-06-11 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2771
2016-06-11 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-11 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-11 14:00 | 1 | 2240 | 1240 | 1000 | 97.67% | 976.6651
2016-06-11 15:00 | 1 | 2240 | 1240 | 1000 | 97.31% | 973.1202
2016-06-11 16:00 | 1 | 2240 | 1240 | 1000 | 97.38% | 973.7964
2016-06-11 17:00 | 1 | 2240 | 1240 | 1000 | 96.71% | 967.0986
2016-06-11 18:00 | 1 | 2240 | 1240 | 1000 | 97.29% | 972.857
2016-06-11 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.008
2016-06-11 20:00 | 1.25 | 3040 | 1240 | 1440 | 97.41% | 1402.6632
2016-06-11 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-11 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.49% | 1394.8491
2016-06-11 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-12 | 1.4 | 3370 | 1240 | 1521.4286 | 96.41% | 1466.8367
2016-06-12 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.3% | 1465.1589
2016-06-12 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.52% | 1453.2473
2016-06-12 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.73% | 1456.3988
2016-06-12 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.64% | 1485.4576
2016-06-12 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.66% | 1501.0615
2016-06-12 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2077
2016-06-12 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.58% | 1499.8004
2016-06-12 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-12 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.48% | 1409.0598
2016-06-12 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2777
2016-06-12 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2771
2016-06-12 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2802
2016-06-12 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0684
2016-06-12 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.67% | 1266.0474
2016-06-12 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.31% | 1261.4521
2016-06-12 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.38% | 1262.3287
2016-06-12 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.71% | 1253.6464
2016-06-12 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.29% | 1261.1109
2016-06-12 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-12 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-12 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.0205
2016-06-12 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-12 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-13 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-13 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-13 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-13 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-13 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-13 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-13 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-13 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-13 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-13 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-13 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-13 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2482
2016-06-13 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-13 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-13 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-13 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-13 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-13 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-13 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-13 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-13 20:00 | 1 | 2280 | 1240 | 1040 | 97.41% | 1013.0345
2016-06-13 21:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0469
2016-06-13 22:00 | 1 | 2240 | 1240 | 1000 | 97.49% | 974.8945
2016-06-13 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-14 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-14 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-14 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-14 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-14 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-14 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-14 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-14 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-14 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-14 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-14 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-14 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-14 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-14 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-14 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-14 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-14 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-14 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-14 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-14 19:00 | 1 | 2140 | 1240 | 900 | 97.5% | 877.5315
2016-06-14 20:00 | 1 | 2280 | 1240 | 1040 | 97.41% | 1013.0345
2016-06-14 21:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0469
2016-06-14 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.49% | 1263.7521
2016-06-14 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-15 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-15 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-15 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-15 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-15 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-15 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-15 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-15 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-15 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-15 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-15 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-15 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7412
2016-06-15 12:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9404
2016-06-15 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-15 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-15 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-15 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-15 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-15 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-15 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-15 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-15 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-15 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-15 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-16 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-16 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-16 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-16 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-16 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-16 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-16 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-16 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-16 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-16 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-16 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-16 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2482
2016-06-16 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7746
2016-06-16 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-16 14:00 | 1 | 2240 | 1240 | 1000 | 97.67% | 976.6651
2016-06-16 15:00 | 1 | 2240 | 1240 | 1000 | 97.31% | 973.1202
2016-06-16 16:00 | 1 | 2240 | 1240 | 1000 | 97.38% | 973.7964
2016-06-16 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-16 18:00 | 1 | 2240 | 1240 | 1000 | 97.29% | 972.857
2016-06-16 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-16 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-16 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-16 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-16 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-17 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-17 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-17 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-17 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-17 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-17 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-17 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-17 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-17 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-17 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.48% | 1409.0598
2016-06-17 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2777
2016-06-17 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2771
2016-06-17 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2802
2016-06-17 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-17 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-17 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-17 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-17 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-17 18:00 | 1 | 2240 | 1240 | 1000 | 97.29% | 972.857
2016-06-17 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-17 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.41% | 1206.8144
2016-06-17 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.5% | 1404.0649
2016-06-17 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-17 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-18 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-18 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-18 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-18 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-18 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-18 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-18 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-18 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-18 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-18 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-18 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2488
2016-06-18 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7412
2016-06-18 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-18 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-18 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-18 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-18 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-18 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-18 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-18 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-18 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-18 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.5% | 1208.0205
2016-06-18 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-18 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.6% | 1396.3999
2016-06-19 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-19 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-19 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-19 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-19 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-19 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-19 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-19 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-19 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0188
2016-06-19 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-19 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-19 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-19 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-19 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-19 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-19 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-19 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-19 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-19 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-19 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-19 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-19 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-19 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-19 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-20 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-20 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-20 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-20 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-20 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-20 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-20 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-20 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-20 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-20 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-20 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-20 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-20 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-20 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-20 14:00 | 1 | 2280 | 1240 | 1040 | 97.67% | 1015.7317
2016-06-20 15:00 | 1 | 2280 | 1240 | 1040 | 97.31% | 1012.045
2016-06-20 16:00 | 1 | 2280 | 1240 | 1040 | 97.38% | 1012.7483
2016-06-20 17:00 | 1 | 2280 | 1240 | 1040 | 96.71% | 1005.7826
2016-06-20 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-20 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-20 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-20 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-20 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-20 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-21 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-21 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-21 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-21 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-21 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-21 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-21 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-21 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.58% | 1410.4298
2016-06-21 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-21 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-21 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-21 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-21 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-21 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-21 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-21 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-21 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-21 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-21 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-21 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-21 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-21 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-21 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-21 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-22 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-22 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-22 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-22 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-22 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-22 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-22 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-22 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-22 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-22 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.1393
2016-06-22 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-22 11:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.3112
2016-06-22 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-22 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-22 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-22 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-22 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-22 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-22 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-22 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-22 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-22 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-22 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.49% | 1403.8481
2016-06-22 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-23 | 1.3 | 3100 | 1240 | 1430.7692 | 96.41% | 1379.4304
2016-06-23 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.3% | 1377.8526
2016-06-23 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.52% | 1366.6508
2016-06-23 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.73% | 1369.6145
2016-06-23 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.64% | 1396.9417
2016-06-23 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.66% | 1411.6158
2016-06-23 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.7533
2016-06-23 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-23 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-23 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.6273
2016-06-23 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-23 11:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4232
2016-06-23 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-23 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-23 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-23 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-23 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-23 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-23 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-23 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-23 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-23 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-23 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.49% | 1263.7521
2016-06-23 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-24 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-24 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-24 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-24 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-24 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-24 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-24 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-24 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-24 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-24 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.6273
2016-06-24 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-24 11:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.3112
2016-06-24 12:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.338
2016-06-24 13:00 | 1 | 2280 | 1240 | 1040 | 97.99% | 1019.1237
2016-06-24 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-24 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-24 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-24 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-24 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-24 19:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.035
2016-06-24 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-24 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-24 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-24 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.6% | 1405.409
2016-06-25 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-25 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-25 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-25 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-25 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-25 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-25 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-25 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-25 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-25 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.6273
2016-06-25 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-25 11:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4232
2016-06-25 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-25 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-25 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-25 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-25 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-25 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-25 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-25 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-25 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-25 21:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.0451
2016-06-25 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-25 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-26 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-26 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-26 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-26 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-26 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-26 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-26 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-26 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-26 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8357
2016-06-26 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.6273
2016-06-26 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-26 11:00 | 1 | 2280 | 1240 | 1040 | 98.49% | 1024.3112
2016-06-26 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-26 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-26 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-26 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-26 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-26 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-26 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-26 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-26 20:00 | 1 | 2240 | 1240 | 1000 | 97.41% | 974.0716
2016-06-26 21:00 | 1 | 2240 | 1240 | 1000 | 97.5% | 975.0451
2016-06-26 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-26 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-27 | 1.25 | 3040 | 1240 | 1440 | 96.41% | 1388.33
2016-06-27 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.3% | 1386.7419
2016-06-27 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.52% | 1375.4679
2016-06-27 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.73% | 1378.4507
2016-06-27 04:00 | 1.25 | 3040 | 1240 | 1440 | 97.64% | 1405.9542
2016-06-27 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.66% | 1420.723
2016-06-27 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8613
2016-06-27 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.58% | 1419.5294
2016-06-27 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1222
2016-06-27 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.1505
2016-06-27 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.49% | 1276.7418
2016-06-27 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-27 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-27 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-27 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-27 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-27 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-27 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-27 18:00 | 1 | 2140 | 1240 | 900 | 97.29% | 875.5713
2016-06-27 19:00 | 1 | 2140 | 1240 | 900 | 97.5% | 877.5315
2016-06-27 20:00 | 1 | 2140 | 1240 | 900 | 97.41% | 876.6645
2016-06-27 21:00 | 1 | 2140 | 1240 | 900 | 97.5% | 877.5406
2016-06-27 22:00 | 1 | 2280 | 1240 | 1040 | 97.49% | 1013.8903
2016-06-27 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.6% | 1265.1572
2016-06-28 | 1.13 | 2640 | 1240 | 1238.9381 | 96.41% | 1194.4825
2016-06-28 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.3% | 1193.1162
2016-06-28 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.52% | 1183.4163
2016-06-28 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.73% | 1185.9827
2016-06-28 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.64% | 1209.646
2016-06-28 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.66% | 1222.3527
2016-06-28 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.67% | 1222.4717
2016-06-28 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.58% | 1221.3257
2016-06-28 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.62% | 1278.4022
2016-06-28 09:00 | 1 | 2280 | 1240 | 1040 | 98.48% | 1024.2198
2016-06-28 10:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4236
2016-06-28 11:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4232
2016-06-28 12:00 | 1 | 2140 | 1240 | 900 | 98.49% | 886.4464
2016-06-28 13:00 | 1 | 2140 | 1240 | 900 | 97.99% | 881.9339
2016-06-28 14:00 | 1 | 2140 | 1240 | 900 | 97.67% | 878.9986
2016-06-28 15:00 | 1 | 2140 | 1240 | 900 | 97.31% | 875.8081
2016-06-28 16:00 | 1 | 2140 | 1240 | 900 | 97.38% | 876.4168
2016-06-28 17:00 | 1 | 2140 | 1240 | 900 | 96.71% | 870.3888
2016-06-28 18:00 | 1 | 2280 | 1240 | 1040 | 97.29% | 1011.7712
2016-06-28 19:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0364
2016-06-28 20:00 | 1 | 2280 | 1240 | 1040 | 97.41% | 1013.0345
2016-06-28 21:00 | 1 | 2280 | 1240 | 1040 | 97.5% | 1014.0469
2016-06-28 22:00 | 1 | 2240 | 1240 | 1000 | 97.49% | 974.8945
2016-06-28 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.6% | 1209.1768
2016-06-29 | 1.13 | 2640 | 1240 | 1238.9381 | 96.41% | 1194.4825
2016-06-29 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.3% | 1193.1162
2016-06-29 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.52% | 1183.4163
2016-06-29 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.73% | 1185.9827
2016-06-29 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.64% | 1209.646
2016-06-29 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.66% | 1222.3527
2016-06-29 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.67% | 1222.4717
2016-06-29 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.58% | 1221.3257
2016-06-29 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.62% | 1278.4022
2016-06-29 09:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.8267
2016-06-29 10:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9151
2016-06-29 11:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9147
2016-06-29 12:00 | 1 | 2240 | 1240 | 1000 | 98.49% | 984.9404
2016-06-29 13:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9266
2016-06-29 14:00 | 1 | 2240 | 1240 | 1000 | 97.67% | 976.6651
2016-06-29 15:00 | 1 | 2240 | 1240 | 1000 | 97.31% | 973.1202
2016-06-29 16:00 | 1 | 2240 | 1240 | 1000 | 97.38% | 973.7964
2016-06-29 17:00 | 1 | 2240 | 1240 | 1000 | 96.71% | 967.0986
2016-06-29 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.29% | 1261.1109
2016-06-29 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9343
2016-06-29 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.41% | 1262.6855
2016-06-29 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.5% | 1263.9473
2016-06-29 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.49% | 1207.8339
2016-06-29 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-06-30 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-06-30 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-06-30 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-06-30 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-06-30 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-06-30 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-06-30 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-06-30 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-06-30 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-06-30 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-06-30 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-06-30 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.34% | 1218.4297
2016-06-30 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.21% | 1216.7517
2016-06-30 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.81% | 1199.4096
2016-06-30 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7741
2016-06-30 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7675
2016-06-30 16:00 | 1.25 | 3040 | 1240 | 1440 | 95.64% | 1377.1532
2016-06-30 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.83% | 1379.9577
2016-06-30 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.45% | 1403.2513
2016-06-30 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3838
2016-06-30 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.16% | 1413.4742
2016-06-30 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2323
2016-06-30 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6733
2016-06-30 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.65% | 1411.4421
2016-07-01 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-01 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-01 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-01 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-01 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-01 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-01 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-01 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-01 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-01 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.34% | 1218.4297
2016-07-01 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.21% | 1273.0828
2016-07-01 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.81% | 1254.9378
2016-07-01 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.63% | 1239.6248
2016-07-01 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.63% | 1239.6178
2016-07-01 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.64% | 1239.7213
2016-07-01 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2793
2016-07-01 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.45% | 1207.3204
2016-07-01 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1778
2016-07-01 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-01 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-01 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-01 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-02 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-02 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-02 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-02 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-02 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-02 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-02 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-02 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.67% | 1222.5008
2016-07-02 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.59% | 1278.0122
2016-07-02 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-02 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-02 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-02 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-02 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-02 14:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.282
2016-07-02 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.63% | 1239.6178
2016-07-02 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.64% | 1184.8663
2016-07-02 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2793
2016-07-02 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.45% | 1207.3204
2016-07-02 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1778
2016-07-02 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-02 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-02 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-02 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-03 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-03 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-03 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-03 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-03 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-03 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-03 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-03 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-03 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-03 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-03 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-03 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.34% | 1218.4297
2016-07-03 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.21% | 1216.7517
2016-07-03 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.81% | 1199.4096
2016-07-03 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7741
2016-07-03 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7675
2016-07-03 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.64% | 1184.8663
2016-07-03 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2793
2016-07-03 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.45% | 1207.3204
2016-07-03 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1778
2016-07-03 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-03 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-03 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-03 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-04 | 1.4 | 3370 | 1240 | 1521.4286 | 96.24% | 1464.2874
2016-07-04 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.77% | 1441.9309
2016-07-04 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.15% | 1432.4484
2016-07-04 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.17% | 1432.7367
2016-07-04 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.65% | 1455.2938
2016-07-04 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.63% | 1500.6097
2016-07-04 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.2416
2016-07-04 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2435
2016-07-04 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.59% | 1499.969
2016-07-04 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8883
2016-07-04 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.48% | 1418.0805
2016-07-04 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.34% | 1416.1634
2016-07-04 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.21% | 1216.7517
2016-07-04 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-04 14:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.282
2016-07-04 15:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.2766
2016-07-04 16:00 | 1 | 2240 | 1240 | 1000 | 95.64% | 956.3564
2016-07-04 17:00 | 1 | 2240 | 1240 | 1000 | 95.83% | 958.304
2016-07-04 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.45% | 1263.2149
2016-07-04 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-04 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-04 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-04 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-04 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-05 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-05 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-05 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-05 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-05 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-05 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-05 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-05 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-05 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.59% | 1410.5884
2016-07-05 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-05 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-05 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-05 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-05 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-05 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-05 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-05 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-05 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-05 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-05 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-05 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-05 21:00 | 1 | 2280 | 1240 | 1040 | 98.35% | 1022.8344
2016-07-05 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-05 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.65% | 1278.7857
2016-07-06 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-06 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-06 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-06 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-06 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-06 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-06 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-06 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.67% | 1222.5008
2016-07-06 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-06 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-06 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-06 11:00 | 1 | 2140 | 1240 | 900 | 98.34% | 885.1021
2016-07-06 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-06 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-06 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-06 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-06 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-06 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-06 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-06 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-06 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-06 21:00 | 1 | 2280 | 1240 | 1040 | 98.35% | 1022.8344
2016-07-06 22:00 | 1 | 2240 | 1240 | 1000 | 98.39% | 983.8577
2016-07-06 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-07 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-07 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-07 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-07 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-07 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-07 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-07 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-07 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-07 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-07 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-07 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-07 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-07 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-07 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-07 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-07 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-07 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-07 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-07 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-07 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-07 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-07 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-07 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-07 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-08 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-08 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-08 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-08 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-08 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-08 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-08 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-08 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-08 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-08 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-08 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-08 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.34% | 1218.4297
2016-07-08 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.21% | 1216.7517
2016-07-08 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.81% | 1199.4096
2016-07-08 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7741
2016-07-08 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.63% | 1184.7675
2016-07-08 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.64% | 1184.8663
2016-07-08 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.83% | 1187.2793
2016-07-08 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.45% | 1207.3204
2016-07-08 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1778
2016-07-08 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-08 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-08 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-08 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-09 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-09 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-09 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-09 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-09 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-09 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-09 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-09 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-09 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-09 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-09 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-09 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-09 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-09 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-09 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-09 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-09 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-09 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-09 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-09 19:00 | 1 | 2240 | 1240 | 1000 | 98.08% | 980.8221
2016-07-09 20:00 | 1 | 2240 | 1240 | 1000 | 98.16% | 981.5793
2016-07-09 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-09 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-09 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-10 | 1.13 | 2640 | 1240 | 1238.9381 | 96.24% | 1192.4065
2016-07-10 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-10 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-10 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-10 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-10 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-10 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-10 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-10 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-10 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-10 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-10 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-10 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-10 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-10 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-10 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-10 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-10 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-10 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-10 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-10 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-10 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-10 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-10 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-11 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-11 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-11 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-11 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-11 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-11 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-11 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-11 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-11 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.59% | 1410.5884
2016-07-11 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-11 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-11 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-11 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-11 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-11 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-11 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-11 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-11 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-11 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-11 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-11 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-11 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-11 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-11 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-12 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-12 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-12 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-12 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-12 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-12 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-12 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-12 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-12 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-12 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-12 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-12 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-12 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-12 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-12 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-12 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-12 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-12 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-12 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-12 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-12 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-12 21:00 | 1 | 2280 | 1240 | 1040 | 98.35% | 1022.8344
2016-07-12 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-12 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-13 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-13 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-13 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-13 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-13 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-13 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-13 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-13 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-13 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-13 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-13 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-13 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-13 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-13 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-13 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-13 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-13 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-13 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-13 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-13 19:00 | 1 | 2280 | 1240 | 1040 | 98.08% | 1020.0549
2016-07-13 20:00 | 1 | 2240 | 1240 | 1000 | 98.16% | 981.5793
2016-07-13 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-13 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-13 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-14 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-14 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-14 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-14 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-14 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-14 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-14 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-14 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-14 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.59% | 1410.5884
2016-07-14 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9908
2016-07-14 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-14 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-14 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.21% | 1273.0828
2016-07-14 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-14 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-14 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-14 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-14 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-14 18:00 | 1 | 2280 | 1240 | 1040 | 97.45% | 1013.4593
2016-07-14 19:00 | 1 | 2240 | 1240 | 1000 | 98.08% | 980.8221
2016-07-14 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-14 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-14 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-14 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.65% | 1411.4421
2016-07-15 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-15 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-15 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-15 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-15 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-15 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-15 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-15 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-15 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-15 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-15 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-15 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-15 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-15 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-15 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-15 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-15 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-15 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-15 18:00 | 1 | 2280 | 1240 | 1040 | 97.45% | 1013.4593
2016-07-15 19:00 | 1 | 2280 | 1240 | 1040 | 98.08% | 1020.0549
2016-07-15 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-15 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-15 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-15 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-16 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-16 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-16 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-16 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-16 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-16 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-16 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-16 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-16 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-16 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-16 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-16 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-16 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-16 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-16 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-16 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-16 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-16 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-16 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-16 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-16 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-16 21:00 | 1 | 2280 | 1240 | 1040 | 98.35% | 1022.8344
2016-07-16 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-16 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-17 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-17 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-17 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-17 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-17 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-17 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-17 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-17 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-17 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-17 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-17 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-17 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-17 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-17 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-17 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-17 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-17 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-17 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-17 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-17 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-17 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-17 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-17 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-17 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-18 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-18 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-18 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-18 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-18 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-18 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-18 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-18 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-18 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-18 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-18 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-18 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-18 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-18 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-18 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-18 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-18 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-18 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-18 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-18 19:00 | 1 | 2280 | 1240 | 1040 | 98.08% | 1020.0549
2016-07-18 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-18 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-18 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-18 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-19 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-19 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-19 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-19 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-19 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-19 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-19 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-19 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-19 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-19 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-19 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-19 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-19 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-19 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-19 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-19 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-19 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-19 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-19 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-19 19:00 | 1 | 2280 | 1240 | 1040 | 98.08% | 1020.0549
2016-07-19 20:00 | 1 | 2240 | 1240 | 1000 | 98.16% | 981.5793
2016-07-19 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-19 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-19 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-20 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-20 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-20 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-20 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-20 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-20 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-20 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-20 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-20 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-20 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-20 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-20 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-20 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-20 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-20 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-20 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-20 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-20 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-20 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-20 19:00 | 1 | 2240 | 1240 | 1000 | 98.08% | 980.8221
2016-07-20 20:00 | 1 | 2240 | 1240 | 1000 | 98.16% | 981.5793
2016-07-20 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-20 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-20 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-21 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-21 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-21 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-21 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-21 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-21 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-21 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-21 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-21 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-21 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-21 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-21 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-21 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-21 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-21 14:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.282
2016-07-21 15:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.2766
2016-07-21 16:00 | 1 | 2240 | 1240 | 1000 | 95.64% | 956.3564
2016-07-21 17:00 | 1 | 2240 | 1240 | 1000 | 95.83% | 958.304
2016-07-21 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.45% | 1263.2149
2016-07-21 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1778
2016-07-21 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-21 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-21 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-21 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.65% | 1411.4421
2016-07-22 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-22 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-22 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-22 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-22 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-22 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-22 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-22 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-22 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-22 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-22 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-22 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-22 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-22 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-22 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-22 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-22 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-22 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-22 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-22 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-22 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-22 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-22 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-22 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-23 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-23 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-23 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-23 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-23 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-23 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-23 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-23 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-23 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-23 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-23 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-23 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-23 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-23 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-23 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-23 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-23 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-23 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-23 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-23 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-23 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.16% | 1216.1159
2016-07-23 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-23 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-23 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-24 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-24 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-24 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-24 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-24 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-24 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-24 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-24 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-24 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-24 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-24 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-24 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-24 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-24 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-24 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-24 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-24 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-24 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-24 18:00 | 1 | 2280 | 1240 | 1040 | 97.45% | 1013.4593
2016-07-24 19:00 | 1 | 2240 | 1240 | 1000 | 98.08% | 980.8221
2016-07-24 20:00 | 1 | 2240 | 1240 | 1000 | 98.16% | 981.5793
2016-07-24 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-24 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3711
2016-07-24 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-25 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-25 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-25 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-25 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-25 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-25 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-25 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-25 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-25 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-25 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-25 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-25 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-25 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-25 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-25 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-25 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-25 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-25 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-25 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-25 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-25 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-25 21:00 | 1 | 2280 | 1240 | 1040 | 98.35% | 1022.8344
2016-07-25 22:00 | 1 | 2240 | 1240 | 1000 | 98.39% | 983.8577
2016-07-25 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.65% | 1222.2022
2016-07-26 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-26 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-26 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-26 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-26 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-26 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-26 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-26 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-26 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-26 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.61% | 1278.2839
2016-07-26 10:00 | 1 | 2280 | 1240 | 1040 | 98.48% | 1024.1692
2016-07-26 11:00 | 1 | 2140 | 1240 | 900 | 98.34% | 885.1021
2016-07-26 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-26 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-26 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-26 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-26 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-26 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-26 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-26 19:00 | 1 | 2240 | 1240 | 1000 | 98.08% | 980.8221
2016-07-26 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-26 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9005
2016-07-26 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-26 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-27 | 1.25 | 3040 | 1240 | 1440 | 96.24% | 1385.9171
2016-07-27 01:00 | 1.25 | 3040 | 1240 | 1440 | 94.77% | 1364.7572
2016-07-27 02:00 | 1.25 | 3040 | 1240 | 1440 | 94.15% | 1355.7821
2016-07-27 03:00 | 1.25 | 3040 | 1240 | 1440 | 94.17% | 1356.055
2016-07-27 04:00 | 1.25 | 3040 | 1240 | 1440 | 95.65% | 1377.4048
2016-07-27 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.63% | 1420.2953
2016-07-27 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.947
2016-07-27 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-27 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.59% | 1221.463
2016-07-27 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-27 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-27 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-27 12:00 | 1 | 2280 | 1240 | 1040 | 98.21% | 1021.3762
2016-07-27 13:00 | 1 | 2280 | 1240 | 1040 | 96.81% | 1006.8187
2016-07-27 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-27 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-27 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-27 17:00 | 1 | 2280 | 1240 | 1040 | 95.83% | 996.6361
2016-07-27 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-27 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-27 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-27 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-27 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-27 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-28 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-28 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-28 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-28 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-28 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-28 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-28 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-28 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-28 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-28 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-28 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.48% | 1220.0791
2016-07-28 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.34% | 1274.8385
2016-07-28 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-28 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-28 14:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.282
2016-07-28 15:00 | 1 | 2240 | 1240 | 1000 | 95.63% | 956.2766
2016-07-28 16:00 | 1 | 2240 | 1240 | 1000 | 95.64% | 956.3564
2016-07-28 17:00 | 1 | 2240 | 1240 | 1000 | 95.83% | 958.304
2016-07-28 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-28 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-28 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-28 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-28 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7551
2016-07-28 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.65% | 1411.4421
2016-07-29 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-29 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-29 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-29 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-29 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-29 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-29 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-29 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.787
2016-07-29 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-29 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-29 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.48% | 1276.5642
2016-07-29 11:00 | 1 | 2240 | 1240 | 1000 | 98.34% | 983.4468
2016-07-29 12:00 | 1 | 2240 | 1240 | 1000 | 98.21% | 982.0925
2016-07-29 13:00 | 1 | 2240 | 1240 | 1000 | 96.81% | 968.0949
2016-07-29 14:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5333
2016-07-29 15:00 | 1 | 2280 | 1240 | 1040 | 95.63% | 994.5277
2016-07-29 16:00 | 1 | 2280 | 1240 | 1040 | 95.64% | 994.6107
2016-07-29 17:00 | 1 | 2240 | 1240 | 1000 | 95.83% | 958.304
2016-07-29 18:00 | 1 | 2240 | 1240 | 1000 | 97.45% | 974.4801
2016-07-29 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.436
2016-07-29 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.16% | 1272.4176
2016-07-29 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.489
2016-07-29 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-29 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.65% | 1420.5482
2016-07-30 | 1.3 | 3100 | 1240 | 1430.7692 | 96.24% | 1377.033
2016-07-30 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.77% | 1356.0087
2016-07-30 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.15% | 1347.0912
2016-07-30 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.17% | 1347.3624
2016-07-30 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.65% | 1368.5753
2016-07-30 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.63% | 1411.1909
2016-07-30 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8447
2016-07-30 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8953
2016-07-30 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.59% | 1419.6889
2016-07-30 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.61% | 1221.7226
2016-07-30 10:00 | 1 | 2240 | 1240 | 1000 | 98.48% | 984.7781
2016-07-30 11:00 | 1 | 2280 | 1240 | 1040 | 98.34% | 1022.7847
2016-07-30 12:00 | 1 | 2140 | 1240 | 900 | 98.21% | 883.8832
2016-07-30 13:00 | 1 | 2140 | 1240 | 900 | 96.81% | 871.2854
2016-07-30 14:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6538
2016-07-30 15:00 | 1 | 2140 | 1240 | 900 | 95.63% | 860.6489
2016-07-30 16:00 | 1 | 2140 | 1240 | 900 | 95.64% | 860.7208
2016-07-30 17:00 | 1 | 2140 | 1240 | 900 | 95.83% | 862.4736
2016-07-30 18:00 | 1 | 2140 | 1240 | 900 | 97.45% | 877.032
2016-07-30 19:00 | 1 | 2140 | 1240 | 900 | 98.08% | 882.7399
2016-07-30 20:00 | 1 | 2280 | 1240 | 1040 | 98.16% | 1020.8425
2016-07-30 21:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4947
2016-07-30 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.39% | 1218.9387
2016-07-30 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-07-31 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-07-31 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-07-31 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-07-31 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-07-31 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-07-31 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-07-31 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-07-31 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-07-31 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-07-31 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-07-31 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-07-31 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-07-31 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-07-31 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-07-31 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-07-31 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-07-31 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-07-31 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-07-31 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-07-31 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-07-31 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-07-31 21:00 | 1 | 2240 | 1240 | 1000 | 97.78% | 977.8461
2016-07-31 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-07-31 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-01 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-01 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-01 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-01 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-01 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-01 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-01 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-01 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-01 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-01 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-01 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-01 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-01 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-01 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-01 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-01 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-01 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-01 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-01 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-01 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-01 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-01 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-01 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-01 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-02 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-02 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-02 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-02 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-02 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-02 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-02 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-02 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-02 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-02 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-02 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-02 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-02 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-02 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-02 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-02 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-02 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-02 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-02 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-02 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-02 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-02 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-02 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-02 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-03 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-03 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-03 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-03 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-03 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-03 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-03 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-03 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-03 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-03 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-03 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-03 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-03 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-03 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-03 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-03 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-03 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-03 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-03 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-03 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-03 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-03 21:00 | 1 | 2240 | 1240 | 1000 | 97.78% | 977.8461
2016-08-03 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-03 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-04 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-04 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-04 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-04 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-04 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-04 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-04 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-04 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-04 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-04 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-04 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-04 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-04 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-04 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-04 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-04 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-04 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-04 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-04 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-04 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-04 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-04 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-04 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-04 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-05 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-05 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-05 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-05 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-05 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-05 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-05 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-05 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-05 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-05 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-05 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-05 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-05 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-05 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-05 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-05 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-05 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-05 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-05 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-05 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-05 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-05 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-05 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-05 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-06 | 1.08 | 2640 | 1240 | 1296.2963 | 93.62% | 1213.5418
2016-08-06 01:00 | 1.08 | 2640 | 1240 | 1296.2963 | 92.51% | 1199.1603
2016-08-06 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-06 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-06 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-06 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-06 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-06 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.42% | 1275.8208
2016-08-06 08:00 | 1 | 2240 | 1240 | 1000 | 98.35% | 983.4994
2016-08-06 09:00 | 1 | 2280 | 1240 | 1040 | 98.1% | 1020.2909
2016-08-06 10:00 | 1 | 2140 | 1240 | 900 | 98.12% | 883.0723
2016-08-06 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-06 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-06 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-06 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-06 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-06 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-06 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-06 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-06 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-06 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-06 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-06 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-06 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-07 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-07 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-07 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-07 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-07 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-07 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-07 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-07 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-07 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-07 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-07 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-07 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-07 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-07 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-07 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-07 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-07 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-07 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-07 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-07 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-07 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-07 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-07 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-07 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-08 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-08 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-08 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-08 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-08 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-08 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-08 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-08 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-08 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-08 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-08 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-08 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-08 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-08 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-08 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-08 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-08 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-08 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-08 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-08 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-08 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-08 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-08 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-08 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-09 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-09 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-09 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-09 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-09 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-09 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-09 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-09 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-09 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9067
2016-08-09 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-09 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-09 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-09 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-09 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-09 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-09 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-09 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-09 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-09 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-09 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-09 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-09 21:00 | 1 | 2140 | 1240 | 900 | 97.78% | 880.0615
2016-08-09 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-09 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-10 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-10 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-10 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-10 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-10 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-10 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-10 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-10 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-10 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-10 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-10 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-10 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-10 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-10 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-10 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-10 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-10 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-10 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-10 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-10 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-10 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-10 21:00 | 1 | 2140 | 1240 | 900 | 97.78% | 880.0615
2016-08-10 22:00 | 1 | 2280 | 1240 | 1040 | 97.84% | 1017.5849
2016-08-10 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-11 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-11 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-11 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-11 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-11 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-11 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-11 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-11 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-11 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-11 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-11 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-11 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-11 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-11 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-11 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-11 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-11 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-11 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-11 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-11 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-11 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-11 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-11 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-11 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-12 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-12 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-12 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-12 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-12 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-12 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-12 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-12 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-12 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-12 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-12 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-12 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-12 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-12 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-12 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-12 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-12 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-12 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-12 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-12 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-12 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-12 21:00 | 1 | 2240 | 1240 | 1000 | 97.78% | 977.8461
2016-08-12 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-12 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-13 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-13 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-13 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-13 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-13 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-13 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-13 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-13 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-13 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-13 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-13 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-13 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-13 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-13 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-13 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-13 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-13 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-13 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-13 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-13 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-13 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-13 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-13 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-13 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-14 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-14 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-14 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-14 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-14 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-14 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-14 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-14 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-14 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-14 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-14 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-14 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-14 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-14 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-14 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-14 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-14 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-14 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-14 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-14 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-14 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-14 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-14 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-14 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-15 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-15 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-15 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-15 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-15 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-15 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-15 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-15 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-15 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-15 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-15 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-15 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-15 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-15 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-15 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-15 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-15 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-15 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-15 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-15 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-15 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-15 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-15 22:00 | 1 | 2280 | 1240 | 1040 | 97.84% | 1017.5849
2016-08-15 23:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9427
2016-08-16 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-16 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-16 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-16 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-16 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-16 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-16 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-16 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-16 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9067
2016-08-16 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-16 10:00 | 1 | 2140 | 1240 | 900 | 98.12% | 883.0723
2016-08-16 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-16 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-16 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-16 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-16 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-16 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-16 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-16 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-16 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-16 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-16 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-16 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-16 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-17 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-17 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-17 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-17 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-17 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-17 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-17 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-17 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-17 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-17 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-17 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-17 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-17 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-17 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-17 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-17 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-17 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-17 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-17 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-17 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-17 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-17 21:00 | 1 | 2280 | 1240 | 1040 | 97.78% | 1016.96
2016-08-17 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-17 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-18 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-18 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-18 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-18 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-18 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-18 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-18 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-18 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-18 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-18 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-18 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-18 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-18 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-18 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-18 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-18 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-18 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-18 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-18 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-18 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-18 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-18 21:00 | 1 | 2240 | 1240 | 1000 | 97.78% | 977.8461
2016-08-18 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.84% | 1268.3572
2016-08-18 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.99% | 1214.0883
2016-08-19 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-19 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-19 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-19 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-19 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-19 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-19 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-19 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-19 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-19 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-19 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-19 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-19 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-19 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-19 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-19 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-19 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-19 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-19 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-19 19:00 | 1 | 2280 | 1240 | 1040 | 97.86% | 1017.793
2016-08-19 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.8% | 1267.7642
2016-08-19 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4908
2016-08-19 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.9637
2016-08-19 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-20 | 1.3 | 3100 | 1240 | 1430.7692 | 93.62% | 1339.4301
2016-08-20 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.51% | 1323.5567
2016-08-20 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.22% | 1319.4361
2016-08-20 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.11% | 1317.857
2016-08-20 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.73% | 1341.0477
2016-08-20 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3787
2016-08-20 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.51% | 1409.4538
2016-08-20 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1696
2016-08-20 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.35% | 1407.1607
2016-08-20 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-20 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.12% | 1271.9149
2016-08-20 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-20 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-20 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-20 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-20 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-20 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-20 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-20 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-20 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-20 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-20 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-20 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-20 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-21 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-21 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-21 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-21 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-21 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-21 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-21 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-21 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-21 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-21 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-21 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-21 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-21 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-21 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-21 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-21 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-21 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-21 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-21 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-21 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-21 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-21 21:00 | 1 | 2140 | 1240 | 900 | 97.78% | 880.0615
2016-08-21 22:00 | 1 | 2240 | 1240 | 1000 | 97.84% | 978.447
2016-08-21 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-22 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-22 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-22 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-22 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-22 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-22 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-22 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-22 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-22 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-22 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-22 10:00 | 1 | 2280 | 1240 | 1040 | 98.12% | 1020.4391
2016-08-22 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-22 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-22 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-22 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-22 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-22 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-22 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-22 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-22 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-22 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-22 21:00 | 1 | 2140 | 1240 | 900 | 97.78% | 880.0615
2016-08-22 22:00 | 1 | 2140 | 1240 | 900 | 97.84% | 880.6023
2016-08-22 23:00 | 1 | 2240 | 1240 | 1000 | 97.99% | 979.9427
2016-08-23 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-23 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-23 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-23 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-23 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-23 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-23 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-23 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-23 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.35% | 1274.9067
2016-08-23 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-23 10:00 | 1 | 2140 | 1240 | 900 | 98.12% | 883.0723
2016-08-23 11:00 | 1 | 2140 | 1240 | 900 | 98.2% | 883.8204
2016-08-23 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-23 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-23 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-23 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-23 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-23 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-23 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-23 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-23 20:00 | 1 | 2140 | 1240 | 900 | 97.8% | 880.1906
2016-08-23 21:00 | 1 | 2140 | 1240 | 900 | 97.78% | 880.0615
2016-08-23 22:00 | 1 | 2280 | 1240 | 1040 | 97.84% | 1017.5849
2016-08-23 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.99% | 1270.2961
2016-08-24 | 1.13 | 2640 | 1240 | 1238.9381 | 93.62% | 1159.8452
2016-08-24 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.51% | 1146.1001
2016-08-24 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.22% | 1142.5319
2016-08-24 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.11% | 1141.1646
2016-08-24 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 93.73% | 1161.246
2016-08-24 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1473
2016-08-24 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-24 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-24 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-24 09:00 | 1 | 2240 | 1240 | 1000 | 98.1% | 981.049
2016-08-24 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-24 11:00 | 1 | 2280 | 1240 | 1040 | 98.2% | 1021.3036
2016-08-24 12:00 | 1 | 2280 | 1240 | 1040 | 98.44% | 1023.8114
2016-08-24 13:00 | 1 | 2280 | 1240 | 1040 | 97.05% | 1009.3357
2016-08-24 14:00 | 1 | 2280 | 1240 | 1040 | 95.93% | 997.6301
2016-08-24 15:00 | 1 | 2280 | 1240 | 1040 | 95.86% | 996.9753
2016-08-24 16:00 | 1 | 2280 | 1240 | 1040 | 95.79% | 996.2553
2016-08-24 17:00 | 1 | 2280 | 1240 | 1040 | 96.23% | 1000.7404
2016-08-24 18:00 | 1 | 2280 | 1240 | 1040 | 97.35% | 1012.4011
2016-08-24 19:00 | 1 | 2240 | 1240 | 1000 | 97.86% | 978.6471
2016-08-24 20:00 | 1 | 2240 | 1240 | 1000 | 97.8% | 977.9895
2016-08-24 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-24 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-24 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-25 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-25 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-25 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-25 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-25 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-25 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-25 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-25 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-25 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-25 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-25 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.12% | 1215.6355
2016-08-25 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.2% | 1216.6652
2016-08-25 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.44% | 1276.1182
2016-08-25 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.05% | 1258.0751
2016-08-25 14:00 | 1 | 2240 | 1240 | 1000 | 95.93% | 959.2597
2016-08-25 15:00 | 1 | 2240 | 1240 | 1000 | 95.86% | 958.6301
2016-08-25 16:00 | 1 | 2240 | 1240 | 1000 | 95.79% | 957.9378
2016-08-25 17:00 | 1 | 2240 | 1240 | 1000 | 96.23% | 962.2504
2016-08-25 18:00 | 1 | 2240 | 1240 | 1000 | 97.35% | 973.4626
2016-08-25 19:00 | 1 | 2240 | 1240 | 1000 | 97.86% | 978.6471
2016-08-25 20:00 | 1 | 2240 | 1240 | 1000 | 97.8% | 977.9895
2016-08-25 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-25 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-25 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-26 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-26 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-26 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-26 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-26 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-26 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-26 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-26 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-26 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-26 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.7105
2016-08-26 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.12% | 1215.6355
2016-08-26 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.2% | 1272.9923
2016-08-26 12:00 | 1 | 2240 | 1240 | 1000 | 98.44% | 984.434
2016-08-26 13:00 | 1 | 2280 | 1240 | 1040 | 97.05% | 1009.3357
2016-08-26 14:00 | 1 | 2280 | 1240 | 1040 | 95.93% | 997.6301
2016-08-26 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-26 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-26 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-26 18:00 | 1 | 2280 | 1240 | 1040 | 97.35% | 1012.4011
2016-08-26 19:00 | 1 | 2280 | 1240 | 1040 | 97.86% | 1017.793
2016-08-26 20:00 | 1 | 2240 | 1240 | 1000 | 97.8% | 977.9895
2016-08-26 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-26 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-26 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-27 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-27 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-27 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-27 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-27 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-27 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-27 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.51% | 1418.5471
2016-08-27 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2546
2016-08-27 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-27 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-27 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.12% | 1271.9149
2016-08-27 11:00 | 1 | 2240 | 1240 | 1000 | 98.2% | 982.0227
2016-08-27 12:00 | 1 | 2280 | 1240 | 1040 | 98.44% | 1023.8114
2016-08-27 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-27 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-27 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-27 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-27 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-27 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-27 19:00 | 1 | 2280 | 1240 | 1040 | 97.86% | 1017.793
2016-08-27 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.8% | 1267.7642
2016-08-27 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4908
2016-08-27 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.9637
2016-08-27 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.99% | 1402.0719
2016-08-28 | 1.4 | 3370 | 1240 | 1521.4286 | 93.62% | 1424.3018
2016-08-28 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.51% | 1407.4226
2016-08-28 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.22% | 1403.0409
2016-08-28 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.11% | 1401.3618
2016-08-28 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 93.73% | 1426.022
2016-08-28 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.8094
2016-08-28 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.51% | 1498.7625
2016-08-28 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.397
2016-08-28 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.35% | 1407.1607
2016-08-28 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.7105
2016-08-28 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.12% | 1215.6355
2016-08-28 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.2% | 1272.9923
2016-08-28 12:00 | 1 | 2280 | 1240 | 1040 | 98.44% | 1023.8114
2016-08-28 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-28 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-28 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-28 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-28 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-28 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-28 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-28 20:00 | 1 | 2240 | 1240 | 1000 | 97.8% | 977.9895
2016-08-28 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-28 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-28 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-29 | 1.3 | 3100 | 1240 | 1430.7692 | 93.62% | 1339.4301
2016-08-29 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.51% | 1323.5567
2016-08-29 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.22% | 1319.4361
2016-08-29 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.11% | 1317.857
2016-08-29 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 93.73% | 1341.0477
2016-08-29 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3787
2016-08-29 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.51% | 1409.4538
2016-08-29 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1696
2016-08-29 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.35% | 1416.2392
2016-08-29 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.1% | 1215.4589
2016-08-29 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.12% | 1271.9149
2016-08-29 11:00 | 1 | 2240 | 1240 | 1000 | 98.2% | 982.0227
2016-08-29 12:00 | 1 | 2140 | 1240 | 900 | 98.44% | 885.9906
2016-08-29 13:00 | 1 | 2140 | 1240 | 900 | 97.05% | 873.4636
2016-08-29 14:00 | 1 | 2140 | 1240 | 900 | 95.93% | 863.3338
2016-08-29 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-29 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-29 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-29 18:00 | 1 | 2140 | 1240 | 900 | 97.35% | 876.1164
2016-08-29 19:00 | 1 | 2140 | 1240 | 900 | 97.86% | 880.7824
2016-08-29 20:00 | 1 | 2280 | 1240 | 1040 | 97.8% | 1017.1091
2016-08-29 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-29 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-29 23:00 | 1.25 | 3040 | 1240 | 1440 | 97.99% | 1411.1175
2016-08-30 | 1.25 | 3040 | 1240 | 1440 | 93.62% | 1348.0715
2016-08-30 01:00 | 1.25 | 3040 | 1240 | 1440 | 92.51% | 1332.0958
2016-08-30 02:00 | 1.25 | 3040 | 1240 | 1440 | 92.22% | 1327.9486
2016-08-30 03:00 | 1.25 | 3040 | 1240 | 1440 | 92.11% | 1326.3593
2016-08-30 04:00 | 1.25 | 3040 | 1240 | 1440 | 93.73% | 1349.6996
2016-08-30 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.4844
2016-08-30 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.51% | 1220.4805
2016-08-30 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3685
2016-08-30 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.35% | 1218.4949
2016-08-30 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.7302
2016-08-30 10:00 | 1 | 2240 | 1240 | 1000 | 98.12% | 981.1915
2016-08-30 11:00 | 1 | 2240 | 1240 | 1000 | 98.2% | 982.0227
2016-08-30 12:00 | 1 | 2240 | 1240 | 1000 | 98.44% | 984.434
2016-08-30 13:00 | 1 | 2280 | 1240 | 1040 | 97.05% | 1009.3357
2016-08-30 14:00 | 1 | 2280 | 1240 | 1040 | 95.93% | 997.6301
2016-08-30 15:00 | 1 | 2140 | 1240 | 900 | 95.86% | 862.7671
2016-08-30 16:00 | 1 | 2140 | 1240 | 900 | 95.79% | 862.144
2016-08-30 17:00 | 1 | 2140 | 1240 | 900 | 96.23% | 866.0253
2016-08-30 18:00 | 1 | 2280 | 1240 | 1040 | 97.35% | 1012.4011
2016-08-30 19:00 | 1 | 2280 | 1240 | 1040 | 97.86% | 1017.793
2016-08-30 20:00 | 1 | 2240 | 1240 | 1000 | 97.8% | 977.9895
2016-08-30 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5783
2016-08-30 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.2352
2016-08-30 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-08-31 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-08-31 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-08-31 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-08-31 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-08-31 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-08-31 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-08-31 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-08-31 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-08-31 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-08-31 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-08-31 10:00 | 1 | 2240 | 1240 | 1000 | 98.05% | 980.5223
2016-08-31 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-08-31 12:00 | 1 | 2140 | 1240 | 900 | 97.83% | 880.473
2016-08-31 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-08-31 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-08-31 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-08-31 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-08-31 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-08-31 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-08-31 19:00 | 1 | 2140 | 1240 | 900 | 98.17% | 883.502
2016-08-31 20:00 | 1 | 2140 | 1240 | 900 | 98.03% | 882.2324
2016-08-31 21:00 | 1 | 2240 | 1240 | 1000 | 97.11% | 971.1409
2016-08-31 22:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.78% | 1267.5638
2016-08-31 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.42% | 1194.5381
2016-09-01 | 1.13 | 2640 | 1240 | 1238.9381 | 92.06% | 1140.5443
2016-09-01 01:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.44% | 1132.8785
2016-09-01 02:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.01% | 1127.5042
2016-09-01 03:00 | 1.13 | 2640 | 1240 | 1238.9381 | 91.22% | 1130.108
2016-09-01 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 92.75% | 1149.1297
2016-09-01 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-01 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-01 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-01 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-01 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-01 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-01 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-01 12:00 | 1 | 2140 | 1240 | 900 | 97.83% | 880.473
2016-09-01 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-01 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-01 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-01 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-01 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-01 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-09-01 19:00 | 1 | 2280 | 1240 | 1040 | 98.17% | 1020.9356
2016-09-01 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-01 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-01 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-01 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-02 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-02 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-02 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-02 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-02 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-02 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-02 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-02 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-02 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-02 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-02 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-02 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-02 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-02 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-02 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-02 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-02 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-02 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-02 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-02 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-02 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-02 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-02 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-02 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-03 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-03 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-03 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-03 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-03 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-03 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-03 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-03 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-03 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-03 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.05% | 1402.9011
2016-09-03 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.26% | 1405.9201
2016-09-03 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7568
2016-09-03 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9836
2016-09-03 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.8498
2016-09-03 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.7914
2016-09-03 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.82% | 1187.1236
2016-09-03 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.39% | 1194.1931
2016-09-03 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.08% | 1202.7211
2016-09-03 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.17% | 1216.2269
2016-09-03 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-03 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-03 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-03 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-04 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-04 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-04 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-04 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-04 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-04 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-04 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-04 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-04 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-04 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-04 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-04 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-04 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-04 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-04 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-04 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-04 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-04 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-04 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-04 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-04 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-04 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-04 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-04 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-05 | 1.4 | 3370 | 1240 | 1521.4286 | 92.06% | 1400.6
2016-09-05 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.44% | 1391.1863
2016-09-05 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-05 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-05 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-05 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-05 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.06% | 1491.9352
2016-09-05 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.01% | 1491.1402
2016-09-05 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.84% | 1488.4939
2016-09-05 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-05 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-05 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-05 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.171
2016-09-05 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-05 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-05 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-05 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-05 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-05 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-05 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-05 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-05 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-05 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-05 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-06 | 1.4 | 3370 | 1240 | 1521.4286 | 92.06% | 1400.6
2016-09-06 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.44% | 1391.1863
2016-09-06 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-06 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-06 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-06 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-06 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.06% | 1491.9352
2016-09-06 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.01% | 1491.1402
2016-09-06 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.84% | 1488.4939
2016-09-06 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-06 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-06 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-06 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.171
2016-09-06 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-06 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-06 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-06 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-06 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-06 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-06 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-06 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-06 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-06 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-06 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-07 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-07 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-07 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-07 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-07 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-07 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-07 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-07 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.01% | 1214.2735
2016-09-07 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.1185
2016-09-07 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-07 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-07 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-07 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0572
2016-09-07 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3241
2016-09-07 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.8498
2016-09-07 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.7914
2016-09-07 16:00 | 1.25 | 3040 | 1240 | 1440 | 95.82% | 1379.7768
2016-09-07 17:00 | 1.25 | 3040 | 1240 | 1440 | 96.39% | 1387.9936
2016-09-07 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.08% | 1397.9056
2016-09-07 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.17% | 1413.6032
2016-09-07 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.03% | 1411.5718
2016-09-07 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-07 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-07 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-08 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-08 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-08 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-08 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-08 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-08 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-08 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-08 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-08 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-08 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-08 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-08 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-08 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0572
2016-09-08 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.32% | 1248.5706
2016-09-08 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.47% | 1237.6113
2016-09-08 15:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.6816
2016-09-08 16:00 | 1 | 2240 | 1240 | 1000 | 95.82% | 958.1783
2016-09-08 17:00 | 1 | 2240 | 1240 | 1000 | 96.39% | 963.8844
2016-09-08 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-08 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-08 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-08 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-08 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-08 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-09 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-09 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-09 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-09 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-09 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-09 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-09 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-09 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-09 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-09 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-09 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-09 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-09 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.171
2016-09-09 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-09 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-09 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-09 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-09 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-09 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-09 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-09 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-09 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-09 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-09 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-10 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-10 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-10 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-10 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-10 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-10 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-10 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-10 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-10 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-10 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-10 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-10 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-10 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-10 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-10 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-10 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-10 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-10 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-10 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-10 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-10 20:00 | 1 | 2240 | 1240 | 1000 | 98.03% | 980.2582
2016-09-10 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-10 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-10 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.42% | 1194.5381
2016-09-11 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-11 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-11 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-11 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-11 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-11 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-11 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-11 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-11 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-11 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-11 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-11 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-11 12:00 | 1 | 2140 | 1240 | 900 | 97.83% | 880.473
2016-09-11 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-11 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-11 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-11 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-11 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-11 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-09-11 19:00 | 1 | 2280 | 1240 | 1040 | 98.17% | 1020.9356
2016-09-11 20:00 | 1 | 2240 | 1240 | 1000 | 98.03% | 980.2582
2016-09-11 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-11 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-11 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.42% | 1194.5381
2016-09-12 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-12 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-12 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-12 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-12 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-12 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-12 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-12 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-12 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-12 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-12 10:00 | 1 | 2240 | 1240 | 1000 | 98.05% | 980.5223
2016-09-12 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-12 12:00 | 1 | 2140 | 1240 | 900 | 97.83% | 880.473
2016-09-12 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-12 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-12 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-12 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-12 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-12 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-09-12 19:00 | 1 | 2140 | 1240 | 900 | 98.17% | 883.502
2016-09-12 20:00 | 1 | 2140 | 1240 | 900 | 98.03% | 882.2324
2016-09-12 21:00 | 1 | 2280 | 1240 | 1040 | 97.11% | 1009.9865
2016-09-12 22:00 | 1 | 2240 | 1240 | 1000 | 97.78% | 977.8349
2016-09-12 23:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.42% | 1249.8408
2016-09-13 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-13 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-13 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-13 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-13 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-13 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-13 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-13 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.01% | 1214.2735
2016-09-13 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.1185
2016-09-13 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-13 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-13 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-13 12:00 | 1 | 2140 | 1240 | 900 | 97.83% | 880.473
2016-09-13 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-13 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-13 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-13 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-13 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-13 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-09-13 19:00 | 1 | 2280 | 1240 | 1040 | 98.17% | 1020.9356
2016-09-13 20:00 | 1 | 2240 | 1240 | 1000 | 98.03% | 980.2582
2016-09-13 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-13 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-13 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-14 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-14 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-14 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-14 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-14 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-14 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-14 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-14 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-14 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-14 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-14 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-14 11:00 | 1 | 2240 | 1240 | 1000 | 98.26% | 982.6323
2016-09-14 12:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4355
2016-09-14 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-14 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-14 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-14 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-14 17:00 | 1 | 2140 | 1240 | 900 | 96.39% | 867.496
2016-09-14 18:00 | 1 | 2140 | 1240 | 900 | 97.08% | 873.691
2016-09-14 19:00 | 1 | 2280 | 1240 | 1040 | 98.17% | 1020.9356
2016-09-14 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-14 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-14 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-14 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-15 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-15 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-15 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-15 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-15 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-15 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-15 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-15 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-15 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-15 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-15 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-15 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-15 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-15 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-15 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-15 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-15 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-15 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-15 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-15 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-15 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-15 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-15 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-15 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-16 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-16 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-16 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-16 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-16 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-16 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-16 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-16 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-16 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-16 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-16 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-16 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-16 12:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4355
2016-09-16 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-16 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-16 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-16 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-16 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-16 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-16 19:00 | 1 | 2280 | 1240 | 1040 | 98.17% | 1020.9356
2016-09-16 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-16 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-16 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-16 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-17 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-17 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-17 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-17 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-17 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-17 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-17 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-17 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.01% | 1214.2735
2016-09-17 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.1185
2016-09-17 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.3605
2016-09-17 10:00 | 1 | 2240 | 1240 | 1000 | 98.05% | 980.5223
2016-09-17 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-17 12:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4355
2016-09-17 13:00 | 1 | 2140 | 1240 | 900 | 96.32% | 866.8647
2016-09-17 14:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2559
2016-09-17 15:00 | 1 | 2140 | 1240 | 900 | 95.47% | 859.2135
2016-09-17 16:00 | 1 | 2140 | 1240 | 900 | 95.82% | 862.3605
2016-09-17 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-17 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-17 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-17 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-17 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-17 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-17 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-18 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-18 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-18 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-18 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-18 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-18 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-18 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-18 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-18 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-18 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-18 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-18 11:00 | 1 | 2280 | 1240 | 1040 | 98.26% | 1021.9376
2016-09-18 12:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4355
2016-09-18 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-18 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-18 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-18 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-18 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-18 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-18 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-18 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-18 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-18 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-18 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-19 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-19 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-19 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-19 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-19 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-19 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-19 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-19 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-19 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-19 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-19 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-19 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-19 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-19 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-19 14:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.7288
2016-09-19 15:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.6816
2016-09-19 16:00 | 1 | 2240 | 1240 | 1000 | 95.82% | 958.1783
2016-09-19 17:00 | 1 | 2240 | 1240 | 1000 | 96.39% | 963.8844
2016-09-19 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.08% | 1258.4027
2016-09-19 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-19 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-19 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-19 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-19 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-20 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-20 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-20 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-20 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-20 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-20 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-20 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-20 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-20 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-20 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-20 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.05% | 1214.8063
2016-09-20 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-20 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.171
2016-09-20 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-20 14:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.7288
2016-09-20 15:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.6816
2016-09-20 16:00 | 1 | 2240 | 1240 | 1000 | 95.82% | 958.1783
2016-09-20 17:00 | 1 | 2240 | 1240 | 1000 | 96.39% | 963.8844
2016-09-20 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-20 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-20 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-20 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-20 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-20 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-21 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-21 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-21 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-21 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-21 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-21 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-21 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-21 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-21 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-21 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-21 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-21 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.26% | 1414.9905
2016-09-21 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0572
2016-09-21 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.32% | 1248.5706
2016-09-21 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.47% | 1237.6113
2016-09-21 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.47% | 1237.5503
2016-09-21 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.82% | 1242.083
2016-09-21 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.39% | 1249.4798
2016-09-21 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.08% | 1202.7211
2016-09-21 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.17% | 1413.6032
2016-09-21 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.03% | 1411.5718
2016-09-21 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4784
2016-09-21 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-21 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.42% | 1466.905
2016-09-22 | 1.4 | 3370 | 1240 | 1521.4286 | 92.06% | 1400.6
2016-09-22 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.44% | 1391.1863
2016-09-22 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-22 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-22 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-22 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-22 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-22 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-22 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-22 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-22 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.05% | 1402.9011
2016-09-22 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.26% | 1405.9201
2016-09-22 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7263
2016-09-22 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.32% | 1378.0926
2016-09-22 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.8094
2016-09-22 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.7416
2016-09-22 16:00 | 1.25 | 3040 | 1240 | 1440 | 95.82% | 1379.7768
2016-09-22 17:00 | 1.25 | 3040 | 1240 | 1440 | 96.39% | 1387.9936
2016-09-22 18:00 | 1.25 | 3040 | 1240 | 1440 | 97.08% | 1397.9056
2016-09-22 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.17% | 1413.6032
2016-09-22 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.03% | 1411.5718
2016-09-22 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.11% | 1389.4784
2016-09-22 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.78% | 1487.706
2016-09-22 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.42% | 1466.905
2016-09-23 | 1.5 | 3750 | 1240 | 1673.3333 | 92.06% | 1540.4408
2016-09-23 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.44% | 1530.0872
2016-09-23 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.01% | 1522.8287
2016-09-23 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 91.22% | 1526.3454
2016-09-23 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 92.75% | 1552.0365
2016-09-23 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.08% | 1641.2396
2016-09-23 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.06% | 1491.9352
2016-09-23 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.01% | 1491.1402
2016-09-23 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.84% | 1488.4939
2016-09-23 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.1621
2016-09-23 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.05% | 1491.7946
2016-09-23 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.26% | 1405.9201
2016-09-23 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.83% | 1399.7263
2016-09-23 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9836
2016-09-23 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.8094
2016-09-23 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.7914
2016-09-23 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.82% | 1242.083
2016-09-23 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.39% | 1249.4798
2016-09-23 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.08% | 1258.4027
2016-09-23 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.17% | 1216.2269
2016-09-23 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-23 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-23 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-23 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-24 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-24 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-24 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-24 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-24 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-24 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-24 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-24 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.01% | 1214.2735
2016-09-24 08:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.84% | 1212.1185
2016-09-24 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.08% | 1271.3605
2016-09-24 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-24 11:00 | 1 | 2240 | 1240 | 1000 | 98.26% | 982.6323
2016-09-24 12:00 | 1 | 2280 | 1240 | 1040 | 97.83% | 1017.4355
2016-09-24 13:00 | 1 | 2280 | 1240 | 1040 | 96.32% | 1001.7103
2016-09-24 14:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.9179
2016-09-24 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-24 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-24 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-24 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-24 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-24 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-24 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-24 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-24 23:00 | 1.25 | 3040 | 1240 | 1440 | 96.42% | 1388.3946
2016-09-25 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-25 01:00 | 1.25 | 3040 | 1240 | 1440 | 91.44% | 1316.7285
2016-09-25 02:00 | 1.25 | 3040 | 1240 | 1440 | 91.01% | 1310.482
2016-09-25 03:00 | 1.25 | 3040 | 1240 | 1440 | 91.22% | 1313.5084
2016-09-25 04:00 | 1.25 | 3040 | 1240 | 1440 | 92.75% | 1335.617
2016-09-25 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.3815
2016-09-25 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.06% | 1412.0852
2016-09-25 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.01% | 1411.3327
2016-09-25 08:00 | 1.25 | 3040 | 1240 | 1440 | 97.84% | 1408.828
2016-09-25 09:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.08% | 1215.1056
2016-09-25 10:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.05% | 1271.0474
2016-09-25 11:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.26% | 1273.7826
2016-09-25 12:00 | 1 | 2240 | 1240 | 1000 | 97.83% | 978.3033
2016-09-25 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-25 14:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.7288
2016-09-25 15:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.6816
2016-09-25 16:00 | 1 | 2240 | 1240 | 1000 | 95.82% | 958.1783
2016-09-25 17:00 | 1 | 2240 | 1240 | 1000 | 96.39% | 963.8844
2016-09-25 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.08% | 1258.4027
2016-09-25 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.17% | 1272.5337
2016-09-25 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-25 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-25 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.78% | 1211.4769
2016-09-25 23:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.42% | 1194.5381
2016-09-26 | 1.25 | 3040 | 1240 | 1440 | 92.06% | 1325.6383
2016-09-26 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-26 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.01% | 1302.0815
2016-09-26 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.22% | 1305.0885
2016-09-26 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 92.75% | 1327.0554
2016-09-26 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.3278
2016-09-26 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-26 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-26 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-26 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-26 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.05% | 1402.9011
2016-09-26 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.26% | 1405.9201
2016-09-26 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7568
2016-09-26 13:00 | 1.25 | 3040 | 1240 | 1440 | 96.32% | 1386.9836
2016-09-26 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.8094
2016-09-26 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.7416
2016-09-26 16:00 | 1.25 | 3040 | 1240 | 1440 | 95.82% | 1379.7768
2016-09-26 17:00 | 1.25 | 3040 | 1240 | 1440 | 96.39% | 1387.9936
2016-09-26 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.08% | 1202.7211
2016-09-26 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.17% | 1216.2269
2016-09-26 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-26 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-26 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-26 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-27 | 1.3 | 3100 | 1240 | 1430.7692 | 92.06% | 1317.1406
2016-09-27 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 91.44% | 1308.2879
2016-09-27 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-27 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-27 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-27 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-27 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.06% | 1491.9352
2016-09-27 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-27 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-27 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-27 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-27 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.26% | 1414.9905
2016-09-27 12:00 | 1.25 | 3040 | 1240 | 1440 | 97.83% | 1408.7568
2016-09-27 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3241
2016-09-27 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.8498
2016-09-27 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.47% | 1237.5503
2016-09-27 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.82% | 1242.083
2016-09-27 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 96.39% | 1249.4798
2016-09-27 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.08% | 1258.4027
2016-09-27 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.17% | 1216.2269
2016-09-27 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.03% | 1214.4792
2016-09-27 21:00 | 1.25 | 3040 | 1240 | 1440 | 97.11% | 1398.4428
2016-09-27 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-27 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.42% | 1466.905
2016-09-28 | 1.4 | 3370 | 1240 | 1521.4286 | 92.06% | 1400.6
2016-09-28 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.44% | 1391.1863
2016-09-28 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-28 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-28 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-28 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-28 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.06% | 1491.9352
2016-09-28 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.01% | 1491.1402
2016-09-28 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 97.84% | 1488.4939
2016-09-28 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.08% | 1403.2467
2016-09-28 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-28 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.26% | 1414.9905
2016-09-28 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.83% | 1212.0572
2016-09-28 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.32% | 1193.3241
2016-09-28 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 95.47% | 1237.6113
2016-09-28 15:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.6816
2016-09-28 16:00 | 1 | 2240 | 1240 | 1000 | 95.82% | 958.1783
2016-09-28 17:00 | 1 | 2240 | 1240 | 1000 | 96.39% | 963.8844
2016-09-28 18:00 | 1 | 2240 | 1240 | 1000 | 97.08% | 970.7678
2016-09-28 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-28 20:00 | 1 | 2240 | 1240 | 1000 | 98.03% | 980.2582
2016-09-28 21:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.11% | 1258.8863
2016-09-28 22:00 | 1.25 | 3040 | 1240 | 1440 | 97.78% | 1408.0823
2016-09-28 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.42% | 1379.4947
2016-09-29 | 1.4 | 3370 | 1240 | 1521.4286 | 92.06% | 1400.6
2016-09-29 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.44% | 1391.1863
2016-09-29 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.01% | 1384.5867
2016-09-29 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 91.22% | 1387.7842
2016-09-29 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 92.75% | 1411.143
2016-09-29 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.08% | 1492.2483
2016-09-29 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.06% | 1403.0333
2016-09-29 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.01% | 1402.2857
2016-09-29 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.84% | 1399.7971
2016-09-29 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.08% | 1412.2999
2016-09-29 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.05% | 1411.9521
2016-09-29 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.26% | 1217.4206
2016-09-29 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 97.83% | 1268.171
2016-09-29 13:00 | 1 | 2240 | 1240 | 1000 | 96.32% | 963.183
2016-09-29 14:00 | 1 | 2240 | 1240 | 1000 | 95.47% | 954.7288
2016-09-29 15:00 | 1 | 2280 | 1240 | 1040 | 95.47% | 992.8689
2016-09-29 16:00 | 1 | 2280 | 1240 | 1040 | 95.82% | 996.5054
2016-09-29 17:00 | 1 | 2280 | 1240 | 1040 | 96.39% | 1002.4398
2016-09-29 18:00 | 1 | 2280 | 1240 | 1040 | 97.08% | 1009.5985
2016-09-29 19:00 | 1 | 2240 | 1240 | 1000 | 98.17% | 981.6689
2016-09-29 20:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.03% | 1270.7051
2016-09-29 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 97.11% | 1203.1834
2016-09-29 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 97.78% | 1399.0561
2016-09-29 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-09-30 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-09-30 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-09-30 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-09-30 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-09-30 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-09-30 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-09-30 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.12% | 1260.743
2016-09-30 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-09-30 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-09-30 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.78% | 1263.9662
2016-09-30 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-09-30 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-09-30 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-09-30 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.43% | 1133.3458
2016-09-30 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.3% | 1131.6335
2016-09-30 15:00 | 1 | 2240 | 1240 | 1000 | 87.56% | 875.6451
2016-09-30 16:00 | 1 | 2240 | 1240 | 1000 | 87.23% | 872.2717
2016-09-30 17:00 | 1 | 2240 | 1240 | 1000 | 87.34% | 873.3745
2016-09-30 18:00 | 1 | 2240 | 1240 | 1000 | 87.5% | 875.0031
2016-09-30 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.51% | 1134.4218
2016-09-30 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 85.87% | 1063.9181
2016-09-30 21:00 | 1.25 | 3040 | 1240 | 1440 | 86.02% | 1238.6412
2016-09-30 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-09-30 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.1% | 1246.2548
2016-10-01 | 1.3 | 3100 | 1240 | 1430.7692 | 87.08% | 1245.9049
2016-10-01 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-01 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-01 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-01 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-01 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.12% | 1260.743
2016-10-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-10-01 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-10-01 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.78% | 1263.9662
2016-10-01 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-01 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.53% | 1084.493
2016-10-01 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-01 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.43% | 1133.3458
2016-10-01 14:00 | 1 | 2240 | 1240 | 1000 | 87.3% | 872.9744
2016-10-01 15:00 | 1 | 2240 | 1240 | 1000 | 87.56% | 875.6451
2016-10-01 16:00 | 1 | 2240 | 1240 | 1000 | 87.23% | 872.2717
2016-10-01 17:00 | 1 | 2240 | 1240 | 1000 | 87.34% | 873.3745
2016-10-01 18:00 | 1 | 2240 | 1240 | 1000 | 87.5% | 875.0031
2016-10-01 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.51% | 1134.4218
2016-10-01 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 85.87% | 1063.9181
2016-10-01 21:00 | 1.25 | 3040 | 1240 | 1440 | 86.02% | 1238.6412
2016-10-01 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-10-01 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.1% | 1246.2548
2016-10-02 | 1.3 | 3100 | 1240 | 1430.7692 | 87.08% | 1245.9049
2016-10-02 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.91% | 1243.5315
2016-10-02 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.74% | 1241.0182
2016-10-02 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.87% | 1242.9719
2016-10-02 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.27% | 1248.6284
2016-10-02 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.1% | 1260.5582
2016-10-02 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.12% | 1260.743
2016-10-02 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-10-02 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-10-02 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-02 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-02 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-02 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-02 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.43% | 1083.1977
2016-10-02 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-02 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-02 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-02 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-02 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-02 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-02 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-02 21:00 | 1.25 | 3040 | 1240 | 1440 | 86.02% | 1238.6412
2016-10-02 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-10-02 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-03 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-03 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-03 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-03 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-03 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-03 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-03 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-03 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-03 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-03 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-03 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-03 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-03 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-03 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-03 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-03 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-03 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-03 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-03 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-03 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-03 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-03 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-03 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-03 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-04 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-04 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-04 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-04 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-04 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-04 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-04 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-04 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-04 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-04 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-04 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-04 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-04 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-04 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-04 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-04 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-04 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-04 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-04 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-04 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-04 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-04 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-04 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-04 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-05 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-05 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-05 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-05 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-05 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-05 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-05 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-05 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-05 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-05 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-05 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-05 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-05 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-05 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-05 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-05 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-05 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-05 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-05 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-05 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-05 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-05 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-05 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-05 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-06 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-06 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-06 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-06 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-06 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-06 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-06 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-06 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-06 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-06 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-06 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-06 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-06 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-06 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-06 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-06 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-06 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-06 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-06 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-06 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-06 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-06 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-06 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-06 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-07 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-07 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-07 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-07 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-07 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-07 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-07 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-07 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-07 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-07 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-07 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-07 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-07 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-07 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-07 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-07 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-07 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-07 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-07 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-07 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-07 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-07 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-07 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-07 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-08 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-08 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-08 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-08 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-08 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-08 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-08 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-08 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-08 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-08 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-08 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-08 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-08 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-08 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.43% | 1083.1977
2016-10-08 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.3% | 1131.6335
2016-10-08 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.56% | 1135.0955
2016-10-08 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.23% | 1130.7226
2016-10-08 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.34% | 1132.1521
2016-10-08 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-08 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-08 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-08 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-08 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-08 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-09 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-09 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-09 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-09 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-09 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-09 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-09 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-09 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-09 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-09 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-09 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-09 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-09 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-09 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.43% | 1083.1977
2016-10-09 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.3% | 1131.6335
2016-10-09 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.56% | 1135.0955
2016-10-09 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.23% | 1130.7226
2016-10-09 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.34% | 1132.1521
2016-10-09 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.5% | 1134.2632
2016-10-09 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.51% | 1084.2261
2016-10-09 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-09 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-09 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-09 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-10 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-10 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-10 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-10 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-10 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-10 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-10 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-10 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-10 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-10 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-10 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-10 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-10 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-10 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-10 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-10 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-10 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-10 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-10 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-10 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.51% | 1084.2261
2016-10-10 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 85.87% | 1063.9181
2016-10-10 21:00 | 1.25 | 3040 | 1240 | 1440 | 86.02% | 1238.6412
2016-10-10 22:00 | 1.25 | 3040 | 1240 | 1440 | 86.19% | 1241.1776
2016-10-10 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.1% | 1246.2548
2016-10-11 | 1.3 | 3100 | 1240 | 1430.7692 | 87.08% | 1245.9049
2016-10-11 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-11 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-11 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-11 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-11 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-11 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-11 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-10-11 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-10-11 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.78% | 1263.9662
2016-10-11 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-11 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.53% | 1084.493
2016-10-11 12:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.48% | 1133.9647
2016-10-11 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.43% | 1133.3458
2016-10-11 14:00 | 1 | 2240 | 1240 | 1000 | 87.3% | 872.9744
2016-10-11 15:00 | 1 | 2240 | 1240 | 1000 | 87.56% | 875.6451
2016-10-11 16:00 | 1 | 2240 | 1240 | 1000 | 87.23% | 872.2717
2016-10-11 17:00 | 1 | 2240 | 1240 | 1000 | 87.34% | 873.3745
2016-10-11 18:00 | 1 | 2240 | 1240 | 1000 | 87.5% | 875.0031
2016-10-11 19:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.51% | 1134.4218
2016-10-11 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 85.87% | 1063.9181
2016-10-11 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 86.02% | 1065.6943
2016-10-11 22:00 | 1.25 | 3040 | 1240 | 1440 | 86.19% | 1241.1776
2016-10-11 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.1% | 1246.2548
2016-10-12 | 1.3 | 3100 | 1240 | 1430.7692 | 87.08% | 1245.9049
2016-10-12 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.91% | 1243.5315
2016-10-12 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.74% | 1241.0182
2016-10-12 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.87% | 1242.9719
2016-10-12 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.27% | 1248.6284
2016-10-12 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.1% | 1260.5582
2016-10-12 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 88.12% | 1260.743
2016-10-12 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-10-12 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-10-12 09:00 | 1.25 | 3040 | 1240 | 1440 | 87.78% | 1263.9662
2016-10-12 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-12 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.53% | 1084.493
2016-10-12 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-12 13:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.43% | 1133.3458
2016-10-12 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.3% | 1131.6335
2016-10-12 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.56% | 1135.0955
2016-10-12 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.23% | 1130.7226
2016-10-12 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.34% | 1132.1521
2016-10-12 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.5% | 1134.2632
2016-10-12 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.51% | 1084.2261
2016-10-12 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 85.87% | 1063.9181
2016-10-12 21:00 | 1.25 | 3040 | 1240 | 1440 | 86.02% | 1238.6412
2016-10-12 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-10-12 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-13 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-13 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-13 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-13 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-13 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-13 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-13 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-13 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-13 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-13 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-13 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-13 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-13 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-13 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-13 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-13 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-13 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-13 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-13 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-13 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-13 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-13 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-13 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-10-13 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-14 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-14 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-14 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-14 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-14 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-14 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-14 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-14 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.98% | 1258.8202
2016-10-14 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.73% | 1255.1658
2016-10-14 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-14 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-14 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-14 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-14 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-14 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-14 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-14 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-14 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-14 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-14 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-14 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-14 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-14 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-14 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-15 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-15 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-15 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-15 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-15 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-15 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-15 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-15 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-15 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-15 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-15 10:00 | 1.25 | 3040 | 1240 | 1440 | 87.65% | 1262.1838
2016-10-15 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-15 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-15 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.43% | 1083.1977
2016-10-15 14:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.3% | 1131.6335
2016-10-15 15:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.56% | 1135.0955
2016-10-15 16:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.23% | 1130.7226
2016-10-15 17:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.34% | 1132.1521
2016-10-15 18:00 | 1.08 | 2640 | 1240 | 1296.2963 | 87.5% | 1134.2632
2016-10-15 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.51% | 1084.2261
2016-10-15 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-15 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-15 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-15 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-16 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-16 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-16 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-16 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-16 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-16 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-16 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-16 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-16 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-16 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-16 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-16 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-16 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-16 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-16 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-16 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-16 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-16 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-16 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-16 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-16 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-16 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-16 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-16 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-17 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-17 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-17 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-17 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-17 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-17 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-17 06:00 | 2 | 4700 | 1240 | 1730 | 88.12% | 1524.4145
2016-10-17 07:00 | 2 | 4700 | 1240 | 1730 | 87.98% | 1522.0896
2016-10-17 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-17 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-17 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-17 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-17 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-17 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-17 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-17 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-17 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-17 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-17 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-17 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-17 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-17 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-17 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-17 23:00 | 2 | 4700 | 1240 | 1730 | 87.1% | 1506.8963
2016-10-18 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-18 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-18 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-18 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-18 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-18 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-18 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-18 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-18 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-18 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-18 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-18 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-18 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-18 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-18 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-18 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-18 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-18 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-18 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-18 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-18 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-18 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-18 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-18 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-19 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-19 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-19 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-19 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-19 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-19 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-19 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-19 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-19 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-19 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.78% | 1255.8639
2016-10-19 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-19 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-19 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.48% | 1083.7893
2016-10-19 13:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.43% | 1083.1977
2016-10-19 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-19 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-19 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-19 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.34% | 1082.0569
2016-10-19 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.5% | 1084.0746
2016-10-19 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-19 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-19 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-19 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.19% | 1233.2213
2016-10-19 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.1% | 1325.2226
2016-10-20 | 1.4 | 3370 | 1240 | 1521.4286 | 87.08% | 1324.8505
2016-10-20 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.91% | 1322.3267
2016-10-20 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.74% | 1319.6541
2016-10-20 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.87% | 1321.7316
2016-10-20 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.27% | 1327.7465
2016-10-20 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.1% | 1340.4323
2016-10-20 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-20 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-20 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-20 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-20 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-20 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-20 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-20 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-20 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.3% | 1081.5612
2016-10-20 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.56% | 1084.8701
2016-10-20 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 87.23% | 1080.6906
2016-10-20 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-20 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-20 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-20 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-20 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-20 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-20 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-21 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-21 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-21 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-21 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-21 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-21 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-21 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-21 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-21 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-21 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-21 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-21 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-21 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-21 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.43% | 1250.9148
2016-10-21 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.3% | 1249.0249
2016-10-21 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.56% | 1252.8461
2016-10-21 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.23% | 1248.0195
2016-10-21 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.34% | 1249.5973
2016-10-21 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.5% | 1251.9275
2016-10-21 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.51% | 1331.4407
2016-10-21 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 85.87% | 1306.5023
2016-10-21 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.02% | 1439.347
2016-10-21 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-21 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-22 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-22 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-22 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-22 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-22 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-22 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-22 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 88.12% | 1340.6288
2016-10-22 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-22 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-22 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-22 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-22 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-22 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-22 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.43% | 1250.9148
2016-10-22 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.3% | 1249.0249
2016-10-22 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-22 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-22 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-22 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-22 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-22 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-22 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-22 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-22 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-23 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-23 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-23 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-23 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-23 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-23 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-23 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-23 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-23 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-23 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-23 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-23 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.53% | 1331.7685
2016-10-23 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.48% | 1330.9043
2016-10-23 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.43% | 1330.1779
2016-10-23 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.3% | 1328.1682
2016-10-23 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.56% | 1332.2315
2016-10-23 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.23% | 1327.0991
2016-10-23 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.34% | 1328.7769
2016-10-23 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.5% | 1331.2547
2016-10-23 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.51% | 1331.4407
2016-10-23 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 85.87% | 1306.5023
2016-10-23 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.02% | 1439.347
2016-10-23 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-23 23:00 | 2 | 4700 | 1240 | 1730 | 87.1% | 1506.8963
2016-10-24 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-24 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-24 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-24 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-24 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-24 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-24 06:00 | 2 | 4700 | 1240 | 1730 | 88.12% | 1524.4145
2016-10-24 07:00 | 2 | 4700 | 1240 | 1730 | 87.98% | 1522.0896
2016-10-24 08:00 | 2 | 4700 | 1240 | 1730 | 87.73% | 1517.6709
2016-10-24 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.78% | 1468.7756
2016-10-24 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-24 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.53% | 1331.7685
2016-10-24 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-24 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.43% | 1250.9148
2016-10-24 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.3% | 1249.0249
2016-10-24 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-24 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-24 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-24 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-24 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-24 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-24 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-24 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-24 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-25 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-25 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-25 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-25 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-25 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-25 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-25 06:00 | 2 | 4700 | 1240 | 1730 | 88.12% | 1524.4145
2016-10-25 07:00 | 2 | 4700 | 1240 | 1730 | 87.98% | 1522.0896
2016-10-25 08:00 | 2 | 4700 | 1240 | 1730 | 87.73% | 1517.6709
2016-10-25 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.78% | 1468.7756
2016-10-25 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.65% | 1466.7043
2016-10-25 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.53% | 1464.7369
2016-10-25 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.48% | 1330.9043
2016-10-25 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.43% | 1250.9148
2016-10-25 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.3% | 1249.0249
2016-10-25 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.56% | 1252.8461
2016-10-25 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.23% | 1248.0195
2016-10-25 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.34% | 1249.5973
2016-10-25 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.5% | 1251.9275
2016-10-25 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-25 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 85.87% | 1306.5023
2016-10-25 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-25 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-25 23:00 | 2 | 4700 | 1240 | 1730 | 87.1% | 1506.8963
2016-10-26 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-26 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-26 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-26 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-26 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-26 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-26 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-26 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-26 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-26 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-26 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.65% | 1254.0929
2016-10-26 11:00 | 1.25 | 3040 | 1240 | 1440 | 87.53% | 1260.4908
2016-10-26 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-26 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-26 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-26 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-26 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-26 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-26 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-26 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-26 20:00 | 1.25 | 3040 | 1240 | 1440 | 85.87% | 1236.5769
2016-10-26 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 86.02% | 1230.7012
2016-10-26 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.19% | 1311.3632
2016-10-26 23:00 | 2 | 4700 | 1240 | 1730 | 87.1% | 1506.8963
2016-10-27 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-27 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-27 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-27 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-27 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-27 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-27 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-27 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-27 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-27 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-27 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-27 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-27 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-27 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-27 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-27 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-27 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-27 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-27 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.5% | 1251.9275
2016-10-27 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.51% | 1252.1025
2016-10-27 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-27 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-27 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-27 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-28 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-28 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-28 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-28 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-28 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-28 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-28 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-28 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-28 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-28 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.78% | 1468.7756
2016-10-28 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-28 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.53% | 1331.7685
2016-10-28 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.48% | 1330.9043
2016-10-28 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.43% | 1330.1779
2016-10-28 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.3% | 1328.1682
2016-10-28 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.56% | 1332.2315
2016-10-28 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.23% | 1327.0991
2016-10-28 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.34% | 1328.7769
2016-10-28 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.5% | 1331.2547
2016-10-28 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.51% | 1331.4407
2016-10-28 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 85.87% | 1306.5023
2016-10-28 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-28 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-28 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.1% | 1457.5375
2016-10-29 | 1.5 | 3750 | 1240 | 1673.3333 | 87.08% | 1457.1282
2016-10-29 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.91% | 1454.3524
2016-10-29 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.74% | 1451.413
2016-10-29 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.87% | 1453.698
2016-10-29 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.27% | 1460.3134
2016-10-29 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.1% | 1474.2658
2016-10-29 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 88.12% | 1474.4819
2016-10-29 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.98% | 1338.5841
2016-10-29 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.73% | 1334.6982
2016-10-29 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-29 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-29 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-29 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.48% | 1251.598
2016-10-29 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.43% | 1250.9148
2016-10-29 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.3% | 1249.0249
2016-10-29 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.56% | 1252.8461
2016-10-29 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.23% | 1248.0195
2016-10-29 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.34% | 1249.5973
2016-10-29 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.5% | 1251.9275
2016-10-29 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.51% | 1331.4407
2016-10-29 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 85.87% | 1436.9481
2016-10-29 21:00 | 2 | 4700 | 1240 | 1730 | 86.02% | 1488.0898
2016-10-29 22:00 | 2 | 4700 | 1240 | 1730 | 86.19% | 1491.137
2016-10-29 23:00 | 2 | 4700 | 1240 | 1730 | 87.1% | 1506.8963
2016-10-30 | 2 | 4700 | 1240 | 1730 | 87.08% | 1506.4732
2016-10-30 01:00 | 2 | 4700 | 1240 | 1730 | 86.91% | 1503.6034
2016-10-30 02:00 | 2 | 4700 | 1240 | 1730 | 86.74% | 1500.5645
2016-10-30 03:00 | 2 | 4700 | 1240 | 1730 | 86.87% | 1502.9268
2016-10-30 04:00 | 2 | 4700 | 1240 | 1730 | 87.27% | 1509.7663
2016-10-30 05:00 | 2 | 4700 | 1240 | 1730 | 88.1% | 1524.1911
2016-10-30 06:00 | 2 | 4700 | 1240 | 1730 | 88.12% | 1524.4145
2016-10-30 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.98% | 1472.2331
2016-10-30 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 87.73% | 1467.9591
2016-10-30 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.78% | 1335.4405
2016-10-30 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 87.65% | 1333.5573
2016-10-30 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 87.53% | 1252.4107
2016-10-30 12:00 | 1.25 | 3040 | 1240 | 1440 | 87.48% | 1259.6728
2016-10-30 13:00 | 1.25 | 3040 | 1240 | 1440 | 87.43% | 1258.9852
2016-10-30 14:00 | 1.25 | 3040 | 1240 | 1440 | 87.3% | 1257.0831
2016-10-30 15:00 | 1.25 | 3040 | 1240 | 1440 | 87.56% | 1260.929
2016-10-30 16:00 | 1.25 | 3040 | 1240 | 1440 | 87.23% | 1256.0712
2016-10-30 17:00 | 1.25 | 3040 | 1240 | 1440 | 87.34% | 1257.6593
2016-10-30 18:00 | 1.25 | 3040 | 1240 | 1440 | 87.5% | 1260.0044
2016-10-30 19:00 | 1.25 | 3040 | 1240 | 1440 | 87.51% | 1260.1805
2016-10-30 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 85.87% | 1228.6501
2016-10-30 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 86.02% | 1308.6835
2016-10-30 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 86.19% | 1442.2943
2016-10-30 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4542
2016-10-31 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-10-31 01:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-10-31 02:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-10-31 03:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-10-31 04:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-10-31 05:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-10-31 06:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-10-31 07:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-10-31 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-10-31 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-10-31 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-10-31 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-10-31 12:00 | 1.25 | 3040 | 1240 | 1440 | 95.58% | 1376.3678
2016-10-31 13:00 | 1.25 | 3040 | 1240 | 1440 | 95.93% | 1381.4426
2016-10-31 14:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.97% | 1189.0487
2016-10-31 15:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.18% | 1191.555
2016-10-31 16:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.35% | 1181.2968
2016-10-31 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.33% | 1181.0781
2016-10-31 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.7948
2016-10-31 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.75% | 1186.2969
2016-10-31 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.07% | 1177.8386
2016-10-31 21:00 | 1.25 | 3040 | 1240 | 1440 | 95.29% | 1372.1292
2016-10-31 22:00 | 1.25 | 3040 | 1240 | 1440 | 95.3% | 1372.3903
2016-10-31 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.29% | 1363.3243
2016-11-01 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-01 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-01 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.7% | 1584.5659
2016-11-01 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.57% | 1582.5128
2016-11-01 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.17% | 1592.4492
2016-11-01 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.38% | 1596.0975
2016-11-01 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-01 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-01 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-01 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-01 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-01 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-01 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-01 13:00 | 1.25 | 3040 | 1240 | 1440 | 95.58% | 1376.3678
2016-11-01 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.93% | 1381.4426
2016-11-01 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.97% | 1382.0144
2016-11-01 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.18% | 1384.9274
2016-11-01 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.35% | 1364.2031
2016-11-01 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-01 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.47% | 1365.9331
2016-11-01 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.75% | 1369.9774
2016-11-01 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-01 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-01 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-02 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-02 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-02 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-02 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-02 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-02 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-02 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-02 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-02 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-02 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-02 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-02 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-02 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-02 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-02 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.93% | 1605.2875
2016-11-02 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.97% | 1605.9519
2016-11-02 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-02 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-02 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-02 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-02 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-02 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-02 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-02 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.3% | 1594.7684
2016-11-03 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4542
2016-11-03 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-03 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-03 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-03 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-03 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-03 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-03 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-03 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-03 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-03 10:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6949
2016-11-03 11:00 | 2 | 4700 | 1240 | 1730 | 95.72% | 1655.9372
2016-11-03 12:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.563
2016-11-03 13:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.5529
2016-11-03 14:00 | 2 | 4700 | 1240 | 1730 | 95.93% | 1659.6498
2016-11-03 15:00 | 2 | 4700 | 1240 | 1730 | 95.97% | 1660.3367
2016-11-03 16:00 | 2 | 4700 | 1240 | 1730 | 96.18% | 1663.8364
2016-11-03 17:00 | 2 | 4700 | 1240 | 1730 | 95.35% | 1649.5122
2016-11-03 18:00 | 2 | 4700 | 1240 | 1730 | 95.33% | 1649.2069
2016-11-03 19:00 | 2 | 4700 | 1240 | 1730 | 95.47% | 1651.604
2016-11-03 20:00 | 2 | 4700 | 1240 | 1730 | 95.75% | 1656.4942
2016-11-03 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-03 22:00 | 2.2 | 5200 | 1240 | 1800 | 95.29% | 1715.1615
2016-11-03 23:00 | 2.2 | 5200 | 1240 | 1800 | 95.3% | 1715.4879
2016-11-04 | 2.2 | 5200 | 1240 | 1800 | 95.29% | 1715.1499
2016-11-04 01:00 | 2.2 | 5200 | 1240 | 1800 | 94.96% | 1709.3581
2016-11-04 02:00 | 2.2 | 5200 | 1240 | 1800 | 94.7% | 1704.5132
2016-11-04 03:00 | 2.2 | 5200 | 1240 | 1800 | 94.57% | 1702.3046
2016-11-04 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-04 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-04 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-04 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-04 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-04 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-04 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-04 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-04 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-04 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-04 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.93% | 1605.2875
2016-11-04 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.97% | 1605.9519
2016-11-04 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-04 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-04 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-04 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-04 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-04 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-04 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7198
2016-11-04 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.3% | 1449.9957
2016-11-05 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7101
2016-11-05 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.96% | 1444.8146
2016-11-05 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.7% | 1440.7195
2016-11-05 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.57% | 1438.8527
2016-11-05 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.17% | 1447.8871
2016-11-05 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.38% | 1364.7294
2016-11-05 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.63% | 1368.2716
2016-11-05 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.76% | 1379.001
2016-11-05 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.81% | 1370.8729
2016-11-05 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.59% | 1367.608
2016-11-05 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-05 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-05 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-05 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5449
2016-11-05 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.93% | 1372.5872
2016-11-05 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.97% | 1373.1553
2016-11-05 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.18% | 1376.0497
2016-11-05 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.35% | 1364.2031
2016-11-05 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-05 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.47% | 1365.9331
2016-11-05 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-05 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-05 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-05 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-06 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-06 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-06 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-06 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-06 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-06 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-06 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-06 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-06 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-06 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-06 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-06 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-06 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-06 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-06 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-06 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-06 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-06 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-06 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-06 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-06 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-06 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-06 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-06 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-07 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-07 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-07 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-07 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-07 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-07 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-07 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-07 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-07 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-07 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-07 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-07 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-07 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-07 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-07 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.93% | 1605.2875
2016-11-07 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.97% | 1605.9519
2016-11-07 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-07 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-07 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-07 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-07 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-07 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-07 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-07 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-08 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-08 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-08 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-08 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-08 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-08 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-08 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-08 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-08 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-08 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-08 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-08 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-08 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-08 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-08 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-08 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-08 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-08 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-08 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-08 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-08 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-08 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-08 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-08 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-09 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-09 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-09 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-09 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-09 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-09 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-09 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-09 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-09 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-09 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-09 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-09 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-09 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-09 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-09 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.93% | 1605.2875
2016-11-09 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.97% | 1605.9519
2016-11-09 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-09 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-09 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-09 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-09 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-09 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-09 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-09 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-10 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-10 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-10 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-10 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-10 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-10 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-10 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-10 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-10 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-10 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-10 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-10 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-10 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-10 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5449
2016-11-10 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.93% | 1381.4426
2016-11-10 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.97% | 1382.0144
2016-11-10 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.18% | 1384.9274
2016-11-10 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.35% | 1373.0044
2016-11-10 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-10 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.47% | 1365.9331
2016-11-10 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.75% | 1369.9774
2016-11-10 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-10 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-10 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-11 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-11 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-11 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-11 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-11 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-11 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-11 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-11 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-11 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-11 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-11 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-11 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-11 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-11 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-11 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-11 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-11 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-11 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-11 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-11 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-11 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-11 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-11 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-11 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-12 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-12 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-12 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-12 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-12 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-12 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-12 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-12 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-12 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-12 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-12 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-12 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-12 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-12 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-12 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.93% | 1605.2875
2016-11-12 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.97% | 1605.9519
2016-11-12 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-12 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-12 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-12 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-12 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-12 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-12 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-12 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.3% | 1594.7684
2016-11-13 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4542
2016-11-13 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-13 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.7% | 1584.5659
2016-11-13 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.57% | 1582.5128
2016-11-13 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.17% | 1592.4492
2016-11-13 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.38% | 1596.0975
2016-11-13 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.63% | 1454.9709
2016-11-13 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-13 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.81% | 1370.8729
2016-11-13 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.59% | 1367.608
2016-11-13 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-13 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-13 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-13 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5449
2016-11-13 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.93% | 1372.5872
2016-11-13 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.97% | 1382.0144
2016-11-13 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.18% | 1384.9274
2016-11-13 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.35% | 1373.0044
2016-11-13 18:00 | 1.25 | 3040 | 1240 | 1440 | 95.33% | 1372.7502
2016-11-13 19:00 | 1.25 | 3040 | 1240 | 1440 | 95.47% | 1374.7456
2016-11-13 20:00 | 1.25 | 3040 | 1240 | 1440 | 95.75% | 1378.816
2016-11-13 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.07% | 1360.2094
2016-11-13 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.29% | 1363.3335
2016-11-13 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.3% | 1449.9957
2016-11-14 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7101
2016-11-14 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.96% | 1444.8146
2016-11-14 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.7% | 1584.5659
2016-11-14 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.57% | 1582.5128
2016-11-14 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.17% | 1592.4492
2016-11-14 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.38% | 1596.0975
2016-11-14 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-14 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-14 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-14 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-14 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-14 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-14 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-14 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-14 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-14 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.97% | 1373.1553
2016-11-14 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.18% | 1376.0497
2016-11-14 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.35% | 1364.2031
2016-11-14 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-14 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.47% | 1365.9331
2016-11-14 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.75% | 1369.9774
2016-11-14 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.07% | 1360.2094
2016-11-14 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7198
2016-11-14 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.3% | 1594.7684
2016-11-15 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4542
2016-11-15 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-15 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.7% | 1584.5659
2016-11-15 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.57% | 1582.5128
2016-11-15 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.17% | 1592.4492
2016-11-15 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.38% | 1596.0975
2016-11-15 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.63% | 1454.9709
2016-11-15 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-15 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-15 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-15 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-15 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-15 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-15 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-15 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-15 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-15 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-15 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-15 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-15 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.47% | 1365.9331
2016-11-15 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.75% | 1369.9774
2016-11-15 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.07% | 1360.2094
2016-11-15 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7198
2016-11-15 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.3% | 1449.9957
2016-11-16 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7101
2016-11-16 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.96% | 1589.07
2016-11-16 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.7% | 1584.5659
2016-11-16 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 94.57% | 1582.5128
2016-11-16 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.17% | 1592.4492
2016-11-16 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.38% | 1451.2041
2016-11-16 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.63% | 1454.9709
2016-11-16 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-16 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-16 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-16 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-16 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-16 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-16 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-16 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-16 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-16 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-16 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-16 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-16 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-16 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-16 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-16 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-16 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-17 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-17 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-17 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-17 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-17 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-17 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-17 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-17 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-17 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-17 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-17 10:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6949
2016-11-17 11:00 | 2 | 4700 | 1240 | 1730 | 95.72% | 1655.9372
2016-11-17 12:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.563
2016-11-17 13:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.5529
2016-11-17 14:00 | 2 | 4700 | 1240 | 1730 | 95.93% | 1659.6498
2016-11-17 15:00 | 2 | 4700 | 1240 | 1730 | 95.97% | 1660.3367
2016-11-17 16:00 | 2 | 4700 | 1240 | 1730 | 96.18% | 1663.8364
2016-11-17 17:00 | 2 | 4700 | 1240 | 1730 | 95.35% | 1649.5122
2016-11-17 18:00 | 2 | 4700 | 1240 | 1730 | 95.33% | 1649.2069
2016-11-17 19:00 | 2 | 4700 | 1240 | 1730 | 95.47% | 1651.604
2016-11-17 20:00 | 2 | 4700 | 1240 | 1730 | 95.75% | 1656.4942
2016-11-17 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-17 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-17 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-18 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-18 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-18 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-18 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-18 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-18 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.38% | 1596.0975
2016-11-18 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.63% | 1454.9709
2016-11-18 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-18 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-18 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-18 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-18 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-18 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-18 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-18 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-18 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-18 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-18 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-18 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-18 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-18 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-18 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-18 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-18 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-19 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-19 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-19 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-19 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-19 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-19 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-19 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-19 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-19 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-19 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.59% | 1454.2652
2016-11-19 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-19 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-19 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-19 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-19 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-19 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-19 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.18% | 1609.3369
2016-11-19 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-19 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-19 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-19 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-19 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-19 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-19 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-20 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-20 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-20 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-20 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-20 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-20 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-20 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-20 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-20 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-20 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-20 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-20 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-20 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-20 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-20 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-20 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-20 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-20 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-20 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-20 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-20 20:00 | 2 | 4700 | 1240 | 1730 | 95.75% | 1656.4942
2016-11-20 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-20 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-20 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-21 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-21 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-21 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-21 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-21 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-21 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-21 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-21 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-21 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-21 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-21 10:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6949
2016-11-21 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-21 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-21 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-21 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-21 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-21 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-21 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-21 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-21 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-21 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-21 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-21 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-21 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.3% | 1594.7684
2016-11-22 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-22 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-22 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-22 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-22 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-22 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-22 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-22 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-22 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-22 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-22 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-22 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-22 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-22 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-22 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-22 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-22 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-22 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-22 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-22 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-22 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-22 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-22 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-22 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-23 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-23 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-23 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-23 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-23 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-23 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-23 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.63% | 1600.2403
2016-11-23 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.76% | 1456.9802
2016-11-23 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.81% | 1457.737
2016-11-23 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.59% | 1367.608
2016-11-23 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-23 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-23 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-23 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5449
2016-11-23 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.93% | 1372.5872
2016-11-23 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.97% | 1373.1553
2016-11-23 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.18% | 1376.0497
2016-11-23 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.35% | 1364.2031
2016-11-23 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.33% | 1363.9506
2016-11-23 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-23 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-23 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-23 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-23 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-24 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-24 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-24 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-24 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-24 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-24 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-24 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-24 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-24 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-24 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-24 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.05% | 1607.2656
2016-11-24 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.72% | 1601.6965
2016-11-24 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.4
2016-11-24 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.58% | 1599.3903
2016-11-24 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-24 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-24 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-24 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-24 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-24 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-24 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-24 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-24 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-24 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-25 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-25 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-25 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-25 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-25 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-25 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-25 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-25 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-25 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-25 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-25 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-25 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-25 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-25 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-25 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-25 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-25 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-25 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-25 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-25 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-25 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-25 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-25 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7198
2016-11-25 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.3% | 1449.9957
2016-11-26 | 1.4 | 3370 | 1240 | 1521.4286 | 95.29% | 1449.7101
2016-11-26 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.96% | 1444.8146
2016-11-26 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.7% | 1440.7195
2016-11-26 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 94.57% | 1438.8527
2016-11-26 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.17% | 1447.8871
2016-11-26 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.38% | 1364.7294
2016-11-26 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.63% | 1368.2716
2016-11-26 07:00 | 1.25 | 3040 | 1240 | 1440 | 95.76% | 1379.001
2016-11-26 08:00 | 1.25 | 3040 | 1240 | 1440 | 95.81% | 1379.7173
2016-11-26 09:00 | 1.25 | 3040 | 1240 | 1440 | 95.59% | 1376.4313
2016-11-26 10:00 | 1.25 | 3040 | 1240 | 1440 | 96.05% | 1383.1449
2016-11-26 11:00 | 1.25 | 3040 | 1240 | 1440 | 95.72% | 1378.3524
2016-11-26 12:00 | 1.25 | 3040 | 1240 | 1440 | 95.58% | 1376.3761
2016-11-26 13:00 | 1.25 | 3040 | 1240 | 1440 | 95.58% | 1376.3678
2016-11-26 14:00 | 1.25 | 3040 | 1240 | 1440 | 95.93% | 1381.4426
2016-11-26 15:00 | 1.25 | 3040 | 1240 | 1440 | 95.97% | 1382.0144
2016-11-26 16:00 | 1.25 | 3040 | 1240 | 1440 | 96.18% | 1384.9274
2016-11-26 17:00 | 1.25 | 3040 | 1240 | 1440 | 95.35% | 1373.0044
2016-11-26 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.33% | 1181.0781
2016-11-26 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.47% | 1182.7948
2016-11-26 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.75% | 1186.2969
2016-11-26 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 95.07% | 1177.8386
2016-11-26 22:00 | 1.25 | 3040 | 1240 | 1440 | 95.29% | 1372.1292
2016-11-26 23:00 | 1.25 | 3040 | 1240 | 1440 | 95.3% | 1372.3903
2016-11-27 | 1.25 | 3040 | 1240 | 1440 | 95.29% | 1372.1199
2016-11-27 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.96% | 1358.7206
2016-11-27 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.7% | 1354.8694
2016-11-27 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 94.57% | 1353.114
2016-11-27 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.17% | 1361.61
2016-11-27 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.38% | 1364.7294
2016-11-27 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.63% | 1368.2716
2016-11-27 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.76% | 1370.1612
2016-11-27 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.81% | 1370.8729
2016-11-27 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.59% | 1367.608
2016-11-27 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.05% | 1374.2786
2016-11-27 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.72% | 1369.5168
2016-11-27 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5532
2016-11-27 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.58% | 1367.5449
2016-11-27 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-27 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-27 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-27 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-27 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-27 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-27 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.75% | 1602.2352
2016-11-27 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.07% | 1590.8113
2016-11-27 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-27 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-28 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-28 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-28 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-28 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-28 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-28 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-28 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-28 07:00 | 2 | 4700 | 1240 | 1730 | 95.76% | 1656.7165
2016-11-28 08:00 | 2 | 4700 | 1240 | 1730 | 95.81% | 1657.577
2016-11-28 09:00 | 2 | 4700 | 1240 | 1730 | 95.59% | 1653.6293
2016-11-28 10:00 | 2 | 4700 | 1240 | 1730 | 96.05% | 1661.6949
2016-11-28 11:00 | 2 | 4700 | 1240 | 1730 | 95.72% | 1655.9372
2016-11-28 12:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.563
2016-11-28 13:00 | 2 | 4700 | 1240 | 1730 | 95.58% | 1653.5529
2016-11-28 14:00 | 2 | 4700 | 1240 | 1730 | 95.93% | 1659.6498
2016-11-28 15:00 | 2 | 4700 | 1240 | 1730 | 95.97% | 1660.3367
2016-11-28 16:00 | 2 | 4700 | 1240 | 1730 | 96.18% | 1663.8364
2016-11-28 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.35% | 1595.4819
2016-11-28 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.33% | 1595.1866
2016-11-28 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.47% | 1597.5052
2016-11-28 20:00 | 2 | 4700 | 1240 | 1730 | 95.75% | 1656.4942
2016-11-28 21:00 | 2 | 4700 | 1240 | 1730 | 95.07% | 1644.6834
2016-11-28 22:00 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4607
2016-11-28 23:00 | 2 | 4700 | 1240 | 1730 | 95.3% | 1648.7745
2016-11-29 | 2 | 4700 | 1240 | 1730 | 95.29% | 1648.4497
2016-11-29 01:00 | 2 | 4700 | 1240 | 1730 | 94.96% | 1642.8831
2016-11-29 02:00 | 2 | 4700 | 1240 | 1730 | 94.7% | 1638.2265
2016-11-29 03:00 | 2 | 4700 | 1240 | 1730 | 94.57% | 1636.1039
2016-11-29 04:00 | 2 | 4700 | 1240 | 1730 | 95.17% | 1646.3768
2016-11-29 05:00 | 2 | 4700 | 1240 | 1730 | 95.38% | 1650.1486
2016-11-29 06:00 | 2 | 4700 | 1240 | 1730 | 95.63% | 1654.4317
2016-11-29 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.76% | 1602.4502
2016-11-29 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.81% | 1603.2826
2016-11-29 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.59% | 1599.4642
2016-11-29 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.05% | 1461.3585
2016-11-29 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.72% | 1456.2949
2016-11-29 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.2069
2016-11-29 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.58% | 1454.1981
2016-11-29 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.93% | 1459.5599
2016-11-29 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.97% | 1460.164
2016-11-29 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.18% | 1463.2418
2016-11-29 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.35% | 1450.6445
2016-11-29 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.33% | 1450.376
2016-11-29 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.47% | 1452.4841
2016-11-29 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.75% | 1456.7847
2016-11-29 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.07% | 1446.3978
2016-11-29 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.29% | 1594.4649
2016-11-29 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.3% | 1594.7684
2016-11-30 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-11-30 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-11-30 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-11-30 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-11-30 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-11-30 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-11-30 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.73% | 1652.0802
2016-11-30 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.83% | 1653.7266
2016-11-30 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.39% | 1646.3157
2016-11-30 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.1% | 1641.5663
2016-11-30 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-11-30 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-11-30 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-11-30 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-11-30 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-11-30 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-11-30 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-11-30 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-11-30 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-11-30 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-11-30 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-11-30 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-11-30 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1348
2016-11-30 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0783
2016-12-01 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.9109
2016-12-01 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-01 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-01 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-01 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-01 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-01 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-01 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-01 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-01 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-01 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-01 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-01 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-01 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-01 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-01 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-01 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-01 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-01 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-01 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-01 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-01 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-01 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.49% | 1648.0311
2016-12-01 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-02 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0739
2016-12-02 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3614
2016-12-02 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.54% | 1598.7424
2016-12-02 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.89% | 1604.5441
2016-12-02 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.88% | 1621.0682
2016-12-02 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-02 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-02 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-02 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-02 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-02 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-02 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-02 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-02 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-02 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-02 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-02 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-02 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-02 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-02 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-02 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-02 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.43% | 1408.3014
2016-12-02 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-02 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-03 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-03 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-03 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-03 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-03 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-03 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-03 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-03 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-03 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-03 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-03 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-03 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-03 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-03 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-03 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-03 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-03 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-03 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-03 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.53% | 1648.8119
2016-12-03 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.64% | 1650.6225
2016-12-03 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.62% | 1650.2695
2016-12-03 21:00 | 2 | 4700 | 1240 | 1730 | 98.43% | 1702.8332
2016-12-03 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-03 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635
2016-12-04 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-04 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-04 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-04 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-04 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-04 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-04 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-04 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-04 08:00 | 2 | 4700 | 1240 | 1730 | 98.39% | 1702.0675
2016-12-04 09:00 | 2 | 4700 | 1240 | 1730 | 98.1% | 1697.1572
2016-12-04 10:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5076
2016-12-04 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.45% | 1647.4378
2016-12-04 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.42% | 1646.9148
2016-12-04 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.61% | 1650.0919
2016-12-04 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.67% | 1651.1294
2016-12-04 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.74% | 1652.3151
2016-12-04 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-04 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-04 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-04 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-04 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-04 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-04 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-04 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-05 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-05 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-05 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-05 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-05 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-05 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-05 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-05 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-05 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-05 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-05 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-05 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-05 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-05 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-05 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-05 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-05 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-05 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-05 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.53% | 1220.7823
2016-12-05 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1229
2016-12-05 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-12-05 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-12-05 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1348
2016-12-05 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0783
2016-12-06 | 1.25 | 3040 | 1240 | 1440 | 97.77% | 1407.9361
2016-12-06 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2273
2016-12-06 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.54% | 1375.8102
2016-12-06 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.89% | 1380.8029
2016-12-06 04:00 | 1.25 | 3040 | 1240 | 1440 | 96.88% | 1395.0228
2016-12-06 05:00 | 1.25 | 3040 | 1240 | 1440 | 98.3% | 1415.4767
2016-12-06 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.73% | 1223.2022
2016-12-06 07:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.83% | 1224.4212
2016-12-06 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7498
2016-12-06 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.6626
2016-12-06 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1161
2016-12-06 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.45% | 1417.7154
2016-12-06 12:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2653
2016-12-06 13:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9994
2016-12-06 14:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8923
2016-12-06 15:00 | 1.25 | 3040 | 1240 | 1440 | 98.74% | 1421.9126
2016-12-06 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-06 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-06 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-06 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-06 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-12-06 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-12-06 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1348
2016-12-06 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-07 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-07 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-07 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-07 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-07 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-07 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-07 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-07 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-07 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-07 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-07 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-07 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-07 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-07 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-07 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-07 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-07 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-07 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-07 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-07 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-07 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-07 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-07 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-07 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-08 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-08 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-08 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-08 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-08 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-08 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-08 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-08 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-08 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-08 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-08 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-08 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-08 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-08 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-08 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-08 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-08 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-08 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-08 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-08 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-08 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-08 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-08 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-08 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-09 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0739
2016-12-09 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3614
2016-12-09 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.54% | 1598.7424
2016-12-09 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.89% | 1604.5441
2016-12-09 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.88% | 1621.0682
2016-12-09 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.3% | 1644.8364
2016-12-09 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-09 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-09 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-09 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-09 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-09 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-09 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-09 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-09 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-09 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-09 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-09 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-09 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-09 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-09 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-09 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-09 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-09 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-10 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-10 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-10 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-10 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-10 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-10 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-10 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.73% | 1421.7105
2016-12-10 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.83% | 1423.1273
2016-12-10 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7498
2016-12-10 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-10 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-10 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-10 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-10 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-10 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-10 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-10 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-10 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-10 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-10 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-10 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.62% | 1650.2695
2016-12-10 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.43% | 1647.0564
2016-12-10 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-10 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635
2016-12-11 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-11 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-11 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-11 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-11 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-11 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-11 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-11 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-11 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.39% | 1646.3157
2016-12-11 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.1% | 1641.5663
2016-12-11 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-11 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-11 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-11 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-11 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-11 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-11 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-11 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-11 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-11 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-11 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-11 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-11 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-11 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-12 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-12 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-12 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-12 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-12 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-12 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-12 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-12 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-12 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-12 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-12 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-12 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-12 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-12 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-12 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-12 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-12 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-12 17:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.75% | 1223.4077
2016-12-12 18:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.53% | 1220.7823
2016-12-12 19:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.64% | 1222.1229
2016-12-12 20:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.62% | 1221.8615
2016-12-12 21:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.43% | 1219.4826
2016-12-12 22:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.49% | 1220.2042
2016-12-12 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1627
2016-12-13 | 1.25 | 3040 | 1240 | 1440 | 97.77% | 1407.9361
2016-12-13 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3605
2016-12-13 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.54% | 1366.9909
2016-12-13 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.89% | 1371.9516
2016-12-13 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.88% | 1386.0804
2016-12-13 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-13 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.73% | 1421.7105
2016-12-13 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.83% | 1423.1273
2016-12-13 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7498
2016-12-13 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-13 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-13 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-13 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-13 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-13 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-13 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-13 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-13 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-13 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-13 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-13 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-13 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-13 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-13 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-14 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-14 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3614
2016-12-14 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-14 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-14 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-14 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-14 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-14 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-14 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-14 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.1% | 1641.5663
2016-12-14 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7414
2016-12-14 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.45% | 1647.4378
2016-12-14 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.42% | 1646.9148
2016-12-14 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.61% | 1650.0919
2016-12-14 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.67% | 1651.1294
2016-12-14 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.74% | 1652.3151
2016-12-14 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.7% | 1651.5771
2016-12-14 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.75% | 1652.3578
2016-12-14 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.53% | 1648.8119
2016-12-14 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.64% | 1650.6225
2016-12-14 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.62% | 1650.2695
2016-12-14 21:00 | 2 | 4700 | 1240 | 1730 | 98.43% | 1702.8332
2016-12-14 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-14 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635
2016-12-15 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-15 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-15 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-15 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-15 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-15 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-15 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-15 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-15 08:00 | 2 | 4700 | 1240 | 1730 | 98.39% | 1702.0675
2016-12-15 09:00 | 2 | 4700 | 1240 | 1730 | 98.1% | 1697.1572
2016-12-15 10:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5076
2016-12-15 11:00 | 2 | 4700 | 1240 | 1730 | 98.45% | 1703.2275
2016-12-15 12:00 | 2 | 4700 | 1240 | 1730 | 98.42% | 1702.6868
2016-12-15 13:00 | 2 | 4700 | 1240 | 1730 | 98.61% | 1705.9715
2016-12-15 14:00 | 2 | 4700 | 1240 | 1730 | 98.67% | 1707.0442
2016-12-15 15:00 | 2 | 4700 | 1240 | 1730 | 98.74% | 1708.27
2016-12-15 16:00 | 2 | 4700 | 1240 | 1730 | 98.7% | 1707.507
2016-12-15 17:00 | 2 | 4700 | 1240 | 1730 | 98.75% | 1708.3141
2016-12-15 18:00 | 2 | 4700 | 1240 | 1730 | 98.53% | 1704.6481
2016-12-15 19:00 | 2 | 4700 | 1240 | 1730 | 98.64% | 1706.52
2016-12-15 20:00 | 2 | 4700 | 1240 | 1730 | 98.62% | 1706.1551
2016-12-15 21:00 | 2 | 4700 | 1240 | 1730 | 98.43% | 1702.8332
2016-12-15 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-15 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635
2016-12-16 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-16 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-16 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-16 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-16 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-16 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-16 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-16 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.83% | 1653.7266
2016-12-16 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.39% | 1646.3157
2016-12-16 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-16 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-16 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-16 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-16 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-16 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-16 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-16 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-16 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-16 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-16 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-16 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-16 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-16 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-16 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-17 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-17 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-17 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-17 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-17 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-17 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-17 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.73% | 1421.7105
2016-12-17 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.83% | 1423.1273
2016-12-17 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7498
2016-12-17 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.6626
2016-12-17 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1161
2016-12-17 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.45% | 1417.7154
2016-12-17 12:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2653
2016-12-17 13:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9994
2016-12-17 14:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8923
2016-12-17 15:00 | 1.25 | 3040 | 1240 | 1440 | 98.74% | 1421.9126
2016-12-17 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-17 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-17 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-17 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-17 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-12-17 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-12-17 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1348
2016-12-17 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0783
2016-12-18 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.9109
2016-12-18 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3605
2016-12-18 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.54% | 1366.9909
2016-12-18 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.89% | 1371.9516
2016-12-18 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.88% | 1386.0804
2016-12-18 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-18 06:00 | 1.25 | 3040 | 1240 | 1440 | 98.73% | 1421.7105
2016-12-18 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.83% | 1423.1273
2016-12-18 08:00 | 1.25 | 3040 | 1240 | 1440 | 98.39% | 1416.7498
2016-12-18 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.6626
2016-12-18 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1161
2016-12-18 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.45% | 1417.7154
2016-12-18 12:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2653
2016-12-18 13:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9994
2016-12-18 14:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8923
2016-12-18 15:00 | 1.25 | 3040 | 1240 | 1440 | 98.74% | 1421.9126
2016-12-18 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-18 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-18 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-18 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-18 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-18 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.43% | 1408.3014
2016-12-18 22:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.49% | 1409.1348
2016-12-18 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0783
2016-12-19 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.9109
2016-12-19 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3605
2016-12-19 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.54% | 1366.9909
2016-12-19 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.89% | 1371.9516
2016-12-19 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.88% | 1386.0804
2016-12-19 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-19 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-19 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-19 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-19 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-19 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-19 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-19 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-19 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-19 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-19 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-19 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-19 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-19 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-19 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-19 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-19 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-19 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-19 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-20 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-20 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-20 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-20 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-20 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-20 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.3% | 1644.8364
2016-12-20 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.73% | 1652.0802
2016-12-20 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.83% | 1653.7266
2016-12-20 08:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.39% | 1646.3157
2016-12-20 09:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.1% | 1641.5663
2016-12-20 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7414
2016-12-20 11:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.45% | 1647.4378
2016-12-20 12:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.42% | 1646.9148
2016-12-20 13:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.61% | 1650.0919
2016-12-20 14:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.67% | 1651.1294
2016-12-20 15:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.74% | 1652.3151
2016-12-20 16:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.7% | 1651.5771
2016-12-20 17:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.75% | 1652.3578
2016-12-20 18:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.53% | 1648.8119
2016-12-20 19:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.64% | 1650.6225
2016-12-20 20:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.62% | 1650.2695
2016-12-20 21:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.43% | 1647.0564
2016-12-20 22:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.49% | 1648.0311
2016-12-20 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-21 | 2 | 4700 | 1240 | 1730 | 97.77% | 1691.4788
2016-12-21 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-21 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-21 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-21 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-21 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-21 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-21 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-21 08:00 | 2 | 4700 | 1240 | 1730 | 98.39% | 1702.0675
2016-12-21 09:00 | 2 | 4700 | 1240 | 1730 | 98.1% | 1697.1572
2016-12-21 10:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7414
2016-12-21 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-21 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-21 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-21 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-21 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-21 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-21 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-21 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-21 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-21 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-21 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.43% | 1408.3014
2016-12-21 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-21 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-22 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0739
2016-12-22 01:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.06% | 1607.3614
2016-12-22 02:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.54% | 1598.7424
2016-12-22 03:00 | 1.5 | 3750 | 1240 | 1673.3333 | 95.89% | 1604.5441
2016-12-22 04:00 | 1.5 | 3750 | 1240 | 1673.3333 | 96.88% | 1621.0682
2016-12-22 05:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.3% | 1644.8364
2016-12-22 06:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.73% | 1652.0802
2016-12-22 07:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.83% | 1653.7266
2016-12-22 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-22 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-22 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-22 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-22 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-22 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-22 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-22 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-22 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-22 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-22 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-22 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-22 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-22 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-22 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-22 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-23 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-23 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-23 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-23 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-23 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-23 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-23 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-23 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-23 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-23 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-23 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-23 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-23 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-23 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-23 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-23 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-23 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-23 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-23 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-23 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-23 20:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.62% | 1500.4584
2016-12-23 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-23 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-23 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-24 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-24 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-24 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-24 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-24 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-24 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-24 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-24 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-24 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-24 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-24 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-24 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-24 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-24 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-24 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-24 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-24 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-24 17:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.75% | 1502.3572
2016-12-24 18:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.53% | 1499.1332
2016-12-24 19:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.64% | 1500.7794
2016-12-24 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-24 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.43% | 1408.3014
2016-12-24 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-24 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-25 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-25 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-25 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-25 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-25 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-25 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-25 06:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.73% | 1502.1048
2016-12-25 07:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.83% | 1503.6017
2016-12-25 08:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.39% | 1496.8636
2016-12-25 09:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.1% | 1492.5453
2016-12-25 10:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2507
2016-12-25 11:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.45% | 1497.8838
2016-12-25 12:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.42% | 1497.4083
2016-12-25 13:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.61% | 1500.297
2016-12-25 14:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.67% | 1501.2403
2016-12-25 15:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.74% | 1502.3183
2016-12-25 16:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.7% | 1501.6474
2016-12-25 17:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.75% | 1412.8343
2016-12-25 18:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.53% | 1409.8024
2016-12-25 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-25 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-12-25 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-12-25 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2259
2016-12-25 23:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1627
2016-12-26 | 1.25 | 3040 | 1240 | 1440 | 97.77% | 1407.9361
2016-12-26 01:00 | 1.25 | 3040 | 1240 | 1440 | 96.06% | 1383.2273
2016-12-26 02:00 | 1.25 | 3040 | 1240 | 1440 | 95.54% | 1375.8102
2016-12-26 03:00 | 1.25 | 3040 | 1240 | 1440 | 95.89% | 1380.8029
2016-12-26 04:00 | 1.13 | 2640 | 1240 | 1238.9381 | 96.88% | 1200.2409
2016-12-26 05:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.3% | 1217.8389
2016-12-26 06:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.73% | 1223.2022
2016-12-26 07:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.83% | 1281.1074
2016-12-26 08:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.39% | 1275.3663
2016-12-26 09:00 | 1.08 | 2640 | 1240 | 1296.2963 | 98.1% | 1271.687
2016-12-26 10:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.41% | 1219.2494
2016-12-26 11:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.45% | 1219.765
2016-12-26 12:00 | 1.13 | 2640 | 1240 | 1238.9381 | 98.42% | 1219.3777
2016-12-26 13:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9994
2016-12-26 14:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8923
2016-12-26 15:00 | 1.25 | 3040 | 1240 | 1440 | 98.74% | 1421.9126
2016-12-26 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-26 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-26 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-26 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-26 20:00 | 1.25 | 3040 | 1240 | 1440 | 98.62% | 1420.1522
2016-12-26 21:00 | 1.25 | 3040 | 1240 | 1440 | 98.43% | 1417.3872
2016-12-26 22:00 | 1.25 | 3040 | 1240 | 1440 | 98.49% | 1418.2259
2016-12-26 23:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0783
2016-12-27 | 1.3 | 3100 | 1240 | 1430.7692 | 97.77% | 1398.9109
2016-12-27 01:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.06% | 1374.3605
2016-12-27 02:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.54% | 1366.9909
2016-12-27 03:00 | 1.3 | 3100 | 1240 | 1430.7692 | 95.89% | 1371.9516
2016-12-27 04:00 | 1.3 | 3100 | 1240 | 1430.7692 | 96.88% | 1386.0804
2016-12-27 05:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.3% | 1406.4032
2016-12-27 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-27 07:00 | 1.25 | 3040 | 1240 | 1440 | 98.83% | 1423.1273
2016-12-27 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-27 09:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.1% | 1403.6071
2016-12-27 10:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.41% | 1408.0321
2016-12-27 11:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.45% | 1408.6275
2016-12-27 12:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.42% | 1408.1803
2016-12-27 13:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.61% | 1410.8969
2016-12-27 14:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.67% | 1411.784
2016-12-27 15:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.74% | 1412.7977
2016-12-27 16:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.7% | 1412.1668
2016-12-27 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-27 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-27 19:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.64% | 1411.3505
2016-12-27 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-27 21:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.43% | 1497.5371
2016-12-27 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-27 23:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.41% | 1497.2998
2016-12-28 | 1.4 | 3370 | 1240 | 1521.4286 | 97.77% | 1487.5516
2016-12-28 01:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.06% | 1461.4455
2016-12-28 02:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.54% | 1453.609
2016-12-28 03:00 | 1.4 | 3370 | 1240 | 1521.4286 | 95.89% | 1458.884
2016-12-28 04:00 | 1.4 | 3370 | 1240 | 1521.4286 | 96.88% | 1473.908
2016-12-28 05:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.3% | 1495.5186
2016-12-28 06:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.73% | 1412.5969
2016-12-28 07:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.83% | 1414.0047
2016-12-28 08:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.39% | 1407.6681
2016-12-28 09:00 | 1.25 | 3040 | 1240 | 1440 | 98.1% | 1412.6626
2016-12-28 10:00 | 1.25 | 3040 | 1240 | 1440 | 98.41% | 1417.1161
2016-12-28 11:00 | 1.25 | 3040 | 1240 | 1440 | 98.45% | 1417.7154
2016-12-28 12:00 | 1.25 | 3040 | 1240 | 1440 | 98.42% | 1417.2653
2016-12-28 13:00 | 1.25 | 3040 | 1240 | 1440 | 98.61% | 1419.9994
2016-12-28 14:00 | 1.25 | 3040 | 1240 | 1440 | 98.67% | 1420.8923
2016-12-28 15:00 | 1.25 | 3040 | 1240 | 1440 | 98.74% | 1421.9126
2016-12-28 16:00 | 1.25 | 3040 | 1240 | 1440 | 98.7% | 1421.2775
2016-12-28 17:00 | 1.25 | 3040 | 1240 | 1440 | 98.75% | 1421.9493
2016-12-28 18:00 | 1.25 | 3040 | 1240 | 1440 | 98.53% | 1418.8979
2016-12-28 19:00 | 1.25 | 3040 | 1240 | 1440 | 98.64% | 1420.456
2016-12-28 20:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.62% | 1411.0487
2016-12-28 21:00 | 1.3 | 3100 | 1240 | 1430.7692 | 98.43% | 1408.3014
2016-12-28 22:00 | 1.4 | 3370 | 1240 | 1521.4286 | 98.49% | 1498.4232
2016-12-28 23:00 | 1.5 | 3750 | 1240 | 1673.3333 | 98.41% | 1646.7955
2016-12-29 | 1.5 | 3750 | 1240 | 1673.3333 | 97.77% | 1636.0739
2016-12-29 01:00 | 2 | 4700 | 1240 | 1730 | 96.06% | 1661.7939
2016-12-29 02:00 | 2 | 4700 | 1240 | 1730 | 95.54% | 1652.8831
2016-12-29 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-29 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-29 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-29 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-29 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-29 08:00 | 2 | 4700 | 1240 | 1730 | 98.39% | 1702.0675
2016-12-29 09:00 | 2 | 4700 | 1240 | 1730 | 98.1% | 1697.1572
2016-12-29 10:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5076
2016-12-29 11:00 | 2 | 4700 | 1240 | 1730 | 98.45% | 1703.2275
2016-12-29 12:00 | 2 | 4700 | 1240 | 1730 | 98.42% | 1702.6868
2016-12-29 13:00 | 2 | 4700 | 1240 | 1730 | 98.61% | 1705.9715
2016-12-29 14:00 | 2 | 4700 | 1240 | 1730 | 98.67% | 1707.0442
2016-12-29 15:00 | 2 | 4700 | 1240 | 1730 | 98.74% | 1708.27
2016-12-29 16:00 | 2 | 4700 | 1240 | 1730 | 98.7% | 1707.507
2016-12-29 17:00 | 2 | 4700 | 1240 | 1730 | 98.75% | 1708.3141
2016-12-29 18:00 | 2 | 4700 | 1240 | 1730 | 98.53% | 1704.6481
2016-12-29 19:00 | 2 | 4700 | 1240 | 1730 | 98.64% | 1706.52
2016-12-29 20:00 | 2 | 4700 | 1240 | 1730 | 98.62% | 1706.1551
2016-12-29 21:00 | 2 | 4700 | 1240 | 1730 | 98.43% | 1702.8332
2016-12-29 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-29 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635
2016-12-30 | 2.2 | 5200 | 1240 | 1800 | 97.77% | 1759.9202
2016-12-30 01:00 | 2.2 | 5200 | 1240 | 1800 | 96.06% | 1729.0342
2016-12-30 02:00 | 2.2 | 5200 | 1240 | 1800 | 95.54% | 1719.7628
2016-12-30 03:00 | 2 | 4700 | 1240 | 1730 | 95.89% | 1658.8812
2016-12-30 04:00 | 2 | 4700 | 1240 | 1730 | 96.88% | 1675.9649
2016-12-30 05:00 | 2 | 4700 | 1240 | 1730 | 98.3% | 1700.538
2016-12-30 06:00 | 2 | 4700 | 1240 | 1730 | 98.73% | 1708.0271
2016-12-30 07:00 | 2 | 4700 | 1240 | 1730 | 98.83% | 1709.7293
2016-12-30 08:00 | 2 | 4700 | 1240 | 1730 | 98.39% | 1702.0675
2016-12-30 09:00 | 2 | 4700 | 1240 | 1730 | 98.1% | 1697.1572
2016-12-30 10:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5076
2016-12-30 11:00 | 2 | 4700 | 1240 | 1730 | 98.45% | 1703.2275
2016-12-30 12:00 | 2 | 4700 | 1240 | 1730 | 98.42% | 1702.6868
2016-12-30 13:00 | 2 | 4700 | 1240 | 1730 | 98.61% | 1705.9715
2016-12-30 14:00 | 2 | 4700 | 1240 | 1730 | 98.67% | 1707.0442
2016-12-30 15:00 | 2 | 4700 | 1240 | 1730 | 98.74% | 1708.27
2016-12-30 16:00 | 2 | 4700 | 1240 | 1730 | 98.7% | 1707.507
2016-12-30 17:00 | 2 | 4700 | 1240 | 1730 | 98.75% | 1708.3141
2016-12-30 18:00 | 2 | 4700 | 1240 | 1730 | 98.53% | 1704.6481
2016-12-30 19:00 | 2 | 4700 | 1240 | 1730 | 98.64% | 1706.52
2016-12-30 20:00 | 2 | 4700 | 1240 | 1730 | 98.62% | 1706.1551
2016-12-30 21:00 | 2 | 4700 | 1240 | 1730 | 98.43% | 1702.8332
2016-12-30 22:00 | 2 | 4700 | 1240 | 1730 | 98.49% | 1703.8409
2016-12-30 23:00 | 2 | 4700 | 1240 | 1730 | 98.41% | 1702.5635

## Current_FAS_2016_Reg
Reg Requirement in Plexos
| 2016-01-01 |  |  | 2016-02-01 |  |  | 2016-03-01 |  |  | 2016-04-01 |  |  | 2016-05-01 |  |  | 2016-06-01 |  |  | 2016-07-01 |  |  | 2016-08-01 |  |  | 2016-09-01 |  |  | 2016-10-01 |  |  | 2016-11-01 |  |  | 2016-12-01
Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements |  | Hour Ending | Regulation Service Requirements
| Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down |  | Up | Down
1 | 351 | 398 | 1 | 374 | 357 | 1 | 455 | 484 | 1 | 497 | 866 | 1 | 442 | 830 | 1 | 462 | 956 | 1 | 589 | 862 | 1 | 647 | 870 | 1 | 746 | 927 | 1 | 677 | 938 | 1 | 624 | 820 | 1 | 350 | 411
2 | 351 | 351 | 2 | 337 | 337 | 2 | 307 | 405 | 2 | 297 | 676 | 2 | 534 | 584 | 2 | 378 | 700 | 2 | 364 | 743 | 2 | 374 | 734 | 2 | 332 | 571 | 2 | 302 | 586 | 2 | 312 | 470 | 2 | 336 | 365
3 | 369 | 351 | 3 | 339 | 337 | 3 | 307 | 370 | 3 | 320 | 388 | 3 | 321 | 468 | 3 | 348 | 482 | 3 | 364 | 533 | 3 | 374 | 508 | 3 | 332 | 443 | 3 | 391 | 352 | 3 | 401 | 333 | 3 | 336 | 336
4 | 453 | 351 | 4 | 399 | 337 | 4 | 351 | 356 | 4 | 348 | 337 | 4 | 339 | 420 | 4 | 363 | 478 | 4 | 364 | 470 | 4 | 394 | 481 | 4 | 377 | 341 | 4 | 305 | 329 | 4 | 346 | 312 | 4 | 398 | 336
5 | 645 | 351 | 5 | 620 | 337 | 5 | 563 | 307 | 5 | 366 | 297 | 5 | 366 | 334 | 5 | 393 | 455 | 5 | 435 | 375 | 5 | 374 | 439 | 5 | 397 | 332 | 5 | 302 | 313 | 5 | 389 | 344 | 5 | 651 | 336
6 | 847 | 351 | 6 | 769 | 337 | 6 | 763 | 307 | 6 | 569 | 297 | 6 | 493 | 321 | 6 | 498 | 348 | 6 | 441 | 376 | 6 | 560 | 374 | 6 | 537 | 374 | 6 | 545 | 302 | 6 | 562 | 346 | 6 | 832 | 336
7 | 586 | 361 | 7 | 578 | 367 | 7 | 505 | 373 | 7 | 809 | 297 | 7 | 642 | 321 | 7 | 542 | 348 | 7 | 537 | 364 | 7 | 641 | 374 | 7 | 668 | 332 | 7 | 695 | 302 | 7 | 726 | 315 | 7 | 523 | 339
8 | 510 | 521 | 8 | 408 | 545 | 8 | 372 | 477 | 8 | 532 | 358 | 8 | 490 | 363 | 8 | 454 | 369 | 8 | 492 | 367 | 8 | 549 | 429 | 8 | 462 | 422 | 8 | 497 | 368 | 8 | 469 | 354 | 8 | 389 | 529
9 | 351 | 590 | 9 | 378 | 555 | 9 | 470 | 503 | 9 | 432 | 476 | 9 | 568 | 329 | 9 | 629 | 354 | 9 | 673 | 364 | 9 | 615 | 412 | 9 | 433 | 405 | 9 | 333 | 393 | 9 | 442 | 425 | 9 | 336 | 609
10 | 387 | 541 | 10 | 404 | 486 | 10 | 452 | 485 | 10 | 470 | 365 | 10 | 530 | 321 | 10 | 667 | 357 | 10 | 704 | 364 | 10 | 810 | 374 | 10 | 562 | 348 | 10 | 560 | 325 | 10 | 446 | 394 | 10 | 436 | 467
11 | 488 | 565 | 11 | 364 | 474 | 11 | 433 | 492 | 11 | 432 | 441 | 11 | 592 | 321 | 11 | 701 | 348 | 11 | 784 | 364 | 11 | 766 | 374 | 11 | 627 | 332 | 11 | 595 | 302 | 11 | 528 | 419 | 11 | 399 | 461
12 | 391 | 487 | 12 | 337 | 478 | 12 | 383 | 405 | 12 | 472 | 408 | 12 | 519 | 482 | 12 | 643 | 348 | 12 | 663 | 364 | 12 | 747 | 374 | 12 | 626 | 332 | 12 | 538 | 302 | 12 | 532 | 420 | 12 | 348 | 444
13 | 376 | 462 | 13 | 350 | 427 | 13 | 347 | 380 | 13 | 456 | 454 | 13 | 601 | 363 | 13 | 612 | 348 | 13 | 657 | 409 | 13 | 766 | 374 | 13 | 587 | 332 | 13 | 497 | 358 | 13 | 379 | 440 | 13 | 427 | 393
14 | 351 | 481 | 14 | 339 | 428 | 14 | 413 | 374 | 14 | 439 | 381 | 14 | 617 | 321 | 14 | 687 | 348 | 14 | 564 | 438 | 14 | 733 | 374 | 14 | 587 | 371 | 14 | 473 | 408 | 14 | 429 | 493 | 14 | 336 | 447
15 | 351 | 449 | 15 | 337 | 433 | 15 | 326 | 348 | 15 | 450 | 362 | 15 | 614 | 321 | 15 | 526 | 364 | 15 | 497 | 401 | 15 | 561 | 374 | 15 | 476 | 332 | 15 | 534 | 414 | 15 | 366 | 464 | 15 | 336 | 377
16 | 512 | 373 | 16 | 354 | 373 | 16 | 366 | 378 | 16 | 435 | 318 | 16 | 511 | 367 | 16 | 457 | 410 | 16 | 451 | 451 | 16 | 457 | 484 | 16 | 512 | 397 | 16 | 521 | 302 | 16 | 335 | 446 | 16 | 420 | 351
17 | 633 | 351 | 17 | 437 | 340 | 17 | 396 | 475 | 17 | 386 | 347 | 17 | 500 | 321 | 17 | 537 | 380 | 17 | 471 | 408 | 17 | 498 | 407 | 17 | 382 | 394 | 17 | 394 | 339 | 17 | 418 | 324 | 17 | 656 | 336
18 | 619 | 351 | 18 | 574 | 337 | 18 | 598 | 307 | 18 | 329 | 335 | 18 | 384 | 415 | 18 | 506 | 470 | 18 | 465 | 489 | 18 | 386 | 513 | 18 | 342 | 469 | 18 | 439 | 378 | 18 | 638 | 331 | 18 | 526 | 336
19 | 561 | 351 | 19 | 690 | 337 | 19 | 723 | 307 | 19 | 426 | 387 | 19 | 321 | 537 | 19 | 348 | 515 | 19 | 364 | 588 | 19 | 374 | 617 | 19 | 332 | 493 | 19 | 524 | 319 | 19 | 524 | 384 | 19 | 401 | 344
20 | 351 | 448 | 20 | 381 | 481 | 20 | 518 | 495 | 20 | 539 | 337 | 20 | 570 | 565 | 20 | 348 | 585 | 20 | 374 | 532 | 20 | 374 | 578 | 20 | 332 | 471 | 20 | 453 | 468 | 20 | 385 | 420 | 20 | 336 | 480
21 | 351 | 524 | 21 | 337 | 539 | 21 | 322 | 520 | 21 | 549 | 345 | 21 | 589 | 549 | 21 | 348 | 627 | 21 | 364 | 525 | 21 | 374 | 562 | 21 | 413 | 512 | 21 | 302 | 525 | 21 | 429 | 446 | 21 | 336 | 457
22 | 351 | 645 | 22 | 337 | 594 | 22 | 307 | 596 | 22 | 307 | 550 | 22 | 423 | 587 | 22 | 360 | 492 | 22 | 416 | 513 | 22 | 374 | 656 | 22 | 332 | 683 | 22 | 302 | 577 | 22 | 326 | 526 | 22 | 336 | 535
23 | 351 | 576 | 23 | 337 | 633 | 23 | 307 | 602 | 23 | 297 | 702 | 23 | 321 | 772 | 23 | 348 | 744 | 23 | 364 | 821 | 23 | 374 | 751 | 23 | 332 | 708 | 23 | 302 | 711 | 23 | 312 | 573 | 23 | 336 | 633
24 | 471 | 754 | 24 | 457 | 803 | 24 | 511 | 822 | 24 | 297 | 721 | 24 | 321 | 752 | 24 | 348 | 757 | 24 | 364 | 858 | 24 | 374 | 780 | 24 | 332 | 648 | 24 | 302 | 640 | 24 | 312 | 537 | 24 | 472 | 698
Total | 11007 | 10983 | Total | 10237 | 10672 | Total | 10495 | 10568 | Total | 10454 | 10445 | Total | 11608 | 10964 | Total | 11503 | 11583 | Total | 11761 | 11979 | Total | 12496 | 12213 | Total | 11058 | 10969 | Total | 10783 | 10251 | Total | 10630 | 10336 | Total | 10252 | 10356

## FAS_2016_CRS
CRS Requirement in Plexos
| Load, MW | Renewables, MW | Inertia, MWs | B-point Frequency, Hz | CRS Req., MW
2016-01-01 | 40904 | 6028.6343 | 198043.0537 | 59.77 | 818.08
2016-01-01 01:00 | 40991 | 6207.5556 | 194570.7637 | 59.77 | 819.82
2016-01-01 02:00 | 41069 | 6362.8019 | 194383.5637 | 59.77 | 821.38
2016-01-01 03:00 | 41298 | 6283.4295 | 194383.5637 | 59.77 | 825.96
2016-01-01 04:00 | 42055 | 6002.8729 | 194383.5637 | 59.77 | 841.1
2016-01-01 05:00 | 43380 | 5719.0153 | 195625.2937 | 59.77 | 867.6
2016-01-01 06:00 | 44746 | 5985.656 | 195625.2937 | 59.77 | 894.92
2016-01-01 07:00 | 45293 | 6144.0206 | 197645.9237 | 59.77 | 905.86
2016-01-01 08:00 | 45366 | 6536.0016 | 195252.6937 | 59.77 | 907.32
2016-01-01 09:00 | 45026 | 7289.4764 | 194516.6937 | 59.77 | 900.52
2016-01-01 10:00 | 44064 | 5952.8562 | 194516.6937 | 59.77 | 881.28
2016-01-01 11:00 | 42563 | 4470.5093 | 194516.6937 | 59.77 | 851.26
2016-01-01 12:00 | 40840 | 3759.9868 | 194021.6937 | 59.77 | 816.8
2016-01-01 13:00 | 39083 | 2669.7386 | 194021.6937 | 59.77 | 781.66
2016-01-01 14:00 | 37622 | 1510.1283 | 194021.6937 | 59.77 | 752.44
2016-01-01 15:00 | 36686 | 1277.9522 | 194021.6937 | 59.77 | 733.72
2016-01-01 16:00 | 37058 | 1412.2465 | 194021.6937 | 59.77 | 741.16
2016-01-01 17:00 | 39432 | 1675.6575 | 196271.6937 | 59.77 | 788.64
2016-01-01 18:00 | 41606 | 2398.4396 | 209850.3837 | 59.77 | 832.12
2016-01-01 19:00 | 43781 | 2681.7107 | 220585.4717 | 59.78 | 831.839
2016-01-01 20:00 | 44330 | 3196.4693 | 221448.7717 | 59.78 | 842.27
2016-01-01 21:00 | 44415 | 5464.2806 | 221448.7717 | 59.78 | 843.885
2016-01-01 22:00 | 43749 | 6353.7514 | 221448.7717 | 59.78 | 831.231
2016-01-01 23:00 | 42745 | 5004.1891 | 221448.7717 | 59.78 | 812.155
2016-01-02 | 42723 | 4863.2634 | 223930.3717 | 59.78 | 811.737
2016-01-02 01:00 | 42700 | 4808.6218 | 223930.3717 | 59.78 | 811.3
2016-01-02 02:00 | 42726 | 4993.3024 | 224034.4467 | 59.78 | 811.794
2016-01-02 03:00 | 43175 | 5950.1373 | 224034.4467 | 59.78 | 820.325
2016-01-02 04:00 | 44009 | 5781.0812 | 224034.4467 | 59.78 | 836.171
2016-01-02 05:00 | 45652 | 5513.8782 | 227867.1667 | 59.78 | 867.388
2016-01-02 06:00 | 47371 | 5470.2196 | 232349.4117 | 59.78 | 900.049
2016-01-02 07:00 | 48782 | 5130.2587 | 234928.0777 | 59.78 | 926.858
2016-01-02 08:00 | 49337 | 5058.6248 | 237321.3077 | 59.78 | 937.403
2016-01-02 09:00 | 48488 | 5846.3145 | 225432.7197 | 59.78 | 921.272
2016-01-02 10:00 | 46641 | 4130.5227 | 225432.7197 | 59.78 | 886.179
2016-01-02 11:00 | 44384 | 2811.7168 | 218682.7197 | 59.78 | 843.296
2016-01-02 12:00 | 42137 | 2790.7681 | 219177.7197 | 59.78 | 800.603
2016-01-02 13:00 | 40226 | 2654.4667 | 213088.389 | 59.77 | 804.52
2016-01-02 14:00 | 38940 | 2765.9739 | 207095.824 | 59.77 | 778.8
2016-01-02 15:00 | 38229 | 2985.4876 | 207095.824 | 59.77 | 764.58
2016-01-02 16:00 | 39125 | 2772.4856 | 207095.824 | 59.77 | 782.5
2016-01-02 17:00 | 41913 | 3270.8793 | 207095.824 | 59.77 | 838.26
2016-01-02 18:00 | 43899 | 4842.7392 | 207095.824 | 59.77 | 877.98
2016-01-02 19:00 | 45886 | 6627.3179 | 207981.674 | 59.77 | 917.72
2016-01-02 20:00 | 46209 | 8252.4811 | 205660.6594 | 59.77 | 924.18
2016-01-02 21:00 | 45746 | 8766.7654 | 205660.6594 | 59.77 | 914.92
2016-01-02 22:00 | 44345 | 8398.7103 | 205660.6594 | 59.77 | 886.9
2016-01-02 23:00 | 42798 | 6547.8071 | 205660.6594 | 59.77 | 855.96
2016-01-03 | 42734 | 6111.5946 | 205660.6594 | 59.77 | 854.68
2016-01-03 01:00 | 42670 | 4768.1387 | 205660.6594 | 59.77 | 853.4
2016-01-03 02:00 | 42261 | 4696.608 | 205743.7844 | 59.77 | 845.22
2016-01-03 03:00 | 42120 | 4453.9977 | 205743.7844 | 59.77 | 842.4
2016-01-03 04:00 | 42476 | 4505.8348 | 205743.7844 | 59.77 | 849.52
2016-01-03 05:00 | 43592 | 5232.4591 | 205743.7844 | 59.77 | 871.84
2016-01-03 06:00 | 44860 | 5447.5219 | 210243.7844 | 59.77 | 897.2
2016-01-03 07:00 | 46116 | 4588.6786 | 222146.6368 | 59.78 | 876.204
2016-01-03 08:00 | 47389 | 4121.4534 | 233019.2248 | 59.78 | 900.391
2016-01-03 09:00 | 48380 | 4526.6266 | 239751.4698 | 59.78 | 919.22
2016-01-03 10:00 | 48538 | 3858.772 | 241781.8298 | 59.78 | 922.222
2016-01-03 11:00 | 48037 | 3914.2245 | 240765.8298 | 59.78 | 912.703
2016-01-03 12:00 | 47399 | 3504.3765 | 240765.8298 | 59.78 | 900.581
2016-01-03 13:00 | 46452 | 3713.5099 | 240765.8298 | 59.78 | 882.588
2016-01-03 14:00 | 45798 | 3497.6993 | 240765.8298 | 59.78 | 870.162
2016-01-03 15:00 | 45628 | 3409.243 | 240765.8298 | 59.78 | 866.932
2016-01-03 16:00 | 46705 | 2833.2723 | 243022.4406 | 59.77 | 934.1
2016-01-03 17:00 | 49088 | 2482.7683 | 256312.4198 | 59.77 | 981.76
2016-01-03 18:00 | 50618 | 2749.5083 | 257328.4198 | 59.77 | 1012.36
2016-01-03 19:00 | 52148 | 2537.0363 | 259376.4129 | 59.77 | 1042.96
2016-01-03 20:00 | 51798 | 2471.0935 | 261545.9775 | 59.77 | 1035.96
2016-01-03 21:00 | 50593 | 2564.0738 | 254431.1244 | 59.77 | 1011.86
2016-01-03 22:00 | 48411 | 2531.7466 | 242678.3914 | 59.77 | 968.22
2016-01-03 23:00 | 46134 | 2520.4791 | 242678.3914 | 59.77 | 922.68
2016-01-04 | 40884 | 2520.1074 | 239076.2914 | 59.78 | 776.796
2016-01-04 01:00 | 40452 | 2734.3124 | 239076.2914 | 59.78 | 768.588
2016-01-04 02:00 | 40509 | 2774.3461 | 239076.2914 | 59.78 | 769.671
2016-01-04 03:00 | 41113 | 3029.7084 | 239076.2914 | 59.78 | 781.147
2016-01-04 04:00 | 42758 | 2854.6396 | 239076.2914 | 59.78 | 812.402
2016-01-04 05:00 | 46247 | 2760.6624 | 239076.2914 | 59.78 | 878.693
2016-01-04 06:00 | 51109 | 2611.2147 | 260513.8444 | 59.77 | 1022.18
2016-01-04 07:00 | 53267 | 2850.6419 | 270283.7143 | 59.78 | 1012.073
2016-01-04 08:00 | 52782 | 3288.1475 | 269179.1044 | 59.78 | 1002.858
2016-01-04 09:00 | 52505 | 3105.8714 | 269179.1044 | 59.78 | 997.595
2016-01-04 10:00 | 51991 | 2533.236 | 269368.7044 | 59.78 | 987.829
2016-01-04 11:00 | 50592 | 2232.8755 | 269368.7044 | 59.78 | 961.248
2016-01-04 12:00 | 49013 | 1709.4268 | 269368.7044 | 59.78 | 931.247
2016-01-04 13:00 | 47426 | 1791.4274 | 269368.7044 | 59.78 | 901.094
2016-01-04 14:00 | 46241 | 1651.9778 | 269368.7044 | 59.78 | 878.579
2016-01-04 15:00 | 45478 | 1479.3944 | 268594.3744 | 59.78 | 864.082
2016-01-04 16:00 | 46167 | 1524.969 | 268594.3744 | 59.78 | 877.173
2016-01-04 17:00 | 49199 | 1523.5963 | 268594.3744 | 59.78 | 934.781
2016-01-04 18:00 | 51727 | 1976.5493 | 269782.9348 | 59.78 | 982.813
2016-01-04 19:00 | 54254 | 2326.3773 | 274252.8948 | 59.78 | 1030.826
2016-01-04 20:00 | 54378 | 2952.1016 | 273236.8948 | 59.78 | 1033.182
2016-01-04 21:00 | 53271 | 4242.9909 | 261299.7278 | 59.77 | 1065.42
2016-01-04 22:00 | 50811 | 5364.1876 | 238226.6155 | 59.78 | 965.409
2016-01-04 23:00 | 48606 | 6487.6416 | 235976.6155 | 59.78 | 923.514
2016-01-05 | 46059 | 7282.4836 | 235285.0155 | 59.78 | 875.121
2016-01-05 01:00 | 45589 | 7530.7062 | 235285.0155 | 59.78 | 866.191
2016-01-05 02:00 | 46101 | 8088.9681 | 235285.0155 | 59.78 | 875.919
2016-01-05 03:00 | 46836 | 8525.766 | 235285.0155 | 59.78 | 889.884
2016-01-05 04:00 | 48246 | 9140.6609 | 235285.0155 | 59.78 | 916.674
2016-01-05 05:00 | 51595 | 9388.7715 | 235285.0155 | 59.78 | 980.305
2016-01-05 06:00 | 56653 | 9026.0023 | 250586.3755 | 59.77 | 1133.06
2016-01-05 07:00 | 57985 | 9098.4965 | 251328.8387 | 59.77 | 1159.7
2016-01-05 08:00 | 55803 | 9398.7425 | 249616.2171 | 59.77 | 1116.06
2016-01-05 09:00 | 53773 | 9899.0725 | 237256.2841 | 59.78 | 1021.687
2016-01-05 10:00 | 51716 | 7703.5712 | 237256.2841 | 59.78 | 982.604
2016-01-05 11:00 | 49494 | 6691.525 | 226383.6961 | 59.78 | 940.386
2016-01-05 12:00 | 47216 | 6729.3562 | 221233.4461 | 59.78 | 897.104
2016-01-05 13:00 | 45308 | 5769.2302 | 221233.4461 | 59.78 | 860.852
2016-01-05 14:00 | 43815 | 5326.6227 | 219141.2581 | 59.78 | 832.485
2016-01-05 15:00 | 43514 | 5006.068 | 219915.5881 | 59.78 | 826.766
2016-01-05 16:00 | 43555 | 5734.7244 | 219915.5881 | 59.78 | 827.545
2016-01-05 17:00 | 46552 | 5934.0848 | 219915.5881 | 59.78 | 884.488
2016-01-05 18:00 | 49292 | 7998.6616 | 219915.5881 | 59.78 | 936.548
2016-01-05 19:00 | 52031 | 9443.2869 | 219915.5881 | 59.78 | 988.589
2016-01-05 20:00 | 52333 | 10458.5521 | 217665.5881 | 59.78 | 994.327
2016-01-05 21:00 | 51028 | 11487.1878 | 202075.2077 | 59.77 | 1020.56
2016-01-05 22:00 | 48683 | 11914.0869 | 189838.1177 | 59.77 | 973.66
2016-01-05 23:00 | 46072 | 12090.388 | 189838.1177 | 59.77 | 921.44
2016-01-06 | 43566 | 11334.1224 | 187309.7977 | 59.79 | 784.188
2016-01-06 01:00 | 43008 | 10867.7801 | 187309.7977 | 59.79 | 774.144
2016-01-06 02:00 | 42911 | 10758.108 | 187309.7977 | 59.79 | 772.398
2016-01-06 03:00 | 43027 | 10317.0132 | 187309.7977 | 59.79 | 774.486
2016-01-06 04:00 | 43919 | 10527.0802 | 187309.7977 | 59.79 | 790.542
2016-01-06 05:00 | 46364 | 10848.2699 | 187309.7977 | 59.79 | 834.552
2016-01-06 06:00 | 50482 | 10588.4256 | 210875.1577 | 59.77 | 1009.64
2016-01-06 07:00 | 51559 | 10844.6536 | 215244.8681 | 59.77 | 1031.18
2016-01-06 08:00 | 50042 | 11149.2649 | 215524.4661 | 59.78 | 950.798
2016-01-06 09:00 | 49162 | 11257.1581 | 216115.4741 | 59.78 | 934.078
2016-01-06 10:00 | 48386 | 10135.3758 | 216115.4741 | 59.78 | 919.334
2016-01-06 11:00 | 47490 | 8665.6257 | 216115.4741 | 59.78 | 902.31
2016-01-06 12:00 | 46479 | 7989.944 | 216115.4741 | 59.78 | 883.101
2016-01-06 13:00 | 45569 | 6672.9163 | 216115.4741 | 59.78 | 865.811
2016-01-06 14:00 | 44608 | 5755.5907 | 216115.4741 | 59.78 | 847.552
2016-01-06 15:00 | 44264 | 4752.2113 | 216889.8041 | 59.78 | 841.016
2016-01-06 16:00 | 44726 | 4699.2892 | 216889.8041 | 59.78 | 849.794
2016-01-06 17:00 | 46375 | 5030.8891 | 217994.4141 | 59.78 | 881.125
2016-01-06 18:00 | 46896 | 5960.104 | 216889.8041 | 59.78 | 891.024
2016-01-06 19:00 | 47417 | 7205.7846 | 213536.0937 | 59.77 | 948.34
2016-01-06 20:00 | 46529 | 7929.444 | 199049.4237 | 59.77 | 930.58
2016-01-06 21:00 | 44926 | 9031.3192 | 183534.8377 | 59.79 | 808.668
2016-01-06 22:00 | 41912 | 11814.8531 | 145987.3813 | 59.79 | 754.416
2016-01-06 23:00 | 38969 | 13333.8895 | 135898.3813 | 59.79 | 701.442
2016-01-07 | 35069 | 12282.1003 | 135898.3813 | 59.79 | 631.242
2016-01-07 01:00 | 34874 | 12690.5182 | 135124.0513 | 59.79 | 627.732
2016-01-07 02:00 | 35223 | 12493.4536 | 135124.0513 | 59.79 | 634.014
2016-01-07 03:00 | 36053 | 12599.8029 | 138282.4513 | 59.79 | 648.954
2016-01-07 04:00 | 37641 | 12033.7993 | 138282.4513 | 59.79 | 677.538
2016-01-07 05:00 | 40904 | 11527.838 | 149487.9113 | 59.79 | 736.272
2016-01-07 06:00 | 45734 | 10691.5801 | 176704.3177 | 59.79 | 823.212
2016-01-07 07:00 | 48063 | 9699.2335 | 202596.9737 | 59.77 | 961.26
2016-01-07 08:00 | 48460 | 9058.3748 | 209142.5737 | 59.77 | 969.2
2016-01-07 09:00 | 49367 | 9575.7178 | 210158.5737 | 59.77 | 987.34
2016-01-07 10:00 | 49826 | 9568.5767 | 210158.5737 | 59.77 | 996.52
2016-01-07 11:00 | 49490 | 10255.1785 | 209142.5737 | 59.77 | 989.8
2016-01-07 12:00 | 48824 | 11628.0517 | 205401.8473 | 59.77 | 976.48
2016-01-07 13:00 | 48048 | 12286.4168 | 205401.8473 | 59.77 | 960.96
2016-01-07 14:00 | 47297 | 12249.5686 | 205401.8473 | 59.77 | 945.94
2016-01-07 15:00 | 47011 | 11659.575 | 205401.8473 | 59.77 | 940.22
2016-01-07 16:00 | 48094 | 10287.6679 | 205401.8473 | 59.77 | 961.88
2016-01-07 17:00 | 51276 | 9028.9425 | 227320.0157 | 59.78 | 974.244
2016-01-07 18:00 | 53276 | 8790.7385 | 238423.2237 | 59.78 | 1012.244
2016-01-07 19:00 | 55276 | 8851.2925 | 251570.7287 | 59.77 | 1105.52
2016-01-07 20:00 | 54978 | 8875.1982 | 251570.7287 | 59.77 | 1099.56
2016-01-07 21:00 | 54090 | 6445.0196 | 252586.7287 | 59.77 | 1081.8
2016-01-07 22:00 | 52055 | 5626.6428 | 251570.7287 | 59.77 | 1041.1
2016-01-07 23:00 | 50374 | 5864.0162 | 248122.3287 | 59.77 | 1007.48
2016-01-08 | 45438 | 6241.2487 | 248122.3287 | 59.77 | 908.76
2016-01-08 01:00 | 45070 | 6261.2706 | 248896.6587 | 59.77 | 901.4
2016-01-08 02:00 | 45263 | 6725.0599 | 248896.6587 | 59.77 | 905.26
2016-01-08 03:00 | 45884 | 6403.544 | 248896.6587 | 59.77 | 917.68
2016-01-08 04:00 | 46980 | 5162.2508 | 248896.6587 | 59.77 | 939.6
2016-01-08 05:00 | 49394 | 4667.8878 | 248896.6587 | 59.77 | 987.88
2016-01-08 06:00 | 53019 | 4279.7024 | 264296.9314 | 59.77 | 1060.38
2016-01-08 07:00 | 54369 | 4704.6846 | 265867.1214 | 59.77 | 1087.38
2016-01-08 08:00 | 53559 | 5260.9347 | 267305.5214 | 59.78 | 1017.621
2016-01-08 09:00 | 53172 | 4359.8421 | 267305.5214 | 59.78 | 1010.268
2016-01-08 10:00 | 52379 | 3808.2475 | 267305.5214 | 59.78 | 995.201
2016-01-08 11:00 | 51085 | 3537.018 | 261523.8879 | 59.77 | 1021.7
2016-01-08 12:00 | 49734 | 3374.5969 | 261523.8879 | 59.77 | 994.68
2016-01-08 13:00 | 48335 | 3292.993 | 261523.8879 | 59.77 | 966.7
2016-01-08 14:00 | 47165 | 3222.6229 | 261523.8879 | 59.77 | 943.3
2016-01-08 15:00 | 46536 | 2717.3746 | 261523.8879 | 59.77 | 930.72
2016-01-08 16:00 | 46980 | 2564.2419 | 261523.8879 | 59.77 | 939.6
2016-01-08 17:00 | 48961 | 2291.9593 | 261523.8879 | 59.77 | 979.22
2016-01-08 18:00 | 50240 | 2060.8003 | 266544.3759 | 59.77 | 1004.8
2016-01-08 19:00 | 51519 | 1932.0966 | 266544.3759 | 59.77 | 1030.38
2016-01-08 20:00 | 51375 | 2175.0559 | 266544.3759 | 59.77 | 1027.5
2016-01-08 21:00 | 50478 | 3147.8915 | 254440.5555 | 59.77 | 1009.56
2016-01-08 22:00 | 49197 | 3968.0616 | 254440.5555 | 59.77 | 983.94
2016-01-08 23:00 | 48024 | 4857.219 | 257495.5555 | 59.77 | 960.48
2016-01-09 | 48024 | 5860.1086 | 257495.5555 | 59.77 | 960.48
2016-01-09 01:00 | 49731 | 6540.6216 | 257495.5555 | 59.77 | 994.62
2016-01-09 02:00 | 52994 | 7524.043 | 257519.0055 | 59.77 | 1059.88
2016-01-09 03:00 | 53444 | 8059.1277 | 257519.0055 | 59.77 | 1068.88
2016-01-09 04:00 | 54330 | 8375.402 | 257519.0055 | 59.77 | 1086.6
2016-01-09 05:00 | 55483 | 9296.5876 | 257519.0055 | 59.77 | 1109.66
2016-01-09 06:00 | 57426 | 9745.5898 | 257519.0055 | 59.77 | 1148.52
2016-01-09 07:00 | 58334 | 9003.9571 | 262353.2556 | 59.77 | 1166.68
2016-01-09 08:00 | 57849 | 8460.453 | 262269.3756 | 59.77 | 1156.98
2016-01-09 09:00 | 56132 | 7861.0221 | 260790.9125 | 59.77 | 1122.64
2016-01-09 10:00 | 53740 | 4979.7118 | 259829.7756 | 59.77 | 1074.8
2016-01-09 11:00 | 50651 | 1826.9451 | 261546.846 | 59.77 | 1013.02
2016-01-09 12:00 | 48042 | 813.6459 | 255387.4512 | 59.77 | 960.84
2016-01-09 13:00 | 45501 | 726.8678 | 251803.1812 | 59.77 | 910.02
2016-01-09 14:00 | 43629 | 710.7359 | 250294.8312 | 59.77 | 872.58
2016-01-09 15:00 | 42515 | 917.7742 | 250294.8312 | 59.77 | 850.3
2016-01-09 16:00 | 42664 | 741.5401 | 250294.8312 | 59.77 | 853.28
2016-01-09 17:00 | 45448 | 646.7901 | 250294.8312 | 59.77 | 908.96
2016-01-09 18:00 | 48084 | 1079.4972 | 251310.8312 | 59.77 | 961.68
2016-01-09 19:00 | 50721 | 2681.7675 | 255327.3943 | 59.77 | 1014.42
2016-01-09 20:00 | 51239 | 5225.4712 | 250577.0242 | 59.77 | 1024.78
2016-01-09 21:00 | 51280 | 7811.036 | 250441.0242 | 59.77 | 1025.6
2016-01-09 22:00 | 50315 | 7062.0694 | 250441.0242 | 59.77 | 1006.3
2016-01-09 23:00 | 49493 | 6240.3205 | 250441.0242 | 59.77 | 989.86
2016-01-10 | 49731 | 6161.5853 | 248281.6242 | 59.77 | 994.62
2016-01-10 01:00 | 50231 | 6921.5634 | 248281.6242 | 59.77 | 1004.62
2016-01-10 02:00 | 50895 | 7613.6697 | 250170.5742 | 59.77 | 1017.9
2016-01-10 03:00 | 51237 | 8180.4927 | 250170.5742 | 59.77 | 1024.74
2016-01-10 04:00 | 52039 | 7928.4289 | 250170.5742 | 59.77 | 1040.78
2016-01-10 05:00 | 53284 | 7728.4298 | 250170.5742 | 59.77 | 1065.68
2016-01-10 06:00 | 55137 | 8181.6356 | 255313.969 | 59.77 | 1102.74
2016-01-10 07:00 | 56442 | 8473.6068 | 256451.4823 | 59.77 | 1128.84
2016-01-10 08:00 | 56324 | 8914.4803 | 256329.969 | 59.77 | 1126.48
2016-01-10 09:00 | 54071 | 9316.6009 | 241763.4065 | 59.78 | 1027.349
2016-01-10 10:00 | 51312 | 7244.5119 | 235349.7985 | 59.78 | 974.928
2016-01-10 11:00 | 48323 | 6702.4587 | 227405.5105 | 59.78 | 918.137
2016-01-10 12:00 | 45834 | 5907.841 | 222457.8305 | 59.78 | 870.846
2016-01-10 13:00 | 43543 | 5281.7271 | 220881.0605 | 59.78 | 827.317
2016-01-10 14:00 | 41753 | 5088.683 | 222389.4105 | 59.78 | 793.307
2016-01-10 15:00 | 40700 | 5396.9586 | 222389.4105 | 59.78 | 773.3
2016-01-10 16:00 | 41245 | 5010.0497 | 222389.4105 | 59.78 | 783.655
2016-01-10 17:00 | 44103 | 4778.7333 | 222389.4105 | 59.78 | 837.957
2016-01-10 18:00 | 47232 | 5809.18 | 225973.6805 | 59.78 | 897.408
2016-01-10 19:00 | 50362 | 7401.8473 | 226343.23 | 59.78 | 956.878
2016-01-10 20:00 | 51036 | 9164.1077 | 222920.402 | 59.78 | 969.684
2016-01-10 21:00 | 50573 | 9977.6788 | 219259.412 | 59.78 | 960.887
2016-01-10 22:00 | 48641 | 9459.2713 | 219259.412 | 59.78 | 924.179
2016-01-10 23:00 | 46729 | 9616.1897 | 218017.682 | 59.78 | 887.851
2016-01-11 | 45411 | 9827.2191 | 216940.412 | 59.78 | 862.809
2016-01-11 01:00 | 45226 | 9237.7441 | 216940.412 | 59.78 | 859.294
2016-01-11 02:00 | 45611 | 9041.5546 | 216940.412 | 59.78 | 866.609
2016-01-11 03:00 | 46374 | 9314.8373 | 216940.412 | 59.78 | 881.106
2016-01-11 04:00 | 47783 | 9407.5186 | 227081.342 | 59.78 | 907.877
2016-01-11 05:00 | 50667 | 8982.7559 | 236132.03 | 59.78 | 962.673
2016-01-11 06:00 | 55315 | 8231.9305 | 264528.966 | 59.77 | 1106.3
2016-01-11 07:00 | 56607 | 7683.5265 | 264528.966 | 59.77 | 1132.14
2016-01-11 08:00 | 54091 | 7340.5823 | 261309.046 | 59.77 | 1081.82
2016-01-11 09:00 | 51177 | 7221.0567 | 248443.8517 | 59.77 | 1023.54
2016-01-11 10:00 | 48550 | 5861.9864 | 248443.8517 | 59.77 | 971
2016-01-11 11:00 | 45907 | 4181.306 | 248443.8517 | 59.77 | 918.14
2016-01-11 12:00 | 43655 | 4017.9522 | 237528.5917 | 59.78 | 829.445
2016-01-11 13:00 | 41879 | 3924.7851 | 239105.3617 | 59.78 | 795.701
2016-01-11 14:00 | 40524 | 3178.1291 | 239105.3617 | 59.78 | 769.956
2016-01-11 15:00 | 39730 | 2617.7702 | 239105.3617 | 59.78 | 754.87
2016-01-11 16:00 | 39826 | 2225.1096 | 237111.8117 | 59.77 | 796.52
2016-01-11 17:00 | 42103 | 1758.2052 | 237111.8117 | 59.77 | 842.06
2016-01-11 18:00 | 44039 | 1816.3711 | 237111.8117 | 59.77 | 880.78
2016-01-11 19:00 | 45975 | 1266.8611 | 243523.2681 | 59.78 | 873.525
2016-01-11 20:00 | 45946 | 923.9954 | 246700.8897 | 59.78 | 872.974
2016-01-11 21:00 | 45045 | 930.0014 | 249481.8797 | 59.78 | 855.855
2016-01-11 22:00 | 42613 | 1055.9846 | 247129.7197 | 59.77 | 852.26
2016-01-11 23:00 | 40394 | 1194.9537 | 247129.7197 | 59.77 | 807.88
2016-01-12 | 40731 | 1127.1832 | 247129.7197 | 59.77 | 814.62
2016-01-12 01:00 | 41482 | 1212.8768 | 247129.7197 | 59.77 | 829.64
2016-01-12 02:00 | 41684 | 1312.2879 | 247129.7197 | 59.77 | 833.68
2016-01-12 03:00 | 42292 | 1426.6223 | 247129.7197 | 59.77 | 845.84
2016-01-12 04:00 | 43710 | 1410.2869 | 246826.5365 | 59.77 | 874.2
2016-01-12 05:00 | 46887 | 1532.1681 | 265720.0057 | 59.78 | 890.853
2016-01-12 06:00 | 51931 | 1511.3807 | 274473.5057 | 59.76 | 1090.551
2016-01-12 07:00 | 53377 | 1277.7663 | 274800.4123 | 59.76 | 1120.917
2016-01-12 08:00 | 51130 | 1191.1092 | 272596.2237 | 59.76 | 1073.73
2016-01-12 09:00 | 48534 | 1418.8747 | 259784.7407 | 59.78 | 922.146
2016-01-12 10:00 | 46409 | 1551.0181 | 255066.8157 | 59.78 | 881.771
2016-01-12 11:00 | 44432 | 1555.8305 | 239043.9777 | 59.78 | 844.208
2016-01-12 12:00 | 42784 | 1931.3689 | 239043.9777 | 59.77 | 855.68
2016-01-12 13:00 | 41337 | 1739.2516 | 223589.0689 | 59.77 | 826.74
2016-01-12 14:00 | 40245 | 1817.0311 | 216510.9605 | 59.77 | 804.9
2016-01-12 15:00 | 39622 | 2598.6616 | 216510.9605 | 59.78 | 752.818
2016-01-12 16:00 | 40262 | 3207.236 | 218504.5105 | 59.78 | 764.978
2016-01-12 17:00 | 42141 | 3093.3281 | 218504.5105 | 59.77 | 842.82
2016-01-12 18:00 | 43899 | 4094.6149 | 214044.1705 | 59.77 | 877.98
2016-01-12 19:00 | 45657 | 4606.5054 | 214044.1705 | 59.77 | 913.14
2016-01-12 20:00 | 45748 | 5393.7798 | 211951.9825 | 59.77 | 914.96
2016-01-12 21:00 | 44815 | 7119.4997 | 193005.2021 | 59.77 | 896.3
2016-01-12 22:00 | 42767 | 8974.5861 | 174208.4921 | 59.78 | 812.573
2016-01-12 23:00 | 40565 | 9217.7491 | 174208.4921 | 59.77 | 811.3
2016-01-13 | 38817 | 9408.9426 | 174208.4921 | 59.77 | 776.34
2016-01-13 01:00 | 38457 | 9543.6679 | 174208.4921 | 59.77 | 769.14
2016-01-13 02:00 | 38529 | 9463.0552 | 172698.1721 | 59.77 | 770.58
2016-01-13 03:00 | 38977 | 9224.2095 | 172698.1721 | 59.77 | 779.54
2016-01-13 04:00 | 40246 | 9862.6625 | 172698.1721 | 59.77 | 804.92
2016-01-13 05:00 | 43292 | 9871.1789 | 175017.4153 | 59.78 | 822.548
2016-01-13 06:00 | 47975 | 9121.678 | 196029.8053 | 59.77 | 959.5
2016-01-13 07:00 | 49235 | 9592.2772 | 197045.8053 | 59.77 | 984.7
2016-01-13 08:00 | 47500 | 10396.4229 | 190580.5793 | 59.78 | 902.5
2016-01-13 09:00 | 46158 | 11538.8181 | 174423.5193 | 59.78 | 877.002
2016-01-13 10:00 | 44864 | 10330.1 | 175286.8193 | 59.78 | 852.416
2016-01-13 11:00 | 43328 | 10664.9508 | 166659.0113 | 59.78 | 823.232
2016-01-13 12:00 | 42171 | 10626.5141 | 166659.0113 | 59.77 | 843.42
2016-01-13 13:00 | 41483 | 10141.9424 | 164271.5113 | 59.77 | 829.66
2016-01-13 14:00 | 40790 | 10039.3763 | 164271.5113 | 59.77 | 815.8
2016-01-13 15:00 | 40616 | 10702.2357 | 164271.5113 | 59.77 | 812.32
2016-01-13 16:00 | 41544 | 10173.9416 | 164271.5113 | 59.77 | 830.88
2016-01-13 17:00 | 43372 | 10192.5851 | 164271.5113 | 59.78 | 824.068
2016-01-13 18:00 | 44181 | 10903.9236 | 164271.5113 | 59.78 | 839.439
2016-01-13 19:00 | 44989 | 11996.8718 | 161034.8413 | 59.78 | 854.791
2016-01-13 20:00 | 44358 | 12759.8685 | 152428.8549 | 59.77 | 887.16
2016-01-13 21:00 | 42873 | 12866.1262 | 143778.3449 | 59.77 | 857.46
2016-01-13 22:00 | 40145 | 12515.5542 | 143778.3449 | 59.77 | 802.9
2016-01-13 23:00 | 37356 | 12044.9986 | 143778.3449 | 59.79 | 672.408
2016-01-14 | 35557 | 11385.7489 | 143778.3449 | 59.79 | 640.026
2016-01-14 01:00 | 34797 | 10103.1003 | 143778.3449 | 59.79 | 626.346
2016-01-14 02:00 | 34525 | 9734.2512 | 143778.3449 | 59.79 | 621.45
2016-01-14 03:00 | 34746 | 8920.684 | 143778.3449 | 59.79 | 625.428
2016-01-14 04:00 | 35540 | 7678.0834 | 143778.3449 | 59.77 | 710.8
2016-01-14 05:00 | 38292 | 7095.073 | 156036.1749 | 59.77 | 765.84
2016-01-14 06:00 | 42509 | 6409.4452 | 182216.1453 | 59.78 | 807.671
2016-01-14 07:00 | 43714 | 7426.8201 | 182710.4653 | 59.78 | 830.566
2016-01-14 08:00 | 42663 | 8637.0655 | 182710.4653 | 59.78 | 810.597
2016-01-14 09:00 | 42572 | 8651.227 | 182710.4653 | 59.78 | 808.868
2016-01-14 10:00 | 42456 | 8948.8024 | 182710.4653 | 59.78 | 806.664
2016-01-14 11:00 | 41976 | 8958.2871 | 182710.4653 | 59.78 | 797.544
2016-01-14 12:00 | 41429 | 7557.6036 | 180389.4508 | 59.78 | 787.151
2016-01-14 13:00 | 41151 | 5171.5405 | 182776.9508 | 59.78 | 781.869
2016-01-14 14:00 | 40819 | 4496.4541 | 182776.9508 | 59.78 | 775.561
2016-01-14 15:00 | 40657 | 3666.1049 | 182776.9508 | 59.78 | 772.483
2016-01-14 16:00 | 41150 | 4223.9648 | 182776.9508 | 59.78 | 781.85
2016-01-14 17:00 | 42448 | 5153.4655 | 184943.9173 | 59.78 | 806.512
2016-01-14 18:00 | 43120 | 5603.3593 | 184943.9173 | 59.77 | 862.4
2016-01-14 19:00 | 43793 | 4734.3074 | 193947.2573 | 59.77 | 875.86
2016-01-14 20:00 | 42982 | 3947.9812 | 194683.2573 | 59.77 | 859.64
2016-01-14 21:00 | 41181 | 4694.9491 | 183511.6213 | 59.78 | 782.439
2016-01-14 22:00 | 38562 | 3698.3185 | 175050.1513 | 59.78 | 732.678
2016-01-14 23:00 | 35960 | 4740.4938 | 175050.1513 | 59.77 | 719.2
2016-01-15 | 34644 | 3917.1412 | 169916.4549 | 59.77 | 692.88
2016-01-15 01:00 | 33783 | 2945.292 | 169916.4549 | 59.77 | 675.66
2016-01-15 02:00 | 33422 | 1691.8058 | 169916.4549 | 59.77 | 668.44
2016-01-15 03:00 | 33475 | 2010.8634 | 169916.4549 | 59.77 | 669.5
2016-01-15 04:00 | 34361 | 2680.8039 | 169916.4549 | 59.77 | 687.22
2016-01-15 05:00 | 36932 | 3039.4574 | 173272.8549 | 59.78 | 701.708
2016-01-15 06:00 | 40963 | 2784.5415 | 195085.1529 | 59.77 | 819.26
2016-01-15 07:00 | 42807 | 3111.2398 | 200601.1529 | 59.77 | 856.14
2016-01-15 08:00 | 42439 | 4075.2589 | 199585.1529 | 59.77 | 848.78
2016-01-15 09:00 | 42830 | 3341.0121 | 200601.1529 | 59.77 | 856.6
2016-01-15 10:00 | 43142 | 4113.9323 | 199585.1529 | 59.77 | 862.84
2016-01-15 11:00 | 42939 | 4054.3195 | 196348.4829 | 59.77 | 858.78
2016-01-15 12:00 | 42507 | 3825.2147 | 198669.4975 | 59.77 | 850.14
2016-01-15 13:00 | 42400 | 4114.9968 | 195313.0975 | 59.77 | 848
2016-01-15 14:00 | 42201 | 4259.103 | 195313.0975 | 59.77 | 844.02
2016-01-15 15:00 | 42264 | 4558.5152 | 194449.7975 | 59.77 | 845.28
2016-01-15 16:00 | 42910 | 4692.1869 | 194449.7975 | 59.77 | 858.2
2016-01-15 17:00 | 44369 | 5104.7175 | 196629.3309 | 59.77 | 887.38
2016-01-15 18:00 | 44644 | 5270.5021 | 196917.3309 | 59.77 | 892.88
2016-01-15 19:00 | 44920 | 5002.7992 | 197197.3309 | 59.77 | 898.4
2016-01-15 20:00 | 44232 | 4983.7217 | 192417.3309 | 59.77 | 884.64
2016-01-15 21:00 | 43054 | 4498.6087 | 191268.4389 | 59.77 | 861.08
2016-01-15 22:00 | 41210 | 4195.6973 | 184439.7489 | 59.78 | 782.99
2016-01-15 23:00 | 39133 | 4613.1288 | 184439.7489 | 59.78 | 743.527
2016-01-16 | 39231 | 4021.8531 | 177633.2029 | 59.78 | 745.389
2016-01-16 01:00 | 39562 | 4391.9852 | 176131.5529 | 59.78 | 751.678
2016-01-16 02:00 | 39256 | 4631.9975 | 176131.5529 | 59.78 | 745.864
2016-01-16 03:00 | 39249 | 4463.4804 | 176131.5529 | 59.78 | 745.731
2016-01-16 04:00 | 39496 | 4407.2404 | 176131.5529 | 59.78 | 750.424
2016-01-16 05:00 | 40621 | 4506.4699 | 181265.2493 | 59.78 | 771.799
2016-01-16 06:00 | 42289 | 4477.4776 | 188371.0373 | 59.77 | 845.78
2016-01-16 07:00 | 44087 | 4508.2904 | 199464.1073 | 59.77 | 881.74
2016-01-16 08:00 | 45516 | 4609.918 | 209567.8177 | 59.77 | 910.32
2016-01-16 09:00 | 46758 | 4331.9593 | 220412.3557 | 59.77 | 935.16
2016-01-16 10:00 | 47206 | 3801.8814 | 221428.3557 | 59.78 | 896.914
2016-01-16 11:00 | 46441 | 3642.7313 | 220412.3557 | 59.78 | 882.379
2016-01-16 12:00 | 44555 | 3706.5804 | 220412.3557 | 59.77 | 891.1
2016-01-16 13:00 | 43047 | 3528.3541 | 220412.3557 | 59.77 | 860.94
2016-01-16 14:00 | 41869 | 3254.4181 | 220412.3557 | 59.77 | 837.38
2016-01-16 15:00 | 41177 | 3206.9822 | 221275.6557 | 59.77 | 823.54
2016-01-16 16:00 | 41093 | 2087.1978 | 221275.6557 | 59.77 | 821.86
2016-01-16 17:00 | 42546 | 1246.8697 | 221275.6557 | 59.77 | 850.92
2016-01-16 18:00 | 44034 | 657.0905 | 232378.8637 | 59.78 | 836.646
2016-01-16 19:00 | 45522 | 519.2564 | 233592.8637 | 59.78 | 864.918
2016-01-16 20:00 | 45244 | 919.583 | 232576.8637 | 59.78 | 859.636
2016-01-16 21:00 | 44485 | 1203.246 | 230123.6557 | 59.78 | 845.215
2016-01-16 22:00 | 42973 | 1369.2796 | 217277.5073 | 59.77 | 859.46
2016-01-16 23:00 | 41389 | 2074.8322 | 204921.1073 | 59.77 | 827.78
2016-01-17 | 41365 | 2249.3599 | 204921.1073 | 59.77 | 827.3
2016-01-17 01:00 | 40855 | 3582.2156 | 206422.7573 | 59.78 | 776.245
2016-01-17 02:00 | 40633 | 5480.3671 | 195319.5493 | 59.78 | 772.027
2016-01-17 03:00 | 40715 | 5918.1508 | 195319.5493 | 59.78 | 773.585
2016-01-17 04:00 | 41242 | 6362.549 | 195319.5493 | 59.78 | 783.598
2016-01-17 05:00 | 42365 | 7127.4793 | 195319.5493 | 59.78 | 804.935
2016-01-17 06:00 | 44142 | 7512.6604 | 195319.5493 | 59.78 | 838.698
2016-01-17 07:00 | 45620 | 6736.751 | 195319.5493 | 59.77 | 912.4
2016-01-17 08:00 | 46723 | 6254.043 | 200031.4793 | 59.77 | 934.46
2016-01-17 09:00 | 46154 | 7199.3567 | 197014.4693 | 59.77 | 923.08
2016-01-17 10:00 | 44463 | 5481.2434 | 196441.9693 | 59.77 | 889.26
2016-01-17 11:00 | 42737 | 3214.9714 | 196441.9693 | 59.77 | 854.74
2016-01-17 12:00 | 41178 | 2497.5118 | 193205.2993 | 59.77 | 823.56
2016-01-17 13:00 | 39929 | 2244.1788 | 184126.6093 | 59.77 | 798.58
2016-01-17 14:00 | 38901 | 2848.3131 | 180889.9393 | 59.78 | 739.119
2016-01-17 15:00 | 38407 | 3116.7253 | 180889.9393 | 59.78 | 729.733
2016-01-17 16:00 | 39054 | 3363.065 | 180889.9393 | 59.78 | 742.026
2016-01-17 17:00 | 40472 | 4540.7231 | 180889.9393 | 59.78 | 768.968
2016-01-17 18:00 | 42230 | 5585.9308 | 180605.5313 | 59.78 | 802.37
2016-01-17 19:00 | 43989 | 6882.4329 | 183763.9313 | 59.78 | 835.791
2016-01-17 20:00 | 43677 | 8138.8758 | 172461.0213 | 59.78 | 829.863
2016-01-17 21:00 | 42959 | 10686.0669 | 148779.1269 | 59.77 | 859.18
2016-01-17 22:00 | 41491 | 12753.5498 | 137573.6669 | 59.77 | 829.82
2016-01-17 23:00 | 39632 | 12599.8863 | 137573.6669 | 59.79 | 713.376
2016-01-18 | 36442 | 12169.2116 | 135180.4369 | 59.79 | 655.956
2016-01-18 01:00 | 35945 | 11853.7464 | 135180.4369 | 59.79 | 647.01
2016-01-18 02:00 | 35950 | 11599.6357 | 135180.4369 | 59.79 | 647.1
2016-01-18 03:00 | 36283 | 11281.2258 | 135180.4369 | 59.79 | 653.094
2016-01-18 04:00 | 37391 | 11493.55 | 135180.4369 | 59.79 | 673.038
2016-01-18 05:00 | 39754 | 11823.4537 | 136746.3069 | 59.77 | 795.08
2016-01-18 06:00 | 43099 | 11173.9556 | 155722.5333 | 59.77 | 861.98
2016-01-18 07:00 | 44711 | 9808.3941 | 172553.5813 | 59.78 | 849.509
2016-01-18 08:00 | 44613 | 8660.8726 | 179150.0813 | 59.78 | 847.647
2016-01-18 09:00 | 44476 | 9359.8746 | 176668.4813 | 59.78 | 845.044
2016-01-18 10:00 | 44111 | 7952.0832 | 183676.8773 | 59.78 | 838.109
2016-01-18 11:00 | 43312 | 5976.8403 | 190385.8373 | 59.78 | 822.928
2016-01-18 12:00 | 42262 | 5784.8743 | 190385.8373 | 59.78 | 802.978
2016-01-18 13:00 | 41389 | 4976.965 | 188197.307 | 59.78 | 786.391
2016-01-18 14:00 | 40727 | 4097.0338 | 188197.307 | 59.78 | 773.813
2016-01-18 15:00 | 40184 | 4627.0586 | 188197.307 | 59.78 | 763.496
2016-01-18 16:00 | 40339 | 5132.0479 | 186181.247 | 59.78 | 766.441
2016-01-18 17:00 | 41227 | 5411.3058 | 189788.567 | 59.78 | 783.313
2016-01-18 18:00 | 42455 | 6064.6288 | 188607.375 | 59.78 | 806.645
2016-01-18 19:00 | 43684 | 6823.252 | 189040.6314 | 59.78 | 829.996
2016-01-18 20:00 | 42837 | 7732.1506 | 181900.305 | 59.78 | 813.903
2016-01-18 21:00 | 41151 | 8221.2438 | 166411.619 | 59.78 | 781.869
2016-01-18 22:00 | 38559 | 8472.8861 | 148564.571 | 59.77 | 771.18
2016-01-18 23:00 | 35615 | 8942.3203 | 138364.6346 | 59.79 | 641.07
2016-01-19 | 33404 | 9575.2527 | 139247.5446 | 59.79 | 601.272
2016-01-19 01:00 | 32460 | 9362.8356 | 139247.5446 | 59.79 | 584.28
2016-01-19 02:00 | 32194 | 9067.1215 | 139247.5446 | 59.79 | 579.492
2016-01-19 03:00 | 32292 | 8738.461 | 139247.5446 | 59.79 | 581.256
2016-01-19 04:00 | 33023 | 8426.9415 | 139247.5446 | 59.79 | 594.414
2016-01-19 05:00 | 35808 | 9585.8108 | 139247.5446 | 59.79 | 644.544
2016-01-19 06:00 | 40483 | 9313.2441 | 163792.739 | 59.77 | 809.66
2016-01-19 07:00 | 41851 | 9348.8574 | 168157.829 | 59.78 | 795.169
2016-01-19 08:00 | 40727 | 9436.8867 | 167141.829 | 59.77 | 814.54
2016-01-19 09:00 | 40652 | 9718.9291 | 169623.429 | 59.77 | 813.04
2016-01-19 10:00 | 40844 | 7881.2964 | 169623.429 | 59.78 | 776.036
2016-01-19 11:00 | 40805 | 7159.1165 | 169623.429 | 59.78 | 775.295
2016-01-19 12:00 | 40668 | 6580.8494 | 169623.429 | 59.78 | 772.692
2016-01-19 13:00 | 40554 | 6341.2595 | 171109.4643 | 59.78 | 770.526
2016-01-19 14:00 | 40238 | 6765.7071 | 167502.1443 | 59.78 | 764.522
2016-01-19 15:00 | 40058 | 7594.8553 | 161819.9643 | 59.77 | 801.16
2016-01-19 16:00 | 40073 | 8499.552 | 156465.9143 | 59.77 | 801.46
2016-01-19 17:00 | 40792 | 9225.1329 | 156465.9143 | 59.77 | 815.84
2016-01-19 18:00 | 41948 | 10163.8577 | 158947.5143 | 59.77 | 838.96
2016-01-19 19:00 | 43104 | 10460.2802 | 158947.5143 | 59.78 | 818.976
2016-01-19 20:00 | 42382 | 10508.8129 | 156381.4263 | 59.77 | 847.64
2016-01-19 21:00 | 40629 | 12591.6931 | 134976.0299 | 59.77 | 812.58
2016-01-19 22:00 | 37920 | 11563.4041 | 133072.0299 | 59.79 | 682.56
2016-01-19 23:00 | 34974 | 9210.6095 | 132521.3424 | 59.79 | 629.532
2016-01-20 | 31933 | 7602.3706 | 132521.3424 | 59.79 | 574.794
2016-01-20 01:00 | 30909 | 6796.949 | 132521.3424 | 59.79 | 556.362
2016-01-20 02:00 | 30406 | 6582.52 | 132521.3424 | 59.79 | 547.308
2016-01-20 03:00 | 30288 | 5457.8771 | 131903.3424 | 59.79 | 545.184
2016-01-20 04:00 | 30884 | 5131.8457 | 131903.3424 | 59.79 | 555.912
2016-01-20 05:00 | 33450 | 4553.6145 | 140766.2624 | 59.77 | 669
2016-01-20 06:00 | 37809 | 4112.3496 | 172143.7468 | 59.78 | 718.371
2016-01-20 07:00 | 39473 | 4633.434 | 172143.7468 | 59.78 | 749.987
2016-01-20 08:00 | 39092 | 6184.5922 | 169887.1361 | 59.78 | 742.748
2016-01-20 09:00 | 39324 | 8201.4444 | 169887.1361 | 59.77 | 786.48
2016-01-20 10:00 | 39760 | 6837.8272 | 169829.1461 | 59.78 | 755.44
2016-01-20 11:00 | 39896 | 4618.8068 | 177020.7361 | 59.78 | 758.024
2016-01-20 12:00 | 40012 | 4656.1359 | 177020.7361 | 59.78 | 760.228
2016-01-20 13:00 | 39888 | 5249.6693 | 177723.2311 | 59.78 | 757.872
2016-01-20 14:00 | 39681 | 7365.6997 | 161566.1711 | 59.77 | 793.62
2016-01-20 15:00 | 39553 | 10525.4176 | 146345.7467 | 59.77 | 791.06
2016-01-20 16:00 | 39849 | 10680.2758 | 146345.7467 | 59.77 | 796.98
2016-01-20 17:00 | 40246 | 10966.5767 | 146345.7467 | 59.77 | 804.92
2016-01-20 18:00 | 41097 | 10659.3754 | 146345.7467 | 59.77 | 821.94
2016-01-20 19:00 | 41948 | 11925.1622 | 142738.4267 | 59.77 | 838.96
2016-01-20 20:00 | 41163 | 12576.3893 | 135896.1867 | 59.77 | 823.26
2016-01-20 21:00 | 39582 | 12544.879 | 128866.4667 | 59.79 | 712.476
2016-01-20 22:00 | 36868 | 12205.8526 | 128866.4667 | 59.79 | 663.624
2016-01-20 23:00 | 34050 | 11625.0875 | 129417.1542 | 59.79 | 612.9
2016-01-21 | 30994 | 10634.2175 | 129417.1542 | 59.79 | 557.892
2016-01-21 01:00 | 30194 | 10318.838 | 129417.1542 | 59.79 | 543.492
2016-01-21 02:00 | 29861 | 10346.2947 | 129417.1542 | 59.79 | 537.498
2016-01-21 03:00 | 29993 | 10576.288 | 130035.1542 | 59.79 | 539.874
2016-01-21 04:00 | 30796 | 11550.9184 | 133642.4742 | 59.79 | 554.328
2016-01-21 05:00 | 33261 | 11431.376 | 139168.7942 | 59.79 | 598.698
2016-01-21 06:00 | 37888 | 10686.1139 | 139168.7942 | 59.79 | 681.984
2016-01-21 07:00 | 39573 | 9716.0774 | 145491.7542 | 59.77 | 791.46
2016-01-21 08:00 | 38676 | 9043.6336 | 145491.7542 | 59.77 | 773.52
2016-01-21 09:00 | 38455 | 7059.0383 | 152814.6049 | 59.77 | 769.1
2016-01-21 10:00 | 38332 | 4949.5197 | 163026.7793 | 59.78 | 728.308
2016-01-21 11:00 | 38143 | 2868.7608 | 168597.3835 | 59.78 | 724.717
2016-01-21 12:00 | 37830 | 1557.8075 | 173959.8835 | 59.78 | 718.77
2016-01-21 13:00 | 37823 | 1527.5607 | 173959.8835 | 59.78 | 718.637
2016-01-21 14:00 | 37677 | 1608.2613 | 172943.8835 | 59.78 | 715.863
2016-01-21 15:00 | 37519 | 1488.6668 | 172943.8835 | 59.78 | 712.861
2016-01-21 16:00 | 37365 | 1658.0203 | 175193.8835 | 59.78 | 709.935
2016-01-21 17:00 | 37484 | 2042.5786 | 175193.8835 | 59.78 | 712.196
2016-01-21 18:00 | 38554 | 3127.5428 | 175193.8835 | 59.78 | 732.526
2016-01-21 19:00 | 39623 | 4194.4724 | 175193.8835 | 59.78 | 752.837
2016-01-21 20:00 | 39076 | 5421.6258 | 164149.2035 | 59.78 | 742.444
2016-01-21 21:00 | 37689 | 7213.6613 | 145321.4591 | 59.77 | 753.78
2016-01-21 22:00 | 35523 | 8879.2006 | 137170.6791 | 59.79 | 639.414
2016-01-21 23:00 | 33047 | 8613.2474 | 137170.6791 | 59.79 | 594.846
2016-01-22 | 32003 | 10559.7765 | 133860.8691 | 59.79 | 576.054
2016-01-22 01:00 | 31240 | 9717.4695 | 133860.8691 | 59.79 | 562.32
2016-01-22 02:00 | 31126 | 9364.0073 | 133310.1816 | 59.79 | 560.268
2016-01-22 03:00 | 31344 | 9188.4719 | 133310.1816 | 59.79 | 564.192
2016-01-22 04:00 | 32236 | 8921.7772 | 133310.1816 | 59.79 | 580.248
2016-01-22 05:00 | 34929 | 8536.739 | 139640.878 | 59.79 | 628.722
2016-01-22 06:00 | 39527 | 8630.6846 | 151101.468 | 59.77 | 790.54
2016-01-22 07:00 | 41090 | 9605.7001 | 151954.348 | 59.77 | 821.8
2016-01-22 08:00 | 39894 | 10676.6434 | 141761.758 | 59.77 | 797.88
2016-01-22 09:00 | 39233 | 12796.445 | 135321.918 | 59.79 | 706.194
2016-01-22 10:00 | 38845 | 11859.346 | 135321.918 | 59.79 | 699.21
2016-01-22 11:00 | 38353 | 12826.0172 | 134560.5438 | 59.79 | 690.354
2016-01-22 12:00 | 38220 | 12988.8689 | 134560.5438 | 59.79 | 687.96
2016-01-22 13:00 | 38030 | 13552.6963 | 129677.7674 | 59.79 | 684.54
2016-01-22 14:00 | 37827 | 13858.3432 | 129677.7674 | 59.79 | 680.886
2016-01-22 15:00 | 37740 | 14410.2012 | 129677.7674 | 59.79 | 679.32
2016-01-22 16:00 | 37757 | 14496.485 | 129677.7674 | 59.79 | 679.626
2016-01-22 17:00 | 37761 | 14725.9496 | 129677.7674 | 59.79 | 679.698
2016-01-22 18:00 | 38273 | 14940.519 | 129677.7674 | 59.79 | 688.914
2016-01-22 19:00 | 38785 | 14889.8455 | 129677.7674 | 59.79 | 698.13
2016-01-22 20:00 | 38018 | 13293.816 | 129677.7674 | 59.79 | 684.324
2016-01-22 21:00 | 36805 | 12342.4491 | 126070.4474 | 59.79 | 662.49
2016-01-22 22:00 | 35095 | 11807.4171 | 126070.4474 | 59.79 | 631.71
2016-01-22 23:00 | 33017 | 9857.4808 | 126266.2585 | 59.79 | 594.306
2016-01-23 | 33031 | 9490.0665 | 124231.8665 | 59.79 | 594.558
2016-01-23 01:00 | 33131 | 9021.5918 | 124231.8665 | 59.79 | 596.358
2016-01-23 02:00 | 33212 | 8970.9757 | 124782.554 | 59.79 | 597.816
2016-01-23 03:00 | 32818 | 8084.8592 | 130639.874 | 59.79 | 590.724
2016-01-23 04:00 | 32857 | 7029.4218 | 135706.114 | 59.79 | 591.426
2016-01-23 05:00 | 33698 | 7809.3067 | 137269.564 | 59.79 | 606.564
2016-01-23 06:00 | 35338 | 7979.4272 | 137269.564 | 59.79 | 636.084
2016-01-23 07:00 | 37002 | 6316.5499 | 147519.204 | 59.77 | 740.04
2016-01-23 08:00 | 38717 | 4708.4206 | 161885.8984 | 59.78 | 735.623
2016-01-23 09:00 | 40587 | 7628.7702 | 160753.0184 | 59.78 | 771.153
2016-01-23 10:00 | 41901 | 9935.8709 | 158246.1993 | 59.77 | 838.02
2016-01-23 11:00 | 42318 | 12070.8221 | 152711.9593 | 59.77 | 846.36
2016-01-23 12:00 | 42018 | 12893.1478 | 152711.9593 | 59.77 | 840.36
2016-01-23 13:00 | 41754 | 12971.3085 | 149553.5593 | 59.77 | 835.08
2016-01-23 14:00 | 41775 | 13823.6991 | 149553.5593 | 59.77 | 835.5
2016-01-23 15:00 | 41521 | 14643.2175 | 149553.5593 | 59.79 | 747.378
2016-01-23 16:00 | 41572 | 14807.5923 | 149553.5593 | 59.79 | 748.296
2016-01-23 17:00 | 42115 | 14809.7503 | 149553.5593 | 59.79 | 758.07
2016-01-23 18:00 | 43153 | 14483.4543 | 149553.5593 | 59.77 | 863.06
2016-01-23 19:00 | 44191 | 13956.9863 | 149553.5593 | 59.77 | 883.82
2016-01-23 20:00 | 43412 | 12724.9442 | 149553.5593 | 59.77 | 868.24
2016-01-23 21:00 | 42275 | 13091.7886 | 144533.0713 | 59.77 | 845.5
2016-01-23 22:00 | 40607 | 14088.7904 | 134333.1349 | 59.79 | 730.926
2016-01-23 23:00 | 38821 | 13968.4522 | 130242.4867 | 59.79 | 698.778
2016-01-24 | 36883 | 13847.2939 | 128740.8367 | 59.79 | 663.894
2016-01-24 01:00 | 35888 | 13973.9894 | 128740.8367 | 59.79 | 645.984
2016-01-24 02:00 | 35485 | 13371.6471 | 128740.8367 | 59.79 | 638.73
2016-01-24 03:00 | 35290 | 12656.3597 | 128740.8367 | 59.79 | 635.22
2016-01-24 04:00 | 35592 | 12842.1528 | 130885.8367 | 59.79 | 640.656
2016-01-24 05:00 | 36456 | 12330.2983 | 138582.3767 | 59.79 | 656.208
2016-01-24 06:00 | 38069 | 11593.3696 | 134847.1787 | 59.79 | 685.242
2016-01-24 07:00 | 39565 | 11751.9895 | 134847.1787 | 59.77 | 791.3
2016-01-24 08:00 | 41016 | 11988.463 | 140301.1787 | 59.77 | 820.32
2016-01-24 09:00 | 41724 | 11904.2913 | 145551.7551 | 59.77 | 834.48
2016-01-24 10:00 | 41507 | 11252.1011 | 146567.7551 | 59.77 | 830.14
2016-01-24 11:00 | 40910 | 11253.15 | 145551.7551 | 59.77 | 818.2
2016-01-24 12:00 | 40405 | 11026.5513 | 143652.2217 | 59.77 | 808.1
2016-01-24 13:00 | 39868 | 10551.6498 | 146530.6217 | 59.77 | 797.36
2016-01-24 14:00 | 39388 | 10949.4443 | 146530.6217 | 59.77 | 787.76
2016-01-24 15:00 | 39086 | 10554.8447 | 146530.6217 | 59.77 | 781.72
2016-01-24 16:00 | 39632 | 10893.3053 | 146530.6217 | 59.77 | 792.64
2016-01-24 17:00 | 40887 | 12368.5397 | 146530.6217 | 59.77 | 817.74
2016-01-24 18:00 | 43157 | 12154.6466 | 156599.4117 | 59.77 | 863.14
2016-01-24 19:00 | 45428 | 10810.8115 | 174267.2917 | 59.78 | 863.132
2016-01-24 20:00 | 45064 | 8678.6498 | 186217.6877 | 59.78 | 856.216
2016-01-24 21:00 | 44252 | 5869.053 | 187816.6308 | 59.77 | 885.04
2016-01-24 22:00 | 42291 | 6154.3036 | 186217.6877 | 59.78 | 803.529
2016-01-24 23:00 | 39803 | 7150.4701 | 179709.6663 | 59.78 | 756.257
2016-01-25 | 35843 | 7086.4587 | 181211.3163 | 59.77 | 716.86
2016-01-25 01:00 | 35442 | 8131.7478 | 181211.3163 | 59.79 | 637.956
2016-01-25 02:00 | 35534 | 9033.2516 | 181211.3163 | 59.79 | 639.612
2016-01-25 03:00 | 36146 | 8000.0712 | 181211.3163 | 59.77 | 722.92
2016-01-25 04:00 | 37714 | 7662.0504 | 181499.3163 | 59.77 | 754.28
2016-01-25 05:00 | 41411 | 6913.2922 | 191653.5007 | 59.78 | 786.809
2016-01-25 06:00 | 47381 | 5877.1681 | 224539.5371 | 59.77 | 947.62
2016-01-25 07:00 | 49428 | 4550.8769 | 238890.9901 | 59.78 | 939.132
2016-01-25 08:00 | 47478 | 3608.8626 | 237874.9901 | 59.78 | 902.082
2016-01-25 09:00 | 45526 | 4438.4397 | 233383.1911 | 59.77 | 910.52
2016-01-25 10:00 | 43978 | 2429.7672 | 231194.6607 | 59.77 | 879.56
2016-01-25 11:00 | 42605 | 969.3066 | 231194.6607 | 59.77 | 852.1
2016-01-25 12:00 | 41475 | 1299.8833 | 233374.1942 | 59.77 | 829.5
2016-01-25 13:00 | 40702 | 1403.6243 | 233374.1942 | 59.77 | 814.04
2016-01-25 14:00 | 39958 | 1100.4318 | 233374.1942 | 59.77 | 799.16
2016-01-25 15:00 | 39436 | 1028.7157 | 233374.1942 | 59.77 | 788.72
2016-01-25 16:00 | 39774 | 1130.8136 | 233374.1942 | 59.77 | 795.48
2016-01-25 17:00 | 40957 | 798.1996 | 232783.1862 | 59.77 | 819.14
2016-01-25 18:00 | 42815 | 772.3788 | 232783.1862 | 59.77 | 856.3
2016-01-25 19:00 | 44673 | 711.7742 | 233799.1862 | 59.78 | 848.787
2016-01-25 20:00 | 44297 | 1055.988 | 232783.1862 | 59.78 | 841.643
2016-01-25 21:00 | 42902 | 833.4228 | 224468.2212 | 59.77 | 858.04
2016-01-25 22:00 | 40315 | 984.7677 | 210399.7348 | 59.77 | 806.3
2016-01-25 23:00 | 37843 | 1387.7344 | 203340.9348 | 59.78 | 719.017
2016-01-26 | 36747 | 1578.9358 | 199513.2568 | 59.78 | 698.193
2016-01-26 01:00 | 36264 | 1785.3986 | 197125.7568 | 59.78 | 689.016
2016-01-26 02:00 | 36385 | 2474.137 | 197125.7568 | 59.78 | 691.315
2016-01-26 03:00 | 37028 | 3486.0186 | 197125.7568 | 59.78 | 703.532
2016-01-26 04:00 | 38489 | 4763.3287 | 194773.5968 | 59.78 | 731.291
2016-01-26 05:00 | 42133 | 5359.6639 | 201619.0372 | 59.78 | 800.527
2016-01-26 06:00 | 47753 | 5283.4179 | 232256.3582 | 59.77 | 955.06
2016-01-26 07:00 | 49383 | 5720.0579 | 231665.9681 | 59.78 | 938.277
2016-01-26 08:00 | 47122 | 6605.9153 | 220100.4382 | 59.77 | 942.44
2016-01-26 09:00 | 44979 | 7092.0372 | 212119.9472 | 59.77 | 899.58
2016-01-26 10:00 | 43438 | 3773.7107 | 211906.0583 | 59.77 | 868.76
2016-01-26 11:00 | 42135 | 3800.8795 | 205309.5583 | 59.77 | 842.7
2016-01-26 12:00 | 41054 | 4849.3462 | 204617.9583 | 59.78 | 780.026
2016-01-26 13:00 | 40378 | 4717.9667 | 201264.2479 | 59.78 | 767.182
2016-01-26 14:00 | 39702 | 5626.3189 | 179984.5069 | 59.78 | 754.338
2016-01-26 15:00 | 39404 | 7238.216 | 179984.5069 | 59.77 | 788.08
2016-01-26 16:00 | 39686 | 7423.6674 | 179984.5069 | 59.77 | 793.72
2016-01-26 17:00 | 40642 | 7578.4869 | 180575.5149 | 59.78 | 772.198
2016-01-26 18:00 | 42413 | 8753.4038 | 174388.116 | 59.78 | 805.847
2016-01-26 19:00 | 44184 | 10871.0345 | 172138.116 | 59.78 | 839.496
2016-01-26 20:00 | 43966 | 12513.954 | 157113.71 | 59.77 | 879.32
2016-01-26 21:00 | 42596 | 13039.399 | 148838.76 | 59.77 | 851.92
2016-01-26 22:00 | 39933 | 13035.0417 | 136691.0256 | 59.79 | 718.794
2016-01-26 23:00 | 37294 | 11901.6708 | 133381.2156 | 59.79 | 671.292
2016-01-27 | 35235 | 11526.8165 | 133381.2156 | 59.79 | 634.23
2016-01-27 01:00 | 34533 | 11816.1907 | 133381.2156 | 59.79 | 621.594
2016-01-27 02:00 | 34260 | 11106.6982 | 133381.2156 | 59.79 | 616.68
2016-01-27 03:00 | 34406 | 10330.5289 | 135768.7156 | 59.79 | 619.308
2016-01-27 04:00 | 35154 | 10310.1562 | 137836.4676 | 59.79 | 632.772
2016-01-27 05:00 | 37862 | 10246.8689 | 137836.4676 | 59.77 | 757.24
2016-01-27 06:00 | 42428 | 9599.4561 | 163373.382 | 59.78 | 806.132
2016-01-27 07:00 | 43834 | 9742.4234 | 166370.8451 | 59.78 | 832.846
2016-01-27 08:00 | 42658 | 10129.637 | 168091.608 | 59.78 | 810.502
2016-01-27 09:00 | 42333 | 11619.5138 | 165834.9972 | 59.77 | 846.66
2016-01-27 10:00 | 42207 | 13363.8763 | 162363.7661 | 59.77 | 844.14
2016-01-27 11:00 | 41550 | 12098.0365 | 162363.7661 | 59.77 | 831
2016-01-27 12:00 | 40863 | 10155.7381 | 163055.3661 | 59.77 | 817.26
2016-01-27 13:00 | 40326 | 8161.7655 | 163055.3661 | 59.77 | 806.52
2016-01-27 14:00 | 39591 | 6539.9888 | 166292.0361 | 59.78 | 752.229
2016-01-27 15:00 | 39166 | 5604.4911 | 175370.7261 | 59.78 | 744.154
2016-01-27 16:00 | 39543 | 5206.9619 | 172490.3301 | 59.78 | 751.317
2016-01-27 17:00 | 40802 | 5468.6597 | 172580.9232 | 59.78 | 775.238
2016-01-27 18:00 | 41620 | 6789.6616 | 177326.553 | 59.78 | 790.78
2016-01-27 19:00 | 42437 | 8751.1723 | 177326.553 | 59.78 | 806.303
2016-01-27 20:00 | 41632 | 10864.0559 | 157562.173 | 59.77 | 832.64
2016-01-27 21:00 | 40122 | 9194.1286 | 159138.943 | 59.77 | 802.44
2016-01-27 22:00 | 37457 | 7905.4662 | 147741.6386 | 59.77 | 749.14
2016-01-27 23:00 | 34577 | 7582.0191 | 133596.7086 | 59.79 | 622.386
2016-01-28 | 31474 | 7628.5869 | 133596.7086 | 59.79 | 566.532
2016-01-28 01:00 | 30584 | 7184.7275 | 133596.7086 | 59.79 | 550.512
2016-01-28 02:00 | 30163 | 6237.6131 | 134187.7166 | 59.79 | 542.934
2016-01-28 03:00 | 30324 | 6916.7485 | 134187.7166 | 59.79 | 545.832
2016-01-28 04:00 | 31205 | 7176.8406 | 134472.1246 | 59.79 | 561.69
2016-01-28 05:00 | 33826 | 9043.6162 | 134472.1246 | 59.79 | 608.868
2016-01-28 06:00 | 38063 | 9711.5721 | 135246.4546 | 59.77 | 761.26
2016-01-28 07:00 | 39956 | 11409.6142 | 135246.4546 | 59.77 | 799.12
2016-01-28 08:00 | 39430 | 12874.4404 | 135246.4546 | 59.79 | 709.74
2016-01-28 09:00 | 39724 | 15226.6355 | 131436.6546 | 59.79 | 715.032
2016-01-28 10:00 | 40088 | 15551.6874 | 128181.1046 | 59.79 | 721.584
2016-01-28 11:00 | 40075 | 15625.2088 | 128181.1046 | 59.79 | 721.35
2016-01-28 12:00 | 40042 | 15216.53 | 124961.1846 | 59.79 | 720.756
2016-01-28 13:00 | 40097 | 15714.381 | 124961.1846 | 59.79 | 721.746
2016-01-28 14:00 | 39828 | 14622.6691 | 124961.1846 | 59.79 | 716.904
2016-01-28 15:00 | 39945 | 14357.4716 | 124961.1846 | 59.79 | 719.01
2016-01-28 16:00 | 40547 | 14444.019 | 127841.5806 | 59.79 | 729.846
2016-01-28 17:00 | 41724 | 14221.9137 | 129349.9306 | 59.77 | 834.48
2016-01-28 18:00 | 42465 | 15095.1077 | 129349.9306 | 59.79 | 764.37
2016-01-28 19:00 | 43206 | 14934.7524 | 129349.9306 | 59.77 | 864.12
2016-01-28 20:00 | 42552 | 14111.4009 | 129349.9306 | 59.77 | 851.04
2016-01-28 21:00 | 41014 | 12406.1929 | 129349.9306 | 59.77 | 820.28
2016-01-28 22:00 | 38614 | 11738.1983 | 129349.9306 | 59.79 | 695.052
2016-01-28 23:00 | 36073 | 10528.4088 | 129349.9306 | 59.79 | 649.314
2016-01-29 | 33601 | 9512.841 | 129349.9306 | 59.79 | 604.818
2016-01-29 01:00 | 32842 | 8784.6165 | 129349.9306 | 59.79 | 591.156
2016-01-29 02:00 | 32571 | 8048.5496 | 129349.9306 | 59.79 | 586.278
2016-01-29 03:00 | 32836 | 8585.7154 | 129349.9306 | 59.79 | 591.048
2016-01-29 04:00 | 33852 | 7710.5985 | 131606.5414 | 59.79 | 609.336
2016-01-29 05:00 | 36878 | 8124.3879 | 142220.5314 | 59.77 | 737.56
2016-01-29 06:00 | 41550 | 7124.6152 | 173081.9158 | 59.78 | 789.45
2016-01-29 07:00 | 44066 | 6336.2923 | 189575.8618 | 59.77 | 881.32
2016-01-29 08:00 | 43959 | 5665.7635 | 190591.8618 | 59.77 | 879.18
2016-01-29 09:00 | 44619 | 7309.7497 | 189575.8618 | 59.78 | 847.761
2016-01-29 10:00 | 45051 | 7896.4393 | 189575.8618 | 59.78 | 855.969
2016-01-29 11:00 | 44943 | 9277.898 | 189575.8618 | 59.78 | 853.917
2016-01-29 12:00 | 44506 | 10543.4301 | 189575.8618 | 59.78 | 845.614
2016-01-29 13:00 | 44496 | 10667.9186 | 189575.8618 | 59.78 | 845.424
2016-01-29 14:00 | 44619 | 10448.4452 | 188712.5618 | 59.78 | 847.761
2016-01-29 15:00 | 44966 | 10935.3701 | 188712.5618 | 59.78 | 854.354
2016-01-29 16:00 | 45727 | 9776.72 | 188712.5618 | 59.78 | 868.813
2016-01-29 17:00 | 47296 | 9110.687 | 194318.9618 | 59.77 | 945.92
2016-01-29 18:00 | 48611 | 8759.2731 | 204425.3618 | 59.77 | 972.22
2016-01-29 19:00 | 49927 | 7781.7632 | 219521.5102 | 59.77 | 998.54
2016-01-29 20:00 | 49580 | 6806.5978 | 223123.6102 | 59.78 | 942.02
2016-01-29 21:00 | 48644 | 5148.4751 | 224139.6102 | 59.78 | 924.236
2016-01-29 22:00 | 47029 | 4230.682 | 222990.7182 | 59.78 | 893.551
2016-01-29 23:00 | 45225 | 2818.7247 | 221974.7182 | 59.77 | 904.5
2016-01-30 | 45107 | 2691.9926 | 221974.7182 | 59.77 | 902.14
2016-01-30 01:00 | 44523 | 3272.9078 | 221974.7182 | 59.77 | 890.46
2016-01-30 02:00 | 44389 | 3182.9942 | 221974.7182 | 59.77 | 887.78
2016-01-30 03:00 | 44726 | 3307.4119 | 221974.7182 | 59.77 | 894.52
2016-01-30 04:00 | 45374 | 4296.8922 | 221974.7182 | 59.77 | 907.48
2016-01-30 05:00 | 46747 | 4750.4623 | 221974.7182 | 59.77 | 934.94
2016-01-30 06:00 | 48609 | 5214.4467 | 230019.5362 | 59.78 | 923.571
2016-01-30 07:00 | 50327 | 4891.7258 | 243627.3092 | 59.78 | 956.213
2016-01-30 08:00 | 51819 | 4965.2681 | 250124.0772 | 59.78 | 984.561
2016-01-30 09:00 | 52738 | 4119.2138 | 264954.639 | 59.76 | 1107.498
2016-01-30 10:00 | 52263 | 3679.2662 | 264954.639 | 59.76 | 1097.523
2016-01-30 11:00 | 50899 | 2523.0068 | 264954.639 | 59.76 | 1068.879
2016-01-30 12:00 | 49185 | 1770.5958 | 264954.639 | 59.78 | 934.515
2016-01-30 13:00 | 47356 | 1707.5139 | 262698.0282 | 59.78 | 899.764
2016-01-30 14:00 | 46010 | 1432.6361 | 263561.3282 | 59.78 | 874.19
2016-01-30 15:00 | 45710 | 1128.3365 | 263561.3282 | 59.78 | 868.49
2016-01-30 16:00 | 46108 | 1039.561 | 263561.3282 | 59.78 | 876.052
2016-01-30 17:00 | 47273 | 822.0862 | 263561.3282 | 59.78 | 898.187
2016-01-30 18:00 | 48824 | 900.7276 | 263811.863 | 59.76 | 1025.304
2016-01-30 19:00 | 50375 | 1770.7455 | 263624.663 | 59.76 | 1057.875
2016-01-30 20:00 | 50205 | 3068.8122 | 254959.403 | 59.78 | 953.895
2016-01-30 21:00 | 49492 | 3692.1762 | 245927.2932 | 59.78 | 940.348
2016-01-30 22:00 | 47803 | 3938.7474 | 232070.6972 | 59.78 | 908.257
2016-01-30 23:00 | 46307 | 5074.8073 | 228468.5972 | 59.77 | 926.14
2016-01-31 | 46281 | 5487.9274 | 222815.0372 | 59.77 | 925.62
2016-01-31 01:00 | 46254 | 6316.5323 | 222815.0372 | 59.77 | 925.08
2016-01-31 02:00 | 45798 | 6795.2641 | 222815.0372 | 59.77 | 915.96
2016-01-31 03:00 | 45717 | 6546.1001 | 222815.0372 | 59.77 | 914.34
2016-01-31 04:00 | 46068 | 6187.6807 | 222815.0372 | 59.77 | 921.36
2016-01-31 05:00 | 47000 | 5825.3937 | 225857.8452 | 59.77 | 940
2016-01-31 06:00 | 48484 | 5874.4592 | 231051.9536 | 59.78 | 921.196
2016-01-31 07:00 | 49918 | 5509.8943 | 240736.7736 | 59.78 | 948.442
2016-01-31 08:00 | 51449 | 5383.9535 | 249483.5416 | 59.78 | 977.531
2016-01-31 09:00 | 52330 | 5164.8501 | 255642.9364 | 59.78 | 994.27
2016-01-31 10:00 | 52221 | 4346.5398 | 255678.0196 | 59.76 | 1096.641
2016-01-31 11:00 | 51151 | 3611.1331 | 255642.9364 | 59.76 | 1074.171
2016-01-31 12:00 | 50137 | 3977.4177 | 247573.142 | 59.78 | 952.603
2016-01-31 13:00 | 49004 | 4474.315 | 244530.334 | 59.78 | 931.076
2016-01-31 14:00 | 47877 | 5257.7979 | 234202.5292 | 59.78 | 909.663
2016-01-31 15:00 | 47139 | 5656.9806 | 234202.5292 | 59.77 | 942.78
2016-01-31 16:00 | 47183 | 5545.7678 | 237943.2556 | 59.77 | 943.66
2016-01-31 17:00 | 48486 | 5715.4331 | 237943.2556 | 59.78 | 921.234
2016-01-31 18:00 | 50753 | 6669.8329 | 240264.2702 | 59.78 | 964.307
2016-01-31 19:00 | 53021 | 7664.6053 | 240264.2702 | 59.78 | 1007.399
2016-01-31 20:00 | 53039 | 8638.9313 | 235120.8754 | 59.78 | 1007.741
2016-01-31 21:00 | 51803 | 8672.5844 | 228624.1074 | 59.78 | 984.257
2016-01-31 22:00 | 49364 | 8733.7437 | 211668.7994 | 59.77 | 987.28
2016-01-31 23:00 | 46669 | 8456.8066 | 210532.7994 | 59.77 | 933.38
2016-02-01 | 43632 | 7114.4223 | 212221.6494 | 59.78 | 829.008
2016-02-01 01:00 | 42959 | 7001.5961 | 212221.6494 | 59.78 | 816.221
2016-02-01 02:00 | 42822 | 6524.4153 | 212221.6494 | 59.78 | 813.618
2016-02-01 03:00 | 42992 | 5423.3741 | 212221.6494 | 59.77 | 859.84
2016-02-01 04:00 | 44042 | 5463.0105 | 212221.6494 | 59.77 | 880.84
2016-02-01 05:00 | 47016 | 5951.4809 | 215777.6094 | 59.77 | 940.32
2016-02-01 06:00 | 51674 | 5427.0018 | 244033.4798 | 59.78 | 981.806
2016-02-01 07:00 | 53019 | 4836.4803 | 252753.8877 | 59.76 | 1113.399
2016-02-01 08:00 | 51608 | 4499.9657 | 251426.8746 | 59.78 | 980.552
2016-02-01 09:00 | 50862 | 4232.0332 | 250277.9826 | 59.78 | 966.378
2016-02-01 10:00 | 50018 | 3546.51 | 250277.9826 | 59.78 | 950.342
2016-02-01 11:00 | 48814 | 3079.2516 | 250277.9826 | 59.78 | 927.466
2016-02-01 12:00 | 47490 | 2078.1091 | 250277.9826 | 59.78 | 902.31
2016-02-01 13:00 | 46341 | 1423.2332 | 250277.9826 | 59.78 | 880.479
2016-02-01 14:00 | 45256 | 1041.5061 | 250277.9826 | 59.78 | 859.864
2016-02-01 15:00 | 44820 | 853.9003 | 250277.9826 | 59.78 | 851.58
2016-02-01 16:00 | 45368 | 1184.757 | 250277.9826 | 59.78 | 861.992
2016-02-01 17:00 | 46913 | 1127.851 | 250277.9826 | 59.78 | 891.347
2016-02-01 18:00 | 47946 | 972.366 | 251293.9826 | 59.78 | 910.974
2016-02-01 19:00 | 48979 | 1079.8985 | 251876.9257 | 59.76 | 1028.559
2016-02-01 20:00 | 48033 | 2346.1462 | 242884.5878 | 59.78 | 912.627
2016-02-01 21:00 | 46227 | 2848.3919 | 232233.5504 | 59.78 | 878.313
2016-02-01 22:00 | 43080 | 2973.0139 | 219139.0124 | 59.77 | 861.6
2016-02-01 23:00 | 40084 | 2716.8216 | 219780.0124 | 59.78 | 761.596
2016-02-02 | 39956 | 2944.4754 | 216075.0364 | 59.78 | 759.164
2016-02-02 01:00 | 39074 | 2978.8158 | 215958.1564 | 59.78 | 742.406
2016-02-02 02:00 | 38850 | 2577.8527 | 215958.1564 | 59.78 | 738.15
2016-02-02 03:00 | 39037 | 1984.7178 | 212949.5664 | 59.78 | 741.703
2016-02-02 04:00 | 40068 | 1523.8812 | 212949.5664 | 59.77 | 801.36
2016-02-02 05:00 | 43024 | 1463.9697 | 223352.6486 | 59.77 | 860.48
2016-02-02 06:00 | 47792 | 1480.3276 | 248743.2946 | 59.78 | 908.048
2016-02-02 07:00 | 49205 | 2182.5952 | 249172.8544 | 59.78 | 934.895
2016-02-02 08:00 | 47907 | 3507.8114 | 245477.2946 | 59.78 | 910.233
2016-02-02 09:00 | 47521 | 3006.0492 | 246626.1866 | 59.78 | 902.899
2016-02-02 10:00 | 47075 | 1207.8529 | 246626.1866 | 59.78 | 894.425
2016-02-02 11:00 | 46036 | 1152.6942 | 244376.1866 | 59.78 | 874.684
2016-02-02 12:00 | 44938 | 1467.1701 | 244376.1866 | 59.78 | 853.822
2016-02-02 13:00 | 43944 | 1375.7179 | 236661.2424 | 59.78 | 834.936
2016-02-02 14:00 | 42988 | 2069.9553 | 234748.8424 | 59.77 | 859.76
2016-02-02 15:00 | 42448 | 2962.1395 | 234748.8424 | 59.77 | 848.96
2016-02-02 16:00 | 42828 | 3349.1835 | 234748.8424 | 59.77 | 856.56
2016-02-02 17:00 | 44387 | 3432.7443 | 234748.8424 | 59.77 | 887.74
2016-02-02 18:00 | 46221 | 4675.0795 | 234748.8424 | 59.77 | 924.42
2016-02-02 19:00 | 48054 | 4987.6075 | 232547.2424 | 59.78 | 913.026
2016-02-02 20:00 | 47703 | 5094.4185 | 232267.2424 | 59.78 | 906.357
2016-02-02 21:00 | 46286 | 5272.7672 | 222727.6664 | 59.77 | 925.72
2016-02-02 22:00 | 43780 | 5324.557 | 203540.1134 | 59.77 | 875.6
2016-02-02 23:00 | 40978 | 4585.3845 | 196792.6754 | 59.78 | 778.582
2016-02-03 | 37006 | 4793.5019 | 196792.6754 | 59.77 | 740.12
2016-02-03 01:00 | 36433 | 5012.4938 | 195497.0774 | 59.77 | 728.66
2016-02-03 02:00 | 36304 | 4673.1047 | 195497.0774 | 59.77 | 726.08
2016-02-03 03:00 | 36455 | 4649.9263 | 198505.6674 | 59.77 | 729.1
2016-02-03 04:00 | 37594 | 5453.304 | 199694.3282 | 59.77 | 751.88
2016-02-03 05:00 | 40552 | 5441.2151 | 199694.3282 | 59.78 | 770.488
2016-02-03 06:00 | 45123 | 5152.0418 | 211097.7422 | 59.77 | 902.46
2016-02-03 07:00 | 46618 | 5994.0398 | 211741.6222 | 59.77 | 932.36
2016-02-03 08:00 | 45615 | 7242.9453 | 205779.6818 | 59.77 | 912.3
2016-02-03 09:00 | 45523 | 8976.6256 | 191293.0118 | 59.78 | 864.937
2016-02-03 10:00 | 45346 | 10482.0687 | 180250.4668 | 59.78 | 861.574
2016-02-03 11:00 | 44908 | 11947.772 | 169468.0708 | 59.78 | 853.252
2016-02-03 12:00 | 44432 | 11470.5472 | 169468.0708 | 59.78 | 844.208
2016-02-03 13:00 | 44211 | 11889.7509 | 169468.0708 | 59.77 | 884.22
2016-02-03 14:00 | 44062 | 12794.7038 | 162225.6328 | 59.77 | 881.24
2016-02-03 15:00 | 44300 | 13394.2577 | 162225.6328 | 59.77 | 886
2016-02-03 16:00 | 44936 | 13907.8498 | 162225.6328 | 59.77 | 898.72
2016-02-03 17:00 | 46443 | 14744.9957 | 162225.6328 | 59.77 | 928.86
2016-02-03 18:00 | 47083 | 14669.9679 | 164138.0328 | 59.77 | 941.66
2016-02-03 19:00 | 47724 | 14334.8133 | 166619.6328 | 59.78 | 906.756
2016-02-03 20:00 | 46908 | 12752.8343 | 166619.6328 | 59.78 | 891.252
2016-02-03 21:00 | 45114 | 11370.8227 | 166619.6328 | 59.78 | 857.166
2016-02-03 22:00 | 42240 | 9326.9919 | 165100.6328 | 59.78 | 802.56
2016-02-03 23:00 | 39498 | 7325.6119 | 165100.6328 | 59.77 | 789.96
2016-02-04 | 36482 | 5834.8649 | 160836.0728 | 59.77 | 729.64
2016-02-04 01:00 | 35650 | 5310.5206 | 162131.6708 | 59.77 | 713
2016-02-04 02:00 | 35254 | 4079.585 | 162131.6708 | 59.77 | 705.08
2016-02-04 03:00 | 35331 | 3379.2802 | 162131.6708 | 59.77 | 706.62
2016-02-04 04:00 | 36015 | 2797.1636 | 171425.8508 | 59.78 | 684.285
2016-02-04 05:00 | 38349 | 2723.5047 | 183183.2763 | 59.78 | 728.631
2016-02-04 06:00 | 42434 | 3269.8994 | 209372.4947 | 59.77 | 848.68
2016-02-04 07:00 | 44045 | 2490.6649 | 220245.0827 | 59.77 | 880.9
2016-02-04 08:00 | 43331 | 2088.5047 | 221753.4327 | 59.77 | 866.62
2016-02-04 09:00 | 43312 | 1538.2749 | 221753.4327 | 59.77 | 866.24
2016-02-04 10:00 | 43520 | 1300.1481 | 226443.6077 | 59.77 | 870.4
2016-02-04 11:00 | 43414 | 1031.3469 | 226443.6077 | 59.77 | 868.28
2016-02-04 12:00 | 43023 | 874.4783 | 226443.6077 | 59.77 | 860.46
2016-02-04 13:00 | 42716 | 1031.8516 | 226443.6077 | 59.77 | 854.32
2016-02-04 14:00 | 42228 | 1176.126 | 226443.6077 | 59.77 | 844.56
2016-02-04 15:00 | 42038 | 1279.7439 | 226443.6077 | 59.77 | 840.76
2016-02-04 16:00 | 42466 | 1882.1356 | 226443.6077 | 59.77 | 849.32
2016-02-04 17:00 | 43467 | 2109.3408 | 226443.6077 | 59.77 | 869.34
2016-02-04 18:00 | 44211 | 2001.3563 | 226443.6077 | 59.77 | 884.22
2016-02-04 19:00 | 44955 | 1354.3234 | 226440.0808 | 59.78 | 854.145
2016-02-04 20:00 | 44147 | 1570.3421 | 225893.7377 | 59.78 | 838.793
2016-02-04 21:00 | 42474 | 1505.3831 | 214790.5297 | 59.77 | 849.48
2016-02-04 22:00 | 39823 | 2144.255 | 191592.2813 | 59.77 | 796.46
2016-02-04 23:00 | 37128 | 2646.2208 | 173917.8513 | 59.78 | 705.432
2016-02-05 | 36441 | 2967.1119 | 171923.5113 | 59.78 | 692.379
2016-02-05 01:00 | 35503 | 3313.7991 | 166903.0233 | 59.77 | 710.06
2016-02-05 02:00 | 35250 | 3733.6737 | 166903.0233 | 59.77 | 705
2016-02-05 03:00 | 35491 | 4796.5925 | 166903.0233 | 59.77 | 709.82
2016-02-05 04:00 | 36456 | 6093.4779 | 166903.0233 | 59.77 | 729.12
2016-02-05 05:00 | 39205 | 6759.1221 | 169929.1838 | 59.77 | 784.1
2016-02-05 06:00 | 43586 | 7177.2921 | 183350.9438 | 59.78 | 828.134
2016-02-05 07:00 | 44940 | 7413.5117 | 188837.6138 | 59.77 | 898.8
2016-02-05 08:00 | 43935 | 7883.8504 | 188837.6138 | 59.78 | 834.765
2016-02-05 09:00 | 43407 | 6788.9322 | 186933.6138 | 59.78 | 824.733
2016-02-05 10:00 | 42646 | 6973.2921 | 186933.6138 | 59.78 | 810.274
2016-02-05 11:00 | 41403 | 4486.333 | 192394.0942 | 59.78 | 786.657
2016-02-05 12:00 | 40093 | 3401.5451 | 192394.0942 | 59.78 | 761.767
2016-02-05 13:00 | 39180 | 3073.116 | 192394.0942 | 59.78 | 744.42
2016-02-05 14:00 | 38244 | 3588.115 | 189961.0942 | 59.78 | 726.636
2016-02-05 15:00 | 37616 | 4029.6117 | 189961.0942 | 59.78 | 714.704
2016-02-05 16:00 | 37371 | 3651.2065 | 189961.0942 | 59.78 | 710.049
2016-02-05 17:00 | 37869 | 3571.4549 | 189961.0942 | 59.78 | 719.511
2016-02-05 18:00 | 39255 | 2781.2345 | 197905.3822 | 59.78 | 745.845
2016-02-05 19:00 | 40642 | 2266.6389 | 207482.5902 | 59.77 | 812.84
2016-02-05 20:00 | 40288 | 2098.0656 | 207482.5902 | 59.77 | 805.76
2016-02-05 21:00 | 39693 | 1639.4223 | 207482.5902 | 59.77 | 793.86
2016-02-05 22:00 | 38496 | 1505.8417 | 207482.5902 | 59.78 | 731.424
2016-02-05 23:00 | 36982 | 1397.1698 | 205000.9902 | 59.78 | 702.658
2016-02-06 | 37231 | 2001.5938 | 201781.0702 | 59.78 | 707.389
2016-02-06 01:00 | 38031 | 2725.2148 | 201567.1813 | 59.78 | 722.589
2016-02-06 02:00 | 38696 | 3038.0968 | 201567.1813 | 59.78 | 735.224
2016-02-06 03:00 | 38973 | 3534.8927 | 201567.1813 | 59.78 | 740.487
2016-02-06 04:00 | 39913 | 3720.2908 | 202934.9693 | 59.78 | 758.347
2016-02-06 05:00 | 41616 | 4150.8387 | 210829.0791 | 59.78 | 790.704
2016-02-06 06:00 | 43915 | 3600.8197 | 223656.7391 | 59.77 | 878.3
2016-02-06 07:00 | 45664 | 2527.2089 | 238678.0761 | 59.78 | 867.616
2016-02-06 08:00 | 46551 | 1972.1393 | 245827.6541 | 59.78 | 884.469
2016-02-06 09:00 | 46362 | 1533.965 | 244448.3709 | 59.78 | 880.878
2016-02-06 10:00 | 45585 | 1098.1964 | 243366.5641 | 59.78 | 866.115
2016-02-06 11:00 | 44229 | 1133.3225 | 237137.2061 | 59.78 | 840.351
2016-02-06 12:00 | 42812 | 1442.4207 | 235381.6581 | 59.77 | 856.24
2016-02-06 13:00 | 41325 | 1434.4647 | 227487.5483 | 59.77 | 826.5
2016-02-06 14:00 | 40157 | 1176.6376 | 218822.2883 | 59.77 | 803.14
2016-02-06 15:00 | 39601 | 1508.9004 | 218822.2883 | 59.77 | 792.02
2016-02-06 16:00 | 39680 | 1608.4303 | 218822.2883 | 59.77 | 793.6
2016-02-06 17:00 | 40717 | 1698.2567 | 218822.2883 | 59.77 | 814.34
2016-02-06 18:00 | 42629 | 2108.317 | 218822.2883 | 59.77 | 852.58
2016-02-06 19:00 | 44541 | 3363.8183 | 220981.6883 | 59.77 | 890.82
2016-02-06 20:00 | 44309 | 5387.9015 | 206298.7175 | 59.77 | 886.18
2016-02-06 21:00 | 43585 | 7069.5847 | 188333.5025 | 59.78 | 828.115
2016-02-06 22:00 | 42313 | 7557.9505 | 180637.6041 | 59.78 | 803.947
2016-02-06 23:00 | 40759 | 6975.9017 | 183119.2041 | 59.78 | 774.421
2016-02-07 | 39945 | 5808.5206 | 183119.2041 | 59.78 | 758.955
2016-02-07 01:00 | 39225 | 5179.3535 | 183333.093 | 59.78 | 745.275
2016-02-07 02:00 | 38817 | 5117.5479 | 183333.093 | 59.78 | 737.523
2016-02-07 03:00 | 38798 | 4904.9069 | 183333.093 | 59.78 | 737.162
2016-02-07 04:00 | 39058 | 4793.7267 | 183720.853 | 59.78 | 742.102
2016-02-07 05:00 | 39954 | 4928.0374 | 183720.853 | 59.78 | 759.126
2016-02-07 06:00 | 41449 | 4484.2115 | 189373.773 | 59.78 | 787.531
2016-02-07 07:00 | 42952 | 4610.9254 | 198740.761 | 59.77 | 859.04
2016-02-07 08:00 | 44675 | 4916.4943 | 203219.3858 | 59.77 | 893.5
2016-02-07 09:00 | 45986 | 5755.881 | 205552.4758 | 59.77 | 919.72
2016-02-07 10:00 | 46239 | 6586.4173 | 205552.4758 | 59.77 | 924.78
2016-02-07 11:00 | 45937 | 7836.1979 | 197756.5758 | 59.77 | 918.74
2016-02-07 12:00 | 45629 | 8570.7675 | 193256.5758 | 59.78 | 866.951
2016-02-07 13:00 | 45310 | 7853.0622 | 192393.2758 | 59.78 | 860.89
2016-02-07 14:00 | 45050 | 8008.4742 | 189156.6058 | 59.78 | 855.95
2016-02-07 15:00 | 44878 | 8264.929 | 185800.2058 | 59.78 | 852.682
2016-02-07 16:00 | 45113 | 8832.1877 | 185800.2058 | 59.78 | 857.147
2016-02-07 17:00 | 46060 | 10459.7438 | 182215.9358 | 59.78 | 875.14
2016-02-07 18:00 | 46599 | 12677.4252 | 176609.5358 | 59.78 | 885.381
2016-02-07 19:00 | 47138 | 12650.8952 | 176609.5358 | 59.78 | 895.622
2016-02-07 20:00 | 46326 | 12187.0668 | 176609.5358 | 59.78 | 880.194
2016-02-07 21:00 | 46067 | 11142.615 | 176609.5358 | 59.78 | 875.273
2016-02-07 22:00 | 43631 | 10572.4672 | 166701.3498 | 59.78 | 828.989
2016-02-07 23:00 | 40500 | 9445.361 | 162960.6234 | 59.77 | 810
2016-02-08 | 36651 | 7805.6283 | 162960.6234 | 59.77 | 733.02
2016-02-08 01:00 | 35646 | 6122.7735 | 162960.6234 | 59.77 | 712.92
2016-02-08 02:00 | 35285 | 5568.4638 | 162960.6234 | 59.77 | 705.7
2016-02-08 03:00 | 35354 | 5617.6187 | 162960.6234 | 59.77 | 707.08
2016-02-08 04:00 | 36311 | 6187.8776 | 162960.6234 | 59.77 | 726.22
2016-02-08 05:00 | 39143 | 6854.918 | 166317.0234 | 59.77 | 782.86
2016-02-08 06:00 | 43637 | 7240.7123 | 187318.2794 | 59.78 | 829.103
2016-02-08 07:00 | 45288 | 7643.7035 | 192554.2794 | 59.77 | 905.76
2016-02-08 08:00 | 44692 | 8533.608 | 191818.2794 | 59.78 | 849.148
2016-02-08 09:00 | 44817 | 8546.93 | 191818.2794 | 59.78 | 851.523
2016-02-08 10:00 | 45129 | 8212.1933 | 191818.2794 | 59.78 | 857.451
2016-02-08 11:00 | 45034 | 8287.1542 | 197364.1794 | 59.78 | 855.646
2016-02-08 12:00 | 44742 | 8296.6606 | 197364.1794 | 59.78 | 850.098
2016-02-08 13:00 | 44551 | 7839.2352 | 198227.4794 | 59.78 | 846.469
2016-02-08 14:00 | 44178 | 7665.3487 | 198227.4794 | 59.78 | 839.382
2016-02-08 15:00 | 44181 | 9065.5567 | 196708.4794 | 59.78 | 839.439
2016-02-08 16:00 | 44765 | 8699.1053 | 196708.4794 | 59.78 | 850.535
2016-02-08 17:00 | 46134 | 9492.4629 | 196708.4794 | 59.78 | 876.546
2016-02-08 18:00 | 47475 | 10336.2419 | 196708.4794 | 59.78 | 902.025
2016-02-08 19:00 | 48816 | 10303.2828 | 196708.4794 | 59.77 | 976.32
2016-02-08 20:00 | 48401 | 9784.793 | 195845.1794 | 59.77 | 968.02
2016-02-08 21:00 | 47191 | 9004.4148 | 195845.1794 | 59.77 | 943.82
2016-02-08 22:00 | 44661 | 7145.8265 | 193595.1794 | 59.77 | 893.22
2016-02-08 23:00 | 42211 | 6697.6236 | 190238.7794 | 59.78 | 802.009
2016-02-09 | 38825 | 7153.1813 | 190238.7794 | 59.77 | 776.5
2016-02-09 01:00 | 38561 | 7741.9278 | 190238.7794 | 59.77 | 771.22
2016-02-09 02:00 | 38903 | 8238.2008 | 190238.7794 | 59.77 | 778.06
2016-02-09 03:00 | 39591 | 8090.0158 | 190238.7794 | 59.77 | 791.82
2016-02-09 04:00 | 41271 | 6764.5566 | 190238.7794 | 59.78 | 784.149
2016-02-09 05:00 | 44953 | 5462.8792 | 205741.7252 | 59.77 | 899.06
2016-02-09 06:00 | 50434 | 4466.5348 | 245426.0526 | 59.78 | 958.246
2016-02-09 07:00 | 52051 | 3897.7462 | 251585.4474 | 59.76 | 1093.071
2016-02-09 08:00 | 50395 | 3092.2117 | 251585.4474 | 59.78 | 957.505
2016-02-09 09:00 | 49173 | 3383.3038 | 250569.4474 | 59.78 | 934.287
2016-02-09 10:00 | 48046 | 3185.762 | 250569.4474 | 59.78 | 912.874
2016-02-09 11:00 | 46820 | 2348.7473 | 250569.4474 | 59.78 | 889.58
2016-02-09 12:00 | 45385 | 1647.4814 | 250569.4474 | 59.78 | 862.315
2016-02-09 13:00 | 43989 | 1303.0751 | 247997.898 | 59.78 | 835.791
2016-02-09 14:00 | 42619 | 1302.5699 | 247997.898 | 59.77 | 852.38
2016-02-09 15:00 | 41774 | 1319.7314 | 246809.2372 | 59.77 | 835.48
2016-02-09 16:00 | 42412 | 1253.1933 | 246809.2372 | 59.77 | 848.24
2016-02-09 17:00 | 44047 | 1428.6861 | 248328.2372 | 59.78 | 836.893
2016-02-09 18:00 | 46830 | 2134.1046 | 248328.2372 | 59.78 | 889.77
2016-02-09 19:00 | 49612 | 2884.1886 | 249344.2372 | 59.78 | 942.628
2016-02-09 20:00 | 50034 | 3940.4573 | 247197.9872 | 59.78 | 950.646
2016-02-09 21:00 | 49216 | 3787.238 | 242054.5924 | 59.78 | 935.104
2016-02-09 22:00 | 46627 | 4239.2668 | 221512.6664 | 59.77 | 932.54
2016-02-09 23:00 | 44235 | 4355.863 | 211566.768 | 59.77 | 884.7
2016-02-10 | 42266 | 4907.5775 | 210948.768 | 59.78 | 803.054
2016-02-10 01:00 | 41668 | 5344.8019 | 210948.768 | 59.78 | 791.692
2016-02-10 02:00 | 41558 | 5945.6024 | 210948.768 | 59.78 | 789.602
2016-02-10 03:00 | 41901 | 7081.9034 | 210948.768 | 59.78 | 796.119
2016-02-10 04:00 | 43133 | 7494.9739 | 209013.1544 | 59.78 | 819.527
2016-02-10 05:00 | 46247 | 6661.471 | 208393.7844 | 59.77 | 924.94
2016-02-10 06:00 | 50974 | 6776.173 | 232246.9828 | 59.78 | 968.506
2016-02-10 07:00 | 52039 | 6491.8732 | 232561.6925 | 59.78 | 988.741
2016-02-10 08:00 | 50333 | 6725.0556 | 227764.7378 | 59.78 | 956.327
2016-02-10 09:00 | 49310 | 6837.8708 | 222343.5178 | 59.77 | 986.2
2016-02-10 10:00 | 48530 | 7680.857 | 215073.0298 | 59.77 | 970.6
2016-02-10 11:00 | 47738 | 9030.9934 | 215073.0298 | 59.77 | 954.76
2016-02-10 12:00 | 46921 | 8108.6965 | 215073.0298 | 59.77 | 938.42
2016-02-10 13:00 | 46359 | 6423.4683 | 215073.0298 | 59.77 | 927.18
2016-02-10 14:00 | 45795 | 7183.4493 | 215073.0298 | 59.77 | 915.9
2016-02-10 15:00 | 45896 | 6711.9746 | 216261.6906 | 59.77 | 917.92
2016-02-10 16:00 | 46934 | 6407.8302 | 216261.6906 | 59.77 | 938.68
2016-02-10 17:00 | 48714 | 7593.1762 | 216261.6906 | 59.77 | 974.28
2016-02-10 18:00 | 49897 | 8112.4708 | 217588.7037 | 59.77 | 997.94
2016-02-10 19:00 | 51080 | 8830.1803 | 217743.7537 | 59.77 | 1021.6
2016-02-10 20:00 | 50304 | 9398.4173 | 212286.2606 | 59.77 | 1006.08
2016-02-10 21:00 | 48772 | 9366.845 | 201421.5026 | 59.77 | 975.44
2016-02-10 22:00 | 45396 | 7197.2795 | 201421.5026 | 59.77 | 907.92
2016-02-10 23:00 | 42798 | 6805.4744 | 201421.5026 | 59.78 | 813.162
2016-02-11 | 38985 | 6912.9782 | 194770.808 | 59.77 | 779.7
2016-02-11 01:00 | 38678 | 5490.1686 | 194897.288 | 59.78 | 734.882
2016-02-11 02:00 | 38182 | 4671.2972 | 194897.288 | 59.78 | 725.458
2016-02-11 03:00 | 38499 | 4080.2924 | 194897.288 | 59.78 | 731.481
2016-02-11 04:00 | 39725 | 3172.1618 | 196832.9016 | 59.78 | 754.775
2016-02-11 05:00 | 42516 | 2450.3511 | 210546.8096 | 59.77 | 850.32
2016-02-11 06:00 | 46847 | 2193.3725 | 236687.8386 | 59.78 | 890.093
2016-02-11 07:00 | 48340 | 2057.7389 | 244503.6728 | 59.78 | 918.46
2016-02-11 08:00 | 47488 | 2209.3734 | 240947.1828 | 59.78 | 902.272
2016-02-11 09:00 | 47461 | 2603.696 | 241519.6828 | 59.78 | 901.759
2016-02-11 10:00 | 47427 | 3227.6038 | 241519.6828 | 59.78 | 901.113
2016-02-11 11:00 | 47435 | 3249.3891 | 241519.6828 | 59.78 | 901.265
2016-02-11 12:00 | 47231 | 2813.7419 | 241519.6828 | 59.78 | 897.389
2016-02-11 13:00 | 47017 | 1292.1082 | 247703.3428 | 59.78 | 893.323
2016-02-11 14:00 | 46678 | 777.3477 | 251141.9032 | 59.78 | 886.882
2016-02-11 15:00 | 46606 | 947.0921 | 252897.4512 | 59.78 | 885.514
2016-02-11 16:00 | 47290 | 1165.1158 | 252897.4512 | 59.78 | 898.51
2016-02-11 17:00 | 48503 | 1489.4608 | 255797.4512 | 59.78 | 921.557
2016-02-11 18:00 | 49292 | 2497.8042 | 254781.4512 | 59.78 | 936.548
2016-02-11 19:00 | 50082 | 2216.0148 | 255865.4378 | 59.76 | 1051.722
2016-02-11 20:00 | 49031 | 2205.005 | 251315.2062 | 59.78 | 931.589
2016-02-11 21:00 | 47282 | 1824.2215 | 242649.9462 | 59.78 | 898.358
2016-02-11 22:00 | 44633 | 1741.4653 | 230480.4416 | 59.78 | 848.027
2016-02-11 23:00 | 42316 | 1771.4801 | 228724.8936 | 59.77 | 846.32
2016-02-12 | 41431 | 1466.8181 | 231045.9082 | 59.77 | 828.62
2016-02-12 01:00 | 40594 | 1666.5227 | 231045.9082 | 59.77 | 811.88
2016-02-12 02:00 | 40421 | 1578.341 | 231045.9082 | 59.77 | 808.42
2016-02-12 03:00 | 40526 | 2026.0861 | 231045.9082 | 59.77 | 810.52
2016-02-12 04:00 | 41608 | 3075.5023 | 231045.9082 | 59.77 | 832.16
2016-02-12 05:00 | 43951 | 3289.854 | 231045.9082 | 59.77 | 879.02
2016-02-12 06:00 | 47452 | 3652.1917 | 232103.4576 | 59.78 | 901.588
2016-02-12 07:00 | 48596 | 3971.8426 | 232292.9575 | 59.78 | 923.324
2016-02-12 08:00 | 48162 | 4781.9768 | 228880.2496 | 59.78 | 915.078
2016-02-12 09:00 | 47923 | 3908.5157 | 233827.9296 | 59.78 | 910.537
2016-02-12 10:00 | 47224 | 2426.6365 | 234563.9296 | 59.78 | 897.256
2016-02-12 11:00 | 46382 | 2180.8885 | 231109.9696 | 59.78 | 881.258
2016-02-12 12:00 | 45434 | 1585.1206 | 230373.9696 | 59.78 | 863.246
2016-02-12 13:00 | 44653 | 1336.7306 | 229812.7616 | 59.78 | 848.407
2016-02-12 14:00 | 43781 | 1069.2114 | 228873.2122 | 59.78 | 831.839
2016-02-12 15:00 | 43224 | 1215.5124 | 228585.2122 | 59.77 | 864.48
2016-02-12 16:00 | 43163 | 1279.6976 | 228585.2122 | 59.77 | 863.26
2016-02-12 17:00 | 44016 | 1197.3046 | 228585.2122 | 59.78 | 836.304
2016-02-12 18:00 | 45334 | 1323.926 | 228585.2122 | 59.78 | 861.346
2016-02-12 19:00 | 46651 | 2341.9733 | 228585.2122 | 59.78 | 886.369
2016-02-12 20:00 | 46325 | 3788.3229 | 217482.0042 | 59.78 | 880.175
2016-02-12 21:00 | 45566 | 3928.8757 | 211629.9042 | 59.77 | 911.32
2016-02-12 22:00 | 43918 | 5838.3795 | 189091.1038 | 59.77 | 878.36
2016-02-12 23:00 | 43531 | 8655.4639 | 189091.1038 | 59.78 | 827.089
2016-02-13 | 43731 | 9065.0588 | 187178.7038 | 59.78 | 830.889
2016-02-13 01:00 | 44231 | 9624.8626 | 187178.7038 | 59.78 | 840.389
2016-02-13 02:00 | 45052 | 10241.4457 | 187178.7038 | 59.78 | 855.988
2016-02-13 03:00 | 45234 | 10056.119 | 187178.7038 | 59.78 | 859.446
2016-02-13 04:00 | 45897 | 9919.728 | 187178.7038 | 59.78 | 872.043
2016-02-13 05:00 | 47293 | 10483.3198 | 190650.9938 | 59.78 | 898.567
2016-02-13 06:00 | 49097 | 10121.616 | 200355.4438 | 59.77 | 981.94
2016-02-13 07:00 | 50631 | 9839.8291 | 208209.1542 | 59.77 | 1012.62
2016-02-13 08:00 | 51624 | 9854.1918 | 218543.4992 | 59.77 | 1032.48
2016-02-13 09:00 | 51695 | 8852.6439 | 227290.2672 | 59.78 | 982.205
2016-02-13 10:00 | 50683 | 7370.3296 | 227910.6752 | 59.78 | 962.977
2016-02-13 11:00 | 48579 | 5869.2621 | 226987.4752 | 59.78 | 923.001
2016-02-13 12:00 | 46199 | 4367.7688 | 225745.7452 | 59.77 | 923.98
2016-02-13 13:00 | 43841 | 4086.6808 | 224179.8752 | 59.77 | 876.82
2016-02-13 14:00 | 41811 | 3924.9072 | 224797.8752 | 59.77 | 836.22
2016-02-13 15:00 | 40378 | 3888.1873 | 225085.8752 | 59.78 | 767.182
2016-02-13 16:00 | 40020 | 4505.5462 | 225085.8752 | 59.78 | 760.38
2016-02-13 17:00 | 41053 | 4779.4808 | 225085.8752 | 59.78 | 780.007
2016-02-13 18:00 | 43321 | 4166.9003 | 225085.8752 | 59.77 | 866.42
2016-02-13 19:00 | 45588 | 3286.2631 | 225085.8752 | 59.77 | 911.76
2016-02-13 20:00 | 45662 | 3154.1842 | 225085.8752 | 59.78 | 867.578
2016-02-13 21:00 | 45136 | 2432.1393 | 225821.8752 | 59.78 | 857.584
2016-02-13 22:00 | 43994 | 2675.6545 | 222043.0672 | 59.77 | 879.88
2016-02-13 23:00 | 42539 | 2830.5104 | 208814.0542 | 59.77 | 850.78
2016-02-14 | 42331 | 3822.3302 | 201413.8042 | 59.77 | 846.62
2016-02-14 01:00 | 42318 | 4790.8616 | 201510.5546 | 59.77 | 846.36
2016-02-14 02:00 | 42109 | 4475.8481 | 201510.5546 | 59.77 | 842.18
2016-02-14 03:00 | 42220 | 5758.5457 | 201510.5546 | 59.78 | 802.18
2016-02-14 04:00 | 42801 | 6447.8541 | 198865.7746 | 59.78 | 813.219
2016-02-14 05:00 | 43904 | 6735.3652 | 198865.7746 | 59.78 | 834.176
2016-02-14 06:00 | 45538 | 6784.4856 | 202286.5246 | 59.77 | 910.76
2016-02-14 07:00 | 46652 | 6441.379 | 204978.3346 | 59.77 | 933.04
2016-02-14 08:00 | 47281 | 6474.4641 | 206340.0143 | 59.77 | 945.62
2016-02-14 09:00 | 46687 | 5924.3996 | 206082.9445 | 59.77 | 933.74
2016-02-14 10:00 | 45654 | 7229.4836 | 193690.8362 | 59.77 | 913.08
2016-02-14 11:00 | 44567 | 9178.8758 | 177032.4062 | 59.78 | 846.773
2016-02-14 12:00 | 44062 | 11470.0414 | 177032.4062 | 59.78 | 837.178
2016-02-14 13:00 | 43734 | 12592.9513 | 177032.4062 | 59.77 | 874.68
2016-02-14 14:00 | 43447 | 12749.0874 | 177032.4062 | 59.77 | 868.94
2016-02-14 15:00 | 43678 | 12851.428 | 177032.4062 | 59.77 | 873.56
2016-02-14 16:00 | 44521 | 13124.201 | 177032.4062 | 59.77 | 890.42
2016-02-14 17:00 | 45973 | 12538.4564 | 177032.4062 | 59.78 | 873.487
2016-02-14 18:00 | 47840 | 12145.8104 | 187766.5742 | 59.78 | 908.96
2016-02-14 19:00 | 49707 | 9611.971 | 204425.0042 | 59.77 | 994.14
2016-02-14 20:00 | 49852 | 6266.3443 | 221396.8146 | 59.78 | 947.188
2016-02-14 21:00 | 49341 | 5263.3848 | 221979.7577 | 59.78 | 937.479
2016-02-14 22:00 | 47788 | 4463.991 | 220096.2436 | 59.78 | 907.972
2016-02-14 23:00 | 46130 | 4679.8637 | 220096.2436 | 59.77 | 922.6
2016-02-15 | 41098 | 5240.1004 | 220283.4436 | 59.78 | 780.862
2016-02-15 01:00 | 41118 | 5874.7513 | 220283.4436 | 59.78 | 781.242
2016-02-15 02:00 | 41511 | 6866.3291 | 220283.4436 | 59.78 | 788.709
2016-02-15 03:00 | 42187 | 6664.844 | 220283.4436 | 59.78 | 801.553
2016-02-15 04:00 | 43686 | 6687.9146 | 222928.2236 | 59.78 | 830.034
2016-02-15 05:00 | 46638 | 6706.1944 | 222928.2236 | 59.77 | 932.76
2016-02-15 06:00 | 50911 | 7447.8618 | 222928.2236 | 59.78 | 967.309
2016-02-15 07:00 | 52535 | 7734.1953 | 224527.1667 | 59.78 | 998.165
2016-02-15 08:00 | 51412 | 8536.669 | 220446.6236 | 59.78 | 976.828
2016-02-15 09:00 | 50419 | 8535.1558 | 214594.5236 | 59.77 | 1008.38
2016-02-15 10:00 | 49308 | 6933.0208 | 215610.5236 | 59.77 | 986.16
2016-02-15 11:00 | 47762 | 6582.8591 | 214594.5236 | 59.77 | 955.24
2016-02-15 12:00 | 46070 | 6914.7609 | 213182.5398 | 59.77 | 921.4
2016-02-15 13:00 | 44531 | 7181.1124 | 213182.5398 | 59.78 | 846.089
2016-02-15 14:00 | 43051 | 6557.6257 | 213182.5398 | 59.78 | 817.969
2016-02-15 15:00 | 42067 | 5630.8447 | 212490.9398 | 59.78 | 799.273
2016-02-15 16:00 | 42350 | 4634.7482 | 210989.2898 | 59.77 | 847
2016-02-15 17:00 | 43390 | 3642.1082 | 210989.2898 | 59.77 | 867.8
2016-02-15 18:00 | 45929 | 2112.7704 | 233162.4402 | 59.78 | 872.651
2016-02-15 19:00 | 48467 | 1796.1274 | 247150.2606 | 59.78 | 920.873
2016-02-15 20:00 | 48735 | 1606.8065 | 247150.2606 | 59.78 | 925.965
2016-02-15 21:00 | 48133 | 1150.2867 | 247150.2606 | 59.78 | 914.527
2016-02-15 22:00 | 46115 | 836.7843 | 247434.8316 | 59.78 | 876.185
2016-02-15 23:00 | 43955 | 700.9116 | 247434.8316 | 59.78 | 835.145
2016-02-16 | 43670 | 980.9412 | 244078.4316 | 59.78 | 829.73
2016-02-16 01:00 | 43467 | 1249.1997 | 244078.4316 | 59.77 | 869.34
2016-02-16 02:00 | 43928 | 1365.8291 | 244078.4316 | 59.78 | 834.632
2016-02-16 03:00 | 44659 | 1589.1872 | 244078.4316 | 59.78 | 848.521
2016-02-16 04:00 | 46201 | 1631.5801 | 254495.6425 | 59.78 | 877.819
2016-02-16 05:00 | 49606 | 1497.1295 | 265251.7925 | 59.76 | 1041.726
2016-02-16 06:00 | 54495 | 1292.6409 | 277302.553 | 59.75 | 1198.89
2016-02-16 07:00 | 55171 | 1311.5087 | 277801.6162 | 59.75 | 1213.762
2016-02-16 08:00 | 52091 | 1501.5577 | 273437.9953 | 59.76 | 1093.911
2016-02-16 09:00 | 49168 | 1516.7687 | 259128.6255 | 59.76 | 1032.528
2016-02-16 10:00 | 46845 | 666.8371 | 252631.8575 | 59.78 | 890.055
2016-02-16 11:00 | 44709 | 650.6058 | 252631.8575 | 59.78 | 849.471
2016-02-16 12:00 | 42972 | 687.3419 | 239543.0969 | 59.77 | 859.44
2016-02-16 13:00 | 41672 | 948.5973 | 234869.6669 | 59.77 | 833.44
2016-02-16 14:00 | 40473 | 1188.9127 | 234869.6669 | 59.77 | 809.46
2016-02-16 15:00 | 39793 | 1960.6106 | 233106.8669 | 59.77 | 795.86
2016-02-16 16:00 | 39920 | 1588.2891 | 234608.5169 | 59.77 | 798.4
2016-02-16 17:00 | 41164 | 1272.8079 | 234608.5169 | 59.77 | 823.28
2016-02-16 18:00 | 44031 | 1103.4318 | 234608.5169 | 59.78 | 836.589
2016-02-16 19:00 | 46898 | 1280.2505 | 243676.8343 | 59.78 | 891.062
2016-02-16 20:00 | 47388 | 1719.7635 | 243676.8343 | 59.78 | 900.372
2016-02-16 21:00 | 46809 | 1907.6416 | 243676.8343 | 59.78 | 889.371
2016-02-16 22:00 | 44737 | 1535.2002 | 243618.8443 | 59.78 | 850.003
2016-02-16 23:00 | 42757 | 1286.0039 | 241266.6843 | 59.77 | 855.14
2016-02-17 | 41851 | 1362.6516 | 241266.6843 | 59.77 | 837.02
2016-02-17 01:00 | 41670 | 1201.4707 | 241266.6843 | 59.77 | 833.4
2016-02-17 02:00 | 42100 | 1217.6114 | 241266.6843 | 59.77 | 842
2016-02-17 03:00 | 42890 | 1404.8179 | 240945.1349 | 59.77 | 857.8
2016-02-17 04:00 | 44588 | 1544.6086 | 249195.4288 | 59.78 | 847.172
2016-02-17 05:00 | 48184 | 1448.6839 | 268113.5448 | 59.78 | 915.496
2016-02-17 06:00 | 53606 | 1676.1683 | 275620.1758 | 59.76 | 1125.726
2016-02-17 07:00 | 54289 | 2337.3495 | 274169.2056 | 59.76 | 1140.069
2016-02-17 08:00 | 50832 | 3578.099 | 265162.35 | 59.78 | 965.808
2016-02-17 09:00 | 47886 | 4380.8337 | 245057.809 | 59.78 | 909.834
2016-02-17 10:00 | 45448 | 3200.3577 | 234185.221 | 59.77 | 908.96
2016-02-17 11:00 | 43297 | 3208.1671 | 226942.783 | 59.77 | 865.94
2016-02-17 12:00 | 41459 | 3192.4269 | 224660.0226 | 59.77 | 829.18
2016-02-17 13:00 | 40234 | 3047.6435 | 201968.9566 | 59.78 | 764.446
2016-02-17 14:00 | 39075 | 3096.0591 | 201968.9566 | 59.78 | 742.425
2016-02-17 15:00 | 38523 | 3003.4072 | 204423.3566 | 59.78 | 731.937
2016-02-17 16:00 | 38796 | 3035.2533 | 201425.1566 | 59.78 | 737.124
2016-02-17 17:00 | 39990 | 3227.9405 | 201425.1566 | 59.78 | 759.81
2016-02-17 18:00 | 42202 | 3970.1498 | 201425.1566 | 59.77 | 844.04
2016-02-17 19:00 | 44414 | 5528.1946 | 201425.1566 | 59.77 | 888.28
2016-02-17 20:00 | 45011 | 7637.3193 | 192465.0462 | 59.78 | 855.209
2016-02-17 21:00 | 44690 | 10227.7039 | 179577.0702 | 59.78 | 849.11
2016-02-17 22:00 | 42661 | 10817.0756 | 172173.3402 | 59.77 | 853.22
2016-02-17 23:00 | 40486 | 11279.2316 | 173751.1702 | 59.77 | 809.72
2016-02-18 | 37431 | 10891.4084 | 172602.2782 | 59.79 | 673.758
2016-02-18 01:00 | 37208 | 10789.5497 | 172602.2782 | 59.79 | 669.744
2016-02-18 02:00 | 37479 | 11047.3556 | 172602.2782 | 59.79 | 674.622
2016-02-18 03:00 | 38141 | 11145.2234 | 172602.2782 | 59.79 | 686.538
2016-02-18 04:00 | 39536 | 11246.4797 | 172602.2782 | 59.77 | 790.72
2016-02-18 05:00 | 43097 | 11065.1437 | 177102.2782 | 59.77 | 861.94
2016-02-18 06:00 | 47860 | 10917.8752 | 192951.9742 | 59.78 | 909.34
2016-02-18 07:00 | 48605 | 10753.5365 | 192672.3762 | 59.77 | 972.1
2016-02-18 08:00 | 45799 | 10721.1256 | 185063.3062 | 59.78 | 870.181
2016-02-18 09:00 | 43216 | 11651.52 | 158998.0602 | 59.77 | 864.32
2016-02-18 10:00 | 41695 | 11406.9255 | 155390.7402 | 59.77 | 833.9
2016-02-18 11:00 | 40111 | 12759.3439 | 139762.5142 | 59.79 | 721.998
2016-02-18 12:00 | 38561 | 13587.3929 | 134814.8342 | 59.79 | 694.098
2016-02-18 13:00 | 37449 | 11792.7742 | 130627.0142 | 59.79 | 674.082
2016-02-18 14:00 | 36622 | 12011.6546 | 130076.3267 | 59.79 | 659.196
2016-02-18 15:00 | 36210 | 12019.4226 | 130076.3267 | 59.79 | 651.78
2016-02-18 16:00 | 36306 | 11428.1712 | 130076.3267 | 59.79 | 653.508
2016-02-18 17:00 | 37087 | 11883.0104 | 130076.3267 | 59.79 | 667.566
2016-02-18 18:00 | 39140 | 13157.4146 | 130076.3267 | 59.79 | 704.52
2016-02-18 19:00 | 41193 | 13333.5906 | 131092.3267 | 59.77 | 823.86
2016-02-18 20:00 | 41239 | 13428.4505 | 131092.3267 | 59.77 | 824.78
2016-02-18 21:00 | 40227 | 13065.1164 | 127826.3267 | 59.79 | 724.086
2016-02-18 22:00 | 38171 | 12821.033 | 127826.3267 | 59.79 | 687.078
2016-02-18 23:00 | 35889 | 12721.6841 | 128600.6567 | 59.79 | 646.002
2016-02-19 | 34939 | 12631.32 | 128600.6567 | 59.79 | 628.902
2016-02-19 01:00 | 34449 | 12339.1445 | 128600.6567 | 59.79 | 620.082
2016-02-19 02:00 | 34162 | 11881.2421 | 128600.6567 | 59.79 | 614.916
2016-02-19 03:00 | 34293 | 11019.7003 | 128600.6567 | 59.79 | 617.274
2016-02-19 04:00 | 35208 | 10382.4737 | 128600.6567 | 59.79 | 633.744
2016-02-19 05:00 | 37673 | 9835.942 | 141888.8187 | 59.77 | 753.46
2016-02-19 06:00 | 41802 | 9288.1406 | 168919.8031 | 59.78 | 794.238
2016-02-19 07:00 | 42904 | 8280.7009 | 180997.7971 | 59.78 | 815.176
2016-02-19 08:00 | 41829 | 7552.8088 | 180997.7971 | 59.78 | 794.751
2016-02-19 09:00 | 41326 | 8093.6376 | 180997.7971 | 59.78 | 785.194
2016-02-19 10:00 | 40896 | 7363.886 | 180997.7971 | 59.78 | 777.024
2016-02-19 11:00 | 40073 | 4719.6493 | 182955.0251 | 59.78 | 761.387
2016-02-19 12:00 | 39158 | 3245.6641 | 186920.2111 | 59.78 | 744.002
2016-02-19 13:00 | 38461 | 2466.5396 | 188496.9811 | 59.78 | 730.759
2016-02-19 14:00 | 37614 | 2141.2939 | 189047.6686 | 59.78 | 714.666
2016-02-19 15:00 | 37214 | 1896.5297 | 189047.6686 | 59.78 | 707.066
2016-02-19 16:00 | 37297 | 1823.9379 | 187570.1486 | 59.78 | 708.643
2016-02-19 17:00 | 37859 | 1858.8106 | 187570.1486 | 59.78 | 719.321
2016-02-19 18:00 | 38695 | 2056.4033 | 187570.1486 | 59.78 | 735.205
2016-02-19 19:00 | 39531 | 2041.8548 | 188586.1486 | 59.78 | 751.089
2016-02-19 20:00 | 38973 | 2603.4853 | 187182.3886 | 59.78 | 740.487
2016-02-19 21:00 | 37912 | 4969.8078 | 169701.8126 | 59.78 | 720.328
2016-02-19 22:00 | 36189 | 6665.1392 | 154000.3682 | 59.77 | 723.78
2016-02-19 23:00 | 34270 | 7072.3018 | 150528.0782 | 59.79 | 616.86
2016-02-20 | 34066 | 7319.2083 | 150528.0782 | 59.79 | 613.188
2016-02-20 01:00 | 33766 | 7471.4377 | 150528.0782 | 59.79 | 607.788
2016-02-20 02:00 | 33222 | 7186.2665 | 150528.0782 | 59.79 | 597.996
2016-02-20 03:00 | 33312 | 7023.1187 | 150528.0782 | 59.79 | 599.616
2016-02-20 04:00 | 33513 | 7621.0885 | 150528.0782 | 59.79 | 603.234
2016-02-20 05:00 | 34615 | 7434.1975 | 150528.0782 | 59.79 | 623.07
2016-02-20 06:00 | 35867 | 6543.9236 | 155548.5662 | 59.77 | 717.34
2016-02-20 07:00 | 37225 | 6526.3413 | 155548.5662 | 59.77 | 744.5
2016-02-20 08:00 | 38509 | 6635.5224 | 159195.0792 | 59.77 | 770.18
2016-02-20 09:00 | 39203 | 7548.9068 | 159040.6626 | 59.77 | 784.06
2016-02-20 10:00 | 39170 | 8026.9825 | 158200.6626 | 59.77 | 783.4
2016-02-20 11:00 | 38484 | 7606.869 | 154593.3426 | 59.77 | 769.68
2016-02-20 12:00 | 37642 | 7361.9741 | 149481.6026 | 59.77 | 752.84
2016-02-20 13:00 | 36660 | 7870.7853 | 144387.0126 | 59.77 | 733.2
2016-02-20 14:00 | 36158 | 8706.1789 | 139366.5246 | 59.79 | 650.844
2016-02-20 15:00 | 35931 | 8988.0905 | 139366.5246 | 59.79 | 646.758
2016-02-20 16:00 | 36026 | 10098.5856 | 139366.5246 | 59.79 | 648.468
2016-02-20 17:00 | 36926 | 10523.8143 | 138815.8371 | 59.79 | 664.668
2016-02-20 18:00 | 37980 | 10813.7596 | 138815.8371 | 59.79 | 683.64
2016-02-20 19:00 | 39034 | 10967.0942 | 138815.8371 | 59.77 | 780.68
2016-02-20 20:00 | 38447 | 10697.1328 | 139203.5971 | 59.77 | 768.94
2016-02-20 21:00 | 37331 | 10339.0475 | 138429.2671 | 59.79 | 671.958
2016-02-20 22:00 | 35849 | 10122.2165 | 138864.1471 | 59.79 | 645.282
2016-02-20 23:00 | 34008 | 9793.8375 | 138864.1471 | 59.79 | 612.144
2016-02-21 | 34031 | 7620.6392 | 138864.1471 | 59.79 | 612.558
2016-02-21 01:00 | 34051 | 5805.0721 | 138864.1471 | 59.77 | 681.02
2016-02-21 02:00 | 34077 | 6431.5828 | 138864.1471 | 59.77 | 681.54
2016-02-21 03:00 | 33931 | 6018.7669 | 138864.1471 | 59.77 | 678.62
2016-02-21 04:00 | 33851 | 6579.6757 | 138864.1471 | 59.79 | 609.318
2016-02-21 05:00 | 34538 | 7051.3636 | 140776.5471 | 59.79 | 621.684
2016-02-21 06:00 | 35717 | 7072.4722 | 143209.5471 | 59.77 | 714.34
2016-02-21 07:00 | 36657 | 6898.6815 | 146657.8171 | 59.77 | 733.14
2016-02-21 08:00 | 38300 | 7259.1076 | 154205.6571 | 59.77 | 766
2016-02-21 09:00 | 39879 | 6416.6005 | 167687.6151 | 59.78 | 757.701
2016-02-21 10:00 | 40571 | 7112.3885 | 167687.6151 | 59.78 | 770.849
2016-02-21 11:00 | 40645 | 7959.4071 | 167687.6151 | 59.78 | 772.255
2016-02-21 12:00 | 40343 | 7080.6557 | 167687.6151 | 59.78 | 766.517
2016-02-21 13:00 | 39815 | 7596.2021 | 167687.6151 | 59.77 | 796.3
2016-02-21 14:00 | 39534 | 7180.5535 | 167687.6151 | 59.77 | 790.68
2016-02-21 15:00 | 39362 | 7697.3194 | 169197.9351 | 59.77 | 787.24
2016-02-21 16:00 | 39694 | 7456.0691 | 169197.9351 | 59.77 | 793.88
2016-02-21 17:00 | 40785 | 6539.9394 | 173355.9426 | 59.78 | 774.915
2016-02-21 18:00 | 42843 | 5169.5633 | 194316.1186 | 59.77 | 856.86
2016-02-21 19:00 | 44900 | 5477.6528 | 201925.1886 | 59.77 | 898
2016-02-21 20:00 | 44767 | 6076.2863 | 200289.8186 | 59.77 | 895.34
2016-02-21 21:00 | 43822 | 5959.4171 | 195930.4522 | 59.77 | 876.44
2016-02-21 22:00 | 41641 | 3894.0861 | 195930.4522 | 59.77 | 832.82
2016-02-21 23:00 | 39110 | 3183.1881 | 195930.4522 | 59.78 | 743.09
2016-02-22 | 33808 | 2971.7916 | 195930.4522 | 59.77 | 676.16
2016-02-22 01:00 | 33295 | 2437.2459 | 195930.4522 | 59.77 | 665.9
2016-02-22 02:00 | 33467 | 2159.5364 | 192693.7822 | 59.77 | 669.34
2016-02-22 03:00 | 34172 | 2271.8882 | 192693.7822 | 59.77 | 683.44
2016-02-22 04:00 | 35622 | 2191.8811 | 192693.7822 | 59.78 | 676.818
2016-02-22 05:00 | 39106 | 2388.6603 | 192693.7822 | 59.78 | 743.014
2016-02-22 06:00 | 44464 | 2451.4345 | 224368.3312 | 59.77 | 889.28
2016-02-22 07:00 | 46442 | 1950.2223 | 236811.4992 | 59.78 | 882.398
2016-02-22 08:00 | 46014 | 1796.8354 | 236811.4992 | 59.78 | 874.266
2016-02-22 09:00 | 46049 | 1727.4708 | 236811.4992 | 59.78 | 874.931
2016-02-22 10:00 | 46165 | 1226.8692 | 237827.4992 | 59.78 | 877.135
2016-02-22 11:00 | 45661 | 1325.2407 | 235434.2692 | 59.78 | 867.559
2016-02-22 12:00 | 44923 | 1572.9631 | 234418.2692 | 59.78 | 853.537
2016-02-22 13:00 | 44241 | 1485.5762 | 234418.2692 | 59.78 | 840.579
2016-02-22 14:00 | 43554 | 1944.2068 | 220451.5162 | 59.77 | 871.08
2016-02-22 15:00 | 43215 | 2397.413 | 216997.5562 | 59.77 | 864.3
2016-02-22 16:00 | 43436 | 3213.2013 | 216997.5562 | 59.77 | 868.72
2016-02-22 17:00 | 44697 | 4953.2158 | 216997.5562 | 59.77 | 893.94
2016-02-22 18:00 | 46666 | 6242.1135 | 216997.5562 | 59.77 | 933.32
2016-02-22 19:00 | 48636 | 8643.3771 | 213164.8362 | 59.77 | 972.72
2016-02-22 20:00 | 48287 | 10491.9701 | 196319.4302 | 59.77 | 965.74
2016-02-22 21:00 | 46941 | 10355.5469 | 189825.8802 | 59.78 | 891.879
2016-02-22 22:00 | 44233 | 8659.0869 | 189825.8802 | 59.78 | 840.427
2016-02-22 23:00 | 41754 | 5743.7245 | 189825.8802 | 59.78 | 793.326
2016-02-23 | 38396 | 4387.1111 | 184759.6402 | 59.78 | 729.524
2016-02-23 01:00 | 38038 | 4544.0124 | 184759.6402 | 59.78 | 722.722
2016-02-23 02:00 | 38179 | 5928.2227 | 184759.6402 | 59.77 | 763.58
2016-02-23 03:00 | 38654 | 6553.923 | 184759.6402 | 59.77 | 773.08
2016-02-23 04:00 | 39867 | 7210.2082 | 184759.6402 | 59.78 | 757.473
2016-02-23 05:00 | 42915 | 7591.4334 | 189893.3366 | 59.78 | 815.385
2016-02-23 06:00 | 47797 | 6899.3284 | 221277.7284 | 59.77 | 955.94
2016-02-23 07:00 | 49419 | 6694.961 | 231842.6934 | 59.78 | 938.961
2016-02-23 08:00 | 48837 | 6339.0041 | 231842.6934 | 59.77 | 976.74
2016-02-23 09:00 | 49051 | 6381.2657 | 231842.6934 | 59.78 | 931.969
2016-02-23 10:00 | 49463 | 6166.1423 | 234654.3414 | 59.78 | 939.797
2016-02-23 11:00 | 49415 | 5104.9961 | 238063.5714 | 59.78 | 938.885
2016-02-23 12:00 | 48957 | 6819.8809 | 237047.5714 | 59.77 | 979.14
2016-02-23 13:00 | 48750 | 8479.6261 | 237047.5714 | 59.77 | 975
2016-02-23 14:00 | 48567 | 8491.0025 | 238196.4634 | 59.77 | 971.34
2016-02-23 15:00 | 48494 | 8015.5227 | 238196.4634 | 59.77 | 969.88
2016-02-23 16:00 | 49338 | 7169.6589 | 238196.4634 | 59.77 | 986.76
2016-02-23 17:00 | 50602 | 7731.709 | 238196.4634 | 59.78 | 961.438
2016-02-23 18:00 | 51953 | 7627.9965 | 238196.4634 | 59.78 | 987.107
2016-02-23 19:00 | 53303 | 6823.6464 | 246382.6662 | 59.78 | 1012.757
2016-02-23 20:00 | 52653 | 5835.1755 | 247398.6662 | 59.78 | 1000.407
2016-02-23 21:00 | 50937 | 4410.1165 | 248376.2162 | 59.78 | 967.803
2016-02-23 22:00 | 47945 | 4567.9424 | 248376.2162 | 59.78 | 910.955
2016-02-23 23:00 | 45403 | 5027.6301 | 248376.2162 | 59.77 | 908.06
2016-02-24 | 44407 | 5021.744 | 248376.2162 | 59.77 | 888.14
2016-02-24 01:00 | 43954 | 5521.0137 | 248328.2162 | 59.77 | 879.08
2016-02-24 02:00 | 44172 | 5663.9128 | 248328.2162 | 59.77 | 883.44
2016-02-24 03:00 | 44520 | 5119.3701 | 248328.2162 | 59.77 | 890.4
2016-02-24 04:00 | 45888 | 4330.488 | 248328.2162 | 59.77 | 917.76
2016-02-24 05:00 | 49093 | 3661.7222 | 263068.485 | 59.78 | 932.767
2016-02-24 06:00 | 54032 | 3438.6657 | 271715.7236 | 59.76 | 1134.672
2016-02-24 07:00 | 54725 | 3424.7192 | 271715.7236 | 59.76 | 1149.225
2016-02-24 08:00 | 51979 | 3788.5495 | 259226.7288 | 59.76 | 1091.559
2016-02-24 09:00 | 49502 | 3780.5743 | 245207.8038 | 59.78 | 940.538
2016-02-24 10:00 | 47322 | 3453.635 | 230777.8978 | 59.78 | 899.118
2016-02-24 11:00 | 45135 | 3631.8088 | 211711.3874 | 59.77 | 902.7
2016-02-24 12:00 | 43225 | 4205.4075 | 211711.3874 | 59.77 | 864.5
2016-02-24 13:00 | 41808 | 4351.1366 | 196380.1106 | 59.78 | 794.352
2016-02-24 14:00 | 40510 | 3987.6199 | 196380.1106 | 59.78 | 769.69
2016-02-24 15:00 | 39600 | 4136.2903 | 196380.1106 | 59.78 | 752.4
2016-02-24 16:00 | 39403 | 4541.9728 | 196380.1106 | 59.78 | 748.657
2016-02-24 17:00 | 40291 | 5025.6862 | 196380.1106 | 59.78 | 765.529
2016-02-24 18:00 | 43121 | 5731.6888 | 196380.1106 | 59.78 | 819.299
2016-02-24 19:00 | 45950 | 7342.6003 | 196380.1106 | 59.77 | 919
2016-02-24 20:00 | 46339 | 8788.6408 | 189671.1506 | 59.77 | 926.78
2016-02-24 21:00 | 45948 | 10867.5621 | 176536.5946 | 59.78 | 873.012
2016-02-24 22:00 | 44029 | 12017.3751 | 162233.1646 | 59.77 | 880.58
2016-02-24 23:00 | 42031 | 12484.9332 | 162233.1646 | 59.77 | 840.62
2016-02-25 | 39345 | 11712.7616 | 161020.5398 | 59.77 | 786.9
2016-02-25 01:00 | 39115 | 11500.299 | 161068.5398 | 59.77 | 782.3
2016-02-25 02:00 | 39296 | 11807.3972 | 161068.5398 | 59.79 | 707.328
2016-02-25 03:00 | 39858 | 11868.2346 | 161068.5398 | 59.77 | 797.16
2016-02-25 04:00 | 41239 | 12312.0883 | 161068.5398 | 59.77 | 824.78
2016-02-25 05:00 | 44433 | 12667.1832 | 164879.4678 | 59.77 | 888.66
2016-02-25 06:00 | 48924 | 12376.1254 | 184244.7038 | 59.78 | 929.556
2016-02-25 07:00 | 49257 | 12452.4821 | 184244.7038 | 59.78 | 935.883
2016-02-25 08:00 | 46448 | 12464.5388 | 168090.8238 | 59.78 | 882.512
2016-02-25 09:00 | 44242 | 11813.3604 | 157936.6394 | 59.77 | 884.84
2016-02-25 10:00 | 42506 | 10694.9471 | 157936.6394 | 59.77 | 850.12
2016-02-25 11:00 | 40678 | 10591.2269 | 155777.2394 | 59.77 | 813.56
2016-02-25 12:00 | 38998 | 11636.9716 | 155777.2394 | 59.79 | 701.964
2016-02-25 13:00 | 37875 | 10182.6228 | 155777.2394 | 59.77 | 757.5
2016-02-25 14:00 | 36982 | 10908.2249 | 155777.2394 | 59.79 | 665.676
2016-02-25 15:00 | 36626 | 11190.5323 | 154268.8894 | 59.79 | 659.268
2016-02-25 16:00 | 37250 | 11241.3889 | 153672.9394 | 59.79 | 670.5
2016-02-25 17:00 | 38186 | 11139.3531 | 153672.9394 | 59.79 | 687.348
2016-02-25 18:00 | 39486 | 10329.9103 | 153384.9394 | 59.77 | 789.72
2016-02-25 19:00 | 40787 | 9924.3932 | 153384.9394 | 59.77 | 815.74
2016-02-25 20:00 | 40804 | 9303.7431 | 154120.9394 | 59.77 | 816.08
2016-02-25 21:00 | 39603 | 7536.4582 | 156473.0994 | 59.77 | 792.06
2016-02-25 22:00 | 37315 | 7541.4761 | 149807.5594 | 59.77 | 746.3
2016-02-25 23:00 | 35144 | 7995.0604 | 148288.5594 | 59.79 | 632.592
2016-02-26 | 35088 | 8127.5224 | 149501.1842 | 59.79 | 631.584
2016-02-26 01:00 | 34389 | 8146.6672 | 149501.1842 | 59.79 | 619.002
2016-02-26 02:00 | 34308 | 7872.3401 | 149501.1842 | 59.79 | 617.544
2016-02-26 03:00 | 34509 | 7797.5366 | 149501.1842 | 59.79 | 621.162
2016-02-26 04:00 | 35586 | 7522.2514 | 153108.5042 | 59.77 | 711.72
2016-02-26 05:00 | 38318 | 7985.1644 | 160561.4438 | 59.77 | 766.36
2016-02-26 06:00 | 42640 | 8163.0308 | 172280.1118 | 59.78 | 810.16
2016-02-26 07:00 | 43666 | 8503.6231 | 173011.7038 | 59.78 | 829.654
2016-02-26 08:00 | 42488 | 9206.9559 | 168796.4778 | 59.78 | 807.272
2016-02-26 09:00 | 41931 | 10092.7603 | 158432.7078 | 59.77 | 838.62
2016-02-26 10:00 | 41901 | 10972.6787 | 158432.7078 | 59.77 | 838.02
2016-02-26 11:00 | 41630 | 11912.7345 | 154781.1278 | 59.77 | 832.6
2016-02-26 12:00 | 41385 | 12973.6317 | 150986.6078 | 59.77 | 827.7
2016-02-26 13:00 | 41323 | 14306.3867 | 150986.6078 | 59.79 | 743.814
2016-02-26 14:00 | 41186 | 14387.5782 | 150986.6078 | 59.79 | 741.348
2016-02-26 15:00 | 41141 | 14996.7359 | 151940.7678 | 59.79 | 740.538
2016-02-26 16:00 | 41501 | 15081.4396 | 152536.7178 | 59.79 | 747.018
2016-02-26 17:00 | 42195 | 14328.128 | 152536.7178 | 59.77 | 843.9
2016-02-26 18:00 | 43352 | 13052.8652 | 152824.7178 | 59.77 | 867.04
2016-02-26 19:00 | 44509 | 9528.7747 | 170386.1678 | 59.78 | 845.671
2016-02-26 20:00 | 43961 | 5944.8299 | 191544.5978 | 59.77 | 879.22
2016-02-26 21:00 | 42993 | 3964.8453 | 196044.5978 | 59.77 | 859.86
2016-02-26 22:00 | 41515 | 3318.9754 | 196907.8978 | 59.77 | 830.3
2016-02-26 23:00 | 39753 | 3156.0705 | 196907.8978 | 59.78 | 755.307
2016-02-27 | 40256 | 3329.9585 | 196907.8978 | 59.78 | 764.864
2016-02-27 01:00 | 40576 | 3095.7171 | 196907.8978 | 59.78 | 770.944
2016-02-27 02:00 | 41379 | 2781.0139 | 196907.8978 | 59.77 | 827.58
2016-02-27 03:00 | 41688 | 2681.4403 | 198675.6702 | 59.77 | 833.76
2016-02-27 04:00 | 42431 | 2624.4819 | 206909.0952 | 59.77 | 848.62
2016-02-27 05:00 | 44074 | 3082.5385 | 218142.0652 | 59.77 | 881.48
2016-02-27 06:00 | 46420 | 3530.5971 | 224325.0532 | 59.78 | 881.98
2016-02-27 07:00 | 47810 | 3590.9912 | 226208.4043 | 59.78 | 908.39
2016-02-27 08:00 | 47436 | 4199.9845 | 225625.4612 | 59.78 | 901.284
2016-02-27 09:00 | 45867 | 4023.7675 | 215609.4612 | 59.77 | 917.34
2016-02-27 10:00 | 43771 | 2071.1554 | 215609.4612 | 59.77 | 875.42
2016-02-27 11:00 | 41742 | 2370.2059 | 203169.5808 | 59.77 | 834.84
2016-02-27 12:00 | 39909 | 2141.3271 | 194345.1478 | 59.77 | 798.18
2016-02-27 13:00 | 38328 | 2093.4639 | 183112.1778 | 59.78 | 728.232
2016-02-27 14:00 | 37215 | 1989.4546 | 174489.5898 | 59.78 | 707.085
2016-02-27 15:00 | 36522 | 1993.2957 | 174829.8909 | 59.78 | 693.918
2016-02-27 16:00 | 36352 | 2079.3147 | 174829.8909 | 59.78 | 690.688
2016-02-27 17:00 | 37045 | 2754.2969 | 174829.8909 | 59.78 | 703.855
2016-02-27 18:00 | 39058 | 4028.784 | 174829.8909 | 59.78 | 742.102
2016-02-27 19:00 | 41071 | 6259.2944 | 174829.8909 | 59.78 | 780.349
2016-02-27 20:00 | 41158 | 9596.093 | 154826.2509 | 59.77 | 823.16
2016-02-27 21:00 | 40931 | 10945.3429 | 149805.7629 | 59.77 | 818.62
2016-02-27 22:00 | 39952 | 11018.1431 | 149805.7629 | 59.77 | 799.04
2016-02-27 23:00 | 38561 | 10916.9364 | 149805.7629 | 59.77 | 771.22
2016-02-28 | 38731 | 11097.8721 | 147893.3629 | 59.77 | 774.62
2016-02-28 01:00 | 39053 | 9941.1775 | 147893.3629 | 59.77 | 781.06
2016-02-28 02:00 | 39042 | 10566.8037 | 147893.3629 | 59.77 | 780.84
2016-02-28 03:00 | 39350 | 11421.1032 | 149479.3009 | 59.77 | 787
2016-02-28 04:00 | 40196 | 11634.7792 | 150070.3089 | 59.77 | 803.92
2016-02-28 05:00 | 41677 | 11645.7152 | 153677.6289 | 59.77 | 833.54
2016-02-28 06:00 | 43222 | 11325.6416 | 161137.7169 | 59.77 | 864.44
2016-02-28 07:00 | 44254 | 11266.4203 | 161137.7169 | 59.78 | 840.826
2016-02-28 08:00 | 44603 | 11096.5844 | 161137.7169 | 59.78 | 847.457
2016-02-28 09:00 | 43565 | 11723.7066 | 156004.0205 | 59.77 | 871.3
2016-02-28 10:00 | 42205 | 14336.2829 | 138599.2305 | 59.77 | 844.1
2016-02-28 11:00 | 41096 | 15652.6466 | 134789.4305 | 59.79 | 739.728
2016-02-28 12:00 | 40071 | 16418.5598 | 134789.4305 | 59.79 | 721.278
2016-02-28 13:00 | 39215 | 16288.1913 | 134789.4305 | 59.79 | 705.87
2016-02-28 14:00 | 38613 | 16054.1133 | 134789.4305 | 59.79 | 695.034
2016-02-28 15:00 | 38558 | 16058.6665 | 135003.3194 | 59.79 | 694.044
2016-02-28 16:00 | 38789 | 15775.1962 | 133426.5494 | 59.79 | 698.202
2016-02-28 17:00 | 40159 | 15352.8592 | 133426.5494 | 59.79 | 722.862
2016-02-28 18:00 | 42193 | 13024.1595 | 148623.8694 | 59.77 | 843.86
2016-02-28 19:00 | 44227 | 13180.5242 | 151056.8694 | 59.77 | 884.54
2016-02-28 20:00 | 43864 | 13006.2702 | 151056.8694 | 59.77 | 877.28
2016-02-28 21:00 | 42649 | 12823.6091 | 151056.8694 | 59.77 | 852.98
2016-02-28 22:00 | 40337 | 11174.9917 | 150669.1094 | 59.77 | 806.74
2016-02-28 23:00 | 37807 | 10130.8636 | 150669.1094 | 59.77 | 756.14
2016-02-29 | 38596 | 11097.8721 | 150669.1094 | 59.79 | 694.728
2016-02-29 01:00 | 39053 | 9941.1775 | 150669.1094 | 59.77 | 781.06
2016-02-29 02:00 | 39042 | 10566.8037 | 150669.1094 | 59.77 | 780.84
2016-02-29 03:00 | 39350 | 11421.1032 | 150669.1094 | 59.77 | 787
2016-02-29 04:00 | 40196 | 11634.7792 | 150669.1094 | 59.77 | 803.92
2016-02-29 05:00 | 41677 | 11645.7152 | 150669.1094 | 59.77 | 833.54
2016-02-29 06:00 | 43222 | 11325.6416 | 157875.6994 | 59.77 | 864.44
2016-02-29 07:00 | 44254 | 11266.4203 | 158891.6994 | 59.78 | 840.826
2016-02-29 08:00 | 44603 | 11096.5844 | 161080.0293 | 59.78 | 847.457
2016-02-29 09:00 | 43565 | 11723.7066 | 156180.7794 | 59.77 | 871.3
2016-02-29 10:00 | 42205 | 14336.2829 | 135151.241 | 59.77 | 844.1
2016-02-29 11:00 | 41096 | 15652.6466 | 130426.831 | 59.79 | 739.728
2016-02-29 12:00 | 40071 | 16418.5598 | 127972.431 | 59.79 | 721.278
2016-02-29 13:00 | 39215 | 16288.1913 | 127972.431 | 59.79 | 705.87
2016-02-29 14:00 | 38613 | 16054.1133 | 127972.431 | 59.79 | 695.034
2016-02-29 15:00 | 38558 | 16058.6665 | 127972.431 | 59.79 | 694.044
2016-02-29 16:00 | 38789 | 15775.1962 | 129549.201 | 59.79 | 698.202
2016-02-29 17:00 | 40159 | 15352.8592 | 129549.201 | 59.79 | 722.862
2016-02-29 18:00 | 42193 | 13024.1595 | 140140.951 | 59.77 | 843.86
2016-02-29 19:00 | 44227 | 13180.5242 | 146195.4011 | 59.77 | 884.54
2016-02-29 20:00 | 43864 | 13006.2702 | 145536.691 | 59.77 | 877.28
2016-02-29 21:00 | 42649 | 12823.6091 | 145080.691 | 59.77 | 852.98
2016-02-29 22:00 | 40337 | 11174.9917 | 144226.721 | 59.77 | 806.74
2016-02-29 23:00 | 37807 | 10130.8636 | 144100.241 | 59.77 | 756.14
2016-03-01 | 33329 | 9110.0237 | 141045.241 | 59.79 | 599.922
2016-03-01 01:00 | 32646 | 7721.7362 | 141045.241 | 59.79 | 587.628
2016-03-01 02:00 | 32551 | 6161.0311 | 139543.591 | 59.79 | 585.918
2016-03-01 03:00 | 32890 | 5746.6316 | 149649.991 | 59.79 | 592.02
2016-03-01 04:00 | 34067 | 5099.8243 | 149649.991 | 59.77 | 681.34
2016-03-01 05:00 | 37300 | 5462.4618 | 167184.8554 | 59.77 | 746
2016-03-01 06:00 | 42592 | 5031.8044 | 197025.4214 | 59.77 | 851.84
2016-03-01 07:00 | 44302 | 5792.0677 | 197114.0313 | 59.77 | 886.04
2016-03-01 08:00 | 43733 | 7513.1461 | 196006.7318 | 59.78 | 830.927
2016-03-01 09:00 | 43913 | 7996.2471 | 196006.7318 | 59.78 | 834.347
2016-03-01 10:00 | 44112 | 10475.197 | 187516.3822 | 59.78 | 838.128
2016-03-01 11:00 | 43872 | 13603.5574 | 177982.4822 | 59.77 | 877.44
2016-03-01 12:00 | 43666 | 13813.3509 | 180436.8822 | 59.77 | 873.32
2016-03-01 13:00 | 43604 | 14638.9202 | 180436.8822 | 59.77 | 872.08
2016-03-01 14:00 | 43431 | 14357.5063 | 180436.8822 | 59.77 | 868.62
2016-03-01 15:00 | 43698 | 14468.4873 | 180436.8822 | 59.77 | 873.96
2016-03-01 16:00 | 44553 | 14146.9752 | 177083.1718 | 59.77 | 891.06
2016-03-01 17:00 | 45840 | 13509.7774 | 177083.1718 | 59.77 | 916.8
2016-03-01 18:00 | 47209 | 13083.6128 | 177083.1718 | 59.78 | 896.971
2016-03-01 19:00 | 48579 | 11384.1428 | 192261.4318 | 59.78 | 923.001
2016-03-01 20:00 | 47936 | 8942.565 | 197759.6768 | 59.77 | 958.72
2016-03-01 21:00 | 46394 | 8751.8519 | 196743.6768 | 59.77 | 927.88
2016-03-01 22:00 | 43642 | 6064.7857 | 194424.4336 | 59.77 | 872.84
2016-03-01 23:00 | 40912 | 5533.4076 | 193255.3156 | 59.78 | 777.328
2016-03-02 | 38764 | 5667.5943 | 193519.426 | 59.78 | 736.516
2016-03-02 01:00 | 38216 | 5249.8708 | 193519.426 | 59.78 | 726.104
2016-03-02 02:00 | 38336 | 4865.8415 | 195021.076 | 59.78 | 728.384
2016-03-02 03:00 | 38880 | 4468.06 | 195021.076 | 59.78 | 738.72
2016-03-02 04:00 | 40456 | 4345.3012 | 196262.806 | 59.78 | 768.664
2016-03-02 05:00 | 43905 | 4152.588 | 213197.896 | 59.77 | 878.1
2016-03-02 06:00 | 49115 | 4395.2125 | 239136.5924 | 59.78 | 933.185
2016-03-02 07:00 | 49666 | 4054.67 | 239381.7988 | 59.78 | 943.654
2016-03-02 08:00 | 47219 | 3966.3357 | 234287.8724 | 59.78 | 897.161
2016-03-02 09:00 | 45654 | 3011.4582 | 232330.6444 | 59.78 | 867.426
2016-03-02 10:00 | 44286 | 3068.4278 | 232330.6444 | 59.77 | 885.72
2016-03-02 11:00 | 42761 | 3038.0728 | 230820.3244 | 59.77 | 855.22
2016-03-02 12:00 | 41403 | 2404.8262 | 230820.3244 | 59.77 | 828.06
2016-03-02 13:00 | 40352 | 2370.5057 | 230820.3244 | 59.77 | 807.04
2016-03-02 14:00 | 39444 | 3161.33 | 230820.3244 | 59.78 | 749.436
2016-03-02 15:00 | 39025 | 2808.8829 | 230820.3244 | 59.78 | 741.475
2016-03-02 16:00 | 38994 | 2161.3811 | 230820.3244 | 59.78 | 740.886
2016-03-02 17:00 | 39700 | 1839.3956 | 230820.3244 | 59.77 | 794
2016-03-02 18:00 | 41948 | 1357.4926 | 234653.0444 | 59.77 | 838.96
2016-03-02 19:00 | 44196 | 627.244 | 237919.0444 | 59.78 | 839.724
2016-03-02 20:00 | 44380 | 567.4 | 237919.0444 | 59.78 | 843.22
2016-03-02 21:00 | 43409 | 1716.2701 | 226716.8394 | 59.77 | 868.18
2016-03-02 22:00 | 41186 | 2788.8138 | 204979.4934 | 59.77 | 823.72
2016-03-02 23:00 | 38982 | 4250.4569 | 193958.581 | 59.78 | 740.658
2016-03-03 | 36338 | 5303.9444 | 194428.456 | 59.77 | 726.76
2016-03-03 01:00 | 36147 | 6062.1218 | 194428.456 | 59.77 | 722.94
2016-03-03 02:00 | 36383 | 5673.6401 | 194428.456 | 59.77 | 727.66
2016-03-03 03:00 | 36952 | 5702.9019 | 194428.456 | 59.77 | 739.04
2016-03-03 04:00 | 38476 | 5699.5507 | 196749.4706 | 59.78 | 731.044
2016-03-03 05:00 | 41924 | 6205.7356 | 199068.7138 | 59.78 | 796.556
2016-03-03 06:00 | 46712 | 6853.7816 | 212400.4067 | 59.77 | 934.24
2016-03-03 07:00 | 46945 | 5544.813 | 213416.4067 | 59.77 | 938.9
2016-03-03 08:00 | 44039 | 4493.303 | 212400.4067 | 59.77 | 880.78
2016-03-03 09:00 | 41621 | 3369.2457 | 204112.5147 | 59.77 | 832.42
2016-03-03 10:00 | 39814 | 2446.7433 | 193176.6187 | 59.78 | 756.466
2016-03-03 11:00 | 38494 | 2182.0943 | 185727.9787 | 59.78 | 731.386
2016-03-03 12:00 | 37333 | 2544.8379 | 177774.1587 | 59.78 | 709.327
2016-03-03 13:00 | 36612 | 2831.631 | 177774.1587 | 59.78 | 695.628
2016-03-03 14:00 | 36008 | 2433.1218 | 168814.0483 | 59.78 | 684.152
2016-03-03 15:00 | 35753 | 2825.7722 | 165457.6483 | 59.78 | 679.307
2016-03-03 16:00 | 35640 | 3134.6955 | 165457.6483 | 59.78 | 677.16
2016-03-03 17:00 | 35972 | 3287.9047 | 165457.6483 | 59.78 | 683.468
2016-03-03 18:00 | 37822 | 4231.2409 | 165457.6483 | 59.78 | 718.618
2016-03-03 19:00 | 39673 | 6906.5249 | 162108.5583 | 59.78 | 753.787
2016-03-03 20:00 | 39664 | 10393.5344 | 144711.3903 | 59.77 | 793.28
2016-03-03 21:00 | 38748 | 11163.9561 | 141632.2903 | 59.77 | 774.96
2016-03-03 22:00 | 36464 | 11120.9652 | 141632.2903 | 59.79 | 656.352
2016-03-03 23:00 | 34281 | 10809.6771 | 141632.2903 | 59.79 | 617.058
2016-03-04 | 33284 | 9652.0854 | 141632.2903 | 59.79 | 599.112
2016-03-04 01:00 | 32919 | 9473.5538 | 141632.2903 | 59.79 | 592.542
2016-03-04 02:00 | 33108 | 9873.5881 | 140504.7145 | 59.79 | 595.944
2016-03-04 03:00 | 33715 | 10063.3345 | 140504.7145 | 59.79 | 606.87
2016-03-04 04:00 | 34996 | 9876.7155 | 144112.0345 | 59.79 | 629.928
2016-03-04 05:00 | 37792 | 10134.3524 | 144112.0345 | 59.77 | 755.84
2016-03-04 06:00 | 42620 | 9701.5926 | 162333.12 | 59.78 | 809.78
2016-03-04 07:00 | 43017 | 9976.0699 | 162333.12 | 59.78 | 817.323
2016-03-04 08:00 | 40831 | 10462.6161 | 150407.8236 | 59.77 | 816.62
2016-03-04 09:00 | 39514 | 9767.3548 | 145460.1436 | 59.77 | 790.28
2016-03-04 10:00 | 38413 | 11085.884 | 135210.5036 | 59.79 | 691.434
2016-03-04 11:00 | 37528 | 11790.6535 | 135210.5036 | 59.79 | 675.504
2016-03-04 12:00 | 36822 | 12483.1058 | 131603.1836 | 59.79 | 662.796
2016-03-04 13:00 | 36513 | 11402.0617 | 131603.1836 | 59.79 | 657.234
2016-03-04 14:00 | 36063 | 10678.1562 | 126582.6956 | 59.79 | 649.134
2016-03-04 15:00 | 35772 | 11536.7879 | 126582.6956 | 59.79 | 643.896
2016-03-04 16:00 | 35460 | 11878.1102 | 126582.6956 | 59.79 | 638.28
2016-03-04 17:00 | 35795 | 12658.382 | 126582.6956 | 59.79 | 644.31
2016-03-04 18:00 | 37360 | 13426.0971 | 126582.6956 | 59.79 | 672.48
2016-03-04 19:00 | 38925 | 13783.878 | 126582.6956 | 59.79 | 700.65
2016-03-04 20:00 | 38773 | 13894.75 | 126582.6956 | 59.79 | 697.914
2016-03-04 21:00 | 37626 | 14035.7915 | 127274.2956 | 59.79 | 677.268
2016-03-04 22:00 | 35409 | 14265.6974 | 125280.7456 | 59.79 | 637.362
2016-03-04 23:00 | 32964 | 14161.8897 | 125537.5527 | 59.79 | 593.352
2016-03-05 | 32731 | 14106.5396 | 124205.6727 | 59.79 | 589.158
2016-03-05 01:00 | 32528 | 13466.4868 | 124205.6727 | 59.79 | 585.504
2016-03-05 02:00 | 32445 | 13284.0655 | 123144.6775 | 59.79 | 584.01
2016-03-05 03:00 | 32717 | 13173.9844 | 123144.6775 | 59.79 | 588.906
2016-03-05 04:00 | 33877 | 13051.8938 | 132769.2675 | 59.79 | 609.786
2016-03-05 05:00 | 36547 | 12495.0376 | 138376.6875 | 59.79 | 657.846
2016-03-05 06:00 | 41442 | 11873.6679 | 150354.0875 | 59.77 | 828.84
2016-03-05 07:00 | 42221 | 11958.7568 | 151370.0875 | 59.77 | 844.42
2016-03-05 08:00 | 41000 | 12126.8458 | 151054.5984 | 59.77 | 820
2016-03-05 09:00 | 40547 | 12227.6397 | 147007.1284 | 59.77 | 810.94
2016-03-05 10:00 | 40075 | 12421.3206 | 147007.1284 | 59.77 | 801.5
2016-03-05 11:00 | 39313 | 12037.7402 | 147007.1284 | 59.79 | 707.634
2016-03-05 12:00 | 38641 | 11254.0798 | 147007.1284 | 59.79 | 695.538
2016-03-05 13:00 | 38320 | 9960.1921 | 147007.1284 | 59.77 | 766.4
2016-03-05 14:00 | 37905 | 9123.8943 | 147007.1284 | 59.77 | 758.1
2016-03-05 15:00 | 37558 | 9189.0888 | 147007.1284 | 59.77 | 751.16
2016-03-05 16:00 | 37458 | 9109.9747 | 147007.1284 | 59.77 | 749.16
2016-03-05 17:00 | 37572 | 9661.6399 | 147007.1284 | 59.77 | 751.44
2016-03-05 18:00 | 38657 | 9928.4204 | 147007.1284 | 59.77 | 773.14
2016-03-05 19:00 | 39741 | 10588.4031 | 147007.1284 | 59.77 | 794.82
2016-03-05 20:00 | 39340 | 10322.0088 | 147007.1284 | 59.77 | 786.8
2016-03-05 21:00 | 38259 | 10849.8771 | 139815.5384 | 59.79 | 688.662
2016-03-05 22:00 | 36543 | 12109.2911 | 141809.0884 | 59.79 | 657.774
2016-03-05 23:00 | 34587 | 11747.3526 | 141809.0884 | 59.79 | 622.566
2016-03-06 | 34597 | 10761.6142 | 139629.5549 | 59.79 | 622.746
2016-03-06 01:00 | 34604 | 10001.3249 | 137189.9549 | 59.79 | 622.872
2016-03-06 02:00 | 34191 | 9622.7004 | 137474.5259 | 59.79 | 615.438
2016-03-06 03:00 | 34418 | 8780.538 | 137474.5259 | 59.79 | 619.524
2016-03-06 04:00 | 34508 | 8318.5882 | 140189.2879 | 59.79 | 621.144
2016-03-06 05:00 | 35062 | 7729.4566 | 143773.5579 | 59.79 | 631.116
2016-03-06 06:00 | 36444 | 6784.4207 | 153432.7423 | 59.77 | 728.88
2016-03-06 07:00 | 37663 | 7681.0933 | 155336.7423 | 59.77 | 753.26
2016-03-06 08:00 | 38945 | 8765.7722 | 155336.7423 | 59.77 | 778.9
2016-03-06 09:00 | 39493 | 9159.9274 | 157818.3423 | 59.77 | 789.86
2016-03-06 10:00 | 39280 | 9325.6522 | 157818.3423 | 59.77 | 785.6
2016-03-06 11:00 | 38770 | 8941.5371 | 154659.9423 | 59.77 | 775.4
2016-03-06 12:00 | 38050 | 8499.643 | 154659.9423 | 59.77 | 761
2016-03-06 13:00 | 37349 | 7258.8675 | 154659.9423 | 59.77 | 746.98
2016-03-06 14:00 | 36876 | 6517.5089 | 154659.9423 | 59.77 | 737.52
2016-03-06 15:00 | 36530 | 5919.2376 | 154659.9423 | 59.77 | 730.6
2016-03-06 16:00 | 36525 | 5941.095 | 154659.9423 | 59.77 | 730.5
2016-03-06 17:00 | 36990 | 6924.5254 | 154659.9423 | 59.77 | 739.8
2016-03-06 18:00 | 38401 | 8596.4218 | 154659.9423 | 59.77 | 768.02
2016-03-06 19:00 | 39812 | 9499.2231 | 154659.9423 | 59.77 | 796.24
2016-03-06 20:00 | 39371 | 10365.9079 | 145487.5443 | 59.77 | 787.42
2016-03-06 21:00 | 38497 | 10456.0471 | 140353.8479 | 59.77 | 769.94
2016-03-06 22:00 | 36883 | 10811.9683 | 134336.5779 | 59.79 | 663.894
2016-03-06 23:00 | 35095 | 9822.5501 | 134336.5779 | 59.79 | 631.71
2016-03-07 | 34632 | 9089.2743 | 134336.5779 | 59.79 | 623.376
2016-03-07 01:00 | 33617 | 9414.0323 | 136776.1779 | 59.79 | 605.106
2016-03-07 02:00 | 33139 | 9309.988 | 136776.1779 | 59.79 | 596.502
2016-03-07 03:00 | 32950 | 9575.9803 | 136776.1779 | 59.79 | 593.1
2016-03-07 04:00 | 33036 | 9677.4677 | 136776.1779 | 59.79 | 594.648
2016-03-07 05:00 | 33518 | 9751.662 | 138955.7114 | 59.79 | 603.324
2016-03-07 06:00 | 34673 | 9039.5873 | 139450.7114 | 59.79 | 624.114
2016-03-07 07:00 | 35846 | 7968.9867 | 139450.7114 | 59.77 | 716.92
2016-03-07 08:00 | 37734 | 7096.1315 | 153189.1658 | 59.77 | 754.68
2016-03-07 09:00 | 39155 | 7638.8095 | 153925.1658 | 59.77 | 783.1
2016-03-07 10:00 | 39747 | 7820.8326 | 154134.2557 | 59.77 | 794.94
2016-03-07 11:00 | 39957 | 8580.5792 | 156347.5658 | 59.77 | 799.14
2016-03-07 12:00 | 39959 | 8936.7861 | 156347.5658 | 59.77 | 799.18
2016-03-07 13:00 | 39772 | 7851.8464 | 156347.5658 | 59.77 | 795.44
2016-03-07 14:00 | 39493 | 8303.1039 | 156347.5658 | 59.77 | 789.86
2016-03-07 15:00 | 39440 | 8762.5309 | 156347.5658 | 59.77 | 788.8
2016-03-07 16:00 | 39904 | 8316.5878 | 156347.5658 | 59.77 | 798.08
2016-03-07 17:00 | 41045 | 8845.5467 | 156347.5658 | 59.77 | 820.9
2016-03-07 18:00 | 42500 | 10017.6782 | 156289.5758 | 59.77 | 850
2016-03-07 19:00 | 43954 | 10079.11 | 160041.5189 | 59.78 | 835.126
2016-03-07 20:00 | 43369 | 9634.731 | 158904.3858 | 59.78 | 824.011
2016-03-07 21:00 | 41924 | 8503.6413 | 158245.5989 | 59.78 | 796.556
2016-03-07 22:00 | 39536 | 8489.7555 | 147508.4714 | 59.77 | 790.72
2016-03-07 23:00 | 37014 | 8402.2605 | 138604.8714 | 59.77 | 740.28
2016-03-08 | 31787 | 8674.7717 | 131575.1514 | 59.79 | 572.166
2016-03-08 01:00 | 30954 | 8474.2375 | 131575.1514 | 59.79 | 557.172
2016-03-08 02:00 | 30563 | 9307.0277 | 131575.1514 | 59.79 | 550.134
2016-03-08 03:00 | 30714 | 10025.7962 | 131575.1514 | 59.79 | 552.852
2016-03-08 04:00 | 31964 | 9732.7923 | 135800.8805 | 59.79 | 575.352
2016-03-08 05:00 | 33617 | 9560.0201 | 136044.8645 | 59.79 | 605.106
2016-03-08 06:00 | 37924 | 9982.8685 | 135800.8805 | 59.77 | 758.48
2016-03-08 07:00 | 39442 | 11779.6168 | 135800.8805 | 59.77 | 788.84
2016-03-08 08:00 | 39226 | 13217.3613 | 132216.6105 | 59.79 | 706.068
2016-03-08 09:00 | 39507 | 14370.2457 | 128594.2905 | 59.79 | 711.126
2016-03-08 10:00 | 39962 | 15393.2755 | 128594.2905 | 59.79 | 719.316
2016-03-08 11:00 | 40045 | 15343.3463 | 128594.2905 | 59.79 | 720.81
2016-03-08 12:00 | 39899 | 15232.2135 | 128594.2905 | 59.79 | 718.182
2016-03-08 13:00 | 39778 | 15023.7889 | 128594.2905 | 59.79 | 716.004
2016-03-08 14:00 | 39603 | 15139.4663 | 128594.2905 | 59.79 | 712.854
2016-03-08 15:00 | 39428 | 15298.7994 | 128594.2905 | 59.79 | 709.704
2016-03-08 16:00 | 39744 | 15283.4662 | 128594.2905 | 59.79 | 715.392
2016-03-08 17:00 | 40077 | 15448.7206 | 128594.2905 | 59.79 | 721.386
2016-03-08 18:00 | 40829 | 15424.0299 | 128713.2765 | 59.79 | 734.922
2016-03-08 19:00 | 41581 | 15584.6123 | 128652.2805 | 59.79 | 748.458
2016-03-08 20:00 | 41032 | 15279.2582 | 129206.4705 | 59.79 | 738.576
2016-03-08 21:00 | 39386 | 14696.8845 | 129206.4705 | 59.79 | 708.948
2016-03-08 22:00 | 36455 | 13576.8125 | 129206.4705 | 59.79 | 656.19
2016-03-08 23:00 | 33745 | 12790.3211 | 129450.4545 | 59.79 | 607.41
2016-03-09 | 32553 | 13222.6583 | 129206.4705 | 59.79 | 585.954
2016-03-09 01:00 | 31586 | 13168.4132 | 129206.4705 | 59.79 | 568.548
2016-03-09 02:00 | 31137 | 12647.2557 | 128735.5855 | 59.79 | 560.466
2016-03-09 03:00 | 31201 | 12086.8362 | 128735.5855 | 59.79 | 561.618
2016-03-09 04:00 | 31962 | 12143.6108 | 135849.6355 | 59.79 | 575.316
2016-03-09 05:00 | 34183 | 12013.1697 | 142289.4755 | 59.79 | 615.294
2016-03-09 06:00 | 38606 | 11476.6201 | 140708.4958 | 59.79 | 694.908
2016-03-09 07:00 | 39455 | 10481.432 | 144518.2958 | 59.77 | 789.1
2016-03-09 08:00 | 38769 | 9053.1694 | 144518.2958 | 59.77 | 775.38
2016-03-09 09:00 | 38891 | 9351.4055 | 144518.2958 | 59.77 | 777.82
2016-03-09 10:00 | 39255 | 8999.3924 | 149651.9922 | 59.77 | 785.1
2016-03-09 11:00 | 39360 | 7403.4666 | 158977.4302 | 59.77 | 787.2
2016-03-09 12:00 | 39372 | 7139.6063 | 158977.4302 | 59.77 | 787.44
2016-03-09 13:00 | 39664 | 7853.2586 | 159855.6416 | 59.77 | 793.28
2016-03-09 14:00 | 39861 | 9013.0537 | 159855.6416 | 59.77 | 797.22
2016-03-09 15:00 | 40088 | 8887.0818 | 159855.6416 | 59.77 | 801.76
2016-03-09 16:00 | 40012 | 8975.0833 | 159855.6416 | 59.77 | 800.24
2016-03-09 17:00 | 39837 | 9104.0906 | 159855.6416 | 59.77 | 796.74
2016-03-09 18:00 | 40799 | 8983.9876 | 171030.8316 | 59.77 | 815.98
2016-03-09 19:00 | 41762 | 6442.2549 | 179609.1216 | 59.78 | 793.478
2016-03-09 20:00 | 41086 | 4674.4163 | 180625.1216 | 59.78 | 780.634
2016-03-09 21:00 | 39328 | 6191.7829 | 166687.3856 | 59.78 | 747.232
2016-03-09 22:00 | 36542 | 8604.5607 | 137765.9712 | 59.77 | 730.84
2016-03-09 23:00 | 33512 | 9487.6133 | 136749.9712 | 59.79 | 603.216
2016-03-10 | 29984 | 9937.3134 | 136749.9712 | 59.79 | 539.712
2016-03-10 01:00 | 29077 | 10566.3358 | 134310.3712 | 59.79 | 523.386
2016-03-10 02:00 | 28749 | 10391.5486 | 126574.7062 | 59.79 | 517.482
2016-03-10 03:00 | 28692 | 10562.9964 | 126574.7062 | 59.79 | 516.456
2016-03-10 04:00 | 29355 | 11028.3718 | 126892.5093 | 59.79 | 528.39
2016-03-10 05:00 | 31428 | 11584.7842 | 127201.1583 | 59.79 | 565.704
2016-03-10 06:00 | 35454 | 11509.4163 | 128155.6859 | 59.79 | 638.172
2016-03-10 07:00 | 36572 | 11487.3256 | 128155.6859 | 59.79 | 658.296
2016-03-10 08:00 | 36543 | 10986.6593 | 129171.6859 | 59.79 | 657.774
2016-03-10 09:00 | 36832 | 13396.919 | 125905.6859 | 59.79 | 662.976
2016-03-10 10:00 | 37352 | 13815.1392 | 125905.6859 | 59.79 | 672.336
2016-03-10 11:00 | 37546 | 13074.4475 | 128298.9159 | 59.79 | 675.828
2016-03-10 12:00 | 37666 | 13441.5794 | 128225.0968 | 59.79 | 677.988
2016-03-10 13:00 | 37850 | 14001.6284 | 128225.0968 | 59.79 | 681.3
2016-03-10 14:00 | 37956 | 14077.449 | 128225.0968 | 59.79 | 683.208
2016-03-10 15:00 | 37818 | 13698.3424 | 128225.0968 | 59.79 | 680.724
2016-03-10 16:00 | 37810 | 13872.8993 | 128225.0968 | 59.79 | 680.58
2016-03-10 17:00 | 37451 | 13395.9118 | 128225.0968 | 59.79 | 674.118
2016-03-10 18:00 | 38331 | 12643.3265 | 131105.2557 | 59.79 | 689.958
2016-03-10 19:00 | 39211 | 10142.7895 | 142218.1957 | 59.77 | 784.22
2016-03-10 20:00 | 38575 | 5038.8323 | 164941.2501 | 59.78 | 732.925
2016-03-10 21:00 | 37040 | 3217.0325 | 166731.5801 | 59.78 | 703.76
2016-03-10 22:00 | 34453 | 2565.3131 | 158751.8601 | 59.77 | 689.06
2016-03-10 23:00 | 31858 | 2999.4024 | 151606.6881 | 59.77 | 637.16
2016-03-11 | 30244 | 3572.7664 | 151606.6881 | 59.79 | 544.392
2016-03-11 01:00 | 29455 | 3877.2097 | 151606.6881 | 59.79 | 530.19
2016-03-11 02:00 | 29155 | 3688.2807 | 151606.6881 | 59.79 | 524.79
2016-03-11 03:00 | 29273 | 3472.9871 | 151606.6881 | 59.79 | 526.914
2016-03-11 04:00 | 30132 | 4473.6989 | 151606.6881 | 59.79 | 542.376
2016-03-11 05:00 | 32620 | 5373.5524 | 151606.6881 | 59.79 | 587.16
2016-03-11 06:00 | 36992 | 5621.8392 | 155775.6988 | 59.77 | 739.84
2016-03-11 07:00 | 38034 | 5567.4439 | 155775.6988 | 59.77 | 760.68
2016-03-11 08:00 | 37370 | 5806.2361 | 155775.6988 | 59.77 | 747.4
2016-03-11 09:00 | 37136 | 4645.7756 | 155775.6988 | 59.77 | 742.72
2016-03-11 10:00 | 37296 | 4728.2446 | 155775.6988 | 59.78 | 708.624
2016-03-11 11:00 | 37495 | 5271.3709 | 155775.6988 | 59.77 | 749.9
2016-03-11 12:00 | 37547 | 5557.3552 | 155775.6988 | 59.77 | 750.94
2016-03-11 13:00 | 37926 | 6224.2299 | 155775.6988 | 59.77 | 758.52
2016-03-11 14:00 | 38067 | 7322.5267 | 155775.6988 | 59.77 | 761.34
2016-03-11 15:00 | 37913 | 9328.2659 | 155775.6988 | 59.77 | 758.26
2016-03-11 16:00 | 37925 | 11041.1531 | 155775.6988 | 59.79 | 682.65
2016-03-11 17:00 | 37809 | 11999.2432 | 155775.6988 | 59.79 | 680.562
2016-03-11 18:00 | 38609 | 12842.4658 | 155775.6988 | 59.79 | 694.962
2016-03-11 19:00 | 39409 | 10796.8197 | 155775.6988 | 59.77 | 788.18
2016-03-11 20:00 | 39008 | 7269.7022 | 155775.6988 | 59.77 | 780.16
2016-03-11 21:00 | 37481 | 4954.2767 | 155775.6988 | 59.78 | 712.139
2016-03-11 22:00 | 35111 | 5209.2252 | 147205.6988 | 59.77 | 702.22
2016-03-11 23:00 | 32599 | 5909.6493 | 143985.7788 | 59.79 | 586.782
2016-03-12 | 32931 | 7546.652 | 141797.2485 | 59.79 | 592.758
2016-03-12 01:00 | 33075 | 9801.7203 | 139861.6348 | 59.79 | 595.35
2016-03-12 02:00 | 32839 | 9406.6302 | 139861.6348 | 59.79 | 591.102
2016-03-12 03:00 | 33038 | 9187.5533 | 139861.6348 | 59.79 | 594.684
2016-03-12 04:00 | 34039 | 10583.4798 | 139861.6348 | 59.79 | 612.702
2016-03-12 05:00 | 36848 | 10463.756 | 139861.6348 | 59.79 | 663.264
2016-03-12 06:00 | 41427 | 9068.3883 | 159387.7348 | 59.77 | 828.54
2016-03-12 07:00 | 42384 | 8920.9667 | 163472.8248 | 59.78 | 805.296
2016-03-12 08:00 | 41552 | 8752.1857 | 165218.4248 | 59.78 | 789.488
2016-03-12 09:00 | 41085 | 5336.276 | 176521.3348 | 59.78 | 780.615
2016-03-12 10:00 | 40749 | 4054.7979 | 176348.674 | 59.78 | 774.231
2016-03-12 11:00 | 40700 | 5379.1225 | 175332.674 | 59.78 | 773.3
2016-03-12 12:00 | 40154 | 6943.9639 | 165178.4896 | 59.78 | 762.926
2016-03-12 13:00 | 40132 | 7622.5999 | 165178.4896 | 59.78 | 762.508
2016-03-12 14:00 | 39810 | 8920.1137 | 163670.1396 | 59.77 | 796.2
2016-03-12 15:00 | 39655 | 9772.866 | 163670.1396 | 59.77 | 793.1
2016-03-12 16:00 | 39425 | 11095.7791 | 163670.1396 | 59.77 | 788.5
2016-03-12 17:00 | 39425 | 11518.0323 | 163670.1396 | 59.77 | 788.5
2016-03-12 18:00 | 40209 | 11229.5148 | 163670.1396 | 59.77 | 804.18
2016-03-12 19:00 | 40994 | 9469.8159 | 163670.1396 | 59.77 | 819.88
2016-03-12 20:00 | 40400 | 7265.0337 | 163670.1396 | 59.78 | 767.6
2016-03-12 21:00 | 39201 | 6255.952 | 162093.3696 | 59.78 | 744.819
2016-03-12 22:00 | 37491 | 4959.2823 | 162093.3696 | 59.78 | 712.329
2016-03-12 23:00 | 35533 | 3253.7566 | 160797.7716 | 59.77 | 710.66
2016-03-13 | 35446 | 2987.0289 | 162986.302 | 59.77 | 708.92
2016-03-13 01:00 | 35386 | 2816.6048 | 164921.9156 | 59.78 | 672.334
2016-03-13 02:00 | 34939 | 3621.6127 | 164921.9156 | 59.77 | 698.78
2016-03-13 03:00 | 34862 | 3527.9046 | 162762.5156 | 59.77 | 697.24
2016-03-13 04:00 | 35426 | 3524.7969 | 162762.5156 | 59.77 | 708.52
2016-03-13 05:00 | 36864 | 4244.9577 | 167896.212 | 59.78 | 700.416
2016-03-13 06:00 | 38790 | 3437.6534 | 179352.596 | 59.78 | 737.01
2016-03-13 07:00 | 40044 | 2538.4159 | 194945.666 | 59.77 | 800.88
2016-03-13 08:00 | 40977 | 2268.9703 | 204891.5644 | 59.77 | 819.54
2016-03-13 09:00 | 41204 | 1484.4404 | 210041.8144 | 59.77 | 824.08
2016-03-13 10:00 | 41001 | 1060.0971 | 211230.4752 | 59.77 | 820.02
2016-03-13 11:00 | 40539 | 1382.1025 | 211230.4752 | 59.77 | 810.78
2016-03-13 12:00 | 39914 | 1399.0983 | 211230.4752 | 59.77 | 798.28
2016-03-13 13:00 | 39332 | 1844.6185 | 211230.4752 | 59.78 | 747.308
2016-03-13 14:00 | 38994 | 2121.2049 | 210386.6652 | 59.78 | 740.886
2016-03-13 15:00 | 38921 | 1446.05 | 210386.6652 | 59.78 | 739.499
2016-03-13 16:00 | 38956 | 1305.2999 | 210386.6652 | 59.77 | 779.12
2016-03-13 17:00 | 39020 | 1324.567 | 210386.6652 | 59.77 | 780.4
2016-03-13 18:00 | 40303 | 1162.3185 | 210386.6652 | 59.77 | 806.06
2016-03-13 19:00 | 41585 | 2901.81 | 209790.7152 | 59.77 | 831.7
2016-03-13 20:00 | 40947 | 6791.0037 | 175001.5268 | 59.78 | 777.993
2016-03-13 21:00 | 39839 | 8696.4257 | 158727.0708 | 59.77 | 796.78
2016-03-13 22:00 | 38111 | 11282.2467 | 153706.5828 | 59.79 | 685.998
2016-03-13 23:00 | 36300 | 12452.6078 | 153706.5828 | 59.79 | 653.4
2016-03-14 | 36531 | 11340.7 | 153706.5828 | 59.79 | 657.558
2016-03-14 01:00 | 36968 | 9926.4912 | 153706.5828 | 59.79 | 665.424
2016-03-14 02:00 | 36562 | 8874.1033 | 153706.5828 | 59.77 | 731.24
2016-03-14 03:00 | 36230 | 8098.7785 | 155865.9828 | 59.77 | 724.6
2016-03-14 04:00 | 36388 | 6932.142 | 155865.9828 | 59.77 | 727.76
2016-03-14 05:00 | 37010 | 6668.8946 | 155865.9828 | 59.77 | 740.2
2016-03-14 06:00 | 38271 | 6503.9474 | 155865.9828 | 59.77 | 765.42
2016-03-14 07:00 | 39825 | 5331.5044 | 171191.9708 | 59.78 | 756.675
2016-03-14 08:00 | 40843 | 5598.4189 | 176554.4708 | 59.78 | 776.017
2016-03-14 09:00 | 41535 | 5386.7682 | 177137.414 | 59.78 | 789.165
2016-03-14 10:00 | 41425 | 6403.4731 | 178453.2888 | 59.78 | 787.075
2016-03-14 11:00 | 41396 | 7509.2751 | 173937.5924 | 59.78 | 786.524
2016-03-14 12:00 | 41584 | 6401.4261 | 173937.5924 | 59.78 | 790.096
2016-03-14 13:00 | 41501 | 6742.8741 | 173937.5924 | 59.78 | 788.519
2016-03-14 14:00 | 41429 | 6718.5908 | 174788.1024 | 59.78 | 787.151
2016-03-14 15:00 | 41612 | 7031.4095 | 171180.7824 | 59.78 | 790.628
2016-03-14 16:00 | 41970 | 8113.2496 | 166834.2824 | 59.78 | 797.43
2016-03-14 17:00 | 42344 | 9950.4531 | 160136.1024 | 59.77 | 846.88
2016-03-14 18:00 | 43047 | 11811.234 | 154482.4764 | 59.77 | 860.94
2016-03-14 19:00 | 43751 | 13327.1902 | 155078.4264 | 59.77 | 875.02
2016-03-14 20:00 | 45787 | 13650.0385 | 156957.7264 | 59.77 | 915.74
2016-03-14 21:00 | 44773 | 12910.2992 | 156957.7264 | 59.77 | 895.46
2016-03-14 22:00 | 42658 | 10982.6221 | 155941.7264 | 59.77 | 853.16
2016-03-14 23:00 | 39724 | 8695.9531 | 155941.7264 | 59.77 | 794.48
2016-03-15 | 33231 | 7917.6547 | 155941.7264 | 59.79 | 598.158
2016-03-15 01:00 | 31967 | 7072.7758 | 155941.7264 | 59.79 | 575.406
2016-03-15 02:00 | 31356 | 6924.0689 | 155941.7264 | 59.79 | 564.408
2016-03-15 03:00 | 31287 | 7130.6956 | 155941.7264 | 59.79 | 563.166
2016-03-15 04:00 | 32025 | 6728.9136 | 155941.7264 | 59.79 | 576.45
2016-03-15 05:00 | 33954 | 6332.0273 | 154052.7764 | 59.77 | 679.08
2016-03-15 06:00 | 37011 | 6057.1637 | 159186.4728 | 59.77 | 740.22
2016-03-15 07:00 | 39388 | 7266.4348 | 162535.5628 | 59.77 | 787.76
2016-03-15 08:00 | 40205 | 8766.711 | 162535.5628 | 59.77 | 804.1
2016-03-15 09:00 | 41154 | 8895.4957 | 163551.5628 | 59.77 | 823.08
2016-03-15 10:00 | 41871 | 10282.8667 | 162819.9708 | 59.77 | 837.42
2016-03-15 11:00 | 41923 | 11199.1749 | 157799.4828 | 59.77 | 838.46
2016-03-15 12:00 | 42169 | 12015.6538 | 155366.4828 | 59.77 | 843.38
2016-03-15 13:00 | 42085 | 12192.3405 | 155366.4828 | 59.77 | 841.7
2016-03-15 14:00 | 41964 | 11694.1798 | 156868.1328 | 59.77 | 839.28
2016-03-15 15:00 | 41729 | 13728.8518 | 156868.1328 | 59.77 | 834.58
2016-03-15 16:00 | 41624 | 13706.4984 | 156868.1328 | 59.77 | 832.48
2016-03-15 17:00 | 41525 | 13259.4999 | 156868.1328 | 59.77 | 830.5
2016-03-15 18:00 | 41634 | 14262.0887 | 159322.5328 | 59.79 | 749.412
2016-03-15 19:00 | 41743 | 13715.943 | 159322.5328 | 59.77 | 834.86
2016-03-15 20:00 | 42996 | 12339.7995 | 156840.9328 | 59.77 | 859.92
2016-03-15 21:00 | 41887 | 10256.5282 | 157120.9328 | 59.77 | 837.74
2016-03-15 22:00 | 39267 | 8410.0897 | 156840.9328 | 59.77 | 785.34
2016-03-15 23:00 | 36402 | 7090.7655 | 154847.3828 | 59.77 | 728.04
2016-03-16 | 34388 | 6015.6683 | 154847.3828 | 59.77 | 687.76
2016-03-16 01:00 | 33112 | 5772.9593 | 154847.3828 | 59.79 | 596.016
2016-03-16 02:00 | 32438 | 5572.5635 | 154847.3828 | 59.79 | 583.884
2016-03-16 03:00 | 32297 | 6285.928 | 154711.3828 | 59.79 | 581.346
2016-03-16 04:00 | 32774 | 6505.2145 | 154711.3828 | 59.79 | 589.932
2016-03-16 05:00 | 34800 | 5674.842 | 156600.3328 | 59.77 | 696
2016-03-16 06:00 | 37981 | 4866.9707 | 169166.2008 | 59.78 | 721.639
2016-03-16 07:00 | 40161 | 5961.0497 | 176122.6108 | 59.78 | 763.059
2016-03-16 08:00 | 40840 | 7255.898 | 176122.6108 | 59.78 | 775.96
2016-03-16 09:00 | 41737 | 6970.2288 | 180469.1108 | 59.78 | 793.003
2016-03-16 10:00 | 42491 | 6773.4255 | 186905.0068 | 59.78 | 807.329
2016-03-16 11:00 | 42793 | 5187.8841 | 198233.6968 | 59.77 | 855.86
2016-03-16 12:00 | 42532 | 4665.5181 | 199601.298 | 59.77 | 850.64
2016-03-16 13:00 | 42085 | 4405.6113 | 199601.298 | 59.77 | 841.7
2016-03-16 14:00 | 41531 | 3687.2047 | 202729.798 | 59.77 | 830.62
2016-03-16 15:00 | 41051 | 4506.5581 | 201713.798 | 59.78 | 779.969
2016-03-16 16:00 | 40683 | 4741.7985 | 201095.798 | 59.78 | 772.977
2016-03-16 17:00 | 40592 | 4132.3996 | 201095.798 | 59.78 | 771.248
2016-03-16 18:00 | 41152 | 3181.6175 | 217544.0464 | 59.77 | 823.04
2016-03-16 19:00 | 41713 | 1697.1468 | 220780.7164 | 59.77 | 834.26
2016-03-16 20:00 | 43017 | 962.3145 | 224673.2095 | 59.77 | 860.34
2016-03-16 21:00 | 42168 | 551.8596 | 224278.3164 | 59.77 | 843.36
2016-03-16 22:00 | 40133 | 466.941 | 212012.3164 | 59.77 | 802.66
2016-03-16 23:00 | 37400 | 664.5555 | 201319.8564 | 59.78 | 710.6
2016-03-17 | 33492 | 772.748 | 193736.6864 | 59.78 | 636.348
2016-03-17 01:00 | 32608 | 1025.4638 | 191779.4584 | 59.77 | 652.16
2016-03-17 02:00 | 32224 | 1294.3288 | 185927.3584 | 59.77 | 644.48
2016-03-17 03:00 | 32282 | 2014.6509 | 186063.3584 | 59.77 | 645.64
2016-03-17 04:00 | 33102 | 3005.2199 | 186063.3584 | 59.77 | 662.04
2016-03-17 05:00 | 35296 | 3392.5323 | 186063.3584 | 59.77 | 705.92
2016-03-17 06:00 | 38731 | 4772.4672 | 186063.3584 | 59.78 | 735.889
2016-03-17 07:00 | 40869 | 4983.9078 | 186063.3584 | 59.78 | 776.511
2016-03-17 08:00 | 40639 | 5733.8384 | 186063.3584 | 59.78 | 772.141
2016-03-17 09:00 | 40177 | 3391.0996 | 192881.1784 | 59.78 | 763.363
2016-03-17 10:00 | 39744 | 2487.7655 | 192881.1784 | 59.78 | 755.136
2016-03-17 11:00 | 39115 | 2147.1557 | 192881.1784 | 59.78 | 743.185
2016-03-17 12:00 | 38434 | 1698.0748 | 190863.3272 | 59.78 | 730.246
2016-03-17 13:00 | 38016 | 1581.3331 | 188888.0192 | 59.78 | 722.304
2016-03-17 14:00 | 37531 | 1788.4407 | 186255.0312 | 59.78 | 713.089
2016-03-17 15:00 | 37300 | 2246.7608 | 179664.6508 | 59.78 | 708.7
2016-03-17 16:00 | 37305 | 3328.2604 | 177083.4248 | 59.78 | 708.795
2016-03-17 17:00 | 37163 | 4350.4958 | 169387.8348 | 59.78 | 706.097
2016-03-17 18:00 | 37306 | 4485.4848 | 169339.8348 | 59.78 | 708.814
2016-03-17 19:00 | 37449 | 4963.117 | 169339.8348 | 59.77 | 748.98
2016-03-17 20:00 | 39049 | 5817.9967 | 169339.8348 | 59.78 | 741.931
2016-03-17 21:00 | 38321 | 6626.8038 | 160620.1348 | 59.77 | 766.42
2016-03-17 22:00 | 36442 | 6121.6709 | 157035.8648 | 59.77 | 728.84
2016-03-17 23:00 | 34003 | 5827.5786 | 156261.5348 | 59.77 | 680.06
2016-03-18 | 33296 | 4979.4345 | 156261.5348 | 59.77 | 665.92
2016-03-18 01:00 | 32330 | 5045.7972 | 156261.5348 | 59.79 | 581.94
2016-03-18 02:00 | 31998 | 4747.1626 | 156261.5348 | 59.79 | 575.964
2016-03-18 03:00 | 32171 | 4603.1218 | 156047.646 | 59.77 | 643.42
2016-03-18 04:00 | 32998 | 4426.2646 | 156047.646 | 59.77 | 659.96
2016-03-18 05:00 | 35342 | 3913.5936 | 161654.046 | 59.77 | 706.84
2016-03-18 06:00 | 38968 | 3424.2016 | 183492.446 | 59.78 | 740.392
2016-03-18 07:00 | 41382 | 3698.9829 | 196467.69 | 59.77 | 827.64
2016-03-18 08:00 | 41358 | 4101.3833 | 196467.69 | 59.78 | 785.802
2016-03-18 09:00 | 41013 | 2527.5347 | 198619.69 | 59.77 | 820.26
2016-03-18 10:00 | 40718 | 2601.693 | 197603.69 | 59.77 | 814.36
2016-03-18 11:00 | 40204 | 4152.4427 | 189120.9036 | 59.78 | 763.876
2016-03-18 12:00 | 39520 | 4348.2667 | 189120.9036 | 59.78 | 750.88
2016-03-18 13:00 | 39356 | 4083.9787 | 183514.5036 | 59.78 | 747.764
2016-03-18 14:00 | 39191 | 4519.0754 | 177041.1636 | 59.78 | 744.629
2016-03-18 15:00 | 38987 | 4768.4417 | 173568.8736 | 59.78 | 740.753
2016-03-18 16:00 | 38825 | 4892.6583 | 170369.6476 | 59.78 | 737.675
2016-03-18 17:00 | 38426 | 5437.0436 | 165432.1396 | 59.78 | 730.094
2016-03-18 18:00 | 38524 | 6850.2544 | 157018.6696 | 59.77 | 770.48
2016-03-18 19:00 | 38621 | 9442.8664 | 142446.3996 | 59.77 | 772.42
2016-03-18 20:00 | 40421 | 12053.9263 | 139964.7996 | 59.77 | 808.42
2016-03-18 21:00 | 39660 | 13116.2139 | 136154.9996 | 59.79 | 713.88
2016-03-18 22:00 | 37581 | 13533.3925 | 136154.9996 | 59.79 | 676.458
2016-03-18 23:00 | 35103 | 14172.8292 | 136154.9996 | 59.79 | 631.854
2016-03-19 | 34967 | 13599.1797 | 133835.7564 | 59.79 | 629.406
2016-03-19 01:00 | 33945 | 12610.6659 | 133835.7564 | 59.79 | 611.01
2016-03-19 02:00 | 33493 | 13033.4052 | 133835.7564 | 59.79 | 602.874
2016-03-19 03:00 | 33486 | 13454.0385 | 134049.6452 | 59.79 | 602.748
2016-03-19 04:00 | 34033 | 13760.649 | 134049.6452 | 59.79 | 612.594
2016-03-19 05:00 | 36227 | 14214.6335 | 136482.6452 | 59.79 | 652.086
2016-03-19 06:00 | 39749 | 13841.5006 | 136770.6452 | 59.79 | 715.482
2016-03-19 07:00 | 41571 | 14068.8433 | 136770.6452 | 59.77 | 831.42
2016-03-19 08:00 | 41782 | 13877.9473 | 136770.6452 | 59.77 | 835.64
2016-03-19 09:00 | 41941 | 14674.6778 | 136770.6452 | 59.79 | 754.938
2016-03-19 10:00 | 42031 | 14487.7707 | 136770.6452 | 59.77 | 840.62
2016-03-19 11:00 | 41720 | 13790.7405 | 136300.7702 | 59.77 | 834.4
2016-03-19 12:00 | 41194 | 13293.0092 | 136300.7702 | 59.77 | 823.88
2016-03-19 13:00 | 40931 | 11957.6249 | 144832.7202 | 59.77 | 818.62
2016-03-19 14:00 | 40555 | 10786.0294 | 144832.7202 | 59.77 | 811.1
2016-03-19 15:00 | 40479 | 10511.1969 | 145848.7202 | 59.77 | 809.58
2016-03-19 16:00 | 40147 | 10378.3699 | 144832.7202 | 59.77 | 802.94
2016-03-19 17:00 | 39637 | 10969.3583 | 143913.4082 | 59.77 | 792.74
2016-03-19 18:00 | 39676 | 12292.5703 | 137071.1682 | 59.79 | 714.168
2016-03-19 19:00 | 39714 | 13672.3402 | 133851.2482 | 59.79 | 714.852
2016-03-19 20:00 | 41257 | 13880.8883 | 136332.8482 | 59.79 | 742.626
2016-03-19 21:00 | 40401 | 14178.0922 | 131385.1682 | 59.79 | 727.218
2016-03-19 22:00 | 38722 | 15573.48 | 127608.7682 | 59.79 | 696.996
2016-03-19 23:00 | 36504 | 15650.3114 | 127682.5873 | 59.79 | 657.072
2016-03-20 | 34759 | 14827.7088 | 127682.5873 | 59.79 | 625.662
2016-03-20 01:00 | 33401 | 11562.5894 | 127682.5873 | 59.79 | 601.218
2016-03-20 02:00 | 32625 | 12490.3181 | 127682.5873 | 59.79 | 587.25
2016-03-20 03:00 | 32254 | 14257.9767 | 127682.5873 | 59.79 | 580.572
2016-03-20 04:00 | 32320 | 14430.0896 | 128235.2203 | 59.79 | 581.76
2016-03-20 05:00 | 33343 | 14486.6901 | 132032.6185 | 59.79 | 600.174
2016-03-20 06:00 | 35151 | 14559.357 | 131304.9073 | 59.79 | 632.718
2016-03-20 07:00 | 37616 | 14721.4497 | 131231.0882 | 59.79 | 677.088
2016-03-20 08:00 | 39588 | 14474.5918 | 131231.0882 | 59.79 | 712.584
2016-03-20 09:00 | 42092 | 15050.5035 | 137670.9282 | 59.79 | 757.656
2016-03-20 10:00 | 44339 | 15066.9674 | 149297.2178 | 59.77 | 886.78
2016-03-20 11:00 | 45633 | 14436.5146 | 161616.2708 | 59.77 | 912.66
2016-03-20 12:00 | 46164 | 14550.5325 | 159427.8628 | 59.77 | 923.28
2016-03-20 13:00 | 45982 | 15998.6214 | 159427.8628 | 59.77 | 919.64
2016-03-20 14:00 | 45754 | 16580.1303 | 157106.8483 | 59.77 | 915.08
2016-03-20 15:00 | 45796 | 16614.4723 | 157106.8483 | 59.77 | 915.92
2016-03-20 16:00 | 46431 | 16638.2196 | 157106.8483 | 59.77 | 928.62
2016-03-20 17:00 | 47250 | 16526.8579 | 158617.1683 | 59.77 | 945
2016-03-20 18:00 | 48646 | 15528.4158 | 201900.8697 | 59.78 | 924.274
2016-03-20 19:00 | 50042 | 13688.6493 | 203317.4397 | 59.78 | 950.798
2016-03-20 20:00 | 51909 | 9952.6552 | 235004.3857 | 59.77 | 1038.18
2016-03-20 21:00 | 51537 | 7259.3806 | 236603.3288 | 59.78 | 979.203
2016-03-20 22:00 | 50122 | 6556.3173 | 239796.7857 | 59.78 | 952.318
2016-03-20 23:00 | 48313 | 6274.545 | 241823.5937 | 59.77 | 966.26
2016-03-21 | 43039 | 7903.1291 | 222407.7193 | 59.78 | 817.741
2016-03-21 01:00 | 42209 | 10070.2727 | 222407.7193 | 59.77 | 844.18
2016-03-21 02:00 | 41774 | 10541.0116 | 193727.7283 | 59.77 | 835.48
2016-03-21 03:00 | 41688 | 10909.0448 | 193727.7283 | 59.77 | 833.76
2016-03-21 04:00 | 41918 | 11186.755 | 193727.7283 | 59.77 | 838.36
2016-03-21 05:00 | 42699 | 10638.1682 | 193727.7283 | 59.77 | 853.98
2016-03-21 06:00 | 44291 | 10495.9145 | 193727.7283 | 59.78 | 841.529
2016-03-21 07:00 | 45948 | 9981.6802 | 196160.7283 | 59.78 | 873.012
2016-03-21 08:00 | 46771 | 9322.9896 | 201226.9683 | 59.78 | 888.649
2016-03-21 09:00 | 46829 | 8489.3707 | 202825.9114 | 59.77 | 936.58
2016-03-21 10:00 | 46304 | 9039.776 | 198958.4903 | 59.78 | 879.776
2016-03-21 11:00 | 45477 | 10713.1602 | 178868.1099 | 59.78 | 864.063
2016-03-21 12:00 | 44495 | 12059.9815 | 173473.3479 | 59.77 | 889.9
2016-03-21 13:00 | 43258 | 12429.5971 | 173473.3479 | 59.77 | 865.16
2016-03-21 14:00 | 41979 | 12349.8826 | 173473.3479 | 59.77 | 839.58
2016-03-21 15:00 | 40900 | 13196.5893 | 173473.3479 | 59.77 | 818
2016-03-21 16:00 | 40353 | 12903.4003 | 173473.3479 | 59.79 | 726.354
2016-03-21 17:00 | 40344 | 12079.785 | 170828.5679 | 59.77 | 806.88
2016-03-21 18:00 | 41196 | 10272.6238 | 170054.2379 | 59.77 | 823.92
2016-03-21 19:00 | 42049 | 5695.5392 | 190184.8223 | 59.78 | 798.931
2016-03-21 20:00 | 43864 | 2508.5568 | 218971.964 | 59.77 | 877.28
2016-03-21 21:00 | 43023 | 1674.2361 | 218876.2206 | 59.77 | 860.46
2016-03-21 22:00 | 40834 | 821.9436 | 214080.4107 | 59.77 | 816.68
2016-03-21 23:00 | 38052 | 681.3522 | 213997.2857 | 59.78 | 722.988
2016-03-22 | 38018 | 978.3327 | 219017.7737 | 59.78 | 722.342
2016-03-22 01:00 | 37314 | 1605.5736 | 217868.8817 | 59.78 | 708.966
2016-03-22 02:00 | 37269 | 2630.1197 | 217868.8817 | 59.78 | 708.111
2016-03-22 03:00 | 37848 | 4072.146 | 217868.8817 | 59.78 | 719.112
2016-03-22 04:00 | 39346 | 5801.952 | 217868.8817 | 59.78 | 747.574
2016-03-22 05:00 | 42754 | 7533.4384 | 217868.8817 | 59.78 | 812.326
2016-03-22 06:00 | 48516 | 7569.4047 | 226626.4517 | 59.77 | 970.32
2016-03-22 07:00 | 50912 | 7891.5606 | 227642.4517 | 59.78 | 967.328
2016-03-22 08:00 | 49034 | 8361.1434 | 219513.7757 | 59.77 | 980.68
2016-03-22 09:00 | 46804 | 6598.1858 | 216160.0653 | 59.77 | 936.08
2016-03-22 10:00 | 44981 | 5085.2229 | 211660.0653 | 59.77 | 899.62
2016-03-22 11:00 | 43163 | 5942.3369 | 194844.7053 | 59.78 | 820.097
2016-03-22 12:00 | 41814 | 6484.8802 | 186158.8093 | 59.78 | 794.466
2016-03-22 13:00 | 40925 | 6827.8384 | 182938.8893 | 59.78 | 777.575
2016-03-22 14:00 | 40186 | 6467.5177 | 177788.6393 | 59.78 | 763.534
2016-03-22 15:00 | 39887 | 5956.0191 | 177788.6393 | 59.78 | 757.853
2016-03-22 16:00 | 39924 | 6339.2407 | 173442.1393 | 59.78 | 758.556
2016-03-22 17:00 | 39729 | 6154.8792 | 176086.9193 | 59.78 | 754.851
2016-03-22 18:00 | 40114 | 6465.2882 | 176861.2493 | 59.78 | 762.166
2016-03-22 19:00 | 40498 | 9172.9172 | 164168.2493 | 59.77 | 809.96
2016-03-22 20:00 | 42546 | 11404.8901 | 161735.2493 | 59.77 | 850.92
2016-03-22 21:00 | 41624 | 13162.1534 | 146468.6849 | 59.77 | 832.48
2016-03-22 22:00 | 38997 | 14442.9528 | 134372.7249 | 59.79 | 701.946
2016-03-22 23:00 | 36189 | 14224.4213 | 134455.8499 | 59.79 | 651.402
2016-03-23 | 34069 | 14232.5881 | 134455.8499 | 59.79 | 613.242
2016-03-23 01:00 | 33325 | 14120.3136 | 134455.8499 | 59.79 | 599.85
2016-03-23 02:00 | 33029 | 13868.0338 | 134455.8499 | 59.79 | 594.522
2016-03-23 03:00 | 33377 | 13432.9018 | 134455.8499 | 59.79 | 600.786
2016-03-23 04:00 | 34450 | 14104.8876 | 138063.1699 | 59.79 | 620.1
2016-03-23 05:00 | 37516 | 13871.0657 | 139956.7319 | 59.79 | 675.288
2016-03-23 06:00 | 42937 | 13553.7751 | 153966.4683 | 59.77 | 858.74
2016-03-23 07:00 | 45274 | 13326.9732 | 164099.3363 | 59.77 | 905.48
2016-03-23 08:00 | 43724 | 12928.1958 | 164099.3363 | 59.77 | 874.48
2016-03-23 09:00 | 42440 | 13059.096 | 164099.3363 | 59.77 | 848.8
2016-03-23 10:00 | 41508 | 12535.1707 | 164099.3363 | 59.77 | 830.16
2016-03-23 11:00 | 40958 | 12141.7543 | 164099.3363 | 59.77 | 819.16
2016-03-23 12:00 | 40518 | 11382.7947 | 164099.3363 | 59.77 | 810.36
2016-03-23 13:00 | 40419 | 10720.0812 | 161644.9363 | 59.77 | 808.38
2016-03-23 14:00 | 40106 | 9763.4907 | 161644.9363 | 59.77 | 802.12
2016-03-23 15:00 | 40122 | 9202.6024 | 161644.9363 | 59.77 | 802.44
2016-03-23 16:00 | 40322 | 9062.3965 | 162660.9363 | 59.77 | 806.44
2016-03-23 17:00 | 40120 | 9452.5585 | 161644.9363 | 59.77 | 802.4
2016-03-23 18:00 | 40244 | 10774.4403 | 152925.2363 | 59.77 | 804.88
2016-03-23 19:00 | 40368 | 11672.3294 | 151627.6163 | 59.77 | 807.36
2016-03-23 20:00 | 42343 | 12091.0059 | 151627.6163 | 59.77 | 846.86
2016-03-23 21:00 | 41318 | 12675.1679 | 141473.4319 | 59.77 | 826.36
2016-03-23 22:00 | 38485 | 12723.3001 | 132597.3919 | 59.79 | 692.73
2016-03-23 23:00 | 35116 | 11352.5781 | 132597.3919 | 59.79 | 632.088
2016-03-24 | 30027 | 10046.4852 | 132597.3919 | 59.79 | 540.486
2016-03-24 01:00 | 28978 | 8178.2018 | 132597.3919 | 59.79 | 521.604
2016-03-24 02:00 | 28413 | 6843.5403 | 132597.3919 | 59.79 | 511.434
2016-03-24 03:00 | 28221 | 7855.4819 | 132006.3839 | 59.79 | 507.978
2016-03-24 04:00 | 28679 | 9049.0062 | 134439.3839 | 59.79 | 516.222
2016-03-24 05:00 | 30561 | 8504.4725 | 139762.0739 | 59.79 | 550.098
2016-03-24 06:00 | 34526 | 7567.2684 | 143654.9861 | 59.79 | 621.468
2016-03-24 07:00 | 36647 | 6985.0761 | 155818.4025 | 59.77 | 732.94
2016-03-24 08:00 | 36064 | 6519.8335 | 155818.4025 | 59.77 | 721.28
2016-03-24 09:00 | 36282 | 6518.0738 | 155818.4025 | 59.77 | 725.64
2016-03-24 10:00 | 36745 | 6677.7287 | 155818.4025 | 59.77 | 734.9
2016-03-24 11:00 | 36960 | 6080.7867 | 156834.4025 | 59.77 | 739.2
2016-03-24 12:00 | 36897 | 6067.0477 | 156834.4025 | 59.77 | 737.94
2016-03-24 13:00 | 36919 | 7771.1269 | 146266.9517 | 59.77 | 738.38
2016-03-24 14:00 | 36902 | 9460.4031 | 137535.7137 | 59.79 | 664.236
2016-03-24 15:00 | 36997 | 9920.7058 | 132402.0173 | 59.79 | 665.946
2016-03-24 16:00 | 37165 | 10378.723 | 132402.0173 | 59.79 | 668.97
2016-03-24 17:00 | 37247 | 11168.334 | 132402.0173 | 59.79 | 670.446
2016-03-24 18:00 | 37671 | 11850.3983 | 132402.0173 | 59.79 | 678.078
2016-03-24 19:00 | 38095 | 11357.7626 | 136087.1373 | 59.79 | 685.71
2016-03-24 20:00 | 38724 | 10426.3092 | 137103.1373 | 59.77 | 774.48
2016-03-24 21:00 | 37655 | 11589.0915 | 132277.3373 | 59.79 | 677.79
2016-03-24 22:00 | 35079 | 11021.445 | 132277.3373 | 59.79 | 631.422
2016-03-24 23:00 | 32383 | 9448.3078 | 132277.3373 | 59.79 | 582.894
2016-03-25 | 30557 | 8763.7593 | 130097.8038 | 59.79 | 550.026
2016-03-25 01:00 | 29534 | 8804.1843 | 130097.8038 | 59.79 | 531.612
2016-03-25 02:00 | 29060 | 8474.7393 | 130097.8038 | 59.79 | 523.08
2016-03-25 03:00 | 29029 | 9041.3001 | 130688.8118 | 59.79 | 522.522
2016-03-25 04:00 | 29684 | 9947.3676 | 133121.8118 | 59.79 | 534.312
2016-03-25 05:00 | 31873 | 8994.7102 | 138699.6318 | 59.79 | 573.714
2016-03-25 06:00 | 36450 | 9381.8527 | 138699.6318 | 59.79 | 656.1
2016-03-25 07:00 | 38581 | 9647.6756 | 142509.4318 | 59.77 | 771.62
2016-03-25 08:00 | 38063 | 9947.1139 | 142509.4318 | 59.77 | 761.26
2016-03-25 09:00 | 38100 | 9523.6614 | 142509.4318 | 59.77 | 762
2016-03-25 10:00 | 38336 | 10195.367 | 142509.4318 | 59.77 | 766.72
2016-03-25 11:00 | 38294 | 9345.7467 | 142509.4318 | 59.77 | 765.88
2016-03-25 12:00 | 37928 | 6730.3751 | 159644.4618 | 59.77 | 758.56
2016-03-25 13:00 | 37635 | 6208.2278 | 160660.4618 | 59.77 | 752.7
2016-03-25 14:00 | 37211 | 5055.1831 | 164136.0318 | 59.77 | 744.22
2016-03-25 15:00 | 36798 | 3903.5495 | 172325.6578 | 59.78 | 699.162
2016-03-25 16:00 | 36681 | 3096.1754 | 182479.8422 | 59.78 | 696.939
2016-03-25 17:00 | 36307 | 2101.7202 | 182479.8422 | 59.78 | 689.833
2016-03-25 18:00 | 36461 | 1725.7251 | 182479.8422 | 59.78 | 692.759
2016-03-25 19:00 | 36615 | 1617.9347 | 182479.8422 | 59.78 | 695.685
2016-03-25 20:00 | 38720 | 2217.9206 | 183736.3187 | 59.78 | 735.68
2016-03-25 21:00 | 37954 | 2895.6768 | 182479.8422 | 59.78 | 721.126
2016-03-25 22:00 | 35717 | 3489.1522 | 167061.9622 | 59.77 | 714.34
2016-03-25 23:00 | 33268 | 4985.7002 | 148658.3762 | 59.77 | 665.36
2016-03-26 | 33216 | 7060.5954 | 143832.3762 | 59.79 | 597.888
2016-03-26 01:00 | 33154 | 9016.0524 | 143832.3762 | 59.79 | 596.772
2016-03-26 02:00 | 32914 | 10246.1399 | 143832.3762 | 59.79 | 592.452
2016-03-26 03:00 | 33093 | 10859.203 | 143832.3762 | 59.79 | 595.674
2016-03-26 04:00 | 34099 | 11301.2721 | 143832.3762 | 59.79 | 613.782
2016-03-26 05:00 | 36908 | 11843.4107 | 146011.9097 | 59.79 | 664.344
2016-03-26 06:00 | 42143 | 12002.2995 | 151200.0997 | 59.77 | 842.86
2016-03-26 07:00 | 44413 | 11595.2734 | 162303.1528 | 59.78 | 843.847
2016-03-26 08:00 | 42878 | 11097.5643 | 161840.6897 | 59.77 | 857.56
2016-03-26 09:00 | 41909 | 12248.3232 | 150670.5053 | 59.77 | 838.18
2016-03-26 10:00 | 41282 | 12612.6811 | 145604.2653 | 59.77 | 825.64
2016-03-26 11:00 | 40667 | 13117.5871 | 137436.6653 | 59.77 | 813.34
2016-03-26 12:00 | 40022 | 13364.9334 | 133626.8653 | 59.79 | 720.396
2016-03-26 13:00 | 40142 | 13680.9355 | 133626.8653 | 59.79 | 722.556
2016-03-26 14:00 | 40133 | 14274.0574 | 132060.9953 | 59.79 | 722.394
2016-03-26 15:00 | 40087 | 14946.2124 | 132060.9953 | 59.79 | 721.566
2016-03-26 16:00 | 39866 | 14853.6449 | 132060.9953 | 59.79 | 717.588
2016-03-26 17:00 | 39443 | 14809.6715 | 132060.9953 | 59.79 | 709.974
2016-03-26 18:00 | 38943 | 15018.1227 | 132060.9953 | 59.79 | 700.974
2016-03-26 19:00 | 38444 | 14845.9265 | 132060.9953 | 59.79 | 691.992
2016-03-26 20:00 | 40124 | 14403.4347 | 132060.9953 | 59.79 | 722.232
2016-03-26 21:00 | 39363 | 14608.6583 | 132060.9953 | 59.79 | 708.534
2016-03-26 22:00 | 37632 | 14996.9989 | 132060.9953 | 59.79 | 677.376
2016-03-26 23:00 | 35365 | 15224.8228 | 132134.8144 | 59.79 | 636.57
2016-03-27 | 35231 | 15804.5001 | 132134.8144 | 59.79 | 634.158
2016-03-27 01:00 | 34200 | 14604.6031 | 132134.8144 | 59.79 | 615.6
2016-03-27 02:00 | 33423 | 13428.4121 | 132134.8144 | 59.79 | 601.614
2016-03-27 03:00 | 32940 | 13465.7723 | 132134.8144 | 59.79 | 592.92
2016-03-27 04:00 | 33186 | 13452.8166 | 132317.8024 | 59.79 | 597.348
2016-03-27 05:00 | 34171 | 13719.5027 | 133620.5284 | 59.79 | 615.078
2016-03-27 06:00 | 36193 | 13572.0487 | 133376.5444 | 59.79 | 651.474
2016-03-27 07:00 | 38003 | 12663.0019 | 133302.7253 | 59.79 | 684.054
2016-03-27 08:00 | 39016 | 10463.6911 | 140332.4453 | 59.77 | 780.32
2016-03-27 09:00 | 40178 | 11447.2773 | 141348.4453 | 59.77 | 803.56
2016-03-27 10:00 | 40698 | 12499.8301 | 140332.4453 | 59.77 | 813.96
2016-03-27 11:00 | 40799 | 11952.1306 | 141348.4453 | 59.77 | 815.98
2016-03-27 12:00 | 40741 | 11878.1943 | 140332.4453 | 59.77 | 814.82
2016-03-27 13:00 | 40615 | 12627.9658 | 140332.4453 | 59.77 | 812.3
2016-03-27 14:00 | 40522 | 13159.1449 | 142589.0561 | 59.79 | 729.396
2016-03-27 15:00 | 40607 | 13803.4793 | 142589.0561 | 59.79 | 730.926
2016-03-27 16:00 | 40882 | 13546.3681 | 142589.0561 | 59.79 | 735.876
2016-03-27 17:00 | 40893 | 13415.1448 | 142589.0561 | 59.79 | 736.074
2016-03-27 18:00 | 40851 | 13196.808 | 142589.0561 | 59.77 | 817.02
2016-03-27 19:00 | 40809 | 12820.8805 | 142589.0561 | 59.77 | 816.18
2016-03-27 20:00 | 42353 | 10820.7798 | 157736.6725 | 59.77 | 847.06
2016-03-27 21:00 | 41224 | 7513.1104 | 164356.1036 | 59.78 | 783.256
2016-03-27 22:00 | 39399 | 6427.7577 | 163773.1605 | 59.78 | 748.581
2016-03-27 23:00 | 37141 | 5497.6212 | 159149.8405 | 59.77 | 742.82
2016-03-28 | 35549 | 6063.9841 | 149510.2505 | 59.77 | 710.98
2016-03-28 01:00 | 34146 | 7328.315 | 149510.2505 | 59.79 | 614.628
2016-03-28 02:00 | 33468 | 8527.8244 | 149510.2505 | 59.79 | 602.424
2016-03-28 03:00 | 33052 | 9306.9944 | 149510.2505 | 59.79 | 594.936
2016-03-28 04:00 | 33202 | 10243.454 | 149510.2505 | 59.79 | 597.636
2016-03-28 05:00 | 33822 | 10429.5174 | 149510.2505 | 59.79 | 608.796
2016-03-28 06:00 | 35205 | 9825.7117 | 149510.2505 | 59.79 | 633.69
2016-03-28 07:00 | 36406 | 8347.6089 | 149510.2505 | 59.77 | 728.12
2016-03-28 08:00 | 37946 | 7031.2995 | 156604.8605 | 59.77 | 758.92
2016-03-28 09:00 | 39059 | 7451.3975 | 156604.8605 | 59.77 | 781.18
2016-03-28 10:00 | 39468 | 8730.9172 | 156604.8605 | 59.77 | 789.36
2016-03-28 11:00 | 39603 | 9899.6775 | 156604.8605 | 59.77 | 792.06
2016-03-28 12:00 | 39559 | 10597.1584 | 154150.4605 | 59.77 | 791.18
2016-03-28 13:00 | 39258 | 11221.2804 | 153554.5105 | 59.77 | 785.16
2016-03-28 14:00 | 39051 | 11288.3102 | 153554.5105 | 59.77 | 781.02
2016-03-28 15:00 | 38844 | 11437.2041 | 153554.5105 | 59.79 | 699.192
2016-03-28 16:00 | 38963 | 10800.5425 | 153554.5105 | 59.77 | 779.26
2016-03-28 17:00 | 39195 | 10409.7208 | 152691.2105 | 59.77 | 783.9
2016-03-28 18:00 | 39897 | 9565.8706 | 179245.8589 | 59.77 | 797.94
2016-03-28 19:00 | 40598 | 4800.6029 | 195290.4689 | 59.78 | 771.362
2016-03-28 20:00 | 43006 | 2008.3401 | 221872.3449 | 59.77 | 860.12
2016-03-28 21:00 | 42384 | 1199.395 | 222048.3449 | 59.77 | 847.68
2016-03-28 22:00 | 39957 | 1351.6917 | 213379.5669 | 59.77 | 799.14
2016-03-28 23:00 | 36931 | 1362.2849 | 203179.6305 | 59.78 | 701.689
2016-03-29 | 32600 | 2318.4211 | 196676.9145 | 59.77 | 652
2016-03-29 01:00 | 31636 | 3413.4848 | 196676.9145 | 59.77 | 632.72
2016-03-29 02:00 | 31474 | 4545.6094 | 180228.6661 | 59.79 | 566.532
2016-03-29 03:00 | 31788 | 5836.1606 | 180228.6661 | 59.79 | 572.184
2016-03-29 04:00 | 32944 | 6687.9696 | 180228.6661 | 59.79 | 592.992
2016-03-29 05:00 | 35968 | 7982.5741 | 180228.6661 | 59.77 | 719.36
2016-03-29 06:00 | 41370 | 8789.8186 | 180228.6661 | 59.78 | 786.03
2016-03-29 07:00 | 43693 | 8321.1931 | 188917.2261 | 59.78 | 830.167
2016-03-29 08:00 | 42485 | 8021.0024 | 188917.2261 | 59.78 | 807.215
2016-03-29 09:00 | 41514 | 4576.3153 | 199071.4105 | 59.78 | 788.766
2016-03-29 10:00 | 41014 | 3533.2926 | 200087.4105 | 59.78 | 779.266
2016-03-29 11:00 | 40661 | 5724.3977 | 197159.0105 | 59.78 | 772.559
2016-03-29 12:00 | 40516 | 6529.7352 | 197159.0105 | 59.78 | 769.804
2016-03-29 13:00 | 40516 | 6652.1164 | 197754.9605 | 59.78 | 769.804
2016-03-29 14:00 | 40526 | 5950.7203 | 197754.9605 | 59.78 | 769.994
2016-03-29 15:00 | 40836 | 5366.6666 | 197754.9605 | 59.78 | 775.884
2016-03-29 16:00 | 41133 | 4685.9069 | 196451.7173 | 59.78 | 781.527
2016-03-29 17:00 | 40887 | 4373.4797 | 197315.0173 | 59.78 | 776.853
2016-03-29 18:00 | 40761 | 5067.8056 | 193429.6473 | 59.78 | 774.459
2016-03-29 19:00 | 40635 | 7513.1708 | 173493.5073 | 59.78 | 772.065
2016-03-29 20:00 | 42654 | 9665.1069 | 170294.2813 | 59.78 | 810.426
2016-03-29 21:00 | 41479 | 12496.4555 | 149116.7333 | 59.77 | 829.58
2016-03-29 22:00 | 38424 | 13700.3394 | 130159.3169 | 59.79 | 691.632
2016-03-29 23:00 | 35002 | 13605.8732 | 128640.3169 | 59.79 | 630.036
2016-03-30 | 33644 | 13387.4843 | 130948.2129 | 59.79 | 605.592
2016-03-30 01:00 | 32552 | 13557.3925 | 130948.2129 | 59.79 | 585.936
2016-03-30 02:00 | 32005 | 13048.4506 | 130948.2129 | 59.79 | 576.09
2016-03-30 03:00 | 32019 | 12748.9323 | 130948.2129 | 59.79 | 576.342
2016-03-30 04:00 | 32722 | 13172.7081 | 130948.2129 | 59.79 | 588.996
2016-03-30 05:00 | 35287 | 13788.3706 | 138145.8929 | 59.79 | 635.166
2016-03-30 06:00 | 40446 | 13629.2843 | 141955.6929 | 59.79 | 728.028
2016-03-30 07:00 | 42538 | 13240.6228 | 156595.6566 | 59.77 | 850.76
2016-03-30 08:00 | 41619 | 12810.6143 | 156512.5316 | 59.77 | 832.38
2016-03-30 09:00 | 41776 | 11176.6334 | 164995.318 | 59.77 | 835.52
2016-03-30 10:00 | 41846 | 11038.348 | 164995.318 | 59.77 | 836.92
2016-03-30 11:00 | 41818 | 10844.1825 | 164995.318 | 59.77 | 836.36
2016-03-30 12:00 | 42025 | 10423.083 | 166011.318 | 59.77 | 840.5
2016-03-30 13:00 | 42449 | 10599.606 | 166183.8079 | 59.77 | 848.98
2016-03-30 14:00 | 42877 | 11825.6006 | 164995.318 | 59.77 | 857.54
2016-03-30 15:00 | 43071 | 13320.2435 | 156785.838 | 59.77 | 861.42
2016-03-30 16:00 | 43362 | 14551.6319 | 148972.2132 | 59.77 | 867.24
2016-03-30 17:00 | 43264 | 14939.0592 | 145623.1232 | 59.77 | 865.28
2016-03-30 18:00 | 42980 | 15127.9416 | 146242.4932 | 59.77 | 859.6
2016-03-30 19:00 | 42697 | 15377.8835 | 146242.4932 | 59.79 | 768.546
2016-03-30 20:00 | 44622 | 15467.9723 | 147346.4363 | 59.77 | 892.44
2016-03-30 21:00 | 43359 | 15164.8001 | 145747.4932 | 59.77 | 867.18
2016-03-30 22:00 | 40121 | 15150.1194 | 130599.8768 | 59.79 | 722.178
2016-03-30 23:00 | 36295 | 15066.5702 | 126863.8959 | 59.79 | 653.31
2016-03-31 | 31701 | 14675.4242 | 122714.8259 | 59.79 | 570.618
2016-03-31 01:00 | 30534 | 14438.8235 | 122118.8759 | 59.79 | 549.612
2016-03-31 02:00 | 29892 | 14289.3838 | 122118.8759 | 59.79 | 538.056
2016-03-31 03:00 | 29698 | 13789.1385 | 124368.8759 | 59.79 | 534.564
2016-03-31 04:00 | 30149 | 13115.4263 | 130091.1459 | 59.79 | 542.682
2016-03-31 05:00 | 32216 | 12454.5587 | 133311.0659 | 59.79 | 579.888
2016-03-31 06:00 | 36528 | 12245.865 | 132619.4659 | 59.79 | 657.504
2016-03-31 07:00 | 38268 | 12106.7434 | 136914.5911 | 59.79 | 688.824
2016-03-31 08:00 | 37772 | 12190.3831 | 133942.7161 | 59.79 | 679.896
2016-03-31 09:00 | 38243 | 10945.8441 | 142429.1741 | 59.79 | 688.374
2016-03-31 10:00 | 39137 | 10349.3169 | 150890.6441 | 59.77 | 782.74
2016-03-31 11:00 | 39788 | 9894.6249 | 160184.8241 | 59.77 | 795.76
2016-03-31 12:00 | 40421 | 8897.2087 | 165251.0641 | 59.77 | 808.42
2016-03-31 13:00 | 41304 | 8795.9312 | 170384.7605 | 59.78 | 784.776
2016-03-31 14:00 | 42132 | 9377.3363 | 170384.7605 | 59.78 | 800.508
2016-03-31 15:00 | 42923 | 10765.0042 | 170486.9205 | 59.77 | 858.46
2016-03-31 16:00 | 43492 | 12353.6678 | 170486.9205 | 59.77 | 869.84
2016-03-31 17:00 | 43499 | 13777.5122 | 159860.7317 | 59.77 | 869.98
2016-03-31 18:00 | 42993 | 14718.1649 | 151399.2617 | 59.77 | 859.86
2016-03-31 19:00 | 42487 | 15830.7131 | 147052.7617 | 59.79 | 764.766
2016-03-31 20:00 | 44092 | 16015.6936 | 147547.7617 | 59.77 | 881.84
2016-03-31 21:00 | 42920 | 15616.6432 | 145388.3617 | 59.79 | 772.56
2016-03-31 22:00 | 39831 | 15338.8893 | 134039.5333 | 59.79 | 716.958
2016-03-31 23:00 | 36280 | 15138.1305 | 130303.5524 | 59.79 | 653.04
2016-04-01 | 32292 | 14467.3836 | 120885.2524 | 59.79 | 581.256
2016-04-01 01:00 | 30826 | 14478.1721 | 120885.2524 | 59.79 | 554.868
2016-04-01 02:00 | 30023 | 14789.7517 | 120289.3024 | 59.79 | 540.414
2016-04-01 03:00 | 29628 | 15011.744 | 120289.3024 | 59.79 | 533.304
2016-04-01 04:00 | 29872 | 14764.6774 | 121939.2344 | 59.79 | 537.696
2016-04-01 05:00 | 31603 | 14363.0189 | 126405.9804 | 59.79 | 568.854
2016-04-01 06:00 | 35354 | 13757.3662 | 125605.6944 | 59.79 | 636.372
2016-04-01 07:00 | 36896 | 13770.1714 | 125531.8753 | 59.79 | 664.128
2016-04-01 08:00 | 36840 | 13688.2682 | 125531.8753 | 59.79 | 663.12
2016-04-01 09:00 | 37680 | 13997.7476 | 124977.6853 | 59.79 | 678.24
2016-04-01 10:00 | 38565 | 13725.2648 | 124977.6853 | 59.79 | 694.17
2016-04-01 11:00 | 39308 | 14327.4469 | 124977.6853 | 59.79 | 707.544
2016-04-01 12:00 | 39790 | 14576.2949 | 124977.6853 | 59.79 | 716.22
2016-04-01 13:00 | 40536 | 15654.0966 | 124977.6853 | 59.79 | 729.648
2016-04-01 14:00 | 41165 | 16156.5929 | 124977.6853 | 59.79 | 740.97
2016-04-01 15:00 | 41512 | 16241.0034 | 124977.6853 | 59.79 | 747.216
2016-04-01 16:00 | 41625 | 16348.2456 | 124977.6853 | 59.79 | 749.25
2016-04-01 17:00 | 41122 | 16256.0784 | 124977.6853 | 59.79 | 740.196
2016-04-01 18:00 | 40574 | 16187.5636 | 124977.6853 | 59.79 | 730.332
2016-04-01 19:00 | 40026 | 16289.5053 | 124977.6853 | 59.79 | 720.468
2016-04-01 20:00 | 41168 | 15975.7282 | 124977.6853 | 59.79 | 741.024
2016-04-01 21:00 | 40135 | 15743.9711 | 127137.0853 | 59.79 | 722.43
2016-04-01 22:00 | 37812 | 15437.2481 | 127137.0853 | 59.79 | 680.616
2016-04-01 23:00 | 34979 | 14910.9132 | 127203.1933 | 59.79 | 629.622
2016-04-02 | 34888 | 13342.7882 | 125496.0053 | 59.79 | 627.984
2016-04-02 01:00 | 33337 | 12982.4942 | 125496.0053 | 59.79 | 600.066
2016-04-02 02:00 | 32515 | 13820.5014 | 125496.0053 | 59.79 | 585.27
2016-04-02 03:00 | 32125 | 13360.9196 | 125496.0053 | 59.79 | 578.25
2016-04-02 04:00 | 32275 | 13416.4874 | 127235.9053 | 59.79 | 580.95
2016-04-02 05:00 | 33454 | 13317.838 | 130843.2253 | 59.79 | 602.172
2016-04-02 06:00 | 35850 | 12564.5297 | 130843.2253 | 59.79 | 645.3
2016-04-02 07:00 | 37525 | 10685.0201 | 140857.1453 | 59.79 | 675.45
2016-04-02 08:00 | 38394 | 8267.3753 | 157688.1933 | 59.77 | 767.88
2016-04-02 09:00 | 39867 | 10034.7532 | 158242.3833 | 59.77 | 797.34
2016-04-02 10:00 | 41104 | 12939.7936 | 158242.3833 | 59.77 | 822.08
2016-04-02 11:00 | 41988 | 12024.5162 | 158242.3833 | 59.77 | 839.76
2016-04-02 12:00 | 42137 | 12310.4987 | 158242.3833 | 59.77 | 842.74
2016-04-02 13:00 | 42248 | 13175.6517 | 154932.5733 | 59.77 | 844.96
2016-04-02 14:00 | 42363 | 13543.0409 | 154932.5733 | 59.77 | 847.26
2016-04-02 15:00 | 42517 | 13628.8801 | 154932.5733 | 59.77 | 850.34
2016-04-02 16:00 | 42750 | 13682.0791 | 154932.5733 | 59.77 | 855
2016-04-02 17:00 | 42724 | 13870.7444 | 154932.5733 | 59.77 | 854.48
2016-04-02 18:00 | 42033 | 13089.041 | 154932.5733 | 59.77 | 840.66
2016-04-02 19:00 | 41342 | 11925.4802 | 159279.0733 | 59.77 | 826.84
2016-04-02 20:00 | 42156 | 10500.3415 | 163494.2993 | 59.77 | 843.12
2016-04-02 21:00 | 41129 | 9586.9384 | 162943.6118 | 59.77 | 822.58
2016-04-02 22:00 | 39004 | 8941.3168 | 161927.6118 | 59.77 | 780.08
2016-04-02 23:00 | 36436 | 6862.5352 | 162044.4918 | 59.77 | 728.72
2016-04-03 | 35385 | 6589.4808 | 162044.4918 | 59.77 | 707.7
2016-04-03 01:00 | 33758 | 5574.882 | 162044.4918 | 59.77 | 675.16
2016-04-03 02:00 | 32617 | 5333.2374 | 162044.4918 | 59.79 | 587.106
2016-04-03 03:00 | 32076 | 4724.1391 | 162044.4918 | 59.79 | 577.368
2016-04-03 04:00 | 31951 | 3433.7941 | 162044.4918 | 59.77 | 639.02
2016-04-03 05:00 | 32418 | 2404.9541 | 167896.5918 | 59.77 | 648.36
2016-04-03 06:00 | 33711 | 2256.7239 | 168380.0918 | 59.77 | 674.22
2016-04-03 07:00 | 34792 | 2137.0663 | 173513.7882 | 59.78 | 661.048
2016-04-03 08:00 | 36758 | 2447.3734 | 186894.7013 | 59.78 | 698.402
2016-04-03 09:00 | 38618 | 2098.358 | 201759.2497 | 59.78 | 733.742
2016-04-03 10:00 | 39852 | 3182.0428 | 202775.2497 | 59.78 | 757.188
2016-04-03 11:00 | 40609 | 6404.9097 | 194213.5237 | 59.78 | 771.571
2016-04-03 12:00 | 41301 | 9250.5894 | 194213.5237 | 59.77 | 826.02
2016-04-03 13:00 | 41625 | 9667.5007 | 188361.4237 | 59.77 | 832.5
2016-04-03 14:00 | 42219 | 9736.1036 | 188361.4237 | 59.77 | 844.38
2016-04-03 15:00 | 42903 | 10560.3096 | 186181.8902 | 59.77 | 858.06
2016-04-03 16:00 | 43526 | 10595.1799 | 186181.8902 | 59.78 | 826.994
2016-04-03 17:00 | 43751 | 10537.0881 | 186181.8902 | 59.78 | 831.269
2016-04-03 18:00 | 43229 | 10246.5548 | 186181.8902 | 59.78 | 821.351
2016-04-03 19:00 | 42706 | 11239.3282 | 181031.6402 | 59.77 | 854.12
2016-04-03 20:00 | 43952 | 11831.6115 | 181031.6402 | 59.77 | 879.04
2016-04-03 21:00 | 43068 | 13363.4031 | 166417.7893 | 59.77 | 861.36
2016-04-03 22:00 | 41094 | 13287.0609 | 156472.1593 | 59.77 | 821.88
2016-04-03 23:00 | 38475 | 12593.4945 | 145760.6893 | 59.79 | 692.55
2016-04-04 | 37657 | 12304.9091 | 139048.5793 | 59.79 | 677.826
2016-04-04 01:00 | 35808 | 12302.5808 | 139048.5793 | 59.79 | 644.544
2016-04-04 02:00 | 34572 | 12228.9413 | 139048.5793 | 59.79 | 622.296
2016-04-04 03:00 | 33902 | 12259.2871 | 139048.5793 | 59.79 | 610.236
2016-04-04 04:00 | 33672 | 11721.2317 | 139048.5793 | 59.79 | 606.096
2016-04-04 05:00 | 33957 | 11539.2325 | 139048.5793 | 59.79 | 611.226
2016-04-04 06:00 | 34928 | 11700.9935 | 140952.5793 | 59.79 | 628.704
2016-04-04 07:00 | 36009 | 11054.0992 | 139063.6293 | 59.79 | 648.162
2016-04-04 08:00 | 37761 | 10522.9417 | 149656.9362 | 59.79 | 679.698
2016-04-04 09:00 | 39715 | 11322.7311 | 155487.6262 | 59.77 | 794.3
2016-04-04 10:00 | 40814 | 12811.3362 | 155487.6262 | 59.77 | 816.28
2016-04-04 11:00 | 41385 | 12531.259 | 155370.7462 | 59.77 | 827.7
2016-04-04 12:00 | 41945 | 12292.2751 | 160819.9722 | 59.77 | 838.9
2016-04-04 13:00 | 42450 | 11866.6567 | 164056.6422 | 59.77 | 849
2016-04-04 14:00 | 43005 | 10611.2386 | 179728.4022 | 59.77 | 860.1
2016-04-04 15:00 | 43542 | 9805.4995 | 188369.9357 | 59.78 | 827.298
2016-04-04 16:00 | 44005 | 9561.5088 | 188369.9357 | 59.78 | 836.095
2016-04-04 17:00 | 44319 | 9883.4061 | 188369.9357 | 59.78 | 842.061
2016-04-04 18:00 | 44573 | 10262.02 | 195612.3737 | 59.78 | 846.887
2016-04-04 19:00 | 44827 | 10549.5599 | 195612.3737 | 59.78 | 851.713
2016-04-04 20:00 | 47157 | 10369.7655 | 196628.3737 | 59.78 | 895.983
2016-04-04 21:00 | 46820 | 11470.1849 | 195612.3737 | 59.78 | 889.58
2016-04-04 22:00 | 44313 | 12369.4832 | 178083.4077 | 59.77 | 886.26
2016-04-04 23:00 | 40619 | 12810.6721 | 149672.7497 | 59.77 | 812.38
2016-04-05 | 34054 | 12287.6422 | 133992.8933 | 59.79 | 612.972
2016-04-05 01:00 | 32564 | 12341.24 | 136432.4933 | 59.79 | 586.152
2016-04-05 02:00 | 31709 | 12448.2755 | 131282.2433 | 59.79 | 570.762
2016-04-05 03:00 | 31289 | 12413.0788 | 131282.2433 | 59.79 | 563.202
2016-04-05 04:00 | 31827 | 12076.1425 | 131282.2433 | 59.79 | 572.886
2016-04-05 05:00 | 33749 | 11598.3603 | 131282.2433 | 59.79 | 607.482
2016-04-05 06:00 | 37715 | 10273.4556 | 146502.6677 | 59.79 | 678.87
2016-04-05 07:00 | 39686 | 10490.5096 | 157111.3177 | 59.77 | 793.72
2016-04-05 08:00 | 39781 | 10618.2173 | 157111.3177 | 59.77 | 795.62
2016-04-05 09:00 | 40878 | 10944.2881 | 160460.4077 | 59.77 | 817.56
2016-04-05 10:00 | 42131 | 11380.0593 | 163809.4977 | 59.77 | 842.62
2016-04-05 11:00 | 42929 | 13113.8364 | 163926.3777 | 59.77 | 858.58
2016-04-05 12:00 | 43630 | 13673.4415 | 163926.3777 | 59.77 | 872.6
2016-04-05 13:00 | 44578 | 14000.1393 | 167722.1902 | 59.77 | 891.56
2016-04-05 14:00 | 45449 | 14449.3362 | 167722.1902 | 59.77 | 908.98
2016-04-05 15:00 | 46336 | 15056.0316 | 168010.1902 | 59.77 | 926.72
2016-04-05 16:00 | 47084 | 15139.6901 | 168010.1902 | 59.77 | 941.68
2016-04-05 17:00 | 47167 | 14720.3015 | 169026.1902 | 59.77 | 943.34
2016-04-05 18:00 | 46360 | 14863.4427 | 165918.0022 | 59.77 | 927.2
2016-04-05 19:00 | 45552 | 15436.4032 | 165918.0022 | 59.77 | 911.04
2016-04-05 20:00 | 46839 | 15208.9606 | 165918.0022 | 59.77 | 936.78
2016-04-05 21:00 | 45452 | 14813.5333 | 158980.1822 | 59.77 | 909.04
2016-04-05 22:00 | 42016 | 15193.055 | 134786.813 | 59.79 | 756.288
2016-04-05 23:00 | 38077 | 15291.3331 | 124772.893 | 59.79 | 685.386
2016-04-06 | 34754 | 15366.69 | 124772.893 | 59.79 | 625.572
2016-04-06 01:00 | 33136 | 15443.4098 | 124772.893 | 59.79 | 596.448
2016-04-06 02:00 | 32146 | 15145.2249 | 124772.893 | 59.79 | 578.628
2016-04-06 03:00 | 31636 | 14690.214 | 124772.893 | 59.79 | 569.448
2016-04-06 04:00 | 31921 | 13970.8699 | 124772.893 | 59.79 | 574.578
2016-04-06 05:00 | 33795 | 14046.2096 | 130862.693 | 59.79 | 608.31
2016-04-06 06:00 | 37901 | 13507.9839 | 135810.373 | 59.79 | 682.218
2016-04-06 07:00 | 39572 | 14161.3117 | 135810.373 | 59.79 | 712.296
2016-04-06 08:00 | 39468 | 14090.6488 | 135810.373 | 59.79 | 710.424
2016-04-06 09:00 | 40356 | 14563.6617 | 135810.373 | 59.79 | 726.408
2016-04-06 10:00 | 41313 | 15011.6819 | 136826.373 | 59.79 | 743.634
2016-04-06 11:00 | 42360 | 15274.5078 | 145943.241 | 59.79 | 762.48
2016-04-06 12:00 | 43495 | 15431.1459 | 152491.557 | 59.77 | 869.9
2016-04-06 13:00 | 44613 | 15065.3725 | 160737.8345 | 59.77 | 892.26
2016-04-06 14:00 | 45570 | 14702.1781 | 170683.4645 | 59.77 | 911.4
2016-04-06 15:00 | 46280 | 14839.0866 | 170683.4645 | 59.77 | 925.6
2016-04-06 16:00 | 46783 | 15459.3205 | 170683.4645 | 59.77 | 935.66
2016-04-06 17:00 | 46449 | 15695.948 | 170683.4645 | 59.77 | 928.98
2016-04-06 18:00 | 45558 | 15448.2453 | 170683.4645 | 59.77 | 911.16
2016-04-06 19:00 | 44667 | 14976.2263 | 170683.4645 | 59.77 | 893.34
2016-04-06 20:00 | 45913 | 13067.3575 | 176833.1609 | 59.78 | 872.347
2016-04-06 21:00 | 44592 | 12251.3332 | 175382.2809 | 59.77 | 891.84
2016-04-06 22:00 | 41358 | 11797.4943 | 171227.9657 | 59.77 | 827.16
2016-04-06 23:00 | 37483 | 10807.6167 | 148399.3897 | 59.79 | 674.694
2016-04-07 | 32652 | 10221.3703 | 133556.4497 | 59.79 | 587.736
2016-04-07 01:00 | 31178 | 11434.5165 | 133556.4497 | 59.79 | 561.204
2016-04-07 02:00 | 30416 | 12110.9579 | 133556.4497 | 59.79 | 547.488
2016-04-07 03:00 | 30081 | 10919.6 | 133556.4497 | 59.79 | 541.458
2016-04-07 04:00 | 30280 | 11380.8644 | 133556.4497 | 59.79 | 545.04
2016-04-07 05:00 | 32009 | 10497.5866 | 136038.0497 | 59.79 | 576.162
2016-04-07 06:00 | 35747 | 10357.0939 | 135753.4787 | 59.79 | 643.446
2016-04-07 07:00 | 36988 | 9999.6997 | 140819.7187 | 59.79 | 665.784
2016-04-07 08:00 | 36851 | 9300.3721 | 145840.2067 | 59.77 | 737.02
2016-04-07 09:00 | 37519 | 9006.6676 | 150952.5867 | 59.77 | 750.38
2016-04-07 10:00 | 38438 | 11259.8819 | 150952.5867 | 59.79 | 691.884
2016-04-07 11:00 | 38911 | 9472.8 | 155317.6767 | 59.77 | 778.22
2016-04-07 12:00 | 39373 | 10653.4438 | 154301.6767 | 59.77 | 787.46
2016-04-07 13:00 | 39695 | 12784.0552 | 154301.6767 | 59.79 | 714.51
2016-04-07 14:00 | 39885 | 13751.0959 | 151908.4467 | 59.79 | 717.93
2016-04-07 15:00 | 40065 | 13971.8624 | 151908.4467 | 59.79 | 721.17
2016-04-07 16:00 | 40158 | 13616.5132 | 151908.4467 | 59.79 | 722.844
2016-04-07 17:00 | 39870 | 14248.0098 | 151908.4467 | 59.79 | 717.66
2016-04-07 18:00 | 39359 | 13739.8314 | 151908.4467 | 59.79 | 708.462
2016-04-07 19:00 | 38848 | 12658.0021 | 151908.4467 | 59.79 | 699.264
2016-04-07 20:00 | 39498 | 10551.7599 | 155257.5367 | 59.77 | 789.96
2016-04-07 21:00 | 38239 | 9611.3002 | 155692.4167 | 59.77 | 764.78
2016-04-07 22:00 | 35476 | 7259.1034 | 153698.8667 | 59.77 | 709.52
2016-04-07 23:00 | 32297 | 4131.0964 | 153698.8667 | 59.77 | 645.94
2016-04-08 | 31877 | 3689.4315 | 153698.8667 | 59.77 | 637.54
2016-04-08 01:00 | 30538 | 4645.5 | 150114.5967 | 59.79 | 549.684
2016-04-08 02:00 | 29811 | 4839.4194 | 150114.5967 | 59.79 | 536.598
2016-04-08 03:00 | 29626 | 5731.9731 | 150114.5967 | 59.79 | 533.268
2016-04-08 04:00 | 30136 | 5140.8994 | 150114.5967 | 59.79 | 542.448
2016-04-08 05:00 | 32244 | 4498.8992 | 153721.9167 | 59.77 | 644.88
2016-04-08 06:00 | 36682 | 3956.6352 | 183854.2437 | 59.78 | 696.958
2016-04-08 07:00 | 38301 | 3769.1089 | 196700.3921 | 59.78 | 727.719
2016-04-08 08:00 | 37853 | 3727.66 | 196700.3921 | 59.78 | 719.207
2016-04-08 09:00 | 38030 | 3371.7981 | 196700.3921 | 59.78 | 722.57
2016-04-08 10:00 | 38278 | 3660.4969 | 197849.2841 | 59.78 | 727.282
2016-04-08 11:00 | 38309 | 3661.9195 | 197849.2841 | 59.78 | 727.871
2016-04-08 12:00 | 38146 | 3538.1543 | 197849.2841 | 59.78 | 724.774
2016-04-08 13:00 | 38354 | 3156.3519 | 197849.2841 | 59.78 | 728.726
2016-04-08 14:00 | 38300 | 2409.1837 | 200242.5141 | 59.78 | 727.7
2016-04-08 15:00 | 38321 | 1911.1311 | 200242.5141 | 59.78 | 728.099
2016-04-08 16:00 | 38409 | 1433.9065 | 201258.5141 | 59.78 | 729.771
2016-04-08 17:00 | 38264 | 1324.9605 | 201258.5141 | 59.78 | 727.016
2016-04-08 18:00 | 38020 | 1397.4702 | 200522.5141 | 59.78 | 722.38
2016-04-08 19:00 | 37776 | 2246.4826 | 195092.2641 | 59.78 | 717.744
2016-04-08 20:00 | 39648 | 3792.8111 | 196108.2641 | 59.78 | 753.312
2016-04-08 21:00 | 38765 | 6050.5761 | 174053.2957 | 59.78 | 736.535
2016-04-08 22:00 | 36254 | 9829.1353 | 135747.3917 | 59.79 | 652.572
2016-04-08 23:00 | 33280 | 12329.8145 | 135747.3917 | 59.79 | 599.04
2016-04-09 | 33231 | 12189.7287 | 132588.9917 | 59.79 | 598.158
2016-04-09 01:00 | 33131 | 11789.0693 | 132588.9917 | 59.79 | 596.358
2016-04-09 02:00 | 33059 | 12122.1153 | 132588.9917 | 59.79 | 595.062
2016-04-09 03:00 | 33049 | 12300.8369 | 132588.9917 | 59.79 | 594.882
2016-04-09 04:00 | 33749 | 12170.8852 | 132588.9917 | 59.79 | 607.482
2016-04-09 05:00 | 36314 | 12067.6766 | 136196.3117 | 59.79 | 653.652
2016-04-09 06:00 | 41320 | 11715.963 | 159623.8597 | 59.77 | 826.4
2016-04-09 07:00 | 43124 | 10675.4773 | 176125.1157 | 59.77 | 862.48
2016-04-09 08:00 | 42547 | 9623.8153 | 179709.3857 | 59.78 | 808.393
2016-04-09 09:00 | 42546 | 8175.8748 | 193169.4961 | 59.78 | 808.374
2016-04-09 10:00 | 42644 | 7251.275 | 196435.4961 | 59.78 | 810.236
2016-04-09 11:00 | 42492 | 7774.2573 | 195419.4961 | 59.78 | 807.348
2016-04-09 12:00 | 42584 | 8742.4651 | 195419.4961 | 59.78 | 809.096
2016-04-09 13:00 | 42774 | 8731.2207 | 195419.4961 | 59.78 | 812.706
2016-04-09 14:00 | 42832 | 8255.951 | 195419.4961 | 59.78 | 813.808
2016-04-09 15:00 | 42826 | 7999.8787 | 195419.4961 | 59.78 | 813.694
2016-04-09 16:00 | 42730 | 8589.4391 | 193909.1761 | 59.78 | 811.87
2016-04-09 17:00 | 42145 | 9645.7405 | 180449.0657 | 59.77 | 842.9
2016-04-09 18:00 | 41591 | 11388.8198 | 165883.7057 | 59.77 | 831.82
2016-04-09 19:00 | 41036 | 13099.5301 | 155101.3097 | 59.77 | 820.72
2016-04-09 20:00 | 42579 | 13534.2667 | 155661.3097 | 59.77 | 851.58
2016-04-09 21:00 | 41822 | 14054.9902 | 151752.2197 | 59.77 | 836.44
2016-04-09 22:00 | 39875 | 14126.228 | 139683.4297 | 59.79 | 717.75
2016-04-09 23:00 | 37222 | 13546.3205 | 139683.4297 | 59.79 | 669.996
2016-04-10 | 36652 | 12992.6899 | 139395.4297 | 59.79 | 659.736
2016-04-10 01:00 | 35018 | 12717.0427 | 139395.4297 | 59.79 | 630.324
2016-04-10 02:00 | 34156 | 11886.5563 | 139395.4297 | 59.79 | 614.808
2016-04-10 03:00 | 33603 | 11676.2694 | 139395.4297 | 59.79 | 604.854
2016-04-10 04:00 | 33632 | 11870.5334 | 139395.4297 | 59.79 | 605.376
2016-04-10 05:00 | 34468 | 11343.832 | 142553.8297 | 59.79 | 620.424
2016-04-10 06:00 | 36182 | 9615.1336 | 142553.8297 | 59.79 | 651.276
2016-04-10 07:00 | 37444 | 9823.5419 | 146161.1497 | 59.77 | 748.88
2016-04-10 08:00 | 39314 | 10311.8456 | 154622.6197 | 59.77 | 786.28
2016-04-10 09:00 | 40931 | 9629.406 | 168989.7257 | 59.77 | 818.62
2016-04-10 10:00 | 41915 | 10498.2071 | 168989.7257 | 59.77 | 838.3
2016-04-10 11:00 | 42199 | 10362.228 | 180082.7957 | 59.77 | 843.98
2016-04-10 12:00 | 42337 | 7617.6542 | 193425.8657 | 59.78 | 804.403
2016-04-10 13:00 | 42383 | 7153.0684 | 196779.5761 | 59.78 | 805.277
2016-04-10 14:00 | 42626 | 7071.3739 | 197235.5761 | 59.78 | 809.894
2016-04-10 15:00 | 42901 | 7575.1393 | 196779.5761 | 59.78 | 815.119
2016-04-10 16:00 | 43236 | 7305.6286 | 198289.8961 | 59.78 | 821.484
2016-04-10 17:00 | 43317 | 7674.0575 | 198289.8961 | 59.78 | 823.023
2016-04-10 18:00 | 43094 | 7953.3664 | 197872.6061 | 59.78 | 818.786
2016-04-10 19:00 | 42871 | 10524.9583 | 179233.8101 | 59.77 | 857.42
2016-04-10 20:00 | 44679 | 12574.538 | 171377.4101 | 59.77 | 893.58
2016-04-10 21:00 | 43916 | 13703.7272 | 158929.7097 | 59.77 | 878.32
2016-04-10 22:00 | 41819 | 13846.9908 | 147119.1497 | 59.77 | 836.38
2016-04-10 23:00 | 39174 | 13357.5362 | 142098.6617 | 59.79 | 705.132
2016-04-11 | 35053 | 12101.0617 | 138357.9353 | 59.79 | 630.954
2016-04-11 01:00 | 33529 | 11616.4032 | 138357.9353 | 59.79 | 603.522
2016-04-11 02:00 | 32602 | 11134.6337 | 138357.9353 | 59.79 | 586.836
2016-04-11 03:00 | 32052 | 10674.2338 | 138357.9353 | 59.79 | 576.936
2016-04-11 04:00 | 31866 | 10338.3999 | 138357.9353 | 59.79 | 573.588
2016-04-11 05:00 | 32070 | 8817.3901 | 138357.9353 | 59.79 | 577.26
2016-04-11 06:00 | 32857 | 6910.477 | 138357.9353 | 59.79 | 591.426
2016-04-11 07:00 | 33451 | 5166.3526 | 148490.8033 | 59.77 | 669.02
2016-04-11 08:00 | 35066 | 4020.1207 | 164984.7093 | 59.77 | 701.32
2016-04-11 09:00 | 36850 | 3830.296 | 179648.1993 | 59.78 | 700.15
2016-04-11 10:00 | 38176 | 4272.2164 | 184148.1993 | 59.78 | 725.344
2016-04-11 11:00 | 39013 | 4154.315 | 192480.9193 | 59.78 | 741.247
2016-04-11 12:00 | 39809 | 3978.1328 | 201188.1177 | 59.78 | 756.371
2016-04-11 13:00 | 40366 | 5045.3575 | 201188.1177 | 59.78 | 766.954
2016-04-11 14:00 | 40752 | 4644.1407 | 206208.6057 | 59.78 | 774.288
2016-04-11 15:00 | 41103 | 3523.0314 | 209810.7057 | 59.77 | 822.06
2016-04-11 16:00 | 41631 | 3594.4288 | 209810.7057 | 59.77 | 832.62
2016-04-11 17:00 | 42065 | 3600.7408 | 210826.7057 | 59.77 | 841.3
2016-04-11 18:00 | 42354 | 5043.4308 | 209810.7057 | 59.78 | 804.726
2016-04-11 19:00 | 42643 | 6181.6848 | 205977.9857 | 59.78 | 810.217
2016-04-11 20:00 | 44348 | 8044.7601 | 200827.7357 | 59.78 | 842.612
2016-04-11 21:00 | 43491 | 7217.2323 | 198735.5477 | 59.78 | 826.329
2016-04-11 22:00 | 40699 | 9704.8911 | 165196.9793 | 59.77 | 813.98
2016-04-11 23:00 | 37260 | 8727.4402 | 161594.8793 | 59.77 | 745.2
2016-04-12 | 32323 | 6863.3716 | 161594.8793 | 59.79 | 581.814
2016-04-12 01:00 | 31027 | 6910.2721 | 157250.1513 | 59.79 | 558.486
2016-04-12 02:00 | 30374 | 7380.0598 | 157250.1513 | 59.79 | 546.732
2016-04-12 03:00 | 30124 | 7669.3828 | 157250.1513 | 59.79 | 542.232
2016-04-12 04:00 | 30582 | 6781.6422 | 157250.1513 | 59.79 | 550.476
2016-04-12 05:00 | 32616 | 6424.9742 | 157250.1513 | 59.79 | 587.088
2016-04-12 06:00 | 36534 | 5248.5796 | 175664.5213 | 59.77 | 730.68
2016-04-12 07:00 | 38167 | 4812.5599 | 186626.4197 | 59.78 | 725.173
2016-04-12 08:00 | 38323 | 4760.4185 | 186626.4197 | 59.78 | 728.137
2016-04-12 09:00 | 39316 | 6073.112 | 184474.4197 | 59.78 | 747.004
2016-04-12 10:00 | 40433 | 9764.2225 | 172625.2417 | 59.77 | 808.66
2016-04-12 11:00 | 41452 | 12656.7964 | 172625.2417 | 59.77 | 829.04
2016-04-12 12:00 | 42047 | 14103.6932 | 172334.6582 | 59.77 | 840.94
2016-04-12 13:00 | 42599 | 13688.6427 | 172334.6582 | 59.77 | 851.98
2016-04-12 14:00 | 43088 | 14125.3882 | 172334.6582 | 59.77 | 861.76
2016-04-12 15:00 | 43508 | 14371.1986 | 172334.6582 | 59.77 | 870.16
2016-04-12 16:00 | 43805 | 15292.9944 | 172334.6582 | 59.77 | 876.1
2016-04-12 17:00 | 43495 | 15189.9177 | 172334.6582 | 59.77 | 869.9
2016-04-12 18:00 | 42950 | 14276.5079 | 172334.6582 | 59.77 | 859
2016-04-12 19:00 | 42406 | 13560.6289 | 172334.6582 | 59.77 | 848.12
2016-04-12 20:00 | 43928 | 11873.6248 | 177091.3846 | 59.77 | 878.56
2016-04-12 21:00 | 42734 | 11532.0033 | 173983.1966 | 59.77 | 854.68
2016-04-12 22:00 | 39471 | 12202.9308 | 147490.6902 | 59.79 | 710.478
2016-04-12 23:00 | 35828 | 12098.7218 | 135680.1302 | 59.79 | 644.904
2016-04-13 | 33084 | 11452.6894 | 133247.1302 | 59.79 | 595.512
2016-04-13 01:00 | 31674 | 10399.2025 | 133247.1302 | 59.79 | 570.132
2016-04-13 02:00 | 30883 | 11123.3627 | 131681.2602 | 59.79 | 555.894
2016-04-13 03:00 | 30468 | 11341.2943 | 131681.2602 | 59.79 | 548.424
2016-04-13 04:00 | 30797 | 10361.7558 | 134068.7602 | 59.79 | 554.346
2016-04-13 05:00 | 32689 | 9212.9349 | 133942.2802 | 59.79 | 588.402
2016-04-13 06:00 | 36746 | 8078.1778 | 153298.5662 | 59.77 | 734.92
2016-04-13 07:00 | 38138 | 9690.2136 | 155255.7942 | 59.77 | 762.76
2016-04-13 08:00 | 38385 | 11361.8478 | 155255.7942 | 59.79 | 690.93
2016-04-13 09:00 | 39388 | 12430.8237 | 156391.7942 | 59.79 | 708.984
2016-04-13 10:00 | 40509 | 14301.149 | 156391.7942 | 59.79 | 729.162
2016-04-13 11:00 | 41673 | 15585.1659 | 156391.7942 | 59.79 | 750.114
2016-04-13 12:00 | 42129 | 15399.4635 | 156391.7942 | 59.79 | 758.322
2016-04-13 13:00 | 42866 | 15381.3558 | 156391.7942 | 59.79 | 771.588
2016-04-13 14:00 | 43260 | 15708.6729 | 156391.7942 | 59.77 | 865.2
2016-04-13 15:00 | 43543 | 15425.9238 | 159628.4642 | 59.77 | 870.86
2016-04-13 16:00 | 43948 | 14820.105 | 159628.4642 | 59.77 | 878.96
2016-04-13 17:00 | 43943 | 14214.1224 | 159628.4642 | 59.77 | 878.86
2016-04-13 18:00 | 43276 | 14276.5078 | 170799.3422 | 59.77 | 865.52
2016-04-13 19:00 | 42609 | 12357.4806 | 170799.3422 | 59.77 | 852.18
2016-04-13 20:00 | 44033 | 9722.0499 | 181309.6213 | 59.78 | 836.627
2016-04-13 21:00 | 42978 | 9648.9583 | 180293.6213 | 59.78 | 816.582
2016-04-13 22:00 | 39712 | 10170.7652 | 165283.8353 | 59.77 | 794.24
2016-04-13 23:00 | 36149 | 11335.8735 | 139692.9589 | 59.79 | 650.682
2016-04-14 | 31724 | 12272.2955 | 126023.4089 | 59.79 | 571.032
2016-04-14 01:00 | 30320 | 12540.8602 | 126023.4089 | 59.79 | 545.76
2016-04-14 02:00 | 29594 | 12168.7805 | 123335.2709 | 59.79 | 532.692
2016-04-14 03:00 | 29228 | 11383.1141 | 123335.2709 | 59.79 | 526.104
2016-04-14 04:00 | 29581 | 10527.1191 | 123335.2709 | 59.79 | 532.458
2016-04-14 05:00 | 31468 | 9850.1918 | 123461.7509 | 59.79 | 566.424
2016-04-14 06:00 | 35275 | 8158.3878 | 142645.7409 | 59.79 | 634.95
2016-04-14 07:00 | 36508 | 7449.1362 | 157958.0573 | 59.77 | 730.16
2016-04-14 08:00 | 36590 | 6936.7281 | 161022.7393 | 59.77 | 731.8
2016-04-14 09:00 | 37351 | 8324.0012 | 158583.1393 | 59.77 | 747.02
2016-04-14 10:00 | 38156 | 8632.4844 | 161068.9293 | 59.77 | 763.12
2016-04-14 11:00 | 38866 | 10639.8632 | 161068.9293 | 59.77 | 777.32
2016-04-14 12:00 | 39524 | 11051.0123 | 161068.9293 | 59.77 | 790.48
2016-04-14 13:00 | 40353 | 11377.1075 | 161068.9293 | 59.77 | 807.06
2016-04-14 14:00 | 41019 | 11958.8301 | 161068.9293 | 59.77 | 820.38
2016-04-14 15:00 | 41491 | 11708.5322 | 165415.4293 | 59.77 | 829.82
2016-04-14 16:00 | 41887 | 11460.2029 | 168614.6553 | 59.77 | 837.74
2016-04-14 17:00 | 41787 | 11528.4766 | 168614.6553 | 59.77 | 835.74
2016-04-14 18:00 | 41151 | 12207.816 | 168614.6553 | 59.77 | 823.02
2016-04-14 19:00 | 40515 | 10875.0895 | 168614.6553 | 59.77 | 810.3
2016-04-14 20:00 | 41505 | 8913.8316 | 183826.7942 | 59.78 | 788.595
2016-04-14 21:00 | 40523 | 7531.774 | 184842.7942 | 59.78 | 769.937
2016-04-14 22:00 | 37671 | 6323.7771 | 180470.3942 | 59.77 | 753.42
2016-04-14 23:00 | 34419 | 6020.498 | 176998.1042 | 59.77 | 688.38
2016-04-15 | 32218 | 5652.464 | 166129.2222 | 59.79 | 579.924
2016-04-15 01:00 | 30886 | 6209.1289 | 166129.2222 | 59.79 | 555.948
2016-04-15 02:00 | 30076 | 6567.7284 | 166725.1722 | 59.79 | 541.368
2016-04-15 03:00 | 29677 | 6024.0875 | 166725.1722 | 59.79 | 534.186
2016-04-15 04:00 | 30005 | 5220.9551 | 166725.1722 | 59.79 | 540.09
2016-04-15 05:00 | 31896 | 5376.6616 | 166725.1722 | 59.79 | 574.128
2016-04-15 06:00 | 35629 | 4448.4685 | 173553.8622 | 59.77 | 712.58
2016-04-15 07:00 | 37115 | 3983.5008 | 184393.5726 | 59.78 | 705.185
2016-04-15 08:00 | 37325 | 3948.1912 | 185460.9806 | 59.78 | 709.175
2016-04-15 09:00 | 38079 | 4738.5552 | 187900.5806 | 59.78 | 723.501
2016-04-15 10:00 | 39051 | 5772.2017 | 188763.8806 | 59.78 | 741.969
2016-04-15 11:00 | 39715 | 6274.6815 | 187253.5606 | 59.78 | 754.585
2016-04-15 12:00 | 40273 | 7367.7871 | 187253.5606 | 59.78 | 765.187
2016-04-15 13:00 | 40949 | 8505.8318 | 183792.6306 | 59.77 | 818.98
2016-04-15 14:00 | 41289 | 7942.9725 | 187797.2186 | 59.78 | 784.491
2016-04-15 15:00 | 41584 | 7781.2915 | 187797.2186 | 59.78 | 790.096
2016-04-15 16:00 | 41694 | 8243.2271 | 187797.2186 | 59.78 | 792.186
2016-04-15 17:00 | 41182 | 7776.8595 | 187797.2186 | 59.78 | 782.458
2016-04-15 18:00 | 40576 | 7908.5867 | 187797.2186 | 59.78 | 770.944
2016-04-15 19:00 | 39970 | 7327.6782 | 187797.2186 | 59.78 | 759.43
2016-04-15 20:00 | 41392 | 6871.2434 | 188533.2186 | 59.78 | 786.448
2016-04-15 21:00 | 40352 | 7313.365 | 187797.2186 | 59.78 | 766.688
2016-04-15 22:00 | 37672 | 5751.4074 | 187680.3386 | 59.77 | 753.44
2016-04-15 23:00 | 34363 | 5411.0739 | 184460.4186 | 59.77 | 687.26
2016-04-16 | 34129 | 5564.2265 | 184460.4186 | 59.77 | 682.58
2016-04-16 01:00 | 32710 | 5536.1373 | 184412.4186 | 59.79 | 588.78
2016-04-16 02:00 | 31893 | 4377.5622 | 184412.4186 | 59.77 | 637.86
2016-04-16 03:00 | 31517 | 3799.4539 | 181930.8186 | 59.77 | 630.34
2016-04-16 04:00 | 31815 | 3254.4756 | 181930.8186 | 59.77 | 636.3
2016-04-16 05:00 | 33784 | 2925.9366 | 181930.8186 | 59.77 | 675.68
2016-04-16 06:00 | 37741 | 2899.0046 | 198923.5766 | 59.78 | 717.079
2016-04-16 07:00 | 39300 | 2718.8838 | 209488.5416 | 59.78 | 746.7
2016-04-16 08:00 | 39654 | 2666.0447 | 211738.5416 | 59.78 | 753.426
2016-04-16 09:00 | 40708 | 3355.2446 | 215192.5016 | 59.78 | 773.452
2016-04-16 10:00 | 41747 | 3520.921 | 216330.0149 | 59.77 | 834.94
2016-04-16 11:00 | 42263 | 4429.9356 | 216702.8216 | 59.77 | 845.26
2016-04-16 12:00 | 42654 | 5686.723 | 218192.8816 | 59.78 | 810.426
2016-04-16 13:00 | 43104 | 5466.7869 | 218439.8816 | 59.77 | 862.08
2016-04-16 14:00 | 43677 | 6064.4247 | 218439.8816 | 59.77 | 873.54
2016-04-16 15:00 | 43937 | 6182.6428 | 218439.8816 | 59.77 | 878.74
2016-04-16 16:00 | 44042 | 5820.3104 | 219455.8816 | 59.77 | 880.84
2016-04-16 17:00 | 43466 | 5251.5504 | 219455.8816 | 59.77 | 869.32
2016-04-16 18:00 | 42528 | 5133.941 | 214985.9216 | 59.78 | 808.032
2016-04-16 19:00 | 41590 | 4804.3631 | 214985.9216 | 59.78 | 790.21
2016-04-16 20:00 | 42683 | 4727.0894 | 216001.9216 | 59.77 | 853.66
2016-04-16 21:00 | 41779 | 4420.7083 | 214985.9216 | 59.78 | 793.801
2016-04-16 22:00 | 39687 | 4837.6051 | 198097.2254 | 59.78 | 754.053
2016-04-16 23:00 | 37000 | 3921.1997 | 193479.1254 | 59.78 | 703
2016-04-17 | 36039 | 3664.0304 | 191229.1254 | 59.77 | 720.78
2016-04-17 01:00 | 34354 | 3713.1464 | 191277.1254 | 59.77 | 687.08
2016-04-17 02:00 | 33191 | 3679.4163 | 191277.1254 | 59.77 | 663.82
2016-04-17 03:00 | 32667 | 3110.6102 | 193758.7254 | 59.77 | 653.34
2016-04-17 04:00 | 32427 | 3007.4157 | 193758.7254 | 59.77 | 648.54
2016-04-17 05:00 | 32927 | 2655.0429 | 193758.7254 | 59.77 | 658.54
2016-04-17 06:00 | 34316 | 1847.0088 | 193758.7254 | 59.77 | 686.32
2016-04-17 07:00 | 35339 | 1975.9672 | 193758.7254 | 59.78 | 671.441
2016-04-17 08:00 | 37234 | 2372.3631 | 193758.7254 | 59.78 | 707.446
2016-04-17 09:00 | 39219 | 3237.1464 | 202381.3134 | 59.78 | 745.161
2016-04-17 10:00 | 40821 | 3947.0989 | 210696.2784 | 59.78 | 775.599
2016-04-17 11:00 | 41817 | 4547.1455 | 210201.2784 | 59.78 | 794.523
2016-04-17 12:00 | 42242 | 4356.6721 | 213823.5984 | 59.77 | 844.84
2016-04-17 13:00 | 42480 | 5669.5714 | 213823.5984 | 59.78 | 807.12
2016-04-17 14:00 | 42556 | 5032.0013 | 213823.5984 | 59.77 | 851.12
2016-04-17 15:00 | 42541 | 4314.3003 | 214839.5984 | 59.77 | 850.82
2016-04-17 16:00 | 42414 | 5889.6451 | 213823.5984 | 59.78 | 805.866
2016-04-17 17:00 | 42043 | 7131.1987 | 210013.7984 | 59.78 | 798.817
2016-04-17 18:00 | 41779 | 7053.6984 | 210013.7984 | 59.78 | 793.801
2016-04-17 19:00 | 41514 | 5925.7974 | 210013.7984 | 59.78 | 788.766
2016-04-17 20:00 | 42217 | 4821.2665 | 211029.7984 | 59.78 | 802.123
2016-04-17 21:00 | 41147 | 3311.2481 | 211475.6682 | 59.77 | 822.94
2016-04-17 22:00 | 39148 | 2171.5596 | 211469.7416 | 59.78 | 743.812
2016-04-17 23:00 | 36706 | 1480.3792 | 201653.1266 | 59.78 | 697.414
2016-04-18 | 35750 | 1241.0875 | 201653.1266 | 59.78 | 679.25
2016-04-18 01:00 | 34169 | 1317.3733 | 196705.4466 | 59.78 | 649.211
2016-04-18 02:00 | 33200 | 1540.3472 | 196705.4466 | 59.77 | 664
2016-04-18 03:00 | 32621 | 1992.0576 | 196705.4466 | 59.77 | 652.42
2016-04-18 04:00 | 32382 | 3357.5309 | 196705.4466 | 59.77 | 647.64
2016-04-18 05:00 | 32660 | 3259.824 | 196705.4466 | 59.77 | 653.2
2016-04-18 06:00 | 33466 | 2752.7168 | 196705.4466 | 59.77 | 669.32
2016-04-18 07:00 | 34111 | 2496.9793 | 196705.4466 | 59.77 | 682.22
2016-04-18 08:00 | 35896 | 2668.2237 | 196151.2566 | 59.78 | 682.024
2016-04-18 09:00 | 37840 | 3247.9758 | 196151.2566 | 59.78 | 718.96
2016-04-18 10:00 | 39180 | 3931.4922 | 199414.7766 | 59.78 | 744.42
2016-04-18 11:00 | 39866 | 3309.8054 | 208422.1466 | 59.78 | 757.454
2016-04-18 12:00 | 40486 | 2905.8684 | 214918.9146 | 59.77 | 809.72
2016-04-18 13:00 | 40544 | 3226.2711 | 214918.9146 | 59.78 | 770.336
2016-04-18 14:00 | 40546 | 3679.4872 | 214918.9146 | 59.78 | 770.374
2016-04-18 15:00 | 40799 | 3912.0001 | 214918.9146 | 59.78 | 775.181
2016-04-18 16:00 | 41353 | 4020.2099 | 212925.3646 | 59.78 | 785.707
2016-04-18 17:00 | 41944 | 4239.1346 | 215885.0476 | 59.77 | 838.88
2016-04-18 18:00 | 42298 | 4545.7123 | 216206.5971 | 59.77 | 845.96
2016-04-18 19:00 | 42652 | 4295.4955 | 217222.5971 | 59.77 | 853.04
2016-04-18 20:00 | 44038 | 4378.2619 | 221121.007 | 59.77 | 880.76
2016-04-18 21:00 | 43013 | 3418.7114 | 221032.3971 | 59.77 | 860.26
2016-04-18 22:00 | 40396 | 2611.5324 | 212132.9291 | 59.77 | 807.92
2016-04-18 23:00 | 37023 | 2966.2195 | 195922.6961 | 59.78 | 703.437
2016-04-19 | 32088 | 2944.0008 | 195922.6961 | 59.77 | 641.76
2016-04-19 01:00 | 30903 | 2519.5728 | 195922.6961 | 59.77 | 618.06
2016-04-19 02:00 | 30253 | 2159.6387 | 195922.6961 | 59.77 | 605.06
2016-04-19 03:00 | 30090 | 2449.339 | 195922.6961 | 59.77 | 601.8
2016-04-19 04:00 | 30711 | 1779.4866 | 195922.6961 | 59.77 | 614.22
2016-04-19 05:00 | 32957 | 1376.0522 | 195922.6961 | 59.77 | 659.14
2016-04-19 06:00 | 37238 | 1350.984 | 204545.2841 | 59.78 | 707.522
2016-04-19 07:00 | 39032 | 1167.4552 | 218153.0571 | 59.77 | 780.64
2016-04-19 08:00 | 39030 | 1211.5834 | 218707.2471 | 59.77 | 780.6
2016-04-19 09:00 | 39592 | 1049.2363 | 218707.2471 | 59.77 | 791.84
2016-04-19 10:00 | 40048 | 1143.7435 | 221188.8471 | 59.77 | 800.96
2016-04-19 11:00 | 40278 | 1426.3654 | 221658.7221 | 59.77 | 805.56
2016-04-19 12:00 | 40369 | 1471.8462 | 221658.7221 | 59.77 | 807.38
2016-04-19 13:00 | 40425 | 1339.5604 | 221658.7221 | 59.77 | 808.5
2016-04-19 14:00 | 40424 | 1459.7395 | 221658.7221 | 59.77 | 808.48
2016-04-19 15:00 | 40438 | 1467.2706 | 221658.7221 | 59.77 | 808.76
2016-04-19 16:00 | 40434 | 1514.79 | 223330.7226 | 59.77 | 808.68
2016-04-19 17:00 | 40242 | 1968.0794 | 215078.2316 | 59.77 | 804.84
2016-04-19 18:00 | 40357 | 2447.7065 | 215078.2316 | 59.77 | 807.14
2016-04-19 19:00 | 40471 | 3013.5714 | 215078.2316 | 59.78 | 768.949
2016-04-19 20:00 | 41853 | 3940.6644 | 215078.2316 | 59.77 | 837.06
2016-04-19 21:00 | 40575 | 4054.0052 | 201742.7786 | 59.78 | 770.925
2016-04-19 22:00 | 37622 | 4461.9544 | 180794.5302 | 59.78 | 714.818
2016-04-19 23:00 | 34393 | 5208.6163 | 165491.4402 | 59.77 | 687.86
2016-04-20 | 31225 | 4794.5134 | 160544.7342 | 59.79 | 562.05
2016-04-20 01:00 | 30098 | 4126.902 | 160544.7342 | 59.79 | 541.764
2016-04-20 02:00 | 29519 | 5787.3076 | 160544.7342 | 59.79 | 531.342
2016-04-20 03:00 | 29367 | 6596.1334 | 160544.7342 | 59.79 | 528.606
2016-04-20 04:00 | 29874 | 5728.6474 | 160544.7342 | 59.79 | 537.732
2016-04-20 05:00 | 31944 | 6172.4319 | 160544.7342 | 59.79 | 574.992
2016-04-20 06:00 | 36021 | 5932.3541 | 165492.4142 | 59.77 | 720.42
2016-04-20 07:00 | 37250 | 3762.3739 | 186927.5042 | 59.78 | 707.75
2016-04-20 08:00 | 37168 | 2218.8319 | 197523.6526 | 59.78 | 706.192
2016-04-20 09:00 | 37633 | 2379.9324 | 197786.3446 | 59.78 | 715.027
2016-04-20 10:00 | 38277 | 3094.1722 | 197786.3446 | 59.78 | 727.263
2016-04-20 11:00 | 38757 | 3143.3974 | 202806.8326 | 59.78 | 736.383
2016-04-20 12:00 | 39209 | 2906.688 | 207289.0776 | 59.78 | 744.971
2016-04-20 13:00 | 39842 | 2726.2539 | 211121.7976 | 59.78 | 756.998
2016-04-20 14:00 | 40382 | 2890.0609 | 211121.7976 | 59.78 | 767.258
2016-04-20 15:00 | 40906 | 3481.4741 | 211121.7976 | 59.78 | 777.214
2016-04-20 16:00 | 41356 | 3843.4872 | 211121.7976 | 59.77 | 827.12
2016-04-20 17:00 | 41293 | 4233.177 | 211121.7976 | 59.78 | 784.567
2016-04-20 18:00 | 40797 | 4818.6602 | 207519.6976 | 59.78 | 775.143
2016-04-20 19:00 | 40300 | 6781.3317 | 191903.0612 | 59.78 | 765.7
2016-04-20 20:00 | 41764 | 8563.8395 | 187420.8162 | 59.78 | 793.516
2016-04-20 21:00 | 40891 | 9977.3976 | 165745.0262 | 59.77 | 817.82
2016-04-20 22:00 | 37910 | 10804.2337 | 145265.9402 | 59.79 | 682.38
2016-04-20 23:00 | 34387 | 11113.1145 | 125445.5722 | 59.79 | 618.966
2016-04-21 | 30659 | 10093.2889 | 120379.3322 | 59.79 | 551.862
2016-04-21 01:00 | 29387 | 9740.1632 | 120379.3322 | 59.79 | 528.966
2016-04-21 02:00 | 28639 | 10029.3264 | 120379.3322 | 59.79 | 515.502
2016-04-21 03:00 | 28317 | 10071.9598 | 120379.3322 | 59.79 | 509.706
2016-04-21 04:00 | 28679 | 10408.1356 | 120379.3322 | 59.79 | 516.222
2016-04-21 05:00 | 30560 | 10730.0334 | 120379.3322 | 59.79 | 550.08
2016-04-21 06:00 | 34333 | 10025.6702 | 129104.7962 | 59.79 | 617.994
2016-04-21 07:00 | 35503 | 7863.8847 | 144522.6762 | 59.77 | 710.06
2016-04-21 08:00 | 35834 | 5851.1398 | 161027.3622 | 59.77 | 716.68
2016-04-21 09:00 | 36908 | 5896.1953 | 167723.1702 | 59.77 | 738.16
2016-04-21 10:00 | 37939 | 6027.1741 | 173329.5702 | 59.77 | 758.78
2016-04-21 11:00 | 38698 | 6990.7628 | 173329.5702 | 59.77 | 773.96
2016-04-21 12:00 | 39515 | 8692.2057 | 173329.5702 | 59.77 | 790.3
2016-04-21 13:00 | 40452 | 8842.2124 | 173329.5702 | 59.77 | 809.04
2016-04-21 14:00 | 41129 | 8842.1171 | 180923.0102 | 59.77 | 822.58
2016-04-21 15:00 | 41963 | 9502.1195 | 180923.0102 | 59.77 | 839.26
2016-04-21 16:00 | 42583 | 9556.7662 | 181939.0102 | 59.78 | 809.077
2016-04-21 17:00 | 42495 | 9979.2303 | 180923.0102 | 59.78 | 807.405
2016-04-21 18:00 | 41693 | 10919.909 | 171960.2102 | 59.77 | 833.86
2016-04-21 19:00 | 40892 | 11509.3768 | 171902.2202 | 59.77 | 817.84
2016-04-21 20:00 | 42031 | 11830.5989 | 169998.2202 | 59.77 | 840.62
2016-04-21 21:00 | 40978 | 12245.8739 | 161039.2602 | 59.77 | 819.56
2016-04-21 22:00 | 38065 | 12571.851 | 137426.6842 | 59.79 | 685.17
2016-04-21 23:00 | 34506 | 12486.3482 | 118552.7998 | 59.79 | 621.108
2016-04-22 | 31843 | 12317.0552 | 114968.5298 | 59.79 | 573.174
2016-04-22 01:00 | 30335 | 12792.7807 | 116096.1056 | 59.79 | 546.03
2016-04-22 02:00 | 29579 | 13598.0449 | 116096.1056 | 59.79 | 532.422
2016-04-22 03:00 | 29218 | 13522.8574 | 116096.1056 | 59.79 | 525.924
2016-04-22 04:00 | 29545 | 13114.1924 | 116096.1056 | 59.79 | 531.81
2016-04-22 05:00 | 31247 | 12727.9418 | 116096.1056 | 59.79 | 562.446
2016-04-22 06:00 | 34886 | 11468.4645 | 129880.312 | 59.79 | 627.948
2016-04-22 07:00 | 36219 | 11654.5442 | 134900.8 | 59.79 | 651.942
2016-04-22 08:00 | 36576 | 11665.0113 | 134900.8 | 59.79 | 658.368
2016-04-22 09:00 | 37446 | 11919.7694 | 140013.18 | 59.79 | 674.028
2016-04-22 10:00 | 38326 | 10610.5913 | 150318.68 | 59.77 | 766.52
2016-04-22 11:00 | 38937 | 10559.8081 | 157864.406 | 59.77 | 778.74
2016-04-22 12:00 | 39345 | 10165.5049 | 163351.076 | 59.77 | 786.9
2016-04-22 13:00 | 39791 | 9844.4875 | 165540.4759 | 59.77 | 795.82
2016-04-22 14:00 | 40023 | 9487.1094 | 170166.1106 | 59.77 | 800.46
2016-04-22 15:00 | 39938 | 9284.9226 | 169150.1106 | 59.77 | 798.76
2016-04-22 16:00 | 39966 | 9551.109 | 169150.1106 | 59.77 | 799.32
2016-04-22 17:00 | 39629 | 9961.2243 | 169150.1106 | 59.77 | 792.58
2016-04-22 18:00 | 39521 | 9644.0141 | 169150.1106 | 59.77 | 790.42
2016-04-22 19:00 | 39413 | 9571.1576 | 169208.1006 | 59.77 | 788.26
2016-04-22 20:00 | 40682 | 9234.4058 | 171288.1006 | 59.77 | 813.64
2016-04-22 21:00 | 40004 | 9107.4585 | 167639.8106 | 59.77 | 800.08
2016-04-22 22:00 | 37561 | 10507.1314 | 144301.9146 | 59.79 | 676.098
2016-04-22 23:00 | 34509 | 11632.0107 | 129035.3502 | 59.79 | 621.162
2016-04-23 | 33888 | 13209.7468 | 129035.3502 | 59.79 | 609.984
2016-04-23 01:00 | 32487 | 12658.9865 | 129035.3502 | 59.79 | 584.766
2016-04-23 02:00 | 31829 | 11857.1273 | 129035.3502 | 59.79 | 572.922
2016-04-23 03:00 | 31403 | 12165.6594 | 129035.3502 | 59.79 | 565.254
2016-04-23 04:00 | 31860 | 12916.2899 | 129035.3502 | 59.79 | 573.48
2016-04-23 05:00 | 33701 | 12018.2596 | 129035.3502 | 59.79 | 606.618
2016-04-23 06:00 | 37620 | 11325.0302 | 142796.8546 | 59.79 | 677.16
2016-04-23 07:00 | 39418 | 9408.5856 | 164290.7206 | 59.77 | 788.36
2016-04-23 08:00 | 39799 | 7423.005 | 177712.4806 | 59.77 | 795.98
2016-04-23 09:00 | 40903 | 8069.4708 | 179962.4806 | 59.78 | 777.157
2016-04-23 10:00 | 42081 | 10484.7491 | 179371.4726 | 59.77 | 841.62
2016-04-23 11:00 | 43323 | 11578.6927 | 179371.4726 | 59.77 | 866.46
2016-04-23 12:00 | 44433 | 12676.5098 | 181825.8726 | 59.77 | 888.66
2016-04-23 13:00 | 45775 | 12835.4567 | 184213.3726 | 59.78 | 869.725
2016-04-23 14:00 | 47115 | 13137.293 | 186463.3726 | 59.78 | 895.185
2016-04-23 15:00 | 48362 | 13198.4473 | 188713.3726 | 59.78 | 918.878
2016-04-23 16:00 | 49231 | 13520.0944 | 189551.7793 | 59.78 | 935.389
2016-04-23 17:00 | 49072 | 13903.0244 | 189449.3726 | 59.78 | 932.368
2016-04-23 18:00 | 47514 | 14233.0625 | 179973.3446 | 59.78 | 902.766
2016-04-23 19:00 | 45957 | 14485.9275 | 169907.9846 | 59.77 | 919.14
2016-04-23 20:00 | 45780 | 14269.1816 | 169171.9846 | 59.77 | 915.6
2016-04-23 21:00 | 44463 | 13217.5805 | 166921.9846 | 59.77 | 889.26
2016-04-23 22:00 | 41944 | 13846.2409 | 143329.1486 | 59.77 | 838.88
2016-04-23 23:00 | 39008 | 13987.1936 | 130924.9642 | 59.79 | 702.144
2016-04-24 | 38409 | 13765.7237 | 126926.0942 | 59.79 | 691.362
2016-04-24 01:00 | 35934 | 13223.1664 | 125777.2022 | 59.79 | 646.812
2016-04-24 02:00 | 34267 | 13505.0823 | 122618.8022 | 59.79 | 616.806
2016-04-24 03:00 | 33366 | 13611.7464 | 122618.8022 | 59.79 | 600.588
2016-04-24 04:00 | 32947 | 15247.0237 | 122618.8022 | 59.79 | 593.046
2016-04-24 05:00 | 33185 | 15217.8157 | 122618.8022 | 59.79 | 597.33
2016-04-24 06:00 | 34109 | 14879.1238 | 122618.8022 | 59.79 | 613.962
2016-04-24 07:00 | 34573 | 14273.9548 | 122482.8022 | 59.79 | 622.314
2016-04-24 08:00 | 36689 | 13348.1001 | 122482.8022 | 59.79 | 660.402
2016-04-24 09:00 | 38758 | 15243.2053 | 122482.8022 | 59.79 | 697.644
2016-04-24 10:00 | 40583 | 15550.0541 | 128207.5066 | 59.79 | 730.494
2016-04-24 11:00 | 41382 | 15213.1473 | 136835.3146 | 59.79 | 744.876
2016-04-24 12:00 | 41867 | 15159.971 | 141947.6946 | 59.79 | 753.606
2016-04-24 13:00 | 42229 | 15194.4338 | 146486.4746 | 59.79 | 760.122
2016-04-24 14:00 | 42850 | 14558.6654 | 151722.4746 | 59.77 | 857
2016-04-24 15:00 | 43667 | 14155.9235 | 164449.2746 | 59.77 | 873.34
2016-04-24 16:00 | 44419 | 14010.9442 | 170171.5646 | 59.77 | 888.38
2016-04-24 17:00 | 44785 | 13188.9769 | 180767.713 | 59.77 | 895.7
2016-04-24 18:00 | 43909 | 11768.5523 | 201912.494 | 59.77 | 878.18
2016-04-24 19:00 | 43034 | 7946.8171 | 201912.494 | 59.78 | 817.646
2016-04-24 20:00 | 43392 | 5130.2785 | 213712.4767 | 59.77 | 867.84
2016-04-24 21:00 | 42392 | 4299.5803 | 213562.79 | 59.77 | 847.84
2016-04-24 22:00 | 39978 | 3726.5714 | 209985.782 | 59.78 | 759.582
2016-04-24 23:00 | 37271 | 4523.2958 | 190665.662 | 59.78 | 708.149
2016-04-25 | 35526 | 5587.7775 | 184943.372 | 59.77 | 710.52
2016-04-25 01:00 | 33665 | 7366.88 | 174347.2236 | 59.79 | 605.97
2016-04-25 02:00 | 32455 | 8490.0575 | 155159.6706 | 59.79 | 584.19
2016-04-25 03:00 | 31708 | 8209.3464 | 155159.6706 | 59.79 | 570.744
2016-04-25 04:00 | 31362 | 7403.0743 | 154771.9106 | 59.79 | 564.516
2016-04-25 05:00 | 31529 | 7833.1489 | 152127.1306 | 59.79 | 567.522
2016-04-25 06:00 | 32117 | 7429.462 | 155285.5306 | 59.79 | 578.106
2016-04-25 07:00 | 32660 | 5426.9675 | 155421.5306 | 59.79 | 587.88
2016-04-25 08:00 | 34778 | 3949.4247 | 164176.6126 | 59.77 | 695.56
2016-04-25 09:00 | 36864 | 3523.8148 | 177601.8026 | 59.78 | 700.416
2016-04-25 10:00 | 38470 | 4917.442 | 177601.8026 | 59.78 | 730.93
2016-04-25 11:00 | 39656 | 5155.9786 | 185458.2026 | 59.78 | 753.464
2016-04-25 12:00 | 40930 | 4937.8294 | 197654.101 | 59.78 | 777.67
2016-04-25 13:00 | 41930 | 6288.1155 | 200587.831 | 59.78 | 796.67
2016-04-25 14:00 | 42895 | 6480.4856 | 200587.831 | 59.78 | 815.005
2016-04-25 15:00 | 43949 | 5530.0408 | 216610.669 | 59.77 | 878.98
2016-04-25 16:00 | 44996 | 5319.6947 | 216610.669 | 59.77 | 899.92
2016-04-25 17:00 | 45820 | 6017.9126 | 216610.669 | 59.77 | 916.4
2016-04-25 18:00 | 45448 | 5056.1267 | 230629.594 | 59.77 | 908.96
2016-04-25 19:00 | 45076 | 3233.2606 | 230629.594 | 59.77 | 901.52
2016-04-25 20:00 | 45906 | 2688.3432 | 231365.594 | 59.78 | 872.214
2016-04-25 21:00 | 45000 | 2826.726 | 230629.594 | 59.77 | 900
2016-04-25 22:00 | 41661 | 4852.6599 | 196664.4132 | 59.78 | 791.559
2016-04-25 23:00 | 37483 | 7824.4358 | 153890.6117 | 59.77 | 749.66
2016-04-26 | 32913 | 8841.3297 | 143736.4273 | 59.79 | 592.434
2016-04-26 01:00 | 31435 | 10054.6152 | 143736.4273 | 59.79 | 565.83
2016-04-26 02:00 | 30566 | 10942.8411 | 140282.4673 | 59.79 | 550.188
2016-04-26 03:00 | 30297 | 9549.9699 | 137842.8673 | 59.79 | 545.346
2016-04-26 04:00 | 30704 | 9339.7879 | 137367.3273 | 59.79 | 552.672
2016-04-26 05:00 | 32765 | 9895.8019 | 140012.1073 | 59.79 | 589.77
2016-04-26 06:00 | 36662 | 9667.684 | 145145.8037 | 59.79 | 659.916
2016-04-26 07:00 | 38019 | 8571.336 | 155278.6717 | 59.77 | 760.38
2016-04-26 08:00 | 38681 | 7186.6774 | 169930.6717 | 59.77 | 773.62
2016-04-26 09:00 | 40126 | 6732.5105 | 179352.5677 | 59.78 | 762.394
2016-04-26 10:00 | 41876 | 7865.3722 | 184644.6677 | 59.78 | 795.644
2016-04-26 11:00 | 43371 | 7647.6524 | 200140.4277 | 59.78 | 824.049
2016-04-26 12:00 | 44525 | 6248.3574 | 219736.5761 | 59.77 | 890.5
2016-04-26 13:00 | 46007 | 6226.2656 | 224757.0641 | 59.77 | 920.14
2016-04-26 14:00 | 47290 | 7009.7846 | 225493.0641 | 59.77 | 945.8
2016-04-26 15:00 | 48066 | 8639.5703 | 224757.0641 | 59.77 | 961.32
2016-04-26 16:00 | 48896 | 8765.7941 | 224757.0641 | 59.77 | 977.92
2016-04-26 17:00 | 48523 | 9049.2715 | 222868.1141 | 59.77 | 970.46
2016-04-26 18:00 | 47307 | 10358.877 | 206451.0491 | 59.78 | 898.833
2016-04-26 19:00 | 46091 | 10114.1291 | 206237.1602 | 59.78 | 875.729
2016-04-26 20:00 | 46655 | 9482.8936 | 206237.1602 | 59.78 | 886.445
2016-04-26 21:00 | 45114 | 8765.5596 | 201216.6722 | 59.78 | 857.166
2016-04-26 22:00 | 41218 | 7851.7263 | 181559.0542 | 59.78 | 783.142
2016-04-26 23:00 | 37147 | 6597.9593 | 182109.7417 | 59.77 | 742.94
2016-04-27 | 34519 | 4949.1446 | 182109.7417 | 59.77 | 690.38
2016-04-27 01:00 | 32895 | 3545.3711 | 182109.7417 | 59.77 | 657.9
2016-04-27 02:00 | 31965 | 3387.9362 | 182109.7417 | 59.77 | 639.3
2016-04-27 03:00 | 31520 | 3785.4596 | 184549.3417 | 59.77 | 630.4
2016-04-27 04:00 | 31835 | 3024.7848 | 185412.6417 | 59.77 | 636.7
2016-04-27 05:00 | 33737 | 3221.4788 | 185412.6417 | 59.77 | 674.74
2016-04-27 06:00 | 37779 | 2653.5069 | 192162.6417 | 59.78 | 717.801
2016-04-27 07:00 | 38917 | 2439.0184 | 203905.0797 | 59.78 | 739.423
2016-04-27 08:00 | 39051 | 2544.8321 | 203905.0797 | 59.78 | 741.969
2016-04-27 09:00 | 39942 | 2217.9933 | 206947.8877 | 59.77 | 798.84
2016-04-27 10:00 | 40833 | 1923.6325 | 217820.4757 | 59.77 | 816.66
2016-04-27 11:00 | 41388 | 1765.3086 | 222302.7207 | 59.77 | 827.76
2016-04-27 12:00 | 41793 | 1982.4272 | 222233.4775 | 59.77 | 835.86
2016-04-27 13:00 | 42559 | 2320.9001 | 225687.4375 | 59.77 | 851.18
2016-04-27 14:00 | 42984 | 2514.2164 | 224498.7767 | 59.77 | 859.68
2016-04-27 15:00 | 43381 | 3452.1864 | 226075.5467 | 59.77 | 867.62
2016-04-27 16:00 | 43827 | 3532.9456 | 226075.5467 | 59.77 | 876.54
2016-04-27 17:00 | 43623 | 3594.6778 | 224921.6887 | 59.77 | 872.46
2016-04-27 18:00 | 42999 | 3655.0864 | 224921.6887 | 59.77 | 859.98
2016-04-27 19:00 | 42374 | 3281.6597 | 222653.9776 | 59.77 | 847.48
2016-04-27 20:00 | 43563 | 3640.4526 | 222653.9776 | 59.77 | 871.26
2016-04-27 21:00 | 42505 | 6103.3796 | 199659.571 | 59.78 | 807.595
2016-04-27 22:00 | 39237 | 6837.8234 | 171217.663 | 59.77 | 784.74
2016-04-27 23:00 | 35632 | 7077.1289 | 152361.297 | 59.77 | 712.64
2016-04-28 | 31789 | 8047.4695 | 139295.097 | 59.79 | 572.202
2016-04-28 01:00 | 30548 | 9937.642 | 134467.805 | 59.79 | 549.864
2016-04-28 02:00 | 29971 | 10642.7756 | 134467.805 | 59.79 | 539.478
2016-04-28 03:00 | 29704 | 11568.7594 | 134467.805 | 59.79 | 534.672
2016-04-28 04:00 | 30133 | 12042.9217 | 131587.409 | 59.79 | 542.394
2016-04-28 05:00 | 32068 | 12275.4561 | 131028.2647 | 59.79 | 577.224
2016-04-28 06:00 | 35885 | 11936.1108 | 131028.2647 | 59.79 | 645.93
2016-04-28 07:00 | 36976 | 11180.2457 | 139747.9647 | 59.79 | 665.568
2016-04-28 08:00 | 37221 | 10299.334 | 143097.0547 | 59.79 | 669.978
2016-04-28 09:00 | 38009 | 10832.1651 | 147443.5547 | 59.79 | 684.162
2016-04-28 10:00 | 39122 | 11715.5801 | 147443.5547 | 59.79 | 704.196
2016-04-28 11:00 | 39974 | 12083.4815 | 150642.7807 | 59.77 | 799.48
2016-04-28 12:00 | 40684 | 12991.7287 | 152962.0239 | 59.77 | 813.68
2016-04-28 13:00 | 41716 | 12847.9226 | 158448.6939 | 59.77 | 834.32
2016-04-28 14:00 | 42703 | 12116.4826 | 166466.0447 | 59.77 | 854.06
2016-04-28 15:00 | 43758 | 12500.775 | 167202.0447 | 59.77 | 875.16
2016-04-28 16:00 | 44662 | 13173.342 | 167403.4079 | 59.77 | 893.24
2016-04-28 17:00 | 44780 | 13676.6052 | 166466.0447 | 59.77 | 895.6
2016-04-28 18:00 | 43811 | 14412.5629 | 160241.7341 | 59.77 | 876.22
2016-04-28 19:00 | 42841 | 14827.1304 | 151062.6381 | 59.77 | 856.82
2016-04-28 20:00 | 43483 | 14999.2208 | 151062.6381 | 59.77 | 869.66
2016-04-28 21:00 | 42615 | 14837.7303 | 145575.9681 | 59.77 | 852.3
2016-04-28 22:00 | 39432 | 15105.3576 | 123526.8537 | 59.79 | 709.776
2016-04-28 23:00 | 35772 | 14871.3653 | 119717.0537 | 59.79 | 643.896
2016-04-29 | 32304 | 15259.6512 | 114769.3737 | 59.79 | 581.472
2016-04-29 01:00 | 30887 | 15250.9669 | 116928.7737 | 59.79 | 555.966
2016-04-29 02:00 | 30073 | 14958.7022 | 113692.1037 | 59.79 | 541.314
2016-04-29 03:00 | 29748 | 14818.6085 | 113692.1037 | 59.79 | 535.464
2016-04-29 04:00 | 30005 | 14583.6342 | 116572.4997 | 59.79 | 540.09
2016-04-29 05:00 | 31788 | 14166.3098 | 120738.964 | 59.79 | 572.184
2016-04-29 06:00 | 35386 | 13527.6536 | 120738.964 | 59.79 | 636.948
2016-04-29 07:00 | 36622 | 14462.0814 | 120738.964 | 59.79 | 659.196
2016-04-29 08:00 | 37233 | 14966.5617 | 120738.964 | 59.79 | 670.194
2016-04-29 09:00 | 38366 | 14983.8359 | 120738.964 | 59.79 | 690.588
2016-04-29 10:00 | 39753 | 15520.526 | 121887.856 | 59.79 | 715.554
2016-04-29 11:00 | 41078 | 15690.0497 | 127216.656 | 59.79 | 739.404
2016-04-29 12:00 | 42297 | 15560.0551 | 132164.336 | 59.79 | 761.346
2016-04-29 13:00 | 43680 | 15534.7027 | 137184.824 | 59.77 | 873.6
2016-04-29 14:00 | 44913 | 15568.6469 | 145646.294 | 59.77 | 898.26
2016-04-29 15:00 | 46151 | 15919.4836 | 155729.3504 | 59.77 | 923.02
2016-04-29 16:00 | 46999 | 15905.103 | 155054.7435 | 59.77 | 939.98
2016-04-29 17:00 | 46828 | 16220.5882 | 154471.8004 | 59.77 | 936.56
2016-04-29 18:00 | 45783 | 16246.3739 | 154984.731 | 59.77 | 915.66
2016-04-29 19:00 | 44739 | 16084.1401 | 154984.731 | 59.77 | 894.78
2016-04-29 20:00 | 45532 | 15591.3596 | 154984.731 | 59.77 | 910.64
2016-04-29 21:00 | 44803 | 15182.0394 | 154984.731 | 59.77 | 896.06
2016-04-29 22:00 | 41974 | 15155.4135 | 141502.773 | 59.79 | 755.532
2016-04-29 23:00 | 38297 | 15314.4751 | 141502.773 | 59.79 | 689.346
2016-04-30 | 37785 | 14979.8832 | 137918.503 | 59.79 | 680.13
2016-04-30 01:00 | 36110 | 13523.717 | 137918.503 | 59.79 | 649.98
2016-04-30 02:00 | 35109 | 13222.0933 | 137918.503 | 59.79 | 631.962
2016-04-30 03:00 | 34701 | 13411.6834 | 137918.503 | 59.79 | 624.618
2016-04-30 04:00 | 35002 | 13068.6505 | 137918.503 | 59.79 | 630.036
2016-04-30 05:00 | 36984 | 12690.7249 | 137634.095 | 59.79 | 665.712
2016-04-30 06:00 | 41083 | 12666.8209 | 146261.903 | 59.77 | 821.66
2016-04-30 07:00 | 42879 | 11502.4873 | 164519.099 | 59.77 | 857.58
2016-04-30 08:00 | 43184 | 9821.8346 | 174464.729 | 59.78 | 820.496
2016-04-30 09:00 | 44324 | 11431.351 | 174464.729 | 59.78 | 842.156
2016-04-30 10:00 | 45548 | 13819.364 | 174464.729 | 59.77 | 910.96
2016-04-30 11:00 | 46448 | 14302.7648 | 174464.729 | 59.77 | 928.96
2016-04-30 12:00 | 47018 | 13750.625 | 176714.729 | 59.78 | 893.342
2016-04-30 13:00 | 47776 | 13792.072 | 180068.4394 | 59.78 | 907.744
2016-04-30 14:00 | 48469 | 13459.9338 | 190402.7844 | 59.78 | 920.911
2016-04-30 15:00 | 49012 | 12967.2049 | 195669.9144 | 59.78 | 931.228
2016-04-30 16:00 | 49276 | 12717.0528 | 197663.4644 | 59.78 | 936.244
2016-04-30 17:00 | 48927 | 12681.833 | 197310.2186 | 59.78 | 929.613
2016-04-30 18:00 | 47776 | 13259.3855 | 202330.7066 | 59.78 | 907.744
2016-04-30 19:00 | 46625 | 9541.2339 | 202666.3366 | 59.78 | 885.875
2016-04-30 20:00 | 46963 | 5124.9443 | 219149.2598 | 59.77 | 939.26
2016-04-30 21:00 | 46010 | 6030.9651 | 218379.1366 | 59.77 | 920.2
2016-04-30 22:00 | 43703 | 6424.3489 | 209173.3262 | 59.78 | 830.357
2016-04-30 23:00 | 40757 | 5137.2541 | 203159.7762 | 59.78 | 774.383
2016-05-01 | 39860 | 5947.5998 | 194430.7312 | 59.78 | 757.34
2016-05-01 01:00 | 37848 | 7676.1654 | 194430.7312 | 59.77 | 756.96
2016-05-01 02:00 | 36519 | 6013.1933 | 194430.7312 | 59.77 | 730.38
2016-05-01 03:00 | 35706 | 4096.9162 | 192929.0812 | 59.77 | 714.12
2016-05-01 04:00 | 35339 | 4949.6878 | 192929.0812 | 59.77 | 706.78
2016-05-01 05:00 | 35525 | 4042.0293 | 193213.4892 | 59.77 | 710.5
2016-05-01 06:00 | 36175 | 4070.7407 | 193213.4892 | 59.77 | 723.5
2016-05-01 07:00 | 36777 | 2975.8248 | 193213.4892 | 59.78 | 698.763
2016-05-01 08:00 | 38974 | 2456.7614 | 197780.8972 | 59.78 | 740.506
2016-05-01 09:00 | 41235 | 1821.4696 | 215753.7456 | 59.77 | 824.7
2016-05-01 10:00 | 43235 | 2287.8333 | 226318.7106 | 59.77 | 864.7
2016-05-01 11:00 | 44698 | 2365.2088 | 232022.6706 | 59.77 | 893.96
2016-05-01 12:00 | 45839 | 3435.5591 | 232022.6706 | 59.77 | 916.78
2016-05-01 13:00 | 46768 | 5557.292 | 232022.6706 | 59.77 | 935.36
2016-05-01 14:00 | 47634 | 5750.0074 | 232022.6706 | 59.77 | 952.68
2016-05-01 15:00 | 48435 | 5863.6015 | 232022.6706 | 59.78 | 920.265
2016-05-01 16:00 | 48989 | 7102.8928 | 228979.8626 | 59.77 | 979.78
2016-05-01 17:00 | 48933 | 8102.8726 | 230107.4384 | 59.77 | 978.66
2016-05-01 18:00 | 47879 | 8948.8901 | 228597.1184 | 59.77 | 957.58
2016-05-01 19:00 | 46826 | 7063.8758 | 230173.8884 | 59.77 | 936.52
2016-05-01 20:00 | 46917 | 4800.1609 | 230173.8884 | 59.77 | 938.34
2016-05-01 21:00 | 45691 | 3841.4973 | 230173.8884 | 59.77 | 913.82
2016-05-01 22:00 | 43147 | 5546.0422 | 200132.1254 | 59.77 | 862.94
2016-05-01 23:00 | 40280 | 6870.5127 | 174350.057 | 59.78 | 765.32
2016-05-02 | 37851 | 7287.4386 | 158730.361 | 59.77 | 757.02
2016-05-02 01:00 | 35922 | 8705.7035 | 145664.161 | 59.79 | 646.596
2016-05-02 02:00 | 34592 | 9234.9392 | 145664.161 | 59.79 | 622.656
2016-05-02 03:00 | 33699 | 9508.1753 | 144007.411 | 59.79 | 606.582
2016-05-02 04:00 | 33181 | 11071.0432 | 144007.411 | 59.79 | 597.258
2016-05-02 05:00 | 33055 | 11141.9299 | 144007.411 | 59.79 | 594.99
2016-05-02 06:00 | 33522 | 11349.4511 | 144007.411 | 59.79 | 603.396
2016-05-02 07:00 | 33794 | 8992.9654 | 144007.411 | 59.79 | 608.292
2016-05-02 08:00 | 36017 | 6182.181 | 159660.471 | 59.77 | 720.34
2016-05-02 09:00 | 37976 | 5457.6463 | 170555.287 | 59.78 | 721.544
2016-05-02 10:00 | 40221 | 6876.6367 | 171982.887 | 59.78 | 764.199
2016-05-02 11:00 | 41526 | 10340.7741 | 171246.887 | 59.77 | 830.52
2016-05-02 12:00 | 43109 | 13155.5059 | 171246.887 | 59.77 | 862.18
2016-05-02 13:00 | 44335 | 14371.6698 | 171246.887 | 59.77 | 886.7
2016-05-02 14:00 | 45910 | 14309.0173 | 171246.887 | 59.77 | 918.2
2016-05-02 15:00 | 47369 | 14422.3511 | 193093.0354 | 59.78 | 900.011
2016-05-02 16:00 | 48809 | 14181.5753 | 193093.0354 | 59.78 | 927.371
2016-05-02 17:00 | 49574 | 13296.5871 | 196695.1354 | 59.78 | 941.906
2016-05-02 18:00 | 48758 | 12129.1754 | 222126.5244 | 59.78 | 926.402
2016-05-02 19:00 | 47942 | 6814.7378 | 228854.9244 | 59.77 | 958.84
2016-05-02 20:00 | 47409 | 2748.7391 | 236397.6237 | 59.78 | 900.771
2016-05-02 21:00 | 46318 | 3677.9462 | 239021.6844 | 59.78 | 880.042
2016-05-02 22:00 | 42695 | 4861.1037 | 222756.2584 | 59.77 | 853.9
2016-05-02 23:00 | 38402 | 6059.8925 | 206060.36 | 59.77 | 768.04
2016-05-03 | 32907 | 7100.6006 | 178991.5056 | 59.79 | 592.326
2016-05-03 01:00 | 31222 | 6893.6542 | 175389.4056 | 59.79 | 561.996
2016-05-03 02:00 | 30308 | 5496.136 | 156488.8246 | 59.79 | 545.544
2016-05-03 03:00 | 30080 | 5292.9976 | 156488.8246 | 59.79 | 541.44
2016-05-03 04:00 | 30486 | 5241.3372 | 156488.8246 | 59.79 | 548.748
2016-05-03 05:00 | 32376 | 5356.2161 | 159647.2246 | 59.79 | 582.768
2016-05-03 06:00 | 35999 | 5923.2367 | 159647.2246 | 59.77 | 719.98
2016-05-03 07:00 | 37448 | 4326.6257 | 174867.649 | 59.78 | 711.512
2016-05-03 08:00 | 38576 | 3524.0364 | 186678.209 | 59.78 | 732.944
2016-05-03 09:00 | 40349 | 4394.8051 | 190285.529 | 59.78 | 766.631
2016-05-03 10:00 | 42302 | 5740.9858 | 194632.029 | 59.78 | 803.738
2016-05-03 11:00 | 43463 | 6679.9108 | 194632.029 | 59.78 | 825.797
2016-05-03 12:00 | 45133 | 7104.263 | 201067.925 | 59.77 | 902.66
2016-05-03 13:00 | 47056 | 7626.5848 | 213421.6354 | 59.77 | 941.12
2016-05-03 14:00 | 48565 | 6768.2739 | 226516.1734 | 59.77 | 971.3
2016-05-03 15:00 | 49426 | 7549.3504 | 226516.1734 | 59.77 | 988.52
2016-05-03 16:00 | 49457 | 7647.769 | 226516.1734 | 59.77 | 989.14
2016-05-03 17:00 | 48908 | 7196.403 | 226516.1734 | 59.77 | 978.16
2016-05-03 18:00 | 47643 | 6742.8192 | 229988.4634 | 59.77 | 952.86
2016-05-03 19:00 | 46377 | 4105.6064 | 229988.4634 | 59.77 | 927.54
2016-05-03 20:00 | 46228 | 2746.6295 | 229988.4634 | 59.78 | 878.332
2016-05-03 21:00 | 44792 | 2952.769 | 226534.5034 | 59.77 | 895.84
2016-05-03 22:00 | 40932 | 2906.4547 | 198315.767 | 59.77 | 818.64
2016-05-03 23:00 | 36778 | 3484.1714 | 173582.301 | 59.78 | 698.782
2016-05-04 | 34725 | 5253.1442 | 153817.921 | 59.77 | 694.5
2016-05-04 01:00 | 32928 | 6552.7279 | 153817.921 | 59.79 | 592.704
2016-05-04 02:00 | 31791 | 8144.3739 | 153817.921 | 59.79 | 572.238
2016-05-04 03:00 | 31250 | 9128.4468 | 153817.921 | 59.79 | 562.5
2016-05-04 04:00 | 31480 | 10333.557 | 153817.921 | 59.79 | 566.64
2016-05-04 05:00 | 33310 | 10568.4737 | 153817.921 | 59.79 | 599.58
2016-05-04 06:00 | 37003 | 10474.8963 | 153817.921 | 59.79 | 666.054
2016-05-04 07:00 | 38342 | 8852.4754 | 153817.921 | 59.77 | 766.84
2016-05-04 08:00 | 39054 | 7050.8521 | 165886.711 | 59.77 | 781.08
2016-05-04 09:00 | 40272 | 5579.567 | 179068.971 | 59.78 | 765.168
2016-05-04 10:00 | 41985 | 5128.0271 | 193518.441 | 59.78 | 797.715
2016-05-04 11:00 | 43683 | 6544.8099 | 194254.441 | 59.78 | 829.977
2016-05-04 12:00 | 45125 | 9533.4752 | 193518.441 | 59.78 | 857.375
2016-05-04 13:00 | 46906 | 10151.3126 | 193518.441 | 59.78 | 891.214
2016-05-04 14:00 | 48547 | 10475.4847 | 203689.179 | 59.77 | 970.94
2016-05-04 15:00 | 50362 | 10900.2238 | 212894.9894 | 59.77 | 1007.24
2016-05-04 16:00 | 51997 | 11253.7457 | 217237.1774 | 59.77 | 1039.94
2016-05-04 17:00 | 52631 | 10672.4319 | 221838.8007 | 59.77 | 1052.62
2016-05-04 18:00 | 51439 | 10520.7801 | 218120.7774 | 59.77 | 1028.78
2016-05-04 19:00 | 50247 | 10865.9307 | 215134.7774 | 59.77 | 1004.94
2016-05-04 20:00 | 49751 | 10593.8962 | 214186.3074 | 59.77 | 995.02
2016-05-04 21:00 | 48249 | 12432.1127 | 196032.9474 | 59.78 | 916.731
2016-05-04 22:00 | 44102 | 13693.3944 | 164550.5394 | 59.77 | 882.04
2016-05-04 23:00 | 39587 | 13962.9659 | 138860.0246 | 59.79 | 712.566
2016-05-05 | 33424 | 13522.9666 | 131297.9166 | 59.79 | 601.632
2016-05-05 01:00 | 31678 | 12613.5896 | 127465.1966 | 59.79 | 570.204
2016-05-05 02:00 | 30486 | 11984.0275 | 127465.1966 | 59.79 | 548.748
2016-05-05 03:00 | 29922 | 10846.1125 | 127465.1966 | 59.79 | 538.596
2016-05-05 04:00 | 30169 | 9717.8619 | 127465.1966 | 59.79 | 543.042
2016-05-05 05:00 | 31570 | 8334.1239 | 131072.5166 | 59.79 | 568.26
2016-05-05 06:00 | 34743 | 7458.3991 | 141272.453 | 59.79 | 625.374
2016-05-05 07:00 | 35937 | 6063.0351 | 154754.411 | 59.77 | 718.74
2016-05-05 08:00 | 36975 | 5213.687 | 168172.291 | 59.77 | 739.5
2016-05-05 09:00 | 38649 | 6165.7668 | 171408.961 | 59.77 | 772.98
2016-05-05 10:00 | 40487 | 6576.3601 | 181358.431 | 59.78 | 769.253
2016-05-05 11:00 | 42436 | 5030.5464 | 201187.1834 | 59.78 | 806.284
2016-05-05 12:00 | 44156 | 3114.7763 | 226501.3534 | 59.77 | 883.12
2016-05-05 13:00 | 46528 | 2074.8001 | 254533.0156 | 59.78 | 884.032
2016-05-05 14:00 | 48940 | 1943.6907 | 271171.7948 | 59.78 | 929.86
2016-05-05 15:00 | 51055 | 2330.6523 | 271724.4278 | 59.76 | 1072.155
2016-05-05 16:00 | 52478 | 2046.9655 | 275688.3028 | 59.76 | 1102.038
2016-05-05 17:00 | 52789 | 2326.8769 | 275688.3028 | 59.76 | 1108.569
2016-05-05 18:00 | 51408 | 2465.7978 | 278056.1408 | 59.76 | 1079.568
2016-05-05 19:00 | 50027 | 4430.2615 | 262727.3883 | 59.78 | 950.513
2016-05-05 20:00 | 48881 | 7607.8397 | 229556.8183 | 59.77 | 977.62
2016-05-05 21:00 | 47039 | 8090.1277 | 209610.4665 | 59.77 | 940.78
2016-05-05 22:00 | 43046 | 8865.0063 | 175976.5577 | 59.78 | 817.874
2016-05-05 23:00 | 38470 | 8376.3137 | 153891.1632 | 59.77 | 769.4
2016-05-06 | 34499 | 8425.1595 | 140815.4128 | 59.79 | 620.982
2016-05-06 01:00 | 32566 | 8433.8684 | 140815.4128 | 59.79 | 586.188
2016-05-06 02:00 | 31283 | 8754.078 | 140815.4128 | 59.79 | 563.094
2016-05-06 03:00 | 30616 | 9178.26 | 140815.4128 | 59.79 | 551.088
2016-05-06 04:00 | 30759 | 9653.8292 | 140219.4628 | 59.79 | 553.662
2016-05-06 05:00 | 32286 | 9607.9777 | 140219.4628 | 59.79 | 581.148
2016-05-06 06:00 | 35400 | 9693.7241 | 140219.4628 | 59.79 | 637.2
2016-05-06 07:00 | 36633 | 9350.838 | 140219.4628 | 59.79 | 659.394
2016-05-06 08:00 | 37999 | 9127.748 | 148505.6228 | 59.77 | 759.98
2016-05-06 09:00 | 39770 | 9182.6072 | 158659.8072 | 59.77 | 795.4
2016-05-06 10:00 | 41799 | 9323.2555 | 169378.5872 | 59.77 | 835.98
2016-05-06 11:00 | 43808 | 9400.9282 | 179549.0572 | 59.78 | 832.352
2016-05-06 12:00 | 45417 | 9349.3436 | 190702.1032 | 59.78 | 862.923
2016-05-06 13:00 | 47540 | 10556.3638 | 198138.6132 | 59.78 | 903.26
2016-05-06 14:00 | 49333 | 11640.2523 | 198138.6132 | 59.77 | 986.66
2016-05-06 15:00 | 50744 | 12539.6775 | 198138.6132 | 59.77 | 1014.88
2016-05-06 16:00 | 52056 | 13553.8345 | 198874.6132 | 59.77 | 1041.12
2016-05-06 17:00 | 52011 | 14125.255 | 198138.6132 | 59.77 | 1040.22
2016-05-06 18:00 | 50336 | 14293.7738 | 192532.2132 | 59.78 | 956.384
2016-05-06 19:00 | 48661 | 13726.409 | 187847.2984 | 59.78 | 924.559
2016-05-06 20:00 | 48309 | 12720.3226 | 187256.2904 | 59.78 | 917.871
2016-05-06 21:00 | 47076 | 13405.3861 | 174227.3244 | 59.78 | 894.444
2016-05-06 22:00 | 43506 | 14077.4776 | 149442.4564 | 59.77 | 870.12
2016-05-06 23:00 | 39451 | 14571.7592 | 144308.76 | 59.79 | 710.118
2016-05-07 | 38320 | 14156.6868 | 138553.46 | 59.79 | 689.76
2016-05-07 01:00 | 36375 | 13389.7825 | 138553.46 | 59.79 | 654.75
2016-05-07 02:00 | 35149 | 13147.1845 | 138553.46 | 59.79 | 632.682
2016-05-07 03:00 | 34350 | 12050.6385 | 138553.46 | 59.79 | 618.3
2016-05-07 04:00 | 34399 | 10264.8556 | 139149.41 | 59.79 | 619.182
2016-05-07 05:00 | 35962 | 8968.4619 | 141470.4245 | 59.79 | 647.316
2016-05-07 06:00 | 39401 | 8654.1997 | 159753.3009 | 59.77 | 788.02
2016-05-07 07:00 | 40683 | 8640.774 | 169221.2109 | 59.77 | 813.66
2016-05-07 08:00 | 41872 | 8659.6613 | 175521.1069 | 59.78 | 795.568
2016-05-07 09:00 | 43879 | 10478.4947 | 177771.1069 | 59.78 | 833.701
2016-05-07 10:00 | 46202 | 10870.6682 | 193863.0924 | 59.78 | 877.838
2016-05-07 11:00 | 48219 | 11261.459 | 200952.0972 | 59.78 | 916.161
2016-05-07 12:00 | 49744 | 10681.661 | 215605.0802 | 59.77 | 994.88
2016-05-07 13:00 | 51919 | 9526.7187 | 232563.6702 | 59.77 | 1038.38
2016-05-07 14:00 | 53534 | 8804.5214 | 247424.3686 | 59.78 | 1017.146
2016-05-07 15:00 | 54653 | 9247.6444 | 246650.0386 | 59.78 | 1038.407
2016-05-07 16:00 | 55168 | 9840.3465 | 247106.0386 | 59.78 | 1048.192
2016-05-07 17:00 | 54494 | 10653.8524 | 244168.4386 | 59.78 | 1035.386
2016-05-07 18:00 | 52293 | 12172.7855 | 223569.8424 | 59.77 | 1045.86
2016-05-07 19:00 | 50093 | 12510.2927 | 214972.4876 | 59.77 | 1001.86
2016-05-07 20:00 | 49095 | 12668.0977 | 200910.5126 | 59.78 | 932.805
2016-05-07 21:00 | 47706 | 10882.982 | 198660.5126 | 59.78 | 906.414
2016-05-07 22:00 | 44694 | 8543.2812 | 193214.6142 | 59.78 | 849.186
2016-05-07 23:00 | 40990 | 7384.9777 | 179751.8142 | 59.78 | 778.81
2016-05-08 | 40209 | 6165.58 | 179809.8042 | 59.78 | 763.971
2016-05-08 01:00 | 39315 | 6092.5192 | 179809.8042 | 59.78 | 746.985
2016-05-08 02:00 | 37695 | 6427.5404 | 179809.8042 | 59.77 | 753.9
2016-05-08 03:00 | 36506 | 7130.6055 | 177852.5762 | 59.77 | 730.12
2016-05-08 04:00 | 35923 | 7513.5966 | 177852.5762 | 59.77 | 718.46
2016-05-08 05:00 | 36110 | 7655.0357 | 177852.5762 | 59.77 | 722.2
2016-05-08 06:00 | 36740 | 7342.0925 | 180831.0842 | 59.77 | 734.8
2016-05-08 07:00 | 37420 | 6998.8026 | 182407.8542 | 59.77 | 748.4
2016-05-08 08:00 | 39314 | 6905.2954 | 182543.8542 | 59.77 | 786.28
2016-05-08 09:00 | 41192 | 7214.6954 | 182543.8542 | 59.78 | 782.648
2016-05-08 10:00 | 42743 | 9071.9442 | 182543.8542 | 59.78 | 812.117
2016-05-08 11:00 | 43624 | 9316.3321 | 184052.2042 | 59.78 | 828.856
2016-05-08 12:00 | 44324 | 7932.2575 | 197325.4042 | 59.78 | 842.156
2016-05-08 13:00 | 44684 | 7328.7018 | 203988.9246 | 59.78 | 848.996
2016-05-08 14:00 | 45167 | 7873.9032 | 204680.5246 | 59.78 | 858.173
2016-05-08 15:00 | 45597 | 8178.0902 | 204680.5246 | 59.78 | 866.343
2016-05-08 16:00 | 45873 | 7166.0972 | 204680.5246 | 59.77 | 917.46
2016-05-08 17:00 | 45691 | 7670.2143 | 207162.1246 | 59.77 | 913.82
2016-05-08 18:00 | 44850 | 8713.1276 | 205249.7246 | 59.78 | 852.15
2016-05-08 19:00 | 44010 | 8155.0682 | 205249.7246 | 59.78 | 836.19
2016-05-08 20:00 | 44798 | 7521.4978 | 205249.7246 | 59.78 | 851.162
2016-05-08 21:00 | 44266 | 7497.2017 | 199646.0142 | 59.78 | 841.054
2016-05-08 22:00 | 42172 | 7699.0864 | 179474.2542 | 59.78 | 801.268
2016-05-08 23:00 | 39361 | 7163.7939 | 170788.3582 | 59.77 | 787.22
2016-05-09 | 38366 | 6790.9087 | 170788.3582 | 59.77 | 767.32
2016-05-09 01:00 | 36415 | 6195.5558 | 170788.3582 | 59.77 | 728.3
2016-05-09 02:00 | 35237 | 5234.7084 | 170788.3582 | 59.77 | 704.74
2016-05-09 03:00 | 34526 | 5064.2694 | 170788.3582 | 59.77 | 690.52
2016-05-09 04:00 | 34144 | 5203.1623 | 170788.3582 | 59.77 | 682.88
2016-05-09 05:00 | 34328 | 4197.1306 | 170788.3582 | 59.77 | 686.56
2016-05-09 06:00 | 34855 | 4117.8612 | 172745.5862 | 59.77 | 697.1
2016-05-09 07:00 | 35650 | 5047.5196 | 170752.0362 | 59.77 | 713
2016-05-09 08:00 | 37687 | 6170.9893 | 170752.0362 | 59.77 | 753.74
2016-05-09 09:00 | 39668 | 6717.9617 | 173087.9622 | 59.78 | 753.692
2016-05-09 10:00 | 40952 | 7726.679 | 173087.9622 | 59.78 | 778.088
2016-05-09 11:00 | 41837 | 9233.3374 | 173087.9622 | 59.78 | 794.903
2016-05-09 12:00 | 42667 | 10479.2908 | 175527.5622 | 59.77 | 853.34
2016-05-09 13:00 | 43308 | 9977.0114 | 175527.5622 | 59.78 | 822.852
2016-05-09 14:00 | 43832 | 9500.5901 | 175527.5622 | 59.78 | 832.808
2016-05-09 15:00 | 44251 | 9612.8764 | 175527.5622 | 59.78 | 840.769
2016-05-09 16:00 | 44620 | 9865.8415 | 175527.5622 | 59.78 | 847.78
2016-05-09 17:00 | 44966 | 10617.1581 | 175139.8022 | 59.78 | 854.354
2016-05-09 18:00 | 45265 | 12616.8206 | 167594.0762 | 59.78 | 860.035
2016-05-09 19:00 | 45565 | 14184.3847 | 163986.7562 | 59.77 | 911.3
2016-05-09 20:00 | 47236 | 14907.1375 | 163986.7562 | 59.77 | 944.72
2016-05-09 21:00 | 47170 | 14784.9476 | 163414.2562 | 59.77 | 943.4
2016-05-09 22:00 | 44910 | 14938.4316 | 146583.2082 | 59.77 | 898.2
2016-05-09 23:00 | 41687 | 13852.8112 | 141449.5118 | 59.77 | 833.74
2016-05-10 | 34995 | 12618.8205 | 132799.0018 | 59.79 | 629.91
2016-05-10 01:00 | 33703 | 12633.7569 | 132799.0018 | 59.79 | 606.654
2016-05-10 02:00 | 33036 | 13545.4709 | 130366.0018 | 59.79 | 594.648
2016-05-10 03:00 | 32858 | 13437.5612 | 130366.0018 | 59.79 | 591.444
2016-05-10 04:00 | 33523 | 13487.6984 | 129815.3143 | 59.79 | 603.414
2016-05-10 05:00 | 35380 | 13625.6194 | 133035.2343 | 59.79 | 636.84
2016-05-10 06:00 | 38962 | 12782.2405 | 133035.2343 | 59.79 | 701.316
2016-05-10 07:00 | 40566 | 13345.8192 | 135028.7843 | 59.79 | 730.188
2016-05-10 08:00 | 41651 | 13888.1554 | 135028.7843 | 59.77 | 833.02
2016-05-10 09:00 | 43487 | 14720.7677 | 139476.3543 | 59.77 | 869.74
2016-05-10 10:00 | 45468 | 15816.4725 | 141828.5143 | 59.77 | 909.36
2016-05-10 11:00 | 47238 | 16247.6208 | 152572.5007 | 59.77 | 944.76
2016-05-10 12:00 | 48755 | 15700.5395 | 168562.6887 | 59.78 | 926.345
2016-05-10 13:00 | 50296 | 15673.3672 | 176381.4787 | 59.78 | 955.624
2016-05-10 14:00 | 51584 | 15996.5453 | 185344.2787 | 59.78 | 980.096
2016-05-10 15:00 | 52750 | 15601.9196 | 195016.8447 | 59.78 | 1002.25
2016-05-10 16:00 | 53597 | 15507.8121 | 195752.8447 | 59.77 | 1071.94
2016-05-10 17:00 | 53529 | 15297.4089 | 196140.6047 | 59.77 | 1070.58
2016-05-10 18:00 | 52371 | 14648.5294 | 205508.3151 | 59.77 | 1047.42
2016-05-10 19:00 | 51213 | 13886.9152 | 205508.3151 | 59.78 | 973.047
2016-05-10 20:00 | 51483 | 10393.2529 | 212975.3984 | 59.77 | 1029.66
2016-05-10 21:00 | 50610 | 9773.1984 | 217929.2451 | 59.77 | 1012.2
2016-05-10 22:00 | 46910 | 8503.5626 | 210420.9351 | 59.77 | 938.2
2016-05-10 23:00 | 42514 | 7984.7959 | 191289.4891 | 59.78 | 807.766
2016-05-11 | 38611 | 8298.7639 | 161133.0547 | 59.77 | 772.22
2016-05-11 01:00 | 36619 | 8347.6115 | 158678.6547 | 59.77 | 732.38
2016-05-11 02:00 | 35490 | 9239.1254 | 158678.6547 | 59.79 | 638.82
2016-05-11 03:00 | 34925 | 10886.6367 | 158678.6547 | 59.79 | 628.65
2016-05-11 04:00 | 35138 | 11193.8791 | 159229.3422 | 59.79 | 632.484
2016-05-11 05:00 | 36892 | 11837.1337 | 159229.3422 | 59.79 | 664.056
2016-05-11 06:00 | 40380 | 11910.8143 | 159229.3422 | 59.77 | 807.6
2016-05-11 07:00 | 41886 | 11122.9843 | 159229.3422 | 59.77 | 837.72
2016-05-11 08:00 | 42966 | 9711.5788 | 169429.2786 | 59.78 | 816.354
2016-05-11 09:00 | 44883 | 8645.57 | 187515.9666 | 59.78 | 852.777
2016-05-11 10:00 | 47100 | 7558.5003 | 209767.8726 | 59.77 | 942
2016-05-11 11:00 | 49014 | 7694.4525 | 220033.7106 | 59.77 | 980.28
2016-05-11 12:00 | 50832 | 8106.1344 | 229242.2106 | 59.78 | 965.808
2016-05-11 13:00 | 53091 | 9719.0506 | 229978.2106 | 59.78 | 1008.729
2016-05-11 14:00 | 55063 | 12980.1289 | 229242.2106 | 59.77 | 1101.26
2016-05-11 15:00 | 56411 | 13900.479 | 229242.2106 | 59.78 | 1071.809
2016-05-11 16:00 | 57236 | 14028.6205 | 228651.2026 | 59.78 | 1087.484
2016-05-11 17:00 | 56893 | 13964.7718 | 228651.2026 | 59.78 | 1080.967
2016-05-11 18:00 | 55273 | 14972.2868 | 214936.6326 | 59.77 | 1105.46
2016-05-11 19:00 | 53652 | 15179.3271 | 209916.1446 | 59.77 | 1073.04
2016-05-11 20:00 | 53615 | 14520.479 | 209916.1446 | 59.77 | 1072.3
2016-05-11 21:00 | 52441 | 14545.5961 | 200710.3342 | 59.77 | 1048.82
2016-05-11 22:00 | 48631 | 14730.0659 | 171852.6782 | 59.78 | 923.989
2016-05-11 23:00 | 43860 | 14712.6677 | 147067.8102 | 59.77 | 877.2
2016-05-12 | 38620 | 15152.8815 | 132134.7118 | 59.79 | 695.16
2016-05-12 01:00 | 36739 | 15113.7034 | 134589.1118 | 59.79 | 661.302
2016-05-12 02:00 | 35515 | 14965.4515 | 132156.1118 | 59.79 | 639.27
2016-05-12 03:00 | 34816 | 14067.7412 | 132156.1118 | 59.79 | 626.688
2016-05-12 04:00 | 34914 | 13747.9487 | 132156.1118 | 59.79 | 628.452
2016-05-12 05:00 | 36587 | 12808.3964 | 132156.1118 | 59.79 | 658.566
2016-05-12 06:00 | 39946 | 11188.1188 | 144958.5318 | 59.77 | 798.92
2016-05-12 07:00 | 41038 | 11042.6519 | 147391.5318 | 59.77 | 820.76
2016-05-12 08:00 | 41874 | 10887.5133 | 157545.7162 | 59.77 | 837.48
2016-05-12 09:00 | 43924 | 11251.0934 | 169614.5062 | 59.78 | 834.556
2016-05-12 10:00 | 46019 | 11493.04 | 177310.0962 | 59.78 | 874.361
2016-05-12 11:00 | 47713 | 11600.6952 | 185995.9922 | 59.78 | 906.547
2016-05-12 12:00 | 48981 | 12574.7784 | 189349.7026 | 59.78 | 930.639
2016-05-12 13:00 | 50516 | 13915.9099 | 189349.7026 | 59.78 | 959.804
2016-05-12 14:00 | 51566 | 15032.7743 | 189349.7026 | 59.78 | 979.754
2016-05-12 15:00 | 52379 | 15511.2874 | 205021.4626 | 59.78 | 995.201
2016-05-12 16:00 | 53025 | 14952.4748 | 205612.4706 | 59.77 | 1060.5
2016-05-12 17:00 | 52466 | 13988.9612 | 205612.4706 | 59.77 | 1049.32
2016-05-12 18:00 | 51245 | 11707.0284 | 208094.0706 | 59.77 | 1024.9
2016-05-12 19:00 | 50024 | 10669.0866 | 208094.0706 | 59.77 | 1000.48
2016-05-12 20:00 | 50231 | 8920.7301 | 208830.0706 | 59.77 | 1004.62
2016-05-12 21:00 | 49121 | 9545.5077 | 210344.0706 | 59.77 | 982.42
2016-05-12 22:00 | 45568 | 10903.3554 | 185242.8846 | 59.78 | 865.792
2016-05-12 23:00 | 41722 | 11738.8196 | 169571.1246 | 59.77 | 834.44
2016-05-13 | 37989 | 10748.9523 | 166217.4142 | 59.79 | 683.802
2016-05-13 01:00 | 36029 | 7851.0075 | 166217.4142 | 59.77 | 720.58
2016-05-13 02:00 | 34793 | 8642.9082 | 166217.4142 | 59.79 | 626.274
2016-05-13 03:00 | 34141 | 9115.4392 | 166217.4142 | 59.79 | 614.538
2016-05-13 04:00 | 34180 | 8863.1086 | 166217.4142 | 59.79 | 615.24
2016-05-13 05:00 | 35746 | 7645.0539 | 166217.4142 | 59.77 | 714.92
2016-05-13 06:00 | 39077 | 5918.5611 | 171764.9465 | 59.78 | 742.463
2016-05-13 07:00 | 40341 | 5329.9345 | 179460.5365 | 59.78 | 766.479
2016-05-13 08:00 | 41051 | 5108.6679 | 182659.7625 | 59.78 | 779.969
2016-05-13 09:00 | 42460 | 4105.5912 | 202331.2525 | 59.77 | 849.2
2016-05-13 10:00 | 44352 | 4963.423 | 210267.4575 | 59.77 | 887.04
2016-05-13 11:00 | 45728 | 5326.6158 | 216036.2955 | 59.77 | 914.56
2016-05-13 12:00 | 46811 | 4704.9242 | 226101.6555 | 59.77 | 936.22
2016-05-13 13:00 | 48206 | 4874.7958 | 235061.7659 | 59.78 | 915.914
2016-05-13 14:00 | 49043 | 4420.0842 | 240492.0159 | 59.78 | 931.817
2016-05-13 15:00 | 49526 | 4399.5542 | 240948.0159 | 59.78 | 940.994
2016-05-13 16:00 | 49730 | 5029.3122 | 240212.0159 | 59.78 | 944.87
2016-05-13 17:00 | 48963 | 5710.8851 | 230527.1959 | 59.78 | 930.297
2016-05-13 18:00 | 47758 | 7266.3178 | 215840.9909 | 59.77 | 955.16
2016-05-13 19:00 | 46552 | 8311.6887 | 208570.5029 | 59.77 | 931.04
2016-05-13 20:00 | 46884 | 9545.958 | 208570.5029 | 59.78 | 890.796
2016-05-13 21:00 | 45909 | 6027.3661 | 208570.5029 | 59.77 | 918.18
2016-05-13 22:00 | 42773 | 6350.9965 | 188944.3425 | 59.78 | 812.687
2016-05-13 23:00 | 39010 | 6991.3469 | 188944.3425 | 59.77 | 780.2
2016-05-14 | 38644 | 6189.3321 | 188944.3425 | 59.77 | 772.88
2016-05-14 01:00 | 36821 | 4783.6499 | 188944.3425 | 59.77 | 736.42
2016-05-14 02:00 | 35755 | 4462.3567 | 188944.3425 | 59.77 | 715.1
2016-05-14 03:00 | 35143 | 4006.6945 | 188944.3425 | 59.77 | 702.86
2016-05-14 04:00 | 35382 | 4280.6413 | 188944.3425 | 59.77 | 707.64
2016-05-14 05:00 | 37173 | 4333.6796 | 188944.3425 | 59.78 | 706.287
2016-05-14 06:00 | 40595 | 4034.6551 | 193265.4022 | 59.78 | 771.305
2016-05-14 07:00 | 42201 | 4598.1768 | 195844.7826 | 59.77 | 844.02
2016-05-14 08:00 | 43194 | 5378.7784 | 198094.7826 | 59.77 | 863.88
2016-05-14 09:00 | 44658 | 5867.9932 | 205951.1826 | 59.77 | 893.16
2016-05-14 10:00 | 46359 | 6011.5631 | 208937.1826 | 59.77 | 927.18
2016-05-14 11:00 | 47475 | 8314.0981 | 209702.8326 | 59.77 | 949.5
2016-05-14 12:00 | 48064 | 9153.9481 | 209702.8326 | 59.77 | 961.28
2016-05-14 13:00 | 48169 | 9486.0096 | 209148.6426 | 59.77 | 963.38
2016-05-14 14:00 | 47862 | 8473.9186 | 209148.6426 | 59.77 | 957.24
2016-05-14 15:00 | 47063 | 8373.1834 | 205794.9322 | 59.77 | 941.26
2016-05-14 16:00 | 46059 | 8561.6655 | 196835.9722 | 59.78 | 875.121
2016-05-14 17:00 | 44899 | 9187.7591 | 183366.4222 | 59.78 | 853.081
2016-05-14 18:00 | 43579 | 9725.2781 | 173570.6962 | 59.78 | 828.001
2016-05-14 19:00 | 42259 | 10935.3362 | 166614.2862 | 59.77 | 845.18
2016-05-14 20:00 | 41904 | 11725.4324 | 166614.2862 | 59.77 | 838.08
2016-05-14 21:00 | 41037 | 8731.0325 | 166614.2862 | 59.77 | 820.74
2016-05-14 22:00 | 38807 | 7819.2491 | 168773.6862 | 59.77 | 776.14
2016-05-14 23:00 | 36295 | 7142.6203 | 168773.6862 | 59.77 | 725.9
2016-05-15 | 36031 | 5585.3715 | 167910.3862 | 59.77 | 720.62
2016-05-15 01:00 | 35740 | 5229.3577 | 167910.3862 | 59.77 | 714.8
2016-05-15 02:00 | 34669 | 5460.8372 | 167910.3862 | 59.77 | 693.38
2016-05-15 03:00 | 33990 | 3733.9715 | 167910.3862 | 59.77 | 679.8
2016-05-15 04:00 | 33755 | 2653.7766 | 167910.3862 | 59.77 | 675.1
2016-05-15 05:00 | 34169 | 3157.8061 | 167910.3862 | 59.77 | 683.38
2016-05-15 06:00 | 35198 | 2096.3154 | 167910.3862 | 59.78 | 668.762
2016-05-15 07:00 | 36230 | 1910.3054 | 172292.0362 | 59.78 | 688.37
2016-05-15 08:00 | 38237 | 2332.8697 | 183186.8522 | 59.78 | 726.503
2016-05-15 09:00 | 40295 | 1660.7965 | 198738.8822 | 59.77 | 805.9
2016-05-15 10:00 | 42242 | 2227.1194 | 208845.2822 | 59.77 | 844.84
2016-05-15 11:00 | 43266 | 2649.3627 | 212390.8802 | 59.77 | 865.32
2016-05-15 12:00 | 43732 | 2821.094 | 212390.8802 | 59.77 | 874.64
2016-05-15 13:00 | 44126 | 1814.3999 | 218947.1806 | 59.77 | 882.52
2016-05-15 14:00 | 44935 | 2107.1566 | 221126.714 | 59.78 | 853.765
2016-05-15 15:00 | 45985 | 2717.398 | 221126.714 | 59.78 | 873.715
2016-05-15 16:00 | 46023 | 3863.0456 | 220390.714 | 59.77 | 920.46
2016-05-15 17:00 | 46625 | 4089.9427 | 220517.194 | 59.78 | 885.875
2016-05-15 18:00 | 46285 | 4733.9844 | 220517.194 | 59.77 | 925.7
2016-05-15 19:00 | 45946 | 3972.8387 | 220517.194 | 59.77 | 918.92
2016-05-15 20:00 | 46470 | 3789.679 | 218197.9508 | 59.78 | 882.93
2016-05-15 21:00 | 45949 | 2817.8879 | 218933.9508 | 59.78 | 873.031
2016-05-15 22:00 | 43765 | 2737.1041 | 205293.5529 | 59.77 | 875.3
2016-05-15 23:00 | 40789 | 2737.8637 | 191871.7929 | 59.77 | 815.78
2016-05-16 | 37727 | 1978.4837 | 185351.3965 | 59.78 | 716.813
2016-05-16 01:00 | 35800 | 1694.3398 | 185351.3965 | 59.78 | 680.2
2016-05-16 02:00 | 34363 | 1910.6322 | 185351.3965 | 59.77 | 687.26
2016-05-16 03:00 | 33467 | 1749.0178 | 185351.3965 | 59.77 | 669.34
2016-05-16 04:00 | 33008 | 1641.1951 | 184733.3965 | 59.77 | 660.16
2016-05-16 05:00 | 33101 | 1585.1485 | 184733.3965 | 59.77 | 662.02
2016-05-16 06:00 | 33375 | 1337.189 | 184733.3965 | 59.77 | 667.5
2016-05-16 07:00 | 34096 | 1147.5547 | 184733.3965 | 59.78 | 647.824
2016-05-16 08:00 | 36686 | 1003.4208 | 184733.3965 | 59.78 | 697.034
2016-05-16 09:00 | 39401 | 754.7447 | 193812.0865 | 59.77 | 788.02
2016-05-16 10:00 | 42159 | 1232.0123 | 209405.1565 | 59.77 | 843.18
2016-05-16 11:00 | 44907 | 1993.6217 | 223761.2169 | 59.78 | 853.233
2016-05-16 12:00 | 47680 | 1430.43 | 244982.5453 | 59.78 | 905.92
2016-05-16 13:00 | 50243 | 1283.3058 | 264157.6268 | 59.76 | 1055.103
2016-05-16 14:00 | 51972 | 1826.2206 | 274149.3616 | 59.76 | 1091.412
2016-05-16 15:00 | 53529 | 1946.371 | 279515.7216 | 59.76 | 1124.109
2016-05-16 16:00 | 54772 | 1827.6864 | 280495.7056 | 59.75 | 1204.984
2016-05-16 17:00 | 55379 | 1855.6069 | 280495.7056 | 59.75 | 1218.338
2016-05-16 18:00 | 54460 | 2272.4609 | 279515.7216 | 59.76 | 1143.66
2016-05-16 19:00 | 53541 | 2058.7935 | 279515.7216 | 59.76 | 1124.361
2016-05-16 20:00 | 53093 | 2338.2268 | 274295.0894 | 59.76 | 1114.953
2016-05-16 21:00 | 52033 | 2346.3943 | 261527.1734 | 59.76 | 1092.693
2016-05-16 22:00 | 48355 | 1675.1261 | 242878.2731 | 59.78 | 918.745
2016-05-16 23:00 | 43715 | 1950.355 | 218688.6101 | 59.77 | 874.3
2016-05-17 | 37047 | 2494.5841 | 204413.6537 | 59.78 | 703.893
2016-05-17 01:00 | 35093 | 2376.7615 | 204413.6537 | 59.78 | 666.767
2016-05-17 02:00 | 33854 | 2412.3858 | 204413.6537 | 59.77 | 677.08
2016-05-17 03:00 | 33222 | 2291.488 | 204413.6537 | 59.77 | 664.44
2016-05-17 04:00 | 33370 | 1845.2544 | 201342.8257 | 59.77 | 667.4
2016-05-17 05:00 | 35244 | 1779.2192 | 201342.8257 | 59.78 | 669.636
2016-05-17 06:00 | 38502 | 1814.4084 | 201342.8257 | 59.78 | 731.538
2016-05-17 07:00 | 40228 | 1379.7243 | 206493.0757 | 59.77 | 804.56
2016-05-17 08:00 | 42184 | 1165.8702 | 221961.1171 | 59.77 | 843.68
2016-05-17 09:00 | 44649 | 1661.7512 | 233186.2631 | 59.78 | 848.331
2016-05-17 10:00 | 47785 | 1731.5522 | 253552.0406 | 59.78 | 907.915
2016-05-17 11:00 | 50589 | 1951.3378 | 269856.8988 | 59.76 | 1062.369
2016-05-17 12:00 | 53052 | 2266.5419 | 276493.5668 | 59.76 | 1114.092
2016-05-17 13:00 | 55391 | 2556.5294 | 287797.9352 | 59.75 | 1218.602
2016-05-17 14:00 | 57145 | 2607.3023 | 289436.7246 | 59.75 | 1257.19
2016-05-17 15:00 | 57691 | 2585.0836 | 288453.0146 | 59.75 | 1269.202
2016-05-17 16:00 | 56965 | 3083.5237 | 287717.0146 | 59.75 | 1253.23
2016-05-17 17:00 | 55204 | 3439.4641 | 283607.7672 | 59.76 | 1159.284
2016-05-17 18:00 | 52621 | 4446.9793 | 277948.2577 | 59.76 | 1105.041
2016-05-17 19:00 | 50037 | 4215.4007 | 251065.7395 | 59.78 | 950.703
2016-05-17 20:00 | 49333 | 4564.7785 | 243290.2635 | 59.78 | 937.327
2016-05-17 21:00 | 47589 | 5499.8753 | 220319.4821 | 59.77 | 951.78
2016-05-17 22:00 | 43590 | 5070.055 | 195297.5767 | 59.77 | 871.8
2016-05-17 23:00 | 39229 | 5452.8177 | 177375.8167 | 59.78 | 745.351
2016-05-18 | 36867 | 5245.2519 | 172243.8967 | 59.77 | 737.34
2016-05-18 01:00 | 34933 | 4177.549 | 172243.8967 | 59.77 | 698.66
2016-05-18 02:00 | 33741 | 4745.3345 | 172243.8967 | 59.77 | 674.82
2016-05-18 03:00 | 33103 | 5106.765 | 172243.8967 | 59.77 | 662.06
2016-05-18 04:00 | 33227 | 4445.7948 | 175932.7247 | 59.77 | 664.54
2016-05-18 05:00 | 34980 | 4117.5946 | 175932.7247 | 59.77 | 699.6
2016-05-18 06:00 | 38451 | 3452.4657 | 179555.0447 | 59.78 | 730.569
2016-05-18 07:00 | 39709 | 3035.8186 | 181805.0447 | 59.78 | 754.471
2016-05-18 08:00 | 40832 | 3106.9822 | 188633.7347 | 59.77 | 816.64
2016-05-18 09:00 | 42482 | 3698.4948 | 195030.2531 | 59.77 | 849.64
2016-05-18 10:00 | 44341 | 3765.4129 | 207705.5561 | 59.77 | 886.82
2016-05-18 11:00 | 46266 | 4883.2182 | 219703.4405 | 59.77 | 925.32
2016-05-18 12:00 | 48318 | 4614.8465 | 234383.5153 | 59.78 | 918.042
2016-05-18 13:00 | 50496 | 5152.6971 | 239989.9153 | 59.78 | 959.424
2016-05-18 14:00 | 52337 | 5747.0016 | 252592.0153 | 59.78 | 994.403
2016-05-18 15:00 | 53774 | 5906.3141 | 252979.7753 | 59.76 | 1129.254
2016-05-18 16:00 | 55080 | 6282.3627 | 252979.7753 | 59.76 | 1156.68
2016-05-18 17:00 | 55440 | 9550.5292 | 243226.8569 | 59.78 | 1053.36
2016-05-18 18:00 | 54085 | 10935.3369 | 227079.2639 | 59.78 | 1027.615
2016-05-18 19:00 | 52731 | 12638.4111 | 210136.2099 | 59.77 | 1054.62
2016-05-18 20:00 | 52082 | 13595.2048 | 195456.1351 | 59.77 | 1041.64
2016-05-18 21:00 | 51021 | 13139.1705 | 191695.8151 | 59.77 | 1020.42
2016-05-18 22:00 | 46811 | 13028.2594 | 164775.7601 | 59.78 | 889.409
2016-05-18 23:00 | 42361 | 13061.6907 | 144442.9557 | 59.77 | 847.22
2016-05-19 | 37067 | 13060.8317 | 136859.8157 | 59.79 | 667.206
2016-05-19 01:00 | 35208 | 12317.3982 | 134680.2823 | 59.79 | 633.744
2016-05-19 02:00 | 34010 | 12600.8618 | 134680.2823 | 59.79 | 612.18
2016-05-19 03:00 | 33235 | 12207.7785 | 134680.2823 | 59.79 | 598.23
2016-05-19 04:00 | 33390 | 11574.2095 | 134680.2823 | 59.79 | 601.02
2016-05-19 05:00 | 35011 | 11259.2166 | 134680.2823 | 59.79 | 630.198
2016-05-19 06:00 | 38222 | 10281.1113 | 138679.1523 | 59.77 | 764.44
2016-05-19 07:00 | 39835 | 9899.039 | 147329.6623 | 59.77 | 796.7
2016-05-19 08:00 | 41201 | 9033.854 | 157483.8467 | 59.77 | 824.02
2016-05-19 09:00 | 43192 | 8336.5202 | 176374.0167 | 59.78 | 820.648
2016-05-19 10:00 | 45538 | 8104.2763 | 192643.0827 | 59.78 | 865.222
2016-05-19 11:00 | 47623 | 8784.8436 | 195999.4827 | 59.77 | 952.46
2016-05-19 12:00 | 49563 | 9208.3865 | 206841.8827 | 59.77 | 991.26
2016-05-19 13:00 | 51447 | 8735.8552 | 221197.9431 | 59.78 | 977.493
2016-05-19 14:00 | 53080 | 10194.8044 | 221547.3195 | 59.78 | 1008.52
2016-05-19 15:00 | 54451 | 12096.1415 | 220461.9431 | 59.77 | 1089.02
2016-05-19 16:00 | 55388 | 12299.5712 | 221435.2064 | 59.78 | 1052.372
2016-05-19 17:00 | 55492 | 12121.67 | 226958.7111 | 59.78 | 1054.348
2016-05-19 18:00 | 54090 | 11782.7366 | 245586.9721 | 59.77 | 1081.8
2016-05-19 19:00 | 52687 | 6687.3122 | 247111.5721 | 59.78 | 1001.053
2016-05-19 20:00 | 51744 | 3751.551 | 247847.5721 | 59.76 | 1086.624
2016-05-19 21:00 | 50592 | 4179.3565 | 247111.5721 | 59.78 | 961.248
2016-05-19 22:00 | 46699 | 4951.3066 | 222649.1117 | 59.77 | 933.98
2016-05-19 23:00 | 42446 | 4553.518 | 202750.5817 | 59.77 | 848.92
2016-05-20 | 39303 | 5288.4085 | 195944.0357 | 59.78 | 746.757
2016-05-20 01:00 | 37325 | 7147.4457 | 189012.3877 | 59.77 | 746.5
2016-05-20 02:00 | 36016 | 7573.5693 | 175404.6147 | 59.77 | 720.32
2016-05-20 03:00 | 35329 | 7138.6652 | 175404.6147 | 59.77 | 706.58
2016-05-20 04:00 | 35355 | 7842.5054 | 175404.6147 | 59.77 | 707.1
2016-05-20 05:00 | 37040 | 8062.5469 | 175404.6147 | 59.77 | 740.8
2016-05-20 06:00 | 40318 | 7569.9892 | 177584.1481 | 59.78 | 766.042
2016-05-20 07:00 | 41814 | 5390.1003 | 179094.4681 | 59.78 | 794.466
2016-05-20 08:00 | 43048 | 4183.5345 | 193484.1841 | 59.77 | 860.96
2016-05-20 09:00 | 44848 | 3897.3278 | 205799.5441 | 59.77 | 896.96
2016-05-20 10:00 | 46829 | 3171.1955 | 224658.2941 | 59.78 | 889.751
2016-05-20 11:00 | 48356 | 3115.1359 | 235573.5541 | 59.78 | 918.764
2016-05-20 12:00 | 49746 | 2944.0162 | 243470.9891 | 59.78 | 945.174
2016-05-20 13:00 | 51093 | 2977.9179 | 250864.3839 | 59.76 | 1072.953
2016-05-20 14:00 | 52185 | 3451.4604 | 258800.5889 | 59.76 | 1095.885
2016-05-20 15:00 | 53516 | 3173.9629 | 270110.1176 | 59.76 | 1123.836
2016-05-20 16:00 | 54768 | 3124.7753 | 268919.5795 | 59.76 | 1150.128
2016-05-20 17:00 | 54898 | 3472.3874 | 268725.7663 | 59.76 | 1152.858
2016-05-20 18:00 | 53362 | 3581.8961 | 264187.003 | 59.76 | 1120.602
2016-05-20 19:00 | 51826 | 3208.6141 | 255521.743 | 59.76 | 1088.346
2016-05-20 20:00 | 50836 | 3396.9085 | 251457.028 | 59.78 | 965.884
2016-05-20 21:00 | 49514 | 4240.7489 | 237460.4252 | 59.78 | 940.766
2016-05-20 22:00 | 45949 | 5412.0666 | 206411.1702 | 59.77 | 918.98
2016-05-20 23:00 | 41770 | 6753.8356 | 190727.5623 | 59.78 | 793.63
2016-05-21 | 40233 | 7645.2501 | 184856.4623 | 59.78 | 764.427
2016-05-21 01:00 | 38101 | 7157.8845 | 185291.3423 | 59.77 | 762.02
2016-05-21 02:00 | 36686 | 6311.0979 | 185291.3423 | 59.77 | 733.72
2016-05-21 03:00 | 35869 | 5923.3721 | 185291.3423 | 59.77 | 717.38
2016-05-21 04:00 | 35907 | 5358.2246 | 185291.3423 | 59.77 | 718.14
2016-05-21 05:00 | 37678 | 5787.8759 | 185291.3423 | 59.77 | 753.56
2016-05-21 06:00 | 41320 | 4971.2583 | 188763.6323 | 59.78 | 785.08
2016-05-21 07:00 | 43018 | 4380.298 | 202226.4323 | 59.77 | 860.36
2016-05-21 08:00 | 44283 | 3891.6297 | 212980.3927 | 59.77 | 885.66
2016-05-21 09:00 | 46318 | 4955.9996 | 219063.1127 | 59.77 | 926.36
2016-05-21 10:00 | 48807 | 6182.3956 | 228206.0517 | 59.78 | 927.333
2016-05-21 11:00 | 51001 | 7924.6044 | 234202.4517 | 59.78 | 969.019
2016-05-21 12:00 | 53140 | 8000.7697 | 254949.0649 | 59.78 | 1009.66
2016-05-21 13:00 | 55550 | 7177.3719 | 267724.3094 | 59.76 | 1166.55
2016-05-21 14:00 | 57854 | 7582.9197 | 270635.4658 | 59.76 | 1214.934
2016-05-21 15:00 | 59574 | 8506.303 | 272773.159 | 59.76 | 1251.054
2016-05-21 16:00 | 60694 | 8289.0914 | 275211.0536 | 59.76 | 1274.574
2016-05-21 17:00 | 60445 | 8207.8355 | 274741.1786 | 59.76 | 1269.345
2016-05-21 18:00 | 58237 | 8460.5741 | 270319.7074 | 59.76 | 1222.977
2016-05-21 19:00 | 56030 | 10397.5102 | 243315.2844 | 59.78 | 1064.57
2016-05-21 20:00 | 54446 | 12613.82 | 222568.6712 | 59.77 | 1088.92
2016-05-21 21:00 | 52994 | 12144.2355 | 210931.4967 | 59.77 | 1059.88
2016-05-21 22:00 | 49813 | 12056.561 | 192554.2139 | 59.77 | 996.26
2016-05-21 23:00 | 45983 | 11736.0265 | 173802.9579 | 59.78 | 873.677
2016-05-22 | 44450 | 11710.8219 | 165083.2579 | 59.78 | 844.55
2016-05-22 01:00 | 42065 | 11284.8808 | 165083.2579 | 59.77 | 841.3
2016-05-22 02:00 | 40397 | 11438.8654 | 165083.2579 | 59.77 | 807.94
2016-05-22 03:00 | 39380 | 12237.5998 | 165083.2579 | 59.79 | 708.84
2016-05-22 04:00 | 38863 | 11709.7578 | 165083.2579 | 59.79 | 699.534
2016-05-22 05:00 | 38958 | 11285.1826 | 165083.2579 | 59.77 | 779.16
2016-05-22 06:00 | 39987 | 10819.364 | 163170.8579 | 59.77 | 799.74
2016-05-22 07:00 | 41015 | 11902.9412 | 163170.8579 | 59.77 | 820.3
2016-05-22 08:00 | 43699 | 13017.4786 | 166329.2579 | 59.77 | 873.98
2016-05-22 09:00 | 46804 | 13710.3107 | 167496.9779 | 59.78 | 889.276
2016-05-22 10:00 | 49520 | 14256.2662 | 174996.8579 | 59.78 | 940.88
2016-05-22 11:00 | 51801 | 14845.0578 | 185539.6883 | 59.78 | 984.219
2016-05-22 12:00 | 54083 | 14925.9907 | 202735.6643 | 59.77 | 1081.66
2016-05-22 13:00 | 55938 | 14069.9875 | 220783.3943 | 59.77 | 1118.76
2016-05-22 14:00 | 57622 | 13798.8894 | 233660.2823 | 59.78 | 1094.818
2016-05-22 15:00 | 58905 | 14037.8689 | 233660.2823 | 59.78 | 1119.195
2016-05-22 16:00 | 59390 | 13864.5871 | 234429.1857 | 59.78 | 1128.41
2016-05-22 17:00 | 58934 | 13873.9698 | 234866.1573 | 59.78 | 1119.746
2016-05-22 18:00 | 57282 | 13130.5042 | 234414.5653 | 59.78 | 1088.358
2016-05-22 19:00 | 55629 | 13550.6653 | 223871.7349 | 59.77 | 1112.58
2016-05-22 20:00 | 55023 | 13807.535 | 214221.4849 | 59.77 | 1100.46
2016-05-22 21:00 | 54132 | 13400.3492 | 209143.7149 | 59.77 | 1082.64
2016-05-22 22:00 | 51336 | 13571.4082 | 189557.8669 | 59.77 | 1026.72
2016-05-22 23:00 | 48003 | 13956.9232 | 172410.5009 | 59.78 | 912.057
2016-05-23 | 45446 | 13363.1581 | 167390.0129 | 59.77 | 908.92
2016-05-23 01:00 | 43144 | 13136.4254 | 166193.1209 | 59.77 | 862.88
2016-05-23 02:00 | 41593 | 12883.1017 | 163183.1209 | 59.77 | 831.86
2016-05-23 03:00 | 40550 | 11722.4265 | 163183.1209 | 59.77 | 811
2016-05-23 04:00 | 39829 | 11361.6677 | 163183.1209 | 59.77 | 796.58
2016-05-23 05:00 | 39771 | 11003.9788 | 161606.3509 | 59.77 | 795.42
2016-05-23 06:00 | 39772 | 9630.9921 | 161606.3509 | 59.77 | 795.44
2016-05-23 07:00 | 40515 | 12089.9194 | 161606.3509 | 59.77 | 810.3
2016-05-23 08:00 | 43474 | 13214.2612 | 161606.3509 | 59.77 | 869.48
2016-05-23 09:00 | 47036 | 13435.9324 | 177093.3469 | 59.78 | 893.684
2016-05-23 10:00 | 50127 | 14489.5785 | 186228.9069 | 59.78 | 952.413
2016-05-23 11:00 | 52937 | 15786.1244 | 196280.5383 | 59.78 | 1005.803
2016-05-23 12:00 | 55528 | 15797.2178 | 208574.7328 | 59.77 | 1110.56
2016-05-23 13:00 | 57727 | 15384.2244 | 227767.2132 | 59.77 | 1154.54
2016-05-23 14:00 | 59656 | 15548.9538 | 243320.2392 | 59.78 | 1133.464
2016-05-23 15:00 | 60971 | 15446.6784 | 251794.6872 | 59.78 | 1158.449
2016-05-23 16:00 | 61527 | 13712.7379 | 260371.3912 | 59.76 | 1292.067
2016-05-23 17:00 | 61408 | 12330.9507 | 258830.9876 | 59.76 | 1289.568
2016-05-23 18:00 | 59758 | 12799.742 | 257694.4072 | 59.78 | 1135.402
2016-05-23 19:00 | 58108 | 14162.4785 | 251771.1638 | 59.78 | 1104.052
2016-05-23 20:00 | 57319 | 14093.2514 | 245404.9188 | 59.78 | 1089.061
2016-05-23 21:00 | 56537 | 13807.5946 | 241595.1188 | 59.78 | 1074.203
2016-05-23 22:00 | 53254 | 13732.496 | 230501.5068 | 59.77 | 1065.08
2016-05-23 23:00 | 48902 | 12960.4721 | 199361.8344 | 59.78 | 929.138
2016-05-24 | 42281 | 13047.7972 | 165796.0589 | 59.77 | 845.62
2016-05-24 01:00 | 40048 | 13366.2054 | 165844.0589 | 59.79 | 720.864
2016-05-24 02:00 | 38482 | 13980.2718 | 167345.7089 | 59.79 | 692.676
2016-05-24 03:00 | 37728 | 13449.2673 | 167345.7089 | 59.79 | 679.104
2016-05-24 04:00 | 37917 | 12620.1992 | 168854.0589 | 59.79 | 682.506
2016-05-24 05:00 | 39624 | 11744.0488 | 170430.8289 | 59.77 | 792.48
2016-05-24 06:00 | 42929 | 10369.6477 | 175451.3169 | 59.78 | 815.651
2016-05-24 07:00 | 44547 | 12180.6375 | 175451.3169 | 59.77 | 890.94
2016-05-24 08:00 | 45862 | 13209.0356 | 175451.3169 | 59.78 | 871.378
2016-05-24 09:00 | 48096 | 12894.6333 | 185273.5769 | 59.78 | 913.824
2016-05-24 10:00 | 50358 | 13201.321 | 195018.6814 | 59.78 | 956.802
2016-05-24 11:00 | 52960 | 13642.2757 | 208278.2094 | 59.77 | 1059.2
2016-05-24 12:00 | 55193 | 13417.6822 | 227344.7198 | 59.77 | 1103.86
2016-05-24 13:00 | 57038 | 12276.848 | 242748.1878 | 59.78 | 1083.722
2016-05-24 14:00 | 58742 | 10964.8007 | 266920.4736 | 59.76 | 1233.582
2016-05-24 15:00 | 60165 | 10457.1845 | 269088.5392 | 59.76 | 1263.465
2016-05-24 16:00 | 60608 | 10967.1883 | 268967.026 | 59.76 | 1272.768
2016-05-24 17:00 | 60091 | 11303.7727 | 266363.434 | 59.76 | 1261.911
2016-05-24 18:00 | 58208 | 11841.4167 | 259485.6215 | 59.78 | 1105.952
2016-05-24 19:00 | 56325 | 11293.0362 | 248183.3215 | 59.78 | 1070.175
2016-05-24 20:00 | 55299 | 10075.595 | 248183.3215 | 59.78 | 1050.681
2016-05-24 21:00 | 53871 | 7440.4008 | 248183.3215 | 59.78 | 1023.549
2016-05-24 22:00 | 49785 | 8689.6486 | 213138.4477 | 59.77 | 995.7
2016-05-24 23:00 | 45108 | 7847.469 | 203445.9269 | 59.78 | 857.052
2016-05-25 | 40797 | 5727.6371 | 203445.9269 | 59.78 | 775.143
2016-05-25 01:00 | 38594 | 5724.1633 | 203445.9269 | 59.78 | 733.286
2016-05-25 02:00 | 37157 | 5931.0455 | 203445.9269 | 59.77 | 743.14
2016-05-25 03:00 | 36334 | 5161.5771 | 203445.9269 | 59.77 | 726.68
2016-05-25 04:00 | 36338 | 4035.9593 | 203445.9269 | 59.77 | 726.76
2016-05-25 05:00 | 38056 | 3746.583 | 203445.9269 | 59.78 | 723.064
2016-05-25 06:00 | 41152 | 3350.344 | 207295.4969 | 59.77 | 823.04
2016-05-25 07:00 | 42775 | 3499.002 | 207295.4969 | 59.77 | 855.5
2016-05-25 08:00 | 44180 | 3983.6434 | 213803.3373 | 59.77 | 883.6
2016-05-25 09:00 | 46186 | 3172.257 | 228638.4073 | 59.78 | 877.534
2016-05-25 10:00 | 48491 | 4156.3555 | 233744.0428 | 59.78 | 921.329
2016-05-25 11:00 | 50537 | 4800.014 | 244836.7288 | 59.78 | 960.203
2016-05-25 12:00 | 52109 | 5039.8883 | 253434.0836 | 59.78 | 990.071
2016-05-25 13:00 | 53882 | 4425.2044 | 269900.654 | 59.76 | 1131.522
2016-05-25 14:00 | 55719 | 5249.4689 | 272112.202 | 59.76 | 1170.099
2016-05-25 15:00 | 57066 | 6935.7102 | 271656.202 | 59.76 | 1198.386
2016-05-25 16:00 | 57863 | 6687.7119 | 272245.9952 | 59.76 | 1215.123
2016-05-25 17:00 | 57044 | 6276.468 | 273027.932 | 59.76 | 1197.924
2016-05-25 18:00 | 55378 | 7782.1803 | 260082.0465 | 59.76 | 1162.938
2016-05-25 19:00 | 53712 | 8477.0943 | 244769.2605 | 59.78 | 1020.528
2016-05-25 20:00 | 52847 | 9105.7027 | 234282.9557 | 59.78 | 1004.093
2016-05-25 21:00 | 51264 | 7788.6763 | 227938.4883 | 59.78 | 974.016
2016-05-25 22:00 | 47408 | 6143.554 | 211529.9573 | 59.77 | 948.16
2016-05-25 23:00 | 42601 | 5557.4155 | 194692.2711 | 59.78 | 809.419
2016-05-26 | 37260 | 4827.5346 | 194692.2711 | 59.77 | 745.2
2016-05-26 01:00 | 35170 | 3671.0806 | 194692.2711 | 59.77 | 703.4
2016-05-26 02:00 | 33908 | 3604.5031 | 192340.1111 | 59.77 | 678.16
2016-05-26 03:00 | 33193 | 3290.6164 | 192340.1111 | 59.77 | 663.86
2016-05-26 04:00 | 33293 | 2460.4263 | 192340.1111 | 59.77 | 665.86
2016-05-26 05:00 | 34772 | 1978.6357 | 192340.1111 | 59.78 | 660.668
2016-05-26 06:00 | 37741 | 1500.0295 | 192340.1111 | 59.78 | 717.079
2016-05-26 07:00 | 39322 | 1382.9295 | 197946.5111 | 59.77 | 786.44
2016-05-26 08:00 | 41169 | 1593.1485 | 208050.2215 | 59.77 | 823.38
2016-05-26 09:00 | 43668 | 2781.6682 | 216802.5715 | 59.77 | 873.36
2016-05-26 10:00 | 46871 | 3052.5067 | 238443.3025 | 59.78 | 890.549
2016-05-26 11:00 | 49710 | 4137.9556 | 247367.4295 | 59.78 | 944.49
2016-05-26 12:00 | 52010 | 4947.6976 | 261490.7783 | 59.78 | 988.19
2016-05-26 13:00 | 54395 | 4646.0203 | 274103.2683 | 59.76 | 1142.295
2016-05-26 14:00 | 56216 | 4400.7829 | 284628.2258 | 59.76 | 1180.536
2016-05-26 15:00 | 57626 | 4821.637 | 287122.2098 | 59.75 | 1267.772
2016-05-26 16:00 | 58270 | 4155.098 | 287858.2098 | 59.75 | 1281.94
2016-05-26 17:00 | 57946 | 4181.3886 | 288688.0798 | 59.75 | 1274.812
2016-05-26 18:00 | 55926 | 4292.0968 | 283690.3478 | 59.76 | 1174.446
2016-05-26 19:00 | 53906 | 4977.4619 | 266784.8478 | 59.76 | 1132.026
2016-05-26 20:00 | 52388 | 5929.6101 | 245770.049 | 59.78 | 995.372
2016-05-26 21:00 | 50797 | 5855.6483 | 233613.559 | 59.78 | 965.143
2016-05-26 22:00 | 46839 | 6629.8269 | 206062.8531 | 59.77 | 936.78
2016-05-26 23:00 | 42125 | 7384.806 | 183781.9989 | 59.78 | 800.375
2016-05-27 | 38406 | 6804.3129 | 190312.8309 | 59.77 | 768.12
2016-05-27 01:00 | 36142 | 6297.7148 | 190312.8309 | 59.77 | 722.84
2016-05-27 02:00 | 34549 | 5962.7528 | 192664.9909 | 59.77 | 690.98
2016-05-27 03:00 | 33619 | 5361.4861 | 192664.9909 | 59.77 | 672.38
2016-05-27 04:00 | 33458 | 4564.306 | 192664.9909 | 59.77 | 669.16
2016-05-27 05:00 | 34907 | 3942.3645 | 188758.262 | 59.77 | 698.14
2016-05-27 06:00 | 37794 | 2836.0814 | 188758.262 | 59.78 | 718.086
2016-05-27 07:00 | 39466 | 1856.6567 | 188758.262 | 59.77 | 789.32
2016-05-27 08:00 | 41394 | 1226.16 | 204310.292 | 59.77 | 827.88
2016-05-27 09:00 | 44085 | 1504.2121 | 219578.0194 | 59.78 | 837.615
2016-05-27 10:00 | 47350 | 1484.2235 | 238268.0298 | 59.78 | 899.65
2016-05-27 11:00 | 50413 | 1836.7539 | 256362.3708 | 59.76 | 1058.673
2016-05-27 12:00 | 53245 | 2118.8458 | 279122.0216 | 59.76 | 1118.145
2016-05-27 13:00 | 55753 | 1855.488 | 285794.3381 | 59.75 | 1226.566
2016-05-27 14:00 | 57605 | 2226.2268 | 295840.8941 | 59.75 | 1267.31
2016-05-27 15:00 | 58773 | 2182.982 | 297613.2543 | 59.75 | 1293.006
2016-05-27 16:00 | 59360 | 2056.3618 | 297711.9643 | 59.75 | 1305.92
2016-05-27 17:00 | 58566 | 2115.1611 | 297613.2543 | 59.75 | 1288.452
2016-05-27 18:00 | 56351 | 2273.5977 | 293173.7217 | 59.75 | 1239.722
2016-05-27 19:00 | 54135 | 2989.1955 | 275363.7887 | 59.76 | 1136.835
2016-05-27 20:00 | 52772 | 4406.7013 | 246615.993 | 59.76 | 1108.212
2016-05-27 21:00 | 51291 | 4972.5365 | 238166.3334 | 59.78 | 974.529
2016-05-27 22:00 | 47241 | 5784.3062 | 204951.129 | 59.77 | 944.82
2016-05-27 23:00 | 42651 | 5646.4034 | 192635.769 | 59.78 | 810.369
2016-05-28 | 39594 | 5351.5193 | 192822.969 | 59.78 | 752.286
2016-05-28 01:00 | 37221 | 5598.4086 | 190341.369 | 59.77 | 744.42
2016-05-28 02:00 | 35644 | 5414.7562 | 190341.369 | 59.77 | 712.88
2016-05-28 03:00 | 34647 | 4501.5917 | 190341.369 | 59.77 | 692.94
2016-05-28 04:00 | 34515 | 4006.9395 | 190341.369 | 59.77 | 690.3
2016-05-28 05:00 | 35786 | 3860.6393 | 194248.0979 | 59.77 | 715.72
2016-05-28 06:00 | 38314 | 3845.5733 | 194248.0979 | 59.78 | 727.966
2016-05-28 07:00 | 40268 | 1640.0569 | 199970.3879 | 59.77 | 805.36
2016-05-28 08:00 | 42716 | 650.5209 | 221169.8579 | 59.77 | 854.32
2016-05-28 09:00 | 45953 | 679.4133 | 237902.6773 | 59.78 | 873.107
2016-05-28 10:00 | 49730 | 693.0437 | 263027.7063 | 59.76 | 1044.33
2016-05-28 11:00 | 53051 | 656.0403 | 279724.7636 | 59.76 | 1114.071
2016-05-28 12:00 | 55727 | 1012.9805 | 303301.6414 | 59.75 | 1225.994
2016-05-28 13:00 | 58139 | 1383.8971 | 310466.3885 | 59.75 | 1279.058
2016-05-28 14:00 | 60000 | 1586.0149 | 314059.5172 | 59.75 | 1320
2016-05-28 15:00 | 61076 | 1886.4529 | 314059.5172 | 59.75 | 1343.672
2016-05-28 16:00 | 61410 | 1814.6277 | 314059.5172 | 59.75 | 1351.02
2016-05-28 17:00 | 60763 | 1757.2539 | 314059.5172 | 59.75 | 1336.786
2016-05-28 18:00 | 58296 | 1627.0622 | 310283.4005 | 59.75 | 1282.512
2016-05-28 19:00 | 55829 | 2086.5599 | 300073.1945 | 59.75 | 1228.238
2016-05-28 20:00 | 53584 | 3204.417 | 273315.0097 | 59.76 | 1125.264
2016-05-28 21:00 | 51620 | 4619.7388 | 251823.7303 | 59.78 | 980.78
2016-05-28 22:00 | 48241 | 6028.7579 | 219790.0289 | 59.77 | 964.82
2016-05-28 23:00 | 44350 | 5842.9482 | 201827.2289 | 59.77 | 887
2016-05-29 | 43256 | 5780.3069 | 199577.2289 | 59.78 | 821.864
2016-05-29 01:00 | 42114 | 6071.7469 | 202058.8289 | 59.78 | 800.166
2016-05-29 02:00 | 39919 | 6082.9471 | 202058.8289 | 59.78 | 758.461
2016-05-29 03:00 | 38418 | 6157.4154 | 202058.8289 | 59.77 | 768.36
2016-05-29 04:00 | 37602 | 6320.342 | 201504.6389 | 59.77 | 752.04
2016-05-29 05:00 | 37553 | 5703.84 | 201504.6389 | 59.77 | 751.06
2016-05-29 06:00 | 37611 | 5371.9205 | 201504.6389 | 59.77 | 752.22
2016-05-29 07:00 | 38898 | 3137.3412 | 201504.6389 | 59.78 | 739.062
2016-05-29 08:00 | 42740 | 1598.1667 | 214967.4389 | 59.77 | 854.8
2016-05-29 09:00 | 47342 | 1853.5776 | 240936.1753 | 59.78 | 899.498
2016-05-29 10:00 | 51869 | 2487.0636 | 264512.1106 | 59.76 | 1089.249
2016-05-29 11:00 | 55875 | 3326.2702 | 283970.362 | 59.75 | 1229.25
2016-05-29 12:00 | 59055 | 3481.4084 | 308875.1504 | 59.75 | 1299.21
2016-05-29 13:00 | 61156 | 2614.2661 | 313651.2197 | 59.75 | 1345.432
2016-05-29 14:00 | 62530 | 3139.6657 | 314573.4401 | 59.75 | 1375.66
2016-05-29 15:00 | 63533 | 3055.8504 | 316251.8453 | 59.75 | 1397.726
2016-05-29 16:00 | 63823 | 2423.5262 | 316084.0853 | 59.75 | 1404.106
2016-05-29 17:00 | 63164 | 3169.2108 | 313971.6073 | 59.75 | 1389.608
2016-05-29 18:00 | 61121 | 3895.4986 | 309847.6675 | 59.75 | 1344.662
2016-05-29 19:00 | 59078 | 5650.1924 | 297561.1871 | 59.75 | 1299.716
2016-05-29 20:00 | 57249 | 7995.2587 | 260621.9152 | 59.76 | 1202.229
2016-05-29 21:00 | 55533 | 9192.2337 | 249601.3868 | 59.78 | 1055.127
2016-05-29 22:00 | 51917 | 9834.9687 | 221667.0658 | 59.77 | 1038.34
2016-05-29 23:00 | 48259 | 10361.9502 | 197566.6054 | 59.77 | 965.18
2016-05-30 | 45691 | 9467.736 | 195654.2054 | 59.78 | 868.129
2016-05-30 01:00 | 43020 | 8081.9062 | 195654.2054 | 59.78 | 817.38
2016-05-30 02:00 | 41098 | 7456.8915 | 195654.2054 | 59.78 | 780.862
2016-05-30 03:00 | 39741 | 7760.6173 | 195654.2054 | 59.77 | 794.82
2016-05-30 04:00 | 38823 | 7503.5494 | 194912.7974 | 59.77 | 776.46
2016-05-30 05:00 | 38465 | 7517.0841 | 194912.7974 | 59.77 | 769.3
2016-05-30 06:00 | 38144 | 7518.4392 | 194912.7974 | 59.77 | 762.88
2016-05-30 07:00 | 38964 | 5230.4019 | 194912.7974 | 59.78 | 740.316
2016-05-30 08:00 | 42406 | 3534.8197 | 209516.5078 | 59.77 | 848.12
2016-05-30 09:00 | 46660 | 4059.9262 | 233854.3108 | 59.78 | 886.54
2016-05-30 10:00 | 50862 | 3896.3695 | 254124.2881 | 59.78 | 966.378
2016-05-30 11:00 | 54706 | 4618.9405 | 273356.5221 | 59.76 | 1148.826
2016-05-30 12:00 | 58146 | 4271.2541 | 305458.3375 | 59.75 | 1279.212
2016-05-30 13:00 | 60937 | 4164.5142 | 313750.395 | 59.75 | 1340.614
2016-05-30 14:00 | 62863 | 4058.6035 | 315514.8454 | 59.75 | 1382.986
2016-05-30 15:00 | 63927 | 3738.0704 | 318101.724 | 59.75 | 1406.394
2016-05-30 16:00 | 64367 | 2957.3339 | 316297.1671 | 59.75 | 1416.074
2016-05-30 17:00 | 63675 | 2550.0911 | 317926.892 | 59.75 | 1400.85
2016-05-30 18:00 | 61305 | 2816.2879 | 315933.7722 | 59.75 | 1348.71
2016-05-30 19:00 | 58935 | 3525.1022 | 313350.355 | 59.75 | 1296.57
2016-05-30 20:00 | 57366 | 5216.9808 | 284164.0731 | 59.76 | 1204.686
2016-05-30 21:00 | 55893 | 7276.9835 | 259936.0696 | 59.76 | 1173.753
2016-05-30 22:00 | 52546 | 9049.0356 | 232608.6773 | 59.78 | 998.374
2016-05-30 23:00 | 48707 | 8067.1778 | 222179.7893 | 59.77 | 974.14
2016-05-31 | 43835 | 7392.8412 | 209843.1693 | 59.78 | 832.865
2016-05-31 01:00 | 41397 | 6922.0159 | 208332.8493 | 59.78 | 786.543
2016-05-31 02:00 | 39660 | 5954.9243 | 208332.8493 | 59.78 | 753.54
2016-05-31 03:00 | 38486 | 5556.0729 | 208332.8493 | 59.78 | 731.234
2016-05-31 04:00 | 37921 | 4661.478 | 209628.4473 | 59.78 | 720.499
2016-05-31 05:00 | 38227 | 4198.4858 | 209628.4473 | 59.78 | 726.313
2016-05-31 06:00 | 38460 | 3258.0532 | 209628.4473 | 59.78 | 730.74
2016-05-31 07:00 | 39141 | 1801.4404 | 211147.4473 | 59.78 | 743.679
2016-05-31 08:00 | 42242 | 1030.292 | 216408.9373 | 59.77 | 844.84
2016-05-31 09:00 | 46329 | 657.3719 | 246039.5483 | 59.78 | 880.251
2016-05-31 10:00 | 50606 | 1055.732 | 267688.4276 | 59.76 | 1062.726
2016-05-31 11:00 | 54471 | 1836.9996 | 285541.8016 | 59.75 | 1198.362
2016-05-31 12:00 | 57712 | 3554.835 | 298240.1767 | 59.75 | 1269.664
2016-05-31 13:00 | 60314 | 4075.2183 | 311206.0924 | 59.75 | 1326.908
2016-05-31 14:00 | 62463 | 3416.0888 | 315879.8272 | 59.75 | 1374.186
2016-05-31 15:00 | 64235 | 3098.8009 | 317613.5726 | 59.75 | 1413.17
2016-05-31 16:00 | 65264 | 3002.6093 | 320001.0726 | 59.75 | 1435.808
2016-05-31 17:00 | 65182 | 2772.1808 | 319137.7726 | 59.75 | 1434.004
2016-05-31 18:00 | 63380 | 2417.7382 | 319137.7726 | 59.75 | 1394.36
2016-05-31 19:00 | 61578 | 3486.4114 | 315967.7144 | 59.75 | 1354.716
2016-05-31 20:00 | 60019 | 5584.968 | 297331.9973 | 59.75 | 1320.418
2016-05-31 21:00 | 58475 | 7345.1782 | 274087.155 | 59.76 | 1227.975
2016-05-31 22:00 | 54046 | 10468.2399 | 227554.4668 | 59.78 | 1026.874
2016-05-31 23:00 | 48991 | 10370.4561 | 202106.2184 | 59.77 | 979.82
2016-06-01 | 43168 | 10591.3804 | 190017.1284 | 59.78 | 820.192
2016-06-01 01:00 | 40675 | 10359.4715 | 190017.1284 | 59.77 | 813.5
2016-06-01 02:00 | 38957 | 9882.1381 | 190017.1284 | 59.77 | 779.14
2016-06-01 03:00 | 37968 | 9314.7671 | 190017.1284 | 59.77 | 759.36
2016-06-01 04:00 | 37847 | 8075.222 | 190017.1284 | 59.77 | 756.94
2016-06-01 05:00 | 39235 | 7755.8898 | 193175.5284 | 59.77 | 784.7
2016-06-01 06:00 | 41933 | 6931.0939 | 193175.5284 | 59.78 | 796.727
2016-06-01 07:00 | 43913 | 6079.3215 | 201514.5384 | 59.77 | 878.26
2016-06-01 08:00 | 46682 | 5330.2147 | 225168.9368 | 59.77 | 933.64
2016-06-01 09:00 | 49858 | 5459.1573 | 243672.3948 | 59.78 | 947.302
2016-06-01 10:00 | 53508 | 6825.6587 | 253533.5202 | 59.78 | 1016.652
2016-06-01 11:00 | 56755 | 9913.9337 | 253533.5202 | 59.78 | 1078.345
2016-06-01 12:00 | 59684 | 10261.7119 | 271599.4766 | 59.76 | 1253.364
2016-06-01 13:00 | 62464 | 8385.9523 | 308724.1089 | 59.75 | 1374.208
2016-06-01 14:00 | 64726 | 7443.4136 | 318181.1764 | 59.75 | 1423.972
2016-06-01 15:00 | 65659 | 7204.0552 | 320094.8596 | 59.75 | 1444.498
2016-06-01 16:00 | 66295 | 5981.5916 | 321967.4994 | 59.75 | 1458.49
2016-06-01 17:00 | 65806 | 4573.4209 | 323377.1425 | 59.75 | 1447.732
2016-06-01 18:00 | 64185 | 4366.4079 | 322929.5095 | 59.75 | 1412.07
2016-06-01 19:00 | 61878 | 6330.8435 | 314720.898 | 59.75 | 1361.316
2016-06-01 20:00 | 59865 | 8015.1887 | 296654.9416 | 59.76 | 1257.165
2016-06-01 21:00 | 58182 | 9239.9602 | 270787.0417 | 59.76 | 1221.822
2016-06-01 22:00 | 53796 | 10575.1377 | 231858.3065 | 59.78 | 1022.124
2016-06-01 23:00 | 48712 | 9892.4427 | 206527.0985 | 59.77 | 974.24
2016-06-02 | 41600 | 9021.7466 | 189405.6281 | 59.78 | 790.4
2016-06-02 01:00 | 39207 | 8547.1 | 189405.6281 | 59.77 | 784.14
2016-06-02 02:00 | 37548 | 9059.7854 | 188846.4838 | 59.77 | 750.96
2016-06-02 03:00 | 36588 | 8357.4679 | 188846.4838 | 59.77 | 731.76
2016-06-02 04:00 | 36528 | 6702.0251 | 188846.4838 | 59.77 | 730.56
2016-06-02 05:00 | 37955 | 6290.5602 | 188846.4838 | 59.77 | 759.1
2016-06-02 06:00 | 40360 | 5597.8207 | 188846.4838 | 59.78 | 766.84
2016-06-02 07:00 | 42030 | 5872.9931 | 188846.4838 | 59.78 | 798.57
2016-06-02 08:00 | 44088 | 6604.7473 | 197521.0358 | 59.78 | 837.672
2016-06-02 09:00 | 46671 | 6430.6795 | 216587.5462 | 59.77 | 933.42
2016-06-02 10:00 | 49729 | 5840.0612 | 234494.0817 | 59.78 | 944.851
2016-06-02 11:00 | 52888 | 4843.3634 | 267715.6435 | 59.76 | 1110.648
2016-06-02 12:00 | 55698 | 3121.8842 | 298548.3042 | 59.75 | 1225.356
2016-06-02 13:00 | 58414 | 2221.701 | 309266.7583 | 59.75 | 1285.108
2016-06-02 14:00 | 60177 | 2062.5645 | 309512.9983 | 59.75 | 1323.894
2016-06-02 15:00 | 61000 | 1783.6216 | 314578.1864 | 59.75 | 1342
2016-06-02 16:00 | 60681 | 2122.5421 | 313995.2433 | 59.75 | 1334.982
2016-06-02 17:00 | 59030 | 2991.4851 | 309461.5806 | 59.75 | 1298.66
2016-06-02 18:00 | 56189 | 3425.6806 | 299053.8211 | 59.75 | 1236.158
2016-06-02 19:00 | 53347 | 4166.6039 | 269434.3593 | 59.76 | 1120.287
2016-06-02 20:00 | 51114 | 5787.1947 | 243622.1867 | 59.78 | 971.166
2016-06-02 21:00 | 48728 | 7361.3272 | 216583.7008 | 59.77 | 974.56
2016-06-02 22:00 | 45610 | 4707.4578 | 214333.7008 | 59.77 | 912.2
2016-06-02 23:00 | 41535 | 4161.2875 | 209851.4558 | 59.78 | 789.165
2016-06-03 | 40954 | 3231.4917 | 204564.9358 | 59.77 | 819.08
2016-06-03 01:00 | 38518 | 2239.8828 | 204564.9358 | 59.78 | 731.842
2016-06-03 02:00 | 36750 | 2338.7256 | 205124.0801 | 59.78 | 698.25
2016-06-03 03:00 | 35684 | 2009.8129 | 205124.0801 | 59.78 | 677.996
2016-06-03 04:00 | 35671 | 1686.2927 | 205124.0801 | 59.78 | 677.749
2016-06-03 05:00 | 37115 | 1354.1982 | 205124.0801 | 59.78 | 705.185
2016-06-03 06:00 | 39695 | 1798.8427 | 205124.0801 | 59.77 | 793.9
2016-06-03 07:00 | 41277 | 1558.3787 | 212629.7005 | 59.77 | 825.54
2016-06-03 08:00 | 42921 | 1489.4031 | 223988.5415 | 59.77 | 858.42
2016-06-03 09:00 | 45241 | 1585.8799 | 240017.9903 | 59.78 | 859.579
2016-06-03 10:00 | 47658 | 1908.374 | 246779.4998 | 59.78 | 905.502
2016-06-03 11:00 | 49963 | 1465.3028 | 264897.9256 | 59.76 | 1049.223
2016-06-03 12:00 | 51509 | 1343.9831 | 277138.5936 | 59.76 | 1081.689
2016-06-03 13:00 | 52370 | 828.9122 | 290360.6616 | 59.76 | 1099.77
2016-06-03 14:00 | 53035 | 398.231 | 293509.9055 | 59.75 | 1166.77
2016-06-03 15:00 | 53642 | 475.0687 | 293908.0787 | 59.75 | 1180.124
2016-06-03 16:00 | 53476 | 592.0083 | 293687.1253 | 59.75 | 1176.472
2016-06-03 17:00 | 52760 | 757.0396 | 290769.1268 | 59.76 | 1107.96
2016-06-03 18:00 | 51449 | 1301.931 | 283873.8241 | 59.76 | 1080.429
2016-06-03 19:00 | 50138 | 2158.4927 | 268852.1183 | 59.76 | 1052.898
2016-06-03 20:00 | 50062 | 4227.8328 | 257347.4503 | 59.78 | 951.178
2016-06-03 21:00 | 49296 | 5535.3389 | 234536.1743 | 59.78 | 936.624
2016-06-03 22:00 | 46065 | 5440.8972 | 215508.3193 | 59.77 | 921.3
2016-06-03 23:00 | 42254 | 5218.9779 | 199798.2089 | 59.78 | 802.826
2016-06-04 | 39815 | 5821.5412 | 197014.3089 | 59.78 | 756.485
2016-06-04 01:00 | 37699 | 5469.3989 | 195825.6481 | 59.77 | 753.98
2016-06-04 02:00 | 36248 | 4827.3268 | 195825.6481 | 59.77 | 724.96
2016-06-04 03:00 | 35425 | 4986.2657 | 195825.6481 | 59.77 | 708.5
2016-06-04 04:00 | 35701 | 4425.5924 | 194524.1181 | 59.77 | 714.02
2016-06-04 05:00 | 36835 | 3784.2526 | 194524.1181 | 59.78 | 699.865
2016-06-04 06:00 | 39196 | 3453.4928 | 192335.5877 | 59.78 | 744.724
2016-06-04 07:00 | 41010 | 2873.4938 | 199045.6981 | 59.77 | 820.2
2016-06-04 08:00 | 43674 | 2609.3893 | 227089.9311 | 59.77 | 873.48
2016-06-04 09:00 | 46592 | 2083.2366 | 248533.9291 | 59.78 | 885.248
2016-06-04 10:00 | 49981 | 1571.7694 | 275513.3864 | 59.76 | 1049.601
2016-06-04 11:00 | 53608 | 1933.1805 | 292831.9175 | 59.76 | 1125.768
2016-06-04 12:00 | 56465 | 2388.7392 | 314690.8414 | 59.75 | 1242.23
2016-06-04 13:00 | 59407 | 2089.7628 | 327106.5262 | 59.75 | 1306.954
2016-06-04 14:00 | 61930 | 2358.8433 | 326888.7659 | 59.75 | 1362.46
2016-06-04 15:00 | 63893 | 2277.9255 | 331609.4081 | 59.75 | 1405.646
2016-06-04 16:00 | 64850 | 2050.8447 | 331987.9912 | 59.75 | 1426.7
2016-06-04 17:00 | 64370 | 2029.9246 | 329853.8601 | 59.75 | 1416.14
2016-06-04 18:00 | 62119 | 2639.2391 | 325133.2179 | 59.75 | 1366.618
2016-06-04 19:00 | 59868 | 4918.5658 | 320882.5211 | 59.75 | 1317.096
2016-06-04 20:00 | 57585 | 8512.2166 | 279473.3492 | 59.76 | 1209.285
2016-06-04 21:00 | 55750 | 10171.4111 | 250426.3846 | 59.78 | 1059.25
2016-06-04 22:00 | 52228 | 9797.4622 | 229246.5391 | 59.77 | 1044.56
2016-06-04 23:00 | 48022 | 9023.1996 | 215473.7011 | 59.77 | 960.44
2016-06-05 | 45996 | 8525.8843 | 203295.5577 | 59.78 | 873.924
2016-06-05 01:00 | 43091 | 8062.138 | 204484.2185 | 59.78 | 818.729
2016-06-05 02:00 | 41023 | 7775.4818 | 202163.2039 | 59.78 | 779.437
2016-06-05 03:00 | 39885 | 8608.242 | 202163.2039 | 59.77 | 797.7
2016-06-05 04:00 | 39179 | 8177.2775 | 203464.7339 | 59.77 | 783.58
2016-06-05 05:00 | 39180 | 8103.7441 | 203464.7339 | 59.77 | 783.6
2016-06-05 06:00 | 39554 | 7081.9111 | 205653.2643 | 59.77 | 791.08
2016-06-05 07:00 | 41010 | 6661.7784 | 205653.2643 | 59.78 | 779.19
2016-06-05 08:00 | 44698 | 6308.4915 | 214205.7347 | 59.77 | 893.96
2016-06-05 09:00 | 48951 | 4975.2544 | 249168.5017 | 59.78 | 930.069
2016-06-05 10:00 | 53268 | 4722.6746 | 277765.6975 | 59.76 | 1118.628
2016-06-05 11:00 | 57330 | 4365.4126 | 302512.3366 | 59.75 | 1261.26
2016-06-05 12:00 | 60272 | 3923.2985 | 326538.3357 | 59.75 | 1325.984
2016-06-05 13:00 | 62820 | 3334.9843 | 331561.2769 | 59.75 | 1382.04
2016-06-05 14:00 | 64947 | 2581.3343 | 337490.6331 | 59.75 | 1428.834
2016-06-05 15:00 | 65627 | 2198.55 | 336064.1011 | 59.75 | 1443.794
2016-06-05 16:00 | 66285 | 2027.6004 | 336647.0442 | 59.75 | 1458.27
2016-06-05 17:00 | 65955 | 2480.725 | 337819.6491 | 59.75 | 1451.01
2016-06-05 18:00 | 64610 | 3009.273 | 334959.5218 | 59.75 | 1421.42
2016-06-05 19:00 | 62577 | 3828.2895 | 332074.4427 | 59.75 | 1376.694
2016-06-05 20:00 | 60503 | 5208.1834 | 310033.1726 | 59.75 | 1331.066
2016-06-05 21:00 | 59116 | 6453.3914 | 293414.7099 | 59.75 | 1300.552
2016-06-05 22:00 | 55844 | 6844.265 | 272585.6815 | 59.76 | 1172.724
2016-06-05 23:00 | 52042 | 7430.5655 | 244643.1917 | 59.78 | 988.798
2016-06-06 | 48604 | 7664.2701 | 227043.2157 | 59.77 | 972.08
2016-06-06 01:00 | 45938 | 6924.7408 | 225287.6677 | 59.77 | 918.76
2016-06-06 02:00 | 44027 | 6681.2894 | 225287.6677 | 59.78 | 836.513
2016-06-06 03:00 | 42708 | 5872.5971 | 225287.6677 | 59.78 | 811.452
2016-06-06 04:00 | 41863 | 4920.8585 | 225287.6677 | 59.78 | 795.397
2016-06-06 05:00 | 41616 | 4311.1055 | 225287.6677 | 59.78 | 790.704
2016-06-06 06:00 | 41472 | 3714.9035 | 224669.6677 | 59.77 | 829.44
2016-06-06 07:00 | 42039 | 2888.3497 | 226990.6823 | 59.77 | 840.78
2016-06-06 08:00 | 45124 | 2306.0877 | 234179.8023 | 59.78 | 857.356
2016-06-06 09:00 | 48911 | 2219.6648 | 256739.3226 | 59.78 | 929.309
2016-06-06 10:00 | 53188 | 1791.2802 | 288178.9656 | 59.76 | 1116.948
2016-06-06 11:00 | 57137 | 2083.7146 | 307927.5196 | 59.75 | 1257.014
2016-06-06 12:00 | 60594 | 3010.3627 | 320087.8174 | 59.75 | 1333.068
2016-06-06 13:00 | 63370 | 4373.7805 | 322329.6802 | 59.75 | 1394.14
2016-06-06 14:00 | 64840 | 4334.148 | 324708.429 | 59.75 | 1426.48
2016-06-06 15:00 | 66379 | 4652.0593 | 328003.4968 | 59.75 | 1460.338
2016-06-06 16:00 | 67043 | 4077.4788 | 324327.3733 | 59.75 | 1474.946
2016-06-06 17:00 | 66265 | 3882.8412 | 324170.7768 | 59.75 | 1457.83
2016-06-06 18:00 | 65105 | 4327.892 | 323503.64 | 59.75 | 1432.31
2016-06-06 19:00 | 63257 | 6412.8068 | 316927.7994 | 59.75 | 1391.654
2016-06-06 20:00 | 61675 | 9026.2368 | 291767.6456 | 59.75 | 1356.85
2016-06-06 21:00 | 60408 | 8258.7045 | 288775.0236 | 59.76 | 1268.568
2016-06-06 22:00 | 56721 | 7785.7491 | 266248.2196 | 59.76 | 1191.141
2016-06-06 23:00 | 52107 | 6350.8923 | 249809.9698 | 59.78 | 990.033
2016-06-07 | 45930 | 5743.2697 | 234009.4073 | 59.77 | 918.6
2016-06-07 01:00 | 43434 | 5822.2362 | 232490.4073 | 59.77 | 868.68
2016-06-07 02:00 | 41788 | 5190.6484 | 232490.4073 | 59.78 | 793.972
2016-06-07 03:00 | 40800 | 4524.7375 | 232490.4073 | 59.78 | 775.2
2016-06-07 04:00 | 40761 | 4102.6201 | 232490.4073 | 59.78 | 774.459
2016-06-07 05:00 | 42118 | 3612.8625 | 232490.4073 | 59.77 | 842.36
2016-06-07 06:00 | 44265 | 2553.4596 | 233108.4073 | 59.77 | 885.3
2016-06-07 07:00 | 46091 | 1752.0227 | 244227.6323 | 59.78 | 875.729
2016-06-07 08:00 | 48784 | 1475.6067 | 260838.7578 | 59.78 | 926.896
2016-06-07 09:00 | 51886 | 2305.3386 | 277919.3196 | 59.76 | 1089.606
2016-06-07 10:00 | 55216 | 2589.6201 | 297348.4371 | 59.75 | 1214.752
2016-06-07 11:00 | 58186 | 3265.3912 | 315690.2898 | 59.75 | 1280.092
2016-06-07 12:00 | 60965 | 3330.4801 | 326189.9874 | 59.75 | 1341.23
2016-06-07 13:00 | 63018 | 2595.8624 | 330358.916 | 59.75 | 1386.396
2016-06-07 14:00 | 64068 | 2410.4164 | 330457.6261 | 59.75 | 1409.496
2016-06-07 15:00 | 64624 | 2515.9412 | 330941.8591 | 59.75 | 1421.728
2016-06-07 16:00 | 64520 | 3576.4078 | 334109.556 | 59.75 | 1419.44
2016-06-07 17:00 | 64181 | 4695.9685 | 331108.8638 | 59.75 | 1411.982
2016-06-07 18:00 | 62474 | 5751.3011 | 326309.1839 | 59.75 | 1374.428
2016-06-07 19:00 | 60767 | 7702.0761 | 297897.6911 | 59.75 | 1336.874
2016-06-07 20:00 | 59352 | 9939.1504 | 272682.5606 | 59.76 | 1246.392
2016-06-07 21:00 | 58066 | 10384.7813 | 259203.5498 | 59.76 | 1219.386
2016-06-07 22:00 | 54332 | 9956.6468 | 237823.2073 | 59.78 | 1032.308
2016-06-07 23:00 | 49953 | 8917.8266 | 219330.7693 | 59.77 | 999.06
2016-06-08 | 46588 | 8139.6761 | 212278.1293 | 59.77 | 931.76
2016-06-08 01:00 | 44057 | 7672.9248 | 212278.1293 | 59.78 | 837.083
2016-06-08 02:00 | 42257 | 8088.5267 | 212278.1293 | 59.78 | 802.883
2016-06-08 03:00 | 41092 | 8875.6236 | 212278.1293 | 59.77 | 821.84
2016-06-08 04:00 | 40791 | 8814.665 | 212278.1293 | 59.77 | 815.82
2016-06-08 05:00 | 42026 | 8192.5653 | 212278.1293 | 59.78 | 798.494
2016-06-08 06:00 | 44147 | 7260.8078 | 212278.1293 | 59.78 | 838.793
2016-06-08 07:00 | 45740 | 5897.8916 | 214470.3593 | 59.77 | 914.8
2016-06-08 08:00 | 47923 | 4836.4337 | 235195.0423 | 59.78 | 910.537
2016-06-08 09:00 | 50639 | 5834.0947 | 247650.3503 | 59.78 | 962.141
2016-06-08 10:00 | 53184 | 6558.8839 | 259439.9263 | 59.78 | 1010.496
2016-06-08 11:00 | 54296 | 6799.2523 | 267084.8603 | 59.78 | 1031.624
2016-06-08 12:00 | 55490 | 7286.4785 | 282808.8227 | 59.76 | 1165.29
2016-06-08 13:00 | 57004 | 5727.198 | 291497.5207 | 59.76 | 1197.084
2016-06-08 14:00 | 58477 | 4708.9483 | 306373.504 | 59.75 | 1286.494
2016-06-08 15:00 | 59755 | 3995.8613 | 310390.7706 | 59.75 | 1314.61
2016-06-08 16:00 | 60610 | 3874.8976 | 310578.0906 | 59.75 | 1333.42
2016-06-08 17:00 | 60266 | 3917.0374 | 310098.8124 | 59.75 | 1325.852
2016-06-08 18:00 | 58187 | 4536.2794 | 305083.018 | 59.75 | 1280.114
2016-06-08 19:00 | 56109 | 7070.8453 | 294375.41 | 59.76 | 1178.289
2016-06-08 20:00 | 54796 | 10267.126 | 267777.655 | 59.78 | 1041.124
2016-06-08 21:00 | 53958 | 9907.9002 | 259088.957 | 59.78 | 1025.202
2016-06-08 22:00 | 50411 | 8323.8874 | 244632.8316 | 59.77 | 1008.22
2016-06-08 23:00 | 46495 | 9588.3433 | 201658.1709 | 59.78 | 883.405
2016-06-09 | 40638 | 9147.9904 | 198301.7709 | 59.77 | 812.76
2016-06-09 01:00 | 38648 | 8516.5301 | 198017.3629 | 59.77 | 772.96
2016-06-09 02:00 | 37364 | 7182.7497 | 198017.3629 | 59.77 | 747.28
2016-06-09 03:00 | 36694 | 6174.0726 | 198017.3629 | 59.77 | 733.88
2016-06-09 04:00 | 36860 | 5722.307 | 198017.3629 | 59.77 | 737.2
2016-06-09 05:00 | 38380 | 5225.1038 | 198017.3629 | 59.78 | 729.22
2016-06-09 06:00 | 40791 | 4799.2548 | 198017.3629 | 59.78 | 775.029
2016-06-09 07:00 | 42408 | 4924.5455 | 202687.5729 | 59.78 | 805.752
2016-06-09 08:00 | 44412 | 4960.7826 | 212670.9583 | 59.77 | 888.24
2016-06-09 09:00 | 46617 | 4902.858 | 228245.3913 | 59.77 | 932.34
2016-06-09 10:00 | 49072 | 4697.0917 | 241504.9044 | 59.78 | 932.368
2016-06-09 11:00 | 51303 | 5265.2434 | 252242.1124 | 59.78 | 974.757
2016-06-09 12:00 | 52953 | 6151.4109 | 258686.7224 | 59.78 | 1006.107
2016-06-09 13:00 | 54006 | 5550.7725 | 267037.2892 | 59.76 | 1134.126
2016-06-09 14:00 | 54740 | 4950.9611 | 275857.6142 | 59.76 | 1149.54
2016-06-09 15:00 | 55298 | 4942.4582 | 279403.2122 | 59.76 | 1161.258
2016-06-09 16:00 | 55648 | 4688.4999 | 279865.6753 | 59.76 | 1168.608
2016-06-09 17:00 | 55395 | 4363.7938 | 279831.1053 | 59.76 | 1163.295
2016-06-09 18:00 | 53896 | 4739.6941 | 271906.2977 | 59.76 | 1131.816
2016-06-09 19:00 | 52397 | 5824.8897 | 258247.2617 | 59.78 | 995.543
2016-06-09 20:00 | 51591 | 7306.8613 | 245145.3085 | 59.78 | 980.229
2016-06-09 21:00 | 50899 | 8382.4709 | 236970.7417 | 59.78 | 967.081
2016-06-09 22:00 | 47989 | 9662.9579 | 203332.7183 | 59.77 | 959.78
2016-06-09 23:00 | 44411 | 8335.7925 | 194373.7583 | 59.78 | 843.809
2016-06-10 | 41108 | 8271.5694 | 190766.4383 | 59.78 | 781.052
2016-06-10 01:00 | 39146 | 8054.5263 | 191050.8463 | 59.77 | 782.92
2016-06-10 02:00 | 37986 | 6796.4512 | 191050.8463 | 59.77 | 759.72
2016-06-10 03:00 | 37411 | 6091.3608 | 191050.8463 | 59.77 | 748.22
2016-06-10 04:00 | 37496 | 6106.797 | 191050.8463 | 59.77 | 749.92
2016-06-10 05:00 | 38930 | 5320.5654 | 191050.8463 | 59.78 | 739.67
2016-06-10 06:00 | 41346 | 4638.1888 | 194523.1363 | 59.78 | 785.574
2016-06-10 07:00 | 42744 | 6550.2149 | 194649.6163 | 59.78 | 812.136
2016-06-10 08:00 | 44500 | 8754.1131 | 194732.7413 | 59.78 | 845.5
2016-06-10 09:00 | 46747 | 10507.1885 | 194157.7813 | 59.78 | 888.193
2016-06-10 10:00 | 49328 | 10549.1404 | 213107.2513 | 59.77 | 986.56
2016-06-10 11:00 | 52108 | 10931.5236 | 229027.9313 | 59.77 | 1042.16
2016-06-10 12:00 | 54382 | 11658.6945 | 240566.5513 | 59.78 | 1033.258
2016-06-10 13:00 | 56733 | 10963.3757 | 257247.9981 | 59.78 | 1077.927
2016-06-10 14:00 | 58737 | 10785.6304 | 276000.4591 | 59.76 | 1233.477
2016-06-10 15:00 | 60222 | 9764.955 | 284613.0422 | 59.76 | 1264.662
2016-06-10 16:00 | 60970 | 9290.8038 | 285796.7534 | 59.76 | 1280.37
2016-06-10 17:00 | 60619 | 8997.9394 | 284286.4334 | 59.76 | 1272.999
2016-06-10 18:00 | 58736 | 9772.3346 | 282647.644 | 59.76 | 1233.456
2016-06-10 19:00 | 56852 | 10704.7265 | 266394.532 | 59.78 | 1080.188
2016-06-10 20:00 | 55296 | 11257.2253 | 256808.372 | 59.78 | 1050.624
2016-06-10 21:00 | 54299 | 12874.41 | 229947.6652 | 59.77 | 1085.98
2016-06-10 22:00 | 51002 | 13905.9466 | 199771.9242 | 59.78 | 969.038
2016-06-10 23:00 | 47024 | 13620.3409 | 191614.4193 | 59.78 | 893.456
2016-06-11 | 46551 | 13312.0157 | 186666.7393 | 59.78 | 884.469
2016-06-11 01:00 | 44228 | 12341.991 | 186666.7393 | 59.77 | 884.56
2016-06-11 02:00 | 42701 | 12462.4057 | 186666.7393 | 59.77 | 854.02
2016-06-11 03:00 | 41931 | 12511.9032 | 182206.3993 | 59.77 | 838.62
2016-06-11 04:00 | 41870 | 11856.4746 | 182206.3993 | 59.77 | 837.4
2016-06-11 05:00 | 43285 | 11379.8863 | 182206.3993 | 59.77 | 865.7
2016-06-11 06:00 | 45325 | 10188.8722 | 186050.2425 | 59.78 | 861.175
2016-06-11 07:00 | 46845 | 10643.9525 | 189522.5325 | 59.78 | 890.055
2016-06-11 08:00 | 49234 | 11434.1609 | 198365.6025 | 59.77 | 984.68
2016-06-11 09:00 | 51873 | 13721.7112 | 202107.0729 | 59.77 | 1037.46
2016-06-11 10:00 | 54932 | 13695.2241 | 217953.2094 | 59.77 | 1098.64
2016-06-11 11:00 | 57775 | 13506.7343 | 239355.4324 | 59.78 | 1097.725
2016-06-11 12:00 | 59939 | 12158.2338 | 268385.2612 | 59.76 | 1258.719
2016-06-11 13:00 | 62090 | 10735.6102 | 291595.7372 | 59.76 | 1303.89
2016-06-11 14:00 | 63748 | 11153.5202 | 299549.6972 | 59.75 | 1402.456
2016-06-11 15:00 | 64754 | 10680.4595 | 304234.8848 | 59.75 | 1424.588
2016-06-11 16:00 | 64547 | 10093.143 | 301750.9648 | 59.75 | 1420.034
2016-06-11 17:00 | 64626 | 10112.3091 | 303261.2848 | 59.75 | 1421.772
2016-06-11 18:00 | 62332 | 11027.9159 | 292194.3507 | 59.76 | 1308.972
2016-06-11 19:00 | 60037 | 13651.2908 | 264280.0173 | 59.78 | 1140.703
2016-06-11 20:00 | 58330 | 14877.0016 | 235250.1885 | 59.78 | 1108.27
2016-06-11 21:00 | 57459 | 14626.1973 | 230532.1505 | 59.78 | 1091.721
2016-06-11 22:00 | 54506 | 14711.086 | 210835.7525 | 59.77 | 1090.12
2016-06-11 23:00 | 51015 | 14829.4237 | 190663.9925 | 59.78 | 969.285
2016-06-12 | 49623 | 14694.8507 | 183445.5118 | 59.78 | 942.837
2016-06-12 01:00 | 47239 | 14591.5611 | 183445.5118 | 59.78 | 897.541
2016-06-12 02:00 | 45415 | 14826.5085 | 183445.5118 | 59.77 | 908.3
2016-06-12 03:00 | 44387 | 13552.0862 | 183445.5118 | 59.77 | 887.74
2016-06-12 04:00 | 43920 | 12173.6025 | 183445.5118 | 59.77 | 878.4
2016-06-12 05:00 | 44067 | 12731.4156 | 183445.5118 | 59.77 | 881.34
2016-06-12 06:00 | 44266 | 11726.7961 | 183445.5118 | 59.78 | 841.054
2016-06-12 07:00 | 45538 | 11667.1252 | 183445.5118 | 59.78 | 865.222
2016-06-12 08:00 | 48739 | 11542.1083 | 198578.2818 | 59.78 | 926.041
2016-06-12 09:00 | 51999 | 14632.8133 | 200828.2818 | 59.78 | 987.981
2016-06-12 10:00 | 55536 | 15845.9469 | 219639.3848 | 59.77 | 1110.72
2016-06-12 11:00 | 58509 | 16165.9573 | 232403.5212 | 59.77 | 1170.18
2016-06-12 12:00 | 60696 | 16170.5232 | 250224.5792 | 59.78 | 1153.224
2016-06-12 13:00 | 62275 | 15713.0051 | 261873.5284 | 59.78 | 1183.225
2016-06-12 14:00 | 63776 | 15888.8764 | 273228.508 | 59.76 | 1339.296
2016-06-12 15:00 | 64981 | 15500.8167 | 281233.814 | 59.76 | 1364.601
2016-06-12 16:00 | 64987 | 14502.8501 | 285153.718 | 59.76 | 1364.727
2016-06-12 17:00 | 64942 | 13852.0495 | 285153.718 | 59.76 | 1363.782
2016-06-12 18:00 | 63997 | 14216.6264 | 284453.734 | 59.76 | 1343.937
2016-06-12 19:00 | 62365 | 15158.3044 | 270365.7526 | 59.78 | 1184.935
2016-06-12 20:00 | 60642 | 15415.7725 | 255342.7846 | 59.78 | 1152.198
2016-06-12 21:00 | 59598 | 14871.1965 | 248067.0186 | 59.78 | 1132.362
2016-06-12 22:00 | 56627 | 14349.3454 | 232338.8558 | 59.77 | 1132.54
2016-06-12 23:00 | 53228 | 15096.8929 | 202546.4518 | 59.77 | 1064.56
2016-06-13 | 50777 | 15071.7308 | 192361.3618 | 59.78 | 964.763
2016-06-13 01:00 | 48405 | 14224.8205 | 192361.3618 | 59.78 | 919.695
2016-06-13 02:00 | 46609 | 14482.1442 | 192361.3618 | 59.77 | 932.18
2016-06-13 03:00 | 45357 | 14314.945 | 192361.3618 | 59.77 | 907.14
2016-06-13 04:00 | 44510 | 13242.6847 | 192361.3618 | 59.77 | 890.2
2016-06-13 05:00 | 44140 | 12976.7563 | 192361.3618 | 59.77 | 882.8
2016-06-13 06:00 | 43774 | 12077.8006 | 191770.3538 | 59.77 | 875.48
2016-06-13 07:00 | 44425 | 10627.3947 | 191770.3538 | 59.78 | 844.075
2016-06-13 08:00 | 47432 | 9068.5123 | 207442.1138 | 59.77 | 948.64
2016-06-13 09:00 | 51326 | 8630.7977 | 240615.8879 | 59.78 | 975.194
2016-06-13 10:00 | 54788 | 10764.5942 | 247548.7759 | 59.78 | 1040.972
2016-06-13 11:00 | 57828 | 12439.6661 | 251381.4959 | 59.78 | 1098.732
2016-06-13 12:00 | 60850 | 12577.4612 | 270748.5162 | 59.76 | 1277.85
2016-06-13 13:00 | 63224 | 12152.7811 | 289673.6723 | 59.76 | 1327.704
2016-06-13 14:00 | 64507 | 11962.9763 | 307366.9286 | 59.75 | 1419.154
2016-06-13 15:00 | 65782 | 10391.4011 | 316872.1123 | 59.75 | 1447.204
2016-06-13 16:00 | 66602 | 9409.8625 | 318143.1153 | 59.75 | 1465.244
2016-06-13 17:00 | 66504 | 8779.7689 | 318421.225 | 59.75 | 1463.088
2016-06-13 18:00 | 64858 | 9027.6436 | 318061.0353 | 59.75 | 1426.876
2016-06-13 19:00 | 63900 | 8400.3857 | 317152.1123 | 59.75 | 1405.8
2016-06-13 20:00 | 62087 | 7929.2223 | 315643.1506 | 59.75 | 1365.914
2016-06-13 21:00 | 60965 | 7236.3812 | 313075.8815 | 59.75 | 1341.23
2016-06-13 22:00 | 57517 | 7442.5931 | 288774.1052 | 59.76 | 1207.857
2016-06-13 23:00 | 52942 | 8640.5718 | 247332.3459 | 59.78 | 1005.898
2016-06-14 | 46905 | 8890.1165 | 239017.3809 | 59.77 | 938.1
2016-06-14 01:00 | 44721 | 8091.2775 | 239017.3809 | 59.78 | 849.699
2016-06-14 02:00 | 43214 | 5112.7305 | 239017.3809 | 59.77 | 864.28
2016-06-14 03:00 | 42314 | 4225.1964 | 239017.3809 | 59.77 | 846.28
2016-06-14 04:00 | 42263 | 4084.9518 | 239017.3809 | 59.77 | 845.26
2016-06-14 05:00 | 43552 | 3869.1057 | 239017.3809 | 59.77 | 871.04
2016-06-14 06:00 | 45349 | 4191.8956 | 239608.3889 | 59.77 | 906.98
2016-06-14 07:00 | 47195 | 4867.8753 | 239608.3889 | 59.77 | 943.9
2016-06-14 08:00 | 49997 | 6267.159 | 244090.6339 | 59.78 | 949.943
2016-06-14 09:00 | 53180 | 7295.0294 | 259693.2634 | 59.78 | 1010.42
2016-06-14 10:00 | 56597 | 9139.8862 | 269122.3336 | 59.78 | 1075.343
2016-06-14 11:00 | 59932 | 9169.1183 | 293407.7436 | 59.76 | 1258.572
2016-06-14 12:00 | 62524 | 8649.7536 | 316843.547 | 59.75 | 1375.528
2016-06-14 13:00 | 64952 | 8025.5593 | 324516.8768 | 59.75 | 1428.944
2016-06-14 14:00 | 66071 | 7793.0597 | 327376.5896 | 59.75 | 1453.562
2016-06-14 15:00 | 67167 | 7177.3797 | 329632.6763 | 59.75 | 1477.674
2016-06-14 16:00 | 67734 | 6977.3356 | 329655.4795 | 59.75 | 1490.148
2016-06-14 17:00 | 67057 | 6257.962 | 329655.4795 | 59.75 | 1475.254
2016-06-14 18:00 | 64715 | 6620.1339 | 326676.2768 | 59.75 | 1423.73
2016-06-14 19:00 | 63060 | 6062.5021 | 325590.1204 | 59.75 | 1387.32
2016-06-14 20:00 | 60848 | 6661.2979 | 310700.656 | 59.75 | 1338.656
2016-06-14 21:00 | 59345 | 4696.4203 | 310700.656 | 59.75 | 1305.59
2016-06-14 22:00 | 55417 | 5188.5865 | 276809.6502 | 59.76 | 1163.757
2016-06-14 23:00 | 50602 | 6070.5215 | 245871.5259 | 59.78 | 961.438
2016-06-15 | 46888 | 5177.4013 | 229506.6329 | 59.77 | 937.76
2016-06-15 01:00 | 44377 | 4523.1943 | 229506.6329 | 59.77 | 887.54
2016-06-15 02:00 | 42181 | 5316.4055 | 229506.6329 | 59.78 | 801.439
2016-06-15 03:00 | 40769 | 5085.5389 | 229506.6329 | 59.78 | 774.611
2016-06-15 04:00 | 40346 | 5001.6265 | 228643.3329 | 59.78 | 766.574
2016-06-15 05:00 | 41526 | 5129.5525 | 227780.0329 | 59.78 | 788.994
2016-06-15 06:00 | 43375 | 4898.6618 | 227780.0329 | 59.77 | 867.5
2016-06-15 07:00 | 45061 | 5001.357 | 227780.0329 | 59.77 | 901.22
2016-06-15 08:00 | 47726 | 5320.205 | 237282.7659 | 59.77 | 954.52
2016-06-15 09:00 | 50636 | 5411.8011 | 256497.0194 | 59.78 | 962.084
2016-06-15 10:00 | 53931 | 6102.1931 | 270832.4816 | 59.76 | 1132.551
2016-06-15 11:00 | 57256 | 7373.5814 | 285121.5821 | 59.76 | 1202.376
2016-06-15 12:00 | 59308 | 7756.1602 | 294100.3736 | 59.76 | 1245.468
2016-06-15 13:00 | 61685 | 7769.2201 | 312197.6439 | 59.75 | 1357.07
2016-06-15 14:00 | 63713 | 6532.1606 | 321426.9047 | 59.75 | 1401.686
2016-06-15 15:00 | 64477 | 5501.3568 | 322052.8686 | 59.75 | 1418.494
2016-06-15 16:00 | 65376 | 6074.569 | 322055.0484 | 59.75 | 1438.272
2016-06-15 17:00 | 65132 | 5898.1431 | 320166.0984 | 59.75 | 1432.904
2016-06-15 18:00 | 64137 | 6939.3955 | 318456.7016 | 59.75 | 1411.014
2016-06-15 19:00 | 62454 | 7360.1336 | 315324.2129 | 59.75 | 1373.988
2016-06-15 20:00 | 60398 | 8160.6772 | 302805.3624 | 59.76 | 1268.358
2016-06-15 21:00 | 58836 | 8840.4239 | 282952.5441 | 59.76 | 1235.556
2016-06-15 22:00 | 54856 | 8580.2357 | 252852.8639 | 59.78 | 1042.264
2016-06-15 23:00 | 50240 | 8803.2743 | 229078.5305 | 59.77 | 1004.8
2016-06-16 | 44269 | 8967.0592 | 211693.7255 | 59.78 | 841.111
2016-06-16 01:00 | 41968 | 8023.1762 | 211693.7255 | 59.78 | 797.392
2016-06-16 02:00 | 40296 | 8093.9947 | 211693.7255 | 59.77 | 805.92
2016-06-16 03:00 | 39335 | 8541.3287 | 209758.1118 | 59.77 | 786.7
2016-06-16 04:00 | 39200 | 6806.9315 | 210621.4118 | 59.77 | 784
2016-06-16 05:00 | 40474 | 5416.09 | 211484.7118 | 59.78 | 769.006
2016-06-16 06:00 | 42274 | 5010.2649 | 211484.7118 | 59.78 | 803.206
2016-06-16 07:00 | 44143 | 5717.2674 | 211484.7118 | 59.77 | 882.86
2016-06-16 08:00 | 46854 | 6911.0797 | 224671.3068 | 59.77 | 937.08
2016-06-16 09:00 | 50181 | 8266.2345 | 235657.6348 | 59.77 | 1003.62
2016-06-16 10:00 | 53749 | 9839.2457 | 242924.8743 | 59.78 | 1021.231
2016-06-16 11:00 | 56947 | 11672.5691 | 248102.6078 | 59.78 | 1081.993
2016-06-16 12:00 | 59660 | 10919.6658 | 275747.7492 | 59.76 | 1252.86
2016-06-16 13:00 | 62139 | 10133.1586 | 296354.2724 | 59.76 | 1304.919
2016-06-16 14:00 | 63923 | 9841.8068 | 303948.82 | 59.75 | 1406.306
2016-06-16 15:00 | 64556 | 10003.4244 | 304112 | 59.75 | 1420.232
2016-06-16 16:00 | 64706 | 9361.8684 | 304112 | 59.75 | 1423.532
2016-06-16 17:00 | 64186 | 8670.1119 | 306000.95 | 59.75 | 1412.092
2016-06-16 18:00 | 62312 | 9267.3403 | 302046.6804 | 59.75 | 1370.864
2016-06-16 19:00 | 60437 | 11560.4888 | 277437.5179 | 59.76 | 1269.177
2016-06-16 20:00 | 58242 | 13146.0577 | 251256.5165 | 59.78 | 1106.598
2016-06-16 21:00 | 56982 | 12588.6283 | 239721.6093 | 59.78 | 1082.658
2016-06-16 22:00 | 53291 | 11869.5521 | 223008.3573 | 59.77 | 1065.82
2016-06-16 23:00 | 48564 | 10975.5286 | 201082.2389 | 59.77 | 971.28
2016-06-17 | 45172 | 9891.9849 | 190041.7389 | 59.78 | 858.268
2016-06-17 01:00 | 42620 | 9205.2264 | 190041.7389 | 59.78 | 809.78
2016-06-17 02:00 | 40818 | 9551.2559 | 190041.7389 | 59.77 | 816.36
2016-06-17 03:00 | 39690 | 9701.6081 | 192265.3525 | 59.77 | 793.8
2016-06-17 04:00 | 39472 | 9239.0369 | 192265.3525 | 59.77 | 789.44
2016-06-17 05:00 | 40531 | 9246.2671 | 192265.3525 | 59.77 | 810.62
2016-06-17 06:00 | 42235 | 8857.5883 | 192265.3525 | 59.78 | 802.465
2016-06-17 07:00 | 43927 | 10259.2657 | 192265.3525 | 59.78 | 834.613
2016-06-17 08:00 | 46992 | 11821.4483 | 192313.3525 | 59.78 | 892.848
2016-06-17 09:00 | 50208 | 11817.4841 | 204865.3225 | 59.77 | 1004.16
2016-06-17 10:00 | 53721 | 12389.0929 | 218678.1384 | 59.77 | 1074.42
2016-06-17 11:00 | 56922 | 13338.3061 | 239173.9874 | 59.78 | 1081.518
2016-06-17 12:00 | 59736 | 12303.4062 | 263632.6422 | 59.78 | 1134.984
2016-06-17 13:00 | 61926 | 9397.962 | 299341.864 | 59.75 | 1362.372
2016-06-17 14:00 | 63377 | 8344.0038 | 308832.8026 | 59.75 | 1394.294
2016-06-17 15:00 | 64198 | 8103.8473 | 311314.4026 | 59.75 | 1412.356
2016-06-17 16:00 | 64461 | 7713.957 | 311314.4026 | 59.75 | 1418.142
2016-06-17 17:00 | 64115 | 8440.8957 | 311314.4026 | 59.75 | 1410.53
2016-06-17 18:00 | 62066 | 9694.7642 | 298863.0461 | 59.76 | 1303.386
2016-06-17 19:00 | 60017 | 11663.0801 | 276275.0091 | 59.76 | 1260.357
2016-06-17 20:00 | 58060 | 12957.7076 | 251816.3543 | 59.78 | 1103.14
2016-06-17 21:00 | 56793 | 13483.1471 | 234963.1929 | 59.78 | 1079.067
2016-06-17 22:00 | 53003 | 11976.4834 | 216890.7769 | 59.77 | 1060.06
2016-06-17 23:00 | 49024 | 12342.1139 | 195358.8565 | 59.78 | 931.456
2016-06-18 | 47555 | 13055.1489 | 195358.8565 | 59.78 | 903.545
2016-06-18 01:00 | 44978 | 11914.0967 | 195358.8565 | 59.78 | 854.582
2016-06-18 02:00 | 43292 | 11453.7687 | 195358.8565 | 59.77 | 865.84
2016-06-18 03:00 | 42258 | 11808.06 | 195358.8565 | 59.77 | 845.16
2016-06-18 04:00 | 41981 | 10774.5076 | 195358.8565 | 59.77 | 839.62
2016-06-18 05:00 | 43115 | 9433.9027 | 195358.8565 | 59.78 | 819.185
2016-06-18 06:00 | 44675 | 8240.9249 | 195358.8565 | 59.78 | 848.825
2016-06-18 07:00 | 46534 | 10340.146 | 195358.8565 | 59.78 | 884.146
2016-06-18 08:00 | 49694 | 12149.1782 | 198668.6665 | 59.77 | 993.88
2016-06-18 09:00 | 53060 | 11636.7678 | 224444.1369 | 59.77 | 1061.2
2016-06-18 10:00 | 56731 | 11554.9998 | 243094.3899 | 59.78 | 1077.889
2016-06-18 11:00 | 59833 | 11453.5041 | 267933.8266 | 59.76 | 1256.493
2016-06-18 12:00 | 62770 | 9712.6217 | 308141.1453 | 59.75 | 1380.94
2016-06-18 13:00 | 64576 | 7120.9308 | 325519.7214 | 59.75 | 1420.672
2016-06-18 14:00 | 66280 | 6574.4676 | 328804.2996 | 59.75 | 1458.16
2016-06-18 15:00 | 67396 | 6431.023 | 327718.4435 | 59.75 | 1482.712
2016-06-18 16:00 | 67603 | 6139.8217 | 328097.0266 | 59.75 | 1487.266
2016-06-18 17:00 | 66998 | 6838.1921 | 327718.4435 | 59.75 | 1473.956
2016-06-18 18:00 | 64632 | 7700.6319 | 322890.0578 | 59.75 | 1421.904
2016-06-18 19:00 | 62953 | 10141.7663 | 301101.6762 | 59.75 | 1384.966
2016-06-18 20:00 | 60809 | 11975.2467 | 269227.0775 | 59.76 | 1276.989
2016-06-18 21:00 | 59450 | 12616.6379 | 256842.1434 | 59.78 | 1129.55
2016-06-18 22:00 | 56140 | 12427.2133 | 231950.6304 | 59.78 | 1066.66
2016-06-18 23:00 | 52068 | 11910.5198 | 213458.1924 | 59.77 | 1041.36
2016-06-19 | 50275 | 11921.6921 | 203391.682 | 59.77 | 1005.5
2016-06-19 01:00 | 47444 | 11734.4807 | 203391.682 | 59.78 | 901.436
2016-06-19 02:00 | 45628 | 11597.28 | 203391.682 | 59.78 | 866.932
2016-06-19 03:00 | 44220 | 11418.2896 | 203391.682 | 59.78 | 840.18
2016-06-19 04:00 | 43373 | 10861.6619 | 203391.682 | 59.78 | 824.087
2016-06-19 05:00 | 43249 | 9428.3573 | 203391.682 | 59.78 | 821.731
2016-06-19 06:00 | 43023 | 8381.5814 | 203391.682 | 59.78 | 817.437
2016-06-19 07:00 | 44224 | 8310.4659 | 203391.682 | 59.78 | 840.256
2016-06-19 08:00 | 47700 | 7965.8529 | 213809.458 | 59.77 | 954
2016-06-19 09:00 | 51466 | 6426.2478 | 248760.4394 | 59.78 | 977.854
2016-06-19 10:00 | 55406 | 5043.1206 | 279979.027 | 59.76 | 1163.526
2016-06-19 11:00 | 59080 | 5641.1424 | 305323.5161 | 59.75 | 1299.76
2016-06-19 12:00 | 62136 | 6553.9516 | 321203.7584 | 59.75 | 1366.992
2016-06-19 13:00 | 64430 | 5598.2262 | 329468.3314 | 59.75 | 1417.46
2016-06-19 14:00 | 65574 | 5730.7491 | 331765.7031 | 59.75 | 1442.628
2016-06-19 15:00 | 66873 | 6549.7582 | 334086.7177 | 59.75 | 1471.206
2016-06-19 16:00 | 67632 | 6893.9003 | 331927.3177 | 59.75 | 1487.904
2016-06-19 17:00 | 67260 | 6742.9037 | 331713.4288 | 59.75 | 1479.72
2016-06-19 18:00 | 65405 | 8479.6401 | 324990.4229 | 59.75 | 1438.91
2016-06-19 19:00 | 64237 | 10560.9712 | 309364.0858 | 59.75 | 1413.214
2016-06-19 20:00 | 61887 | 12407.268 | 277282.7815 | 59.76 | 1299.627
2016-06-19 21:00 | 60296 | 11623.9136 | 270302.3211 | 59.76 | 1266.216
2016-06-19 22:00 | 56793 | 10515.895 | 252921.0073 | 59.78 | 1079.067
2016-06-19 23:00 | 52846 | 8988.8354 | 240812.7779 | 59.78 | 1004.074
2016-06-20 | 50522 | 8743.0002 | 227837.7549 | 59.77 | 1010.44
2016-06-20 01:00 | 47688 | 9067.8289 | 224235.6549 | 59.77 | 953.76
2016-06-20 02:00 | 45399 | 8282.1361 | 224235.6549 | 59.78 | 862.581
2016-06-20 03:00 | 43710 | 7388.5505 | 221754.0549 | 59.78 | 830.49
2016-06-20 04:00 | 42578 | 6864.4836 | 221754.0549 | 59.78 | 808.982
2016-06-20 05:00 | 42113 | 6262.4053 | 221754.0549 | 59.78 | 800.147
2016-06-20 06:00 | 41634 | 5681.5354 | 224147.2849 | 59.78 | 791.046
2016-06-20 07:00 | 42752 | 5875.8702 | 224147.2849 | 59.78 | 812.288
2016-06-20 08:00 | 46695 | 6193.0275 | 224147.2849 | 59.77 | 933.9
2016-06-20 09:00 | 50719 | 5859.4762 | 249813.1279 | 59.78 | 963.661
2016-06-20 10:00 | 54737 | 7070.579 | 267052.2485 | 59.76 | 1149.477
2016-06-20 11:00 | 58475 | 6724.5837 | 297175.0153 | 59.76 | 1227.975
2016-06-20 12:00 | 61692 | 7587.0978 | 312134.1139 | 59.75 | 1357.224
2016-06-20 13:00 | 64212 | 8554.4041 | 314362.8029 | 59.75 | 1412.664
2016-06-20 14:00 | 65564 | 9611.5741 | 315751.2516 | 59.75 | 1442.408
2016-06-20 15:00 | 67077 | 9941.3958 | 316052.8768 | 59.75 | 1475.694
2016-06-20 16:00 | 67977 | 10509.9281 | 318123.6668 | 59.75 | 1495.494
2016-06-20 17:00 | 67951 | 10306.7447 | 318358.1791 | 59.75 | 1494.922
2016-06-20 18:00 | 66178 | 10597.1959 | 317321.646 | 59.75 | 1455.916
2016-06-20 19:00 | 65091 | 11891.1525 | 301216.9312 | 59.75 | 1432.002
2016-06-20 20:00 | 63034 | 12714.8738 | 274875.4086 | 59.76 | 1323.714
2016-06-20 21:00 | 61829 | 11748.3679 | 274875.4086 | 59.76 | 1298.409
2016-06-20 22:00 | 58068 | 11252.2025 | 252562.7239 | 59.78 | 1103.292
2016-06-20 23:00 | 53300 | 10450.5114 | 230474.9209 | 59.78 | 1012.7
2016-06-21 | 46804 | 9019.5038 | 213779.0225 | 59.77 | 936.08
2016-06-21 01:00 | 44265 | 8504.7617 | 212260.0225 | 59.78 | 841.035
2016-06-21 02:00 | 42674 | 7980.193 | 212260.0225 | 59.78 | 810.806
2016-06-21 03:00 | 41624 | 9090.6408 | 214741.6225 | 59.78 | 790.856
2016-06-21 04:00 | 41478 | 7846.0724 | 214741.6225 | 59.78 | 788.082
2016-06-21 05:00 | 42564 | 6897.1219 | 214741.6225 | 59.78 | 808.716
2016-06-21 06:00 | 43882 | 5790.9131 | 214741.6225 | 59.77 | 877.64
2016-06-21 07:00 | 45745 | 5846.5493 | 214741.6225 | 59.77 | 914.9
2016-06-21 08:00 | 48850 | 5806.2808 | 232817.6229 | 59.78 | 928.15
2016-06-21 09:00 | 52455 | 6020.9408 | 253164.8939 | 59.78 | 996.645
2016-06-21 10:00 | 56348 | 6406.0426 | 271358.7394 | 59.76 | 1183.308
2016-06-21 11:00 | 60057 | 6026.2078 | 302483.8427 | 59.75 | 1321.254
2016-06-21 12:00 | 63101 | 5085.8446 | 328564.0871 | 59.75 | 1388.222
2016-06-21 13:00 | 65209 | 5800.004 | 329359.6407 | 59.75 | 1434.598
2016-06-21 14:00 | 67353 | 6768.2262 | 331387.7988 | 59.75 | 1481.766
2016-06-21 15:00 | 68690 | 7659.1409 | 331983.7488 | 59.75 | 1511.18
2016-06-21 16:00 | 69219 | 7903.4722 | 328298.6288 | 59.75 | 1522.818
2016-06-21 17:00 | 68643 | 8229.942 | 323816.3838 | 59.75 | 1510.146
2016-06-21 18:00 | 66564 | 9048.0193 | 319907.6211 | 59.75 | 1464.408
2016-06-21 19:00 | 64484 | 11622.4743 | 293408.1376 | 59.75 | 1418.648
2016-06-21 20:00 | 62864 | 13437.4854 | 269069.0866 | 59.76 | 1320.144
2016-06-21 21:00 | 61444 | 11108.6105 | 269805.0866 | 59.76 | 1290.324
2016-06-21 22:00 | 57207 | 10775.3356 | 247354.0989 | 59.78 | 1086.933
2016-06-21 23:00 | 52377 | 11010.7937 | 224302.6425 | 59.77 | 1047.54
2016-06-22 | 47847 | 9287.2384 | 219802.6425 | 59.77 | 956.94
2016-06-22 01:00 | 45263 | 9027.0264 | 219802.6425 | 59.78 | 859.997
2016-06-22 02:00 | 43185 | 8975.4605 | 219802.6425 | 59.78 | 820.515
2016-06-22 03:00 | 41800 | 8042.087 | 219802.6425 | 59.78 | 794.2
2016-06-22 04:00 | 41505 | 6909.9142 | 219802.6425 | 59.78 | 788.595
2016-06-22 05:00 | 42520 | 6146.5627 | 219802.6425 | 59.78 | 807.88
2016-06-22 06:00 | 44117 | 4793.8705 | 219802.6425 | 59.77 | 882.34
2016-06-22 07:00 | 46247 | 4791.3447 | 219111.0425 | 59.77 | 924.94
2016-06-22 08:00 | 49365 | 4843.1233 | 239328.2909 | 59.78 | 937.935
2016-06-22 09:00 | 53052 | 4089.8898 | 264792.6244 | 59.76 | 1114.092
2016-06-22 10:00 | 57024 | 4197.1747 | 289128.7206 | 59.75 | 1254.528
2016-06-22 11:00 | 60702 | 4653.9675 | 317201.3601 | 59.75 | 1335.444
2016-06-22 12:00 | 63574 | 5682.6939 | 323701.1244 | 59.75 | 1398.628
2016-06-22 13:00 | 65413 | 5383.6394 | 326529.0652 | 59.75 | 1439.086
2016-06-22 14:00 | 67398 | 5932.4173 | 329991.5875 | 59.75 | 1482.756
2016-06-22 15:00 | 68291 | 6599.8838 | 330080.1975 | 59.75 | 1502.402
2016-06-22 16:00 | 68343 | 6207.1613 | 331290.6343 | 59.75 | 1503.546
2016-06-22 17:00 | 67289 | 7185.0657 | 329782.4039 | 59.75 | 1480.358
2016-06-22 18:00 | 65259 | 7795.2987 | 326096.3604 | 59.75 | 1435.698
2016-06-22 19:00 | 63917 | 9744.4729 | 302484.0609 | 59.75 | 1406.174
2016-06-22 20:00 | 61670 | 11696.0842 | 273253.6392 | 59.76 | 1295.07
2016-06-22 21:00 | 60330 | 11267.6497 | 268110.2444 | 59.76 | 1266.93
2016-06-22 22:00 | 56661 | 11834.4893 | 239043.8109 | 59.78 | 1076.559
2016-06-22 23:00 | 51920 | 11062.7538 | 219793.6625 | 59.77 | 1038.4
2016-06-23 | 46325 | 10974.7504 | 215156.1625 | 59.78 | 880.175
2016-06-23 01:00 | 43732 | 10718.5701 | 215156.1625 | 59.78 | 830.908
2016-06-23 02:00 | 41835 | 9808.6298 | 215156.1625 | 59.77 | 836.7
2016-06-23 03:00 | 40579 | 8110.8549 | 215156.1625 | 59.77 | 811.58
2016-06-23 04:00 | 40204 | 6599.6568 | 215156.1625 | 59.78 | 763.876
2016-06-23 05:00 | 41255 | 5459.0283 | 213579.3925 | 59.78 | 783.845
2016-06-23 06:00 | 43223 | 4926.0465 | 213579.3925 | 59.77 | 864.46
2016-06-23 07:00 | 44725 | 4184.4401 | 222521.5425 | 59.77 | 894.5
2016-06-23 08:00 | 47538 | 3567.4384 | 247822.9989 | 59.78 | 903.222
2016-06-23 09:00 | 51229 | 3422.5548 | 271787.9866 | 59.76 | 1075.809
2016-06-23 10:00 | 54999 | 3171.811 | 300404.1521 | 59.76 | 1154.979
2016-06-23 11:00 | 58420 | 3011.028 | 325022.3104 | 59.75 | 1285.24
2016-06-23 12:00 | 61124 | 2532.3499 | 329430.4279 | 59.75 | 1344.728
2016-06-23 13:00 | 63216 | 2843.3707 | 330758.7344 | 59.75 | 1390.752
2016-06-23 14:00 | 64724 | 3472.3734 | 330758.7344 | 59.75 | 1423.928
2016-06-23 15:00 | 64632 | 3921.4858 | 330478.7344 | 59.75 | 1421.904
2016-06-23 16:00 | 64701 | 4971.4365 | 331603.9539 | 59.75 | 1423.422
2016-06-23 17:00 | 64958 | 7416.2635 | 325296.5834 | 59.75 | 1429.076
2016-06-23 18:00 | 63210 | 7957.5482 | 317279.9589 | 59.75 | 1390.62
2016-06-23 19:00 | 61462 | 7922.5177 | 303474.3626 | 59.75 | 1352.164
2016-06-23 20:00 | 59409 | 7125.151 | 294071.6606 | 59.76 | 1247.589
2016-06-23 21:00 | 58139 | 7123.0325 | 284650.0346 | 59.76 | 1220.919
2016-06-23 22:00 | 54390 | 5963.4096 | 267884.7592 | 59.76 | 1142.19
2016-06-23 23:00 | 49949 | 5443.0938 | 242634.9909 | 59.78 | 949.031
2016-06-24 | 46658 | 6163.2398 | 235833.6649 | 59.77 | 933.16
2016-06-24 01:00 | 44134 | 6026.5155 | 232675.2649 | 59.77 | 882.68
2016-06-24 02:00 | 42334 | 5845.0615 | 232675.2649 | 59.78 | 804.346
2016-06-24 03:00 | 41304 | 6132.1305 | 232675.2649 | 59.78 | 784.776
2016-06-24 04:00 | 40925 | 4948.7616 | 232675.2649 | 59.78 | 777.575
2016-06-24 05:00 | 41972 | 4162.5086 | 233477.7049 | 59.77 | 839.44
2016-06-24 06:00 | 43776 | 3309.7718 | 235314.5174 | 59.77 | 875.52
2016-06-24 07:00 | 44998 | 1689.83 | 235910.4674 | 59.78 | 854.962
2016-06-24 08:00 | 46984 | 710.3431 | 250615.7754 | 59.78 | 892.696
2016-06-24 09:00 | 49746 | 964.0366 | 268916.3357 | 59.76 | 1044.666
2016-06-24 10:00 | 52923 | 1183.2422 | 290789.7083 | 59.76 | 1111.383
2016-06-24 11:00 | 56059 | 1426.2255 | 315371.3974 | 59.75 | 1233.298
2016-06-24 12:00 | 58560 | 1731.7821 | 322620.4201 | 59.75 | 1288.32
2016-06-24 13:00 | 60692 | 2271.0032 | 323356.3249 | 59.75 | 1335.224
2016-06-24 14:00 | 61985 | 2312.8901 | 325667.6226 | 59.75 | 1363.67
2016-06-24 15:00 | 62511 | 1836.7304 | 325947.6226 | 59.75 | 1375.242
2016-06-24 16:00 | 62690 | 1957.5915 | 325947.6226 | 59.75 | 1379.18
2016-06-24 17:00 | 62208 | 2980.4642 | 325024.7736 | 59.75 | 1368.576
2016-06-24 18:00 | 60058 | 3469.9626 | 321521.7181 | 59.75 | 1321.276
2016-06-24 19:00 | 57907 | 4754.071 | 296757.041 | 59.75 | 1273.954
2016-06-24 20:00 | 56215 | 6642.949 | 269605.1263 | 59.76 | 1180.515
2016-06-24 21:00 | 54935 | 6105.8572 | 267394.6589 | 59.76 | 1153.635
2016-06-24 22:00 | 51500 | 4453.4172 | 253915.6481 | 59.78 | 978.5
2016-06-24 23:00 | 47417 | 5328.4507 | 228622.0226 | 59.77 | 948.34
2016-06-25 | 47041 | 5589.3078 | 223087.3026 | 59.77 | 940.82
2016-06-25 01:00 | 44540 | 4805.4488 | 223087.3026 | 59.77 | 890.8
2016-06-25 02:00 | 42890 | 4266.1081 | 223087.3026 | 59.77 | 857.8
2016-06-25 03:00 | 41948 | 4824.0678 | 223087.3026 | 59.78 | 797.012
2016-06-25 04:00 | 41929 | 4684.1522 | 223087.3026 | 59.78 | 796.651
2016-06-25 05:00 | 43246 | 4469.8139 | 227020.0326 | 59.77 | 864.92
2016-06-25 06:00 | 44988 | 4584.3564 | 227570.7201 | 59.77 | 899.76
2016-06-25 07:00 | 46731 | 4628.8847 | 227570.7201 | 59.77 | 934.62
2016-06-25 08:00 | 49783 | 4850.5528 | 244786.8661 | 59.78 | 945.877
2016-06-25 09:00 | 53366 | 3541.1212 | 271803.6605 | 59.76 | 1120.686
2016-06-25 10:00 | 57037 | 3312.9233 | 302917.8876 | 59.75 | 1254.814
2016-06-25 11:00 | 60085 | 2623.6724 | 325456.4673 | 59.75 | 1321.87
2016-06-25 12:00 | 62259 | 1798.3725 | 334016.236 | 59.75 | 1369.698
2016-06-25 13:00 | 63936 | 1775.1415 | 337194.7557 | 59.75 | 1406.592
2016-06-25 14:00 | 64715 | 1973.758 | 337358.9157 | 59.75 | 1423.73
2016-06-25 15:00 | 64583 | 2423.9115 | 337358.9157 | 59.75 | 1420.826
2016-06-25 16:00 | 64662 | 2102.3937 | 334331.5657 | 59.75 | 1422.564
2016-06-25 17:00 | 64644 | 2373.0785 | 334331.5657 | 59.75 | 1422.168
2016-06-25 18:00 | 62716 | 3229.7419 | 331371.1863 | 59.75 | 1379.752
2016-06-25 19:00 | 60788 | 5345.3514 | 321500.314 | 59.75 | 1337.336
2016-06-25 20:00 | 58801 | 8622.0766 | 287985.5956 | 59.76 | 1234.821
2016-06-25 21:00 | 57707 | 7374.6766 | 287985.5956 | 59.76 | 1211.847
2016-06-25 22:00 | 54414 | 7958.1321 | 258733.4642 | 59.78 | 1033.866
2016-06-25 23:00 | 50685 | 7401.9756 | 244503.2739 | 59.78 | 963.015
2016-06-26 | 48099 | 6458.605 | 236170.5539 | 59.77 | 961.98
2016-06-26 01:00 | 45740 | 6187.149 | 236170.5539 | 59.77 | 914.8
2016-06-26 02:00 | 43948 | 6250.4851 | 233849.5394 | 59.77 | 878.96
2016-06-26 03:00 | 42820 | 6860.6236 | 231497.3794 | 59.78 | 813.58
2016-06-26 04:00 | 42331 | 7092.3474 | 231497.3794 | 59.78 | 804.289
2016-06-26 05:00 | 42466 | 6393.3321 | 231497.3794 | 59.78 | 806.854
2016-06-26 06:00 | 42517 | 5158.0003 | 229995.7294 | 59.78 | 807.823
2016-06-26 07:00 | 43834 | 5513.5714 | 229995.7294 | 59.77 | 876.68
2016-06-26 08:00 | 47930 | 5707.1892 | 244432.3694 | 59.77 | 958.6
2016-06-26 09:00 | 52450 | 5465.8103 | 276725.017 | 59.78 | 996.55
2016-06-26 10:00 | 56838 | 5833.9048 | 298536.018 | 59.76 | 1193.598
2016-06-26 11:00 | 60528 | 6755.3354 | 312649.2107 | 59.75 | 1331.616
2016-06-26 12:00 | 63761 | 6566.7728 | 328789.2638 | 59.75 | 1402.742
2016-06-26 13:00 | 65442 | 6946.6027 | 329139.4202 | 59.75 | 1439.724
2016-06-26 14:00 | 67127 | 7153.5911 | 331949.1736 | 59.75 | 1476.794
2016-06-26 15:00 | 68198 | 7023.4642 | 329789.7736 | 59.75 | 1500.356
2016-06-26 16:00 | 68708 | 6683.1984 | 332817.1236 | 59.75 | 1511.576
2016-06-26 17:00 | 68316 | 6547.6215 | 332817.1236 | 59.75 | 1502.952
2016-06-26 18:00 | 66530 | 7284.3088 | 330007.3702 | 59.75 | 1463.66
2016-06-26 19:00 | 64743 | 8853.4837 | 323210.6374 | 59.75 | 1424.346
2016-06-26 20:00 | 63026 | 10503.6844 | 298876.728 | 59.75 | 1386.572
2016-06-26 21:00 | 61280 | 10242.5637 | 289754.026 | 59.76 | 1286.88
2016-06-26 22:00 | 57781 | 10041.2606 | 264023.1246 | 59.76 | 1213.401
2016-06-26 23:00 | 53921 | 9662.9328 | 244518.6044 | 59.78 | 1024.499
2016-06-27 | 50682 | 9070.6483 | 224663.0464 | 59.77 | 1013.64
2016-06-27 01:00 | 47698 | 8842.7566 | 219221.7684 | 59.77 | 953.96
2016-06-27 02:00 | 45670 | 8884.8314 | 219221.7684 | 59.78 | 867.73
2016-06-27 03:00 | 44205 | 8900.0294 | 221573.9284 | 59.78 | 839.895
2016-06-27 04:00 | 43192 | 8795.1012 | 221573.9284 | 59.78 | 820.648
2016-06-27 05:00 | 42786 | 8668.1775 | 221573.9284 | 59.78 | 812.934
2016-06-27 06:00 | 42219 | 7723.5503 | 223075.5784 | 59.78 | 802.161
2016-06-27 07:00 | 43033 | 6985.4831 | 223075.5784 | 59.78 | 817.627
2016-06-27 08:00 | 46707 | 6603.0667 | 225396.5929 | 59.77 | 934.14
2016-06-27 09:00 | 51134 | 7135.5567 | 239590.2209 | 59.78 | 971.546
2016-06-27 10:00 | 55307 | 5452.1901 | 275394.4166 | 59.76 | 1161.447
2016-06-27 11:00 | 59239 | 5503.0251 | 302789.3526 | 59.75 | 1303.258
2016-06-27 12:00 | 62699 | 4856.533 | 324603.6517 | 59.75 | 1379.378
2016-06-27 13:00 | 64912 | 3559.1334 | 336262.0577 | 59.75 | 1428.064
2016-06-27 14:00 | 67102 | 3528.9245 | 338230.7413 | 59.75 | 1476.244
2016-06-27 15:00 | 68600 | 3685.1213 | 340390.1413 | 59.75 | 1509.2
2016-06-27 16:00 | 69379 | 3895.9818 | 340666.0712 | 59.75 | 1526.338
2016-06-27 17:00 | 69357 | 5477.1817 | 340223.3571 | 59.75 | 1525.854
2016-06-27 18:00 | 67596 | 5864.4632 | 336696.7786 | 59.75 | 1487.112
2016-06-27 19:00 | 65835 | 5442.1015 | 334342.1669 | 59.75 | 1448.37
2016-06-27 20:00 | 64338 | 4932.6421 | 334842.4669 | 59.75 | 1415.436
2016-06-27 21:00 | 62890 | 3758.0272 | 330457.7524 | 59.75 | 1383.58
2016-06-27 22:00 | 59106 | 4138.9444 | 310865.3759 | 59.75 | 1300.332
2016-06-27 23:00 | 54395 | 3477.0487 | 283470.4399 | 59.76 | 1142.295
2016-06-28 | 48516 | 2529.5707 | 264528.3623 | 59.78 | 921.804
2016-06-28 01:00 | 45835 | 1983.2721 | 263003.7623 | 59.78 | 870.865
2016-06-28 02:00 | 44055 | 1403.3498 | 263003.7623 | 59.78 | 837.045
2016-06-28 03:00 | 43082 | 1267.7738 | 263003.7623 | 59.77 | 861.64
2016-06-28 04:00 | 42909 | 868.236 | 263003.7623 | 59.77 | 858.18
2016-06-28 05:00 | 44181 | 726.8649 | 263003.7623 | 59.78 | 839.439
2016-06-28 06:00 | 45966 | 784.1979 | 266001.9623 | 59.78 | 873.354
2016-06-28 07:00 | 47605 | 466.3972 | 266001.9623 | 59.78 | 904.495
2016-06-28 08:00 | 50677 | 446.6337 | 281004.2315 | 59.76 | 1064.217
2016-06-28 09:00 | 54530 | 880.1961 | 309353.5695 | 59.75 | 1199.66
2016-06-28 10:00 | 58195 | 1277.2865 | 328752.9193 | 59.75 | 1280.29
2016-06-28 11:00 | 61480 | 1542.9697 | 332356.131 | 59.75 | 1352.56
2016-06-28 12:00 | 63614 | 2813.3192 | 333292.906 | 59.75 | 1399.508
2016-06-28 13:00 | 64861 | 3306.5572 | 333325.8093 | 59.75 | 1426.942
2016-06-28 14:00 | 66222 | 4322.0577 | 330449.1226 | 59.75 | 1456.884
2016-06-28 15:00 | 66234 | 5154.758 | 330294.706 | 59.75 | 1457.148
2016-06-28 16:00 | 64759 | 4944.3558 | 329182.8528 | 59.75 | 1424.698
2016-06-28 17:00 | 63316 | 6750.0569 | 325632.7273 | 59.75 | 1392.952
2016-06-28 18:00 | 61022 | 7341.3485 | 309636.7862 | 59.75 | 1342.484
2016-06-28 19:00 | 58729 | 4914.9316 | 308393.5997 | 59.75 | 1292.038
2016-06-28 20:00 | 57075 | 2945.1535 | 307225.5997 | 59.75 | 1255.65
2016-06-28 21:00 | 55723 | 2186.5677 | 306592.5929 | 59.75 | 1225.906
2016-06-28 22:00 | 52666 | 1594.3389 | 291589.2142 | 59.76 | 1105.986
2016-06-28 23:00 | 48631 | 1575.6675 | 263593.3384 | 59.78 | 923.989
2016-06-29 | 46084 | 2073.4557 | 256317.3889 | 59.78 | 875.596
2016-06-29 01:00 | 43992 | 2616.4348 | 256317.3889 | 59.77 | 879.84
2016-06-29 02:00 | 42601 | 2870.2139 | 256317.3889 | 59.77 | 852.02
2016-06-29 03:00 | 41840 | 2379.5594 | 256317.3889 | 59.77 | 836.8
2016-06-29 04:00 | 41882 | 1926.3517 | 256317.3889 | 59.77 | 837.64
2016-06-29 05:00 | 43303 | 1691.1788 | 255454.0889 | 59.77 | 866.06
2016-06-29 06:00 | 45374 | 1426.0843 | 255454.0889 | 59.78 | 862.106
2016-06-29 07:00 | 46942 | 1311.6659 | 256978.6889 | 59.78 | 891.898
2016-06-29 08:00 | 49219 | 1469.4182 | 268884.8282 | 59.76 | 1033.599
2016-06-29 09:00 | 51996 | 1513.7677 | 288138.2446 | 59.76 | 1091.916
2016-06-29 10:00 | 54812 | 2845.7634 | 299798.6486 | 59.76 | 1151.052
2016-06-29 11:00 | 57239 | 3756.176 | 305021.7692 | 59.75 | 1259.258
2016-06-29 12:00 | 59189 | 5471.2161 | 305932.8474 | 59.75 | 1302.158
2016-06-29 13:00 | 61144 | 7200.8636 | 305932.8474 | 59.75 | 1345.168
2016-06-29 14:00 | 62572 | 8893.3384 | 305932.8474 | 59.75 | 1376.584
2016-06-29 15:00 | 63331 | 11078.9923 | 302073.009 | 59.76 | 1329.951
2016-06-29 16:00 | 63323 | 11005.0168 | 302073.009 | 59.76 | 1329.783
2016-06-29 17:00 | 62147 | 11575.7547 | 292608.0506 | 59.76 | 1305.087
2016-06-29 18:00 | 59854 | 12526.8893 | 269296.3866 | 59.78 | 1137.226
2016-06-29 19:00 | 57560 | 11353.177 | 267808.5066 | 59.78 | 1093.64
2016-06-29 20:00 | 56785 | 9611.7416 | 269712.5066 | 59.78 | 1078.915
2016-06-29 21:00 | 56133 | 7290.4018 | 269712.5066 | 59.76 | 1178.793
2016-06-29 22:00 | 52816 | 5259.3651 | 262358.6444 | 59.76 | 1109.136
2016-06-29 23:00 | 48743 | 4267.8292 | 245747.5189 | 59.78 | 926.117
2016-06-30 | 44707 | 4309.4404 | 227359.6909 | 59.77 | 894.14
2016-06-30 01:00 | 42583 | 4536.0219 | 227359.6909 | 59.77 | 851.66
2016-06-30 02:00 | 41261 | 3898.0784 | 226741.6909 | 59.78 | 783.959
2016-06-30 03:00 | 40543 | 4111.8999 | 226741.6909 | 59.78 | 770.317
2016-06-30 04:00 | 40662 | 4681.5 | 226741.6909 | 59.78 | 772.578
2016-06-30 05:00 | 42110 | 4333.0745 | 227604.9909 | 59.77 | 842.2
2016-06-30 06:00 | 43890 | 4133.4733 | 227604.9909 | 59.77 | 877.8
2016-06-30 07:00 | 45127 | 3251.2196 | 227604.9909 | 59.77 | 902.54
2016-06-30 08:00 | 47051 | 2701.8068 | 239106.5989 | 59.78 | 893.969
2016-06-30 09:00 | 49561 | 3802.088 | 250108.9489 | 59.78 | 941.659
2016-06-30 10:00 | 51917 | 7260.7286 | 249372.9489 | 59.78 | 986.423
2016-06-30 11:00 | 53927 | 9440.5777 | 249084.9489 | 59.78 | 1024.613
2016-06-30 12:00 | 55417 | 10389.9882 | 249084.9489 | 59.78 | 1052.923
2016-06-30 13:00 | 56613 | 11626.1198 | 249084.9489 | 59.78 | 1075.647
2016-06-30 14:00 | 57665 | 11386.9521 | 249820.9489 | 59.78 | 1095.635
2016-06-30 15:00 | 57894 | 11982.6176 | 249084.9489 | 59.78 | 1099.986
2016-06-30 16:00 | 57356 | 12929.514 | 240231.7409 | 59.78 | 1089.764
2016-06-30 17:00 | 56202 | 12046.2959 | 235373.7909 | 59.78 | 1067.838
2016-06-30 18:00 | 54510 | 11769.0144 | 232545.6029 | 59.78 | 1035.69
2016-06-30 19:00 | 52818 | 10416.3133 | 231973.1029 | 59.77 | 1056.36
2016-06-30 20:00 | 52180 | 8607.1364 | 231688.5319 | 59.78 | 991.42
2016-06-30 21:00 | 51499 | 7113.9696 | 232424.5319 | 59.78 | 978.481
2016-06-30 22:00 | 48912 | 7278.0076 | 213728.4215 | 59.77 | 978.24
2016-06-30 23:00 | 45584 | 6056.3265 | 210372.0215 | 59.77 | 911.68
2016-07-01 | 42895 | 5445.4495 | 210372.0215 | 59.78 | 815.005
2016-07-01 01:00 | 41073 | 5450.7275 | 210372.0215 | 59.78 | 780.387
2016-07-01 02:00 | 39855 | 4795.0715 | 207517.7315 | 59.78 | 757.245
2016-07-01 03:00 | 39250 | 4650.222 | 207517.7315 | 59.78 | 745.75
2016-07-01 04:00 | 39445 | 4257.0911 | 207517.7315 | 59.78 | 749.455
2016-07-01 05:00 | 40873 | 4494.2896 | 207517.7315 | 59.78 | 776.587
2016-07-01 06:00 | 43146 | 4231.9234 | 207517.7315 | 59.77 | 862.92
2016-07-01 07:00 | 44541 | 3995.3603 | 213543.241 | 59.77 | 890.82
2016-07-01 08:00 | 46125 | 3543.9347 | 223670.341 | 59.78 | 876.375
2016-07-01 09:00 | 47863 | 3011.9351 | 235779.711 | 59.78 | 909.397
2016-07-01 10:00 | 49782 | 1973.954 | 260708.7902 | 59.76 | 1045.422
2016-07-01 11:00 | 51478 | 3211.3629 | 260996.7902 | 59.76 | 1081.038
2016-07-01 12:00 | 52615 | 3338.6331 | 269329.5102 | 59.76 | 1104.915
2016-07-01 13:00 | 53384 | 4224.9698 | 269329.5102 | 59.76 | 1121.064
2016-07-01 14:00 | 53800 | 4548.2109 | 268201.9344 | 59.76 | 1129.8
2016-07-01 15:00 | 54184 | 6959.7501 | 268673.1929 | 59.78 | 1029.496
2016-07-01 16:00 | 54708 | 7153.1335 | 268673.1929 | 59.76 | 1148.868
2016-07-01 17:00 | 54799 | 7628.6229 | 265316.7929 | 59.78 | 1041.181
2016-07-01 18:00 | 53900 | 8523.679 | 257130.5901 | 59.78 | 1024.1
2016-07-01 19:00 | 53001 | 7827.4967 | 257703.0901 | 59.78 | 1007.019
2016-07-01 20:00 | 52754 | 6999.4371 | 257987.6611 | 59.78 | 1002.326
2016-07-01 21:00 | 52356 | 5360.8656 | 257987.6611 | 59.78 | 994.764
2016-07-01 22:00 | 49881 | 5009.0377 | 241180.4931 | 59.78 | 947.739
2016-07-01 23:00 | 46419 | 3721.4314 | 238137.6851 | 59.78 | 881.961
2016-07-02 | 45270 | 3490.3513 | 238137.6851 | 59.77 | 905.4
2016-07-02 01:00 | 44494 | 3524.1473 | 238137.6851 | 59.77 | 889.88
2016-07-02 02:00 | 43248 | 2629.0431 | 236180.4571 | 59.77 | 864.96
2016-07-02 03:00 | 42478 | 2608.6761 | 236180.4571 | 59.77 | 849.56
2016-07-02 04:00 | 42530 | 2496.7935 | 236180.4571 | 59.77 | 850.6
2016-07-02 05:00 | 43899 | 2146.6971 | 236180.4571 | 59.77 | 877.98
2016-07-02 06:00 | 45961 | 1705.1985 | 238752.0066 | 59.78 | 873.259
2016-07-02 07:00 | 47478 | 1786.3826 | 249778.527 | 59.78 | 902.082
2016-07-02 08:00 | 49313 | 2039.9871 | 268146.02 | 59.78 | 936.947
2016-07-02 09:00 | 51387 | 2946.3809 | 270655.574 | 59.76 | 1079.127
2016-07-02 10:00 | 53412 | 3922.6369 | 279665.922 | 59.76 | 1121.652
2016-07-02 11:00 | 55209 | 4662.6225 | 283498.642 | 59.76 | 1159.389
2016-07-02 12:00 | 56522 | 4296.6652 | 291872.0208 | 59.76 | 1186.962
2016-07-02 13:00 | 57067 | 4317.163 | 291872.0208 | 59.75 | 1255.474
2016-07-02 14:00 | 57073 | 5404.9959 | 291698.0631 | 59.76 | 1198.533
2016-07-02 15:00 | 56349 | 6263.8981 | 278421.5427 | 59.76 | 1183.329
2016-07-02 16:00 | 55802 | 8092.1463 | 260112.0397 | 59.76 | 1171.842
2016-07-02 17:00 | 54513 | 7516.1803 | 254881.5157 | 59.78 | 1035.747
2016-07-02 18:00 | 52907 | 7908.4446 | 254881.5157 | 59.78 | 1005.233
2016-07-02 19:00 | 51301 | 6408.1066 | 254881.5157 | 59.78 | 974.719
2016-07-02 20:00 | 51436 | 5083.7067 | 254881.5157 | 59.78 | 977.284
2016-07-02 21:00 | 51441 | 3853.0705 | 255718.4057 | 59.76 | 1080.261
2016-07-02 22:00 | 49682 | 3664.5868 | 249738.1209 | 59.78 | 943.958
2016-07-02 23:00 | 47036 | 3628.0881 | 236017.5509 | 59.78 | 893.684
2016-07-03 | 45784 | 3412.5633 | 227394.9629 | 59.77 | 915.68
2016-07-03 01:00 | 43945 | 3881.489 | 223390.3749 | 59.77 | 878.9
2016-07-03 02:00 | 42509 | 4330.4597 | 223390.3749 | 59.77 | 850.18
2016-07-03 03:00 | 41757 | 3878.0983 | 223390.3749 | 59.77 | 835.14
2016-07-03 04:00 | 41388 | 4032.3317 | 223390.3749 | 59.78 | 786.372
2016-07-03 05:00 | 41841 | 4438.2474 | 223390.3749 | 59.78 | 794.979
2016-07-03 06:00 | 42594 | 4665.5793 | 223390.3749 | 59.77 | 851.88
2016-07-03 07:00 | 43563 | 6790.3828 | 221396.8249 | 59.78 | 827.697
2016-07-03 08:00 | 46339 | 9085.0624 | 223354.0529 | 59.78 | 880.441
2016-07-03 09:00 | 49836 | 8818.3626 | 226710.4529 | 59.77 | 996.72
2016-07-03 10:00 | 53163 | 9039.7259 | 247325.1869 | 59.78 | 1010.097
2016-07-03 11:00 | 55975 | 10842.0796 | 250927.2869 | 59.78 | 1063.525
2016-07-03 12:00 | 57586 | 12060.8958 | 250927.2869 | 59.78 | 1094.134
2016-07-03 13:00 | 58401 | 12080.6902 | 255947.7749 | 59.78 | 1109.619
2016-07-03 14:00 | 58756 | 12706.6194 | 255947.7749 | 59.78 | 1116.364
2016-07-03 15:00 | 59315 | 12605.3023 | 260447.7749 | 59.78 | 1126.985
2016-07-03 16:00 | 59499 | 11606.964 | 263755.3244 | 59.76 | 1249.479
2016-07-03 17:00 | 59117 | 11215.4945 | 263755.3244 | 59.76 | 1241.457
2016-07-03 18:00 | 57431 | 11594.5795 | 250383.0284 | 59.78 | 1091.189
2016-07-03 19:00 | 55746 | 10360.2793 | 249647.0284 | 59.78 | 1059.174
2016-07-03 20:00 | 54745 | 9220.4524 | 249647.0284 | 59.78 | 1040.155
2016-07-03 21:00 | 54334 | 8479.5579 | 250656.4082 | 59.78 | 1032.346
2016-07-03 22:00 | 52369 | 9559.265 | 232261.3916 | 59.78 | 995.011
2016-07-03 23:00 | 49921 | 8753.9117 | 222512.3216 | 59.77 | 998.42
2016-07-04 | 44932 | 8525.3702 | 185883.5758 | 59.78 | 853.708
2016-07-04 01:00 | 42980 | 8917.2763 | 182276.2558 | 59.78 | 816.62
2016-07-04 02:00 | 41492 | 9215.4982 | 182276.2558 | 59.77 | 829.84
2016-07-04 03:00 | 40488 | 8735.1582 | 182276.2558 | 59.77 | 809.76
2016-07-04 04:00 | 39888 | 8896.0052 | 182276.2558 | 59.77 | 797.76
2016-07-04 05:00 | 39840 | 8261.0522 | 182276.2558 | 59.77 | 796.8
2016-07-04 06:00 | 39835 | 7531.2091 | 182276.2558 | 59.77 | 796.7
2016-07-04 07:00 | 40436 | 8107.0206 | 184269.8058 | 59.77 | 808.72
2016-07-04 08:00 | 43371 | 8872.2577 | 184269.8058 | 59.78 | 824.049
2016-07-04 09:00 | 46884 | 7068.3118 | 211322.4818 | 59.77 | 937.68
2016-07-04 10:00 | 50509 | 7860.5288 | 231539.209 | 59.78 | 959.671
2016-07-04 11:00 | 53864 | 9911.6631 | 240068.687 | 59.78 | 1023.416
2016-07-04 12:00 | 56771 | 9482.9152 | 265940.759 | 59.78 | 1078.649
2016-07-04 13:00 | 58891 | 8606.9848 | 288820.125 | 59.76 | 1236.711
2016-07-04 14:00 | 60588 | 9744.7983 | 290732.525 | 59.76 | 1272.348
2016-07-04 15:00 | 61601 | 9911.8123 | 292644.925 | 59.76 | 1293.621
2016-07-04 16:00 | 62121 | 9038.2321 | 293624.909 | 59.75 | 1366.662
2016-07-04 17:00 | 61865 | 9246.0691 | 293624.909 | 59.75 | 1361.03
2016-07-04 18:00 | 59773 | 9510.8369 | 283728.9082 | 59.76 | 1255.233
2016-07-04 19:00 | 57682 | 8351.614 | 280686.1002 | 59.76 | 1211.322
2016-07-04 20:00 | 55526 | 7458.066 | 269538.4542 | 59.76 | 1166.046
2016-07-04 21:00 | 54055 | 7134.9241 | 258445.7682 | 59.78 | 1027.045
2016-07-04 22:00 | 52014 | 6467.5841 | 246659.0882 | 59.78 | 988.266
2016-07-04 23:00 | 49738 | 6763.5635 | 236488.3502 | 59.78 | 945.022
2016-07-05 | 46518 | 9227.2363 | 208235.8218 | 59.78 | 883.842
2016-07-05 01:00 | 44266 | 9125.4911 | 205103.4229 | 59.78 | 841.054
2016-07-05 02:00 | 42643 | 8211.1333 | 205103.4229 | 59.78 | 810.217
2016-07-05 03:00 | 41578 | 7139.3332 | 203967.4229 | 59.78 | 789.982
2016-07-05 04:00 | 41196 | 6363.7552 | 203967.4229 | 59.78 | 782.724
2016-07-05 05:00 | 41544 | 5570.5828 | 203967.4229 | 59.78 | 789.336
2016-07-05 06:00 | 41779 | 4877.8639 | 203967.4229 | 59.78 | 793.801
2016-07-05 07:00 | 42431 | 6158.9751 | 203376.4149 | 59.78 | 806.189
2016-07-05 08:00 | 45076 | 7871.3363 | 203376.4149 | 59.78 | 856.444
2016-07-05 09:00 | 48963 | 6691.2609 | 232643.8241 | 59.77 | 979.26
2016-07-05 10:00 | 53135 | 6399.4193 | 261341.0999 | 59.78 | 1009.565
2016-07-05 11:00 | 56941 | 6453.4828 | 284903.0301 | 59.76 | 1195.761
2016-07-05 12:00 | 60160 | 5842.8242 | 308631.5616 | 59.75 | 1323.52
2016-07-05 13:00 | 62822 | 5287.1612 | 326196.5605 | 59.75 | 1382.084
2016-07-05 14:00 | 64727 | 6147.8691 | 327107.6387 | 59.75 | 1423.994
2016-07-05 15:00 | 66129 | 5964.5228 | 330524.7067 | 59.75 | 1454.838
2016-07-05 16:00 | 67027 | 5288.8568 | 330557.61 | 59.75 | 1474.594
2016-07-05 17:00 | 66663 | 6386.5402 | 330524.7067 | 59.75 | 1466.586
2016-07-05 18:00 | 64713 | 7583.9919 | 324427.8271 | 59.75 | 1423.686
2016-07-05 19:00 | 62763 | 5759.6419 | 324427.8271 | 59.75 | 1380.786
2016-07-05 20:00 | 60691 | 4330.5213 | 321368.4996 | 59.75 | 1335.202
2016-07-05 21:00 | 59257 | 4314.5821 | 308667.5837 | 59.75 | 1303.654
2016-07-05 22:00 | 55523 | 3530.0739 | 282723.7197 | 59.76 | 1165.983
2016-07-05 23:00 | 50917 | 2292.3311 | 267827.0495 | 59.76 | 1069.257
2016-07-06 | 45005 | 1558.6164 | 238224.7741 | 59.78 | 855.095
2016-07-06 01:00 | 42378 | 1256.451 | 241357.1729 | 59.77 | 847.56
2016-07-06 02:00 | 40822 | 1759.6724 | 241357.1729 | 59.77 | 816.44
2016-07-06 03:00 | 39862 | 1862.098 | 242493.1729 | 59.77 | 797.24
2016-07-06 04:00 | 39697 | 1565.5537 | 242493.1729 | 59.77 | 793.94
2016-07-06 05:00 | 40893 | 1166.4864 | 242493.1729 | 59.77 | 817.86
2016-07-06 06:00 | 42782 | 708.8112 | 242493.1729 | 59.77 | 855.64
2016-07-06 07:00 | 44457 | 837.3042 | 243084.1809 | 59.78 | 844.683
2016-07-06 08:00 | 47705 | 1282.9191 | 256857.0189 | 59.78 | 906.395
2016-07-06 09:00 | 51448 | 1149.3327 | 282444.2592 | 59.76 | 1080.408
2016-07-06 10:00 | 55584 | 1415.1047 | 303852.9046 | 59.75 | 1222.848
2016-07-06 11:00 | 59495 | 2085.2932 | 324607.8981 | 59.75 | 1308.89
2016-07-06 12:00 | 62445 | 2411.3754 | 342415.694 | 59.75 | 1373.79
2016-07-06 13:00 | 64730 | 2471.7095 | 343022.3037 | 59.75 | 1424.06
2016-07-06 14:00 | 65987 | 1827.5041 | 342086.5467 | 59.75 | 1451.714
2016-07-06 15:00 | 66341 | 2465.6855 | 342086.5467 | 59.75 | 1459.502
2016-07-06 16:00 | 66005 | 3403.6413 | 340509.7767 | 59.75 | 1452.11
2016-07-06 17:00 | 65025 | 3611.3025 | 339058.0337 | 59.75 | 1430.55
2016-07-06 18:00 | 63225 | 4554.4427 | 334730.159 | 59.75 | 1390.95
2016-07-06 19:00 | 61426 | 5071.187 | 325495.5565 | 59.75 | 1351.372
2016-07-06 20:00 | 59303 | 5771.8484 | 308549.0426 | 59.75 | 1304.666
2016-07-06 21:00 | 57793 | 3416.09 | 308725.0426 | 59.75 | 1271.446
2016-07-06 22:00 | 53921 | 2402.1982 | 288705.1666 | 59.76 | 1132.341
2016-07-06 23:00 | 49457 | 2490.7013 | 260216.4284 | 59.78 | 939.683
2016-07-07 | 44186 | 3021.8131 | 239485.6109 | 59.77 | 883.72
2016-07-07 01:00 | 41629 | 2795.2418 | 238336.7189 | 59.77 | 832.58
2016-07-07 02:00 | 40007 | 2421.6821 | 238336.7189 | 59.77 | 800.14
2016-07-07 03:00 | 39057 | 2119.2398 | 238336.7189 | 59.78 | 742.083
2016-07-07 04:00 | 38887 | 2057.8874 | 238336.7189 | 59.78 | 738.853
2016-07-07 05:00 | 40046 | 1886.6211 | 238219.8389 | 59.77 | 800.92
2016-07-07 06:00 | 41916 | 1702.1589 | 238219.8389 | 59.77 | 838.32
2016-07-07 07:00 | 43169 | 1050.0025 | 238032.6389 | 59.77 | 863.38
2016-07-07 08:00 | 45639 | 792.7464 | 251155.2269 | 59.78 | 867.141
2016-07-07 09:00 | 48679 | 995.3692 | 269505.4733 | 59.76 | 1022.259
2016-07-07 10:00 | 51891 | 1324.3224 | 287561.1253 | 59.76 | 1089.711
2016-07-07 11:00 | 54830 | 1700.9138 | 307371.4853 | 59.75 | 1206.26
2016-07-07 12:00 | 56641 | 2262.3869 | 309029.8693 | 59.75 | 1246.102
2016-07-07 13:00 | 58298 | 2645.5051 | 314304.2369 | 59.75 | 1282.556
2016-07-07 14:00 | 59751 | 3047.8227 | 315894.2436 | 59.75 | 1314.522
2016-07-07 15:00 | 61183 | 3065.8337 | 315927.147 | 59.75 | 1346.026
2016-07-07 16:00 | 61533 | 4254.3694 | 317405.2069 | 59.75 | 1353.726
2016-07-07 17:00 | 60683 | 5319.6883 | 311557.8662 | 59.75 | 1335.026
2016-07-07 18:00 | 58986 | 6433.7948 | 294690.7746 | 59.75 | 1297.692
2016-07-07 19:00 | 57289 | 7849.8002 | 270419.9472 | 59.76 | 1203.069
2016-07-07 20:00 | 55632 | 8483.2005 | 269741.5472 | 59.78 | 1057.008
2016-07-07 21:00 | 54276 | 4842.5117 | 268967.2172 | 59.76 | 1139.796
2016-07-07 22:00 | 50890 | 4932.3905 | 245178.2089 | 59.78 | 966.91
2016-07-07 23:00 | 46943 | 3195.7785 | 236425.8589 | 59.78 | 891.917
2016-07-08 | 44385 | 2262.7409 | 233597.6709 | 59.77 | 887.7
2016-07-08 01:00 | 42182 | 2002.0937 | 233597.6709 | 59.77 | 843.64
2016-07-08 02:00 | 40651 | 2135.3044 | 233597.6709 | 59.77 | 813.02
2016-07-08 03:00 | 39902 | 1885.3106 | 233597.6709 | 59.77 | 798.04
2016-07-08 04:00 | 39981 | 1544.741 | 233006.6629 | 59.77 | 799.62
2016-07-08 05:00 | 41250 | 1372.2927 | 233123.5429 | 59.77 | 825
2016-07-08 06:00 | 43360 | 1457.0607 | 234272.4349 | 59.77 | 867.2
2016-07-08 07:00 | 44546 | 1888.2914 | 234272.4349 | 59.78 | 846.374
2016-07-08 08:00 | 45902 | 2433.3628 | 234272.4349 | 59.78 | 872.138
2016-07-08 09:00 | 47668 | 3397.4496 | 244130.6644 | 59.78 | 905.692
2016-07-08 10:00 | 49684 | 4373.128 | 246225.9144 | 59.78 | 943.996
2016-07-08 11:00 | 51824 | 6958.5714 | 248318.1024 | 59.78 | 984.656
2016-07-08 12:00 | 53098 | 6604.3637 | 251920.2024 | 59.78 | 1008.862
2016-07-08 13:00 | 54598 | 6871.4026 | 257676.6904 | 59.76 | 1146.558
2016-07-08 14:00 | 55190 | 7567.7673 | 257803.9904 | 59.76 | 1158.99
2016-07-08 15:00 | 55284 | 7389.6083 | 257803.9904 | 59.76 | 1160.964
2016-07-08 16:00 | 54331 | 6635.9859 | 257803.9904 | 59.76 | 1140.951
2016-07-08 17:00 | 52794 | 6432.7901 | 254350.0304 | 59.78 | 1003.086
2016-07-08 18:00 | 51955 | 7452.9707 | 251778.4809 | 59.78 | 987.145
2016-07-08 19:00 | 51115 | 6478.058 | 247945.7609 | 59.78 | 971.185
2016-07-08 20:00 | 50901 | 5793.3397 | 247945.7609 | 59.78 | 967.119
2016-07-08 21:00 | 50204 | 3398.3796 | 249456.0909 | 59.78 | 953.876
2016-07-08 22:00 | 47776 | 3311.2721 | 234947.2529 | 59.78 | 907.744
2016-07-08 23:00 | 44499 | 2222.0529 | 232855.0649 | 59.77 | 889.98
2016-07-09 | 43232 | 2119.1153 | 232424.2649 | 59.77 | 864.64
2016-07-09 01:00 | 41355 | 2128.2664 | 231865.1206 | 59.77 | 827.1
2016-07-09 02:00 | 40147 | 1625.3293 | 231865.1206 | 59.77 | 802.94
2016-07-09 03:00 | 39435 | 1624.033 | 231865.1206 | 59.77 | 788.7
2016-07-09 04:00 | 39540 | 1259.3924 | 232456.1286 | 59.77 | 790.8
2016-07-09 05:00 | 40890 | 908.2341 | 232456.1286 | 59.77 | 817.8
2016-07-09 06:00 | 43068 | 798.2748 | 232456.1286 | 59.77 | 861.36
2016-07-09 07:00 | 44463 | 1348.3763 | 232456.1286 | 59.78 | 844.797
2016-07-09 08:00 | 46908 | 2454.9239 | 238150.4166 | 59.78 | 891.252
2016-07-09 09:00 | 49769 | 2404.1027 | 260107.8346 | 59.78 | 945.611
2016-07-09 10:00 | 53139 | 2805.5895 | 277477.3645 | 59.76 | 1115.919
2016-07-09 11:00 | 55989 | 4321.0952 | 286626.7665 | 59.76 | 1175.769
2016-07-09 12:00 | 58129 | 4641.7713 | 297062.9693 | 59.75 | 1278.838
2016-07-09 13:00 | 60054 | 4384.4064 | 313270.2687 | 59.75 | 1321.188
2016-07-09 14:00 | 60945 | 4393.275 | 315217.7071 | 59.75 | 1340.79
2016-07-09 15:00 | 61476 | 4633.6442 | 315217.7071 | 59.75 | 1352.472
2016-07-09 16:00 | 61625 | 4916.5929 | 315217.7071 | 59.75 | 1355.75
2016-07-09 17:00 | 60479 | 4932.7962 | 312716.0787 | 59.75 | 1330.538
2016-07-09 18:00 | 58116 | 4746.1768 | 298723.0983 | 59.75 | 1278.552
2016-07-09 19:00 | 55753 | 3428.3892 | 292616.5043 | 59.76 | 1170.813
2016-07-09 20:00 | 54310 | 2709.8123 | 287976.2465 | 59.76 | 1140.51
2016-07-09 21:00 | 53257 | 2097.7016 | 279011.6078 | 59.76 | 1118.397
2016-07-09 22:00 | 50557 | 1521.1973 | 266445.7643 | 59.76 | 1061.697
2016-07-09 23:00 | 47259 | 1225.0171 | 249834.6389 | 59.78 | 897.921
2016-07-10 | 45464 | 896.9095 | 246619.9189 | 59.78 | 863.816
2016-07-10 01:00 | 43038 | 666.0566 | 242434.5432 | 59.77 | 860.76
2016-07-10 02:00 | 41420 | 757.3249 | 242434.5432 | 59.77 | 828.4
2016-07-10 03:00 | 40280 | 746.7202 | 239994.9432 | 59.77 | 805.6
2016-07-10 04:00 | 39806 | 696.6637 | 239994.9432 | 59.77 | 796.12
2016-07-10 05:00 | 40107 | 814.538 | 239994.9432 | 59.77 | 802.14
2016-07-10 06:00 | 40824 | 723.3186 | 239994.9432 | 59.77 | 816.48
2016-07-10 07:00 | 41634 | 900.5403 | 239994.9432 | 59.77 | 832.68
2016-07-10 08:00 | 44641 | 1071.1168 | 244477.1882 | 59.78 | 848.179
2016-07-10 09:00 | 48409 | 1746.1261 | 264148.6836 | 59.78 | 919.771
2016-07-10 10:00 | 52433 | 1986.205 | 292209.1198 | 59.76 | 1101.093
2016-07-10 11:00 | 56050 | 2156.9808 | 312112.5969 | 59.75 | 1233.1
2016-07-10 12:00 | 59295 | 2931.3937 | 328613.2046 | 59.75 | 1304.49
2016-07-10 13:00 | 61552 | 3794.0252 | 329832.9318 | 59.75 | 1354.144
2016-07-10 14:00 | 63149 | 3561.9019 | 332844.5423 | 59.75 | 1389.278
2016-07-10 15:00 | 63817 | 3324.2765 | 330362.9423 | 59.75 | 1403.974
2016-07-10 16:00 | 63951 | 3409.9328 | 330362.9423 | 59.75 | 1406.922
2016-07-10 17:00 | 63818 | 3410.1487 | 330917.1323 | 59.75 | 1403.996
2016-07-10 18:00 | 62173 | 3402.64 | 329994.2833 | 59.75 | 1367.806
2016-07-10 19:00 | 60528 | 4025.8321 | 327730.4436 | 59.75 | 1331.616
2016-07-10 20:00 | 58837 | 4495.6644 | 312722.0263 | 59.75 | 1294.414
2016-07-10 21:00 | 57732 | 4286.1273 | 305125.6996 | 59.75 | 1270.104
2016-07-10 22:00 | 54649 | 4431.8504 | 285073.0536 | 59.76 | 1147.629
2016-07-10 23:00 | 51054 | 5085.4595 | 258468.3154 | 59.78 | 970.026
2016-07-11 | 47728 | 6018.8254 | 227426.6029 | 59.77 | 954.56
2016-07-11 01:00 | 45188 | 6048.5123 | 212822.8925 | 59.77 | 903.76
2016-07-11 02:00 | 43375 | 6518.6043 | 212822.8925 | 59.78 | 824.125
2016-07-11 03:00 | 42090 | 6762.778 | 215262.4925 | 59.78 | 799.71
2016-07-11 04:00 | 41302 | 6895.7285 | 215262.4925 | 59.78 | 784.738
2016-07-11 05:00 | 41116 | 7097.4315 | 215262.4925 | 59.78 | 781.204
2016-07-11 06:00 | 41062 | 7522.4406 | 215262.4925 | 59.78 | 780.178
2016-07-11 07:00 | 41549 | 7165.2902 | 215262.4925 | 59.78 | 789.431
2016-07-11 08:00 | 45100 | 7121.2157 | 215262.4925 | 59.77 | 902
2016-07-11 09:00 | 49618 | 7146.134 | 229369.0729 | 59.77 | 992.36
2016-07-11 10:00 | 54063 | 7858.7045 | 250846.2189 | 59.78 | 1027.197
2016-07-11 11:00 | 58066 | 8109.2685 | 276433.4592 | 59.76 | 1219.386
2016-07-11 12:00 | 61560 | 8127.2692 | 303115.2865 | 59.75 | 1354.32
2016-07-11 13:00 | 64145 | 8567.6925 | 318642.6964 | 59.75 | 1411.19
2016-07-11 14:00 | 66193 | 7876.3876 | 329277.2764 | 59.75 | 1456.246
2016-07-11 15:00 | 66910 | 6119.6426 | 334758.7161 | 59.75 | 1472.02
2016-07-11 16:00 | 67856 | 5742.2576 | 336210.4591 | 59.75 | 1492.832
2016-07-11 17:00 | 68040 | 5607.5103 | 334273.4622 | 59.75 | 1496.88
2016-07-11 18:00 | 66921 | 5972.5729 | 331569.4591 | 59.75 | 1472.262
2016-07-11 19:00 | 65115 | 7247.6848 | 327853.8764 | 59.75 | 1432.53
2016-07-11 20:00 | 62697 | 8778.9536 | 312700.4945 | 59.75 | 1379.334
2016-07-11 21:00 | 61298 | 9094.677 | 297173.0846 | 59.76 | 1287.258
2016-07-11 22:00 | 57549 | 9095.583 | 268975.8644 | 59.76 | 1208.529
2016-07-11 23:00 | 53007 | 9392.8799 | 237677.1859 | 59.78 | 1007.133
2016-07-12 | 46335 | 9332.2933 | 214268.4875 | 59.78 | 880.365
2016-07-12 01:00 | 43914 | 8375.8041 | 212758.1675 | 59.78 | 834.366
2016-07-12 02:00 | 42323 | 7321.9853 | 212758.1675 | 59.78 | 804.137
2016-07-12 03:00 | 41483 | 7069.9611 | 212758.1675 | 59.78 | 788.177
2016-07-12 04:00 | 41547 | 7774.9129 | 212758.1675 | 59.78 | 789.393
2016-07-12 05:00 | 42767 | 7639.2309 | 212758.1675 | 59.78 | 812.573
2016-07-12 06:00 | 44628 | 7598.9429 | 212758.1675 | 59.78 | 847.932
2016-07-12 07:00 | 46318 | 8576.3663 | 212066.5675 | 59.77 | 926.36
2016-07-12 08:00 | 49372 | 9010.7673 | 221029.3675 | 59.77 | 987.44
2016-07-12 09:00 | 52920 | 9482.1184 | 240523.3559 | 59.78 | 1005.48
2016-07-12 10:00 | 56667 | 7919.5703 | 274541.9094 | 59.76 | 1190.007
2016-07-12 11:00 | 59765 | 6483.8368 | 305925.6176 | 59.75 | 1314.83
2016-07-12 12:00 | 62761 | 7600.6521 | 323534.4984 | 59.75 | 1380.742
2016-07-12 13:00 | 65044 | 7949.8007 | 330946.0102 | 59.75 | 1430.968
2016-07-12 14:00 | 66700 | 7337.935 | 333770.7717 | 59.75 | 1467.4
2016-07-12 15:00 | 67010 | 7837.4061 | 333770.7717 | 59.75 | 1474.22
2016-07-12 16:00 | 67368 | 7380.7573 | 325767.4748 | 59.75 | 1482.096
2016-07-12 17:00 | 66703 | 6903.5278 | 327615.8617 | 59.75 | 1467.466
2016-07-12 18:00 | 65499 | 7167.31 | 328183.7784 | 59.75 | 1440.978
2016-07-12 19:00 | 63608 | 6423.2549 | 326964.0512 | 59.75 | 1399.376
2016-07-12 20:00 | 61633 | 5976.8019 | 318164.1469 | 59.75 | 1355.926
2016-07-12 21:00 | 60258 | 5701.6574 | 309048.712 | 59.75 | 1325.676
2016-07-12 22:00 | 56316 | 5518.5555 | 278222.4616 | 59.76 | 1182.636
2016-07-12 23:00 | 51910 | 5013.0141 | 262211.4339 | 59.78 | 986.29
2016-07-13 | 47138 | 5482.5704 | 226723.7725 | 59.77 | 942.76
2016-07-13 01:00 | 44809 | 6689.6156 | 226723.7725 | 59.77 | 896.18
2016-07-13 02:00 | 43335 | 7219.5961 | 226723.7725 | 59.78 | 823.365
2016-07-13 03:00 | 42601 | 8182.8287 | 226723.7725 | 59.78 | 809.419
2016-07-13 04:00 | 42477 | 7628.7842 | 225216.612 | 59.78 | 807.063
2016-07-13 05:00 | 43755 | 7377.1424 | 225216.612 | 59.78 | 831.345
2016-07-13 06:00 | 45475 | 6511.9927 | 225216.612 | 59.77 | 909.5
2016-07-13 07:00 | 46611 | 6359.2743 | 227418.532 | 59.77 | 932.22
2016-07-13 08:00 | 48995 | 6330.5179 | 230772.2424 | 59.78 | 930.905
2016-07-13 09:00 | 52306 | 5960.067 | 253036.7934 | 59.78 | 993.814
2016-07-13 10:00 | 55880 | 5276.2576 | 278624.0336 | 59.76 | 1173.48
2016-07-13 11:00 | 59357 | 4610.7536 | 306014.1325 | 59.75 | 1305.854
2016-07-13 12:00 | 62315 | 4751.3067 | 324814.7865 | 59.75 | 1370.93
2016-07-13 13:00 | 64614 | 4762.5005 | 328123.2751 | 59.75 | 1421.508
2016-07-13 14:00 | 66448 | 5101.8392 | 329079.0275 | 59.75 | 1461.856
2016-07-13 15:00 | 66882 | 5734.3817 | 329079.0275 | 59.75 | 1471.404
2016-07-13 16:00 | 67309 | 5801.5525 | 337360.4341 | 59.75 | 1480.798
2016-07-13 17:00 | 66809 | 6048.9131 | 334874.0583 | 59.75 | 1469.798
2016-07-13 18:00 | 65488 | 6916.1629 | 331529.3085 | 59.75 | 1440.736
2016-07-13 19:00 | 63480 | 7198.7551 | 318647.963 | 59.75 | 1396.56
2016-07-13 20:00 | 61570 | 7389.5597 | 304490.637 | 59.75 | 1354.54
2016-07-13 21:00 | 60033 | 7282.9062 | 296792.897 | 59.75 | 1320.726
2016-07-13 22:00 | 56176 | 8235.127 | 261365.2234 | 59.76 | 1179.696
2016-07-13 23:00 | 51747 | 8331.0334 | 234935.2324 | 59.78 | 983.193
2016-07-14 | 45339 | 9106.6975 | 207558.922 | 59.78 | 861.441
2016-07-14 01:00 | 42978 | 7983.0511 | 207558.922 | 59.78 | 816.582
2016-07-14 02:00 | 41448 | 7700.8544 | 207558.922 | 59.78 | 787.512
2016-07-14 03:00 | 40539 | 7484.3227 | 207558.922 | 59.78 | 770.241
2016-07-14 04:00 | 40408 | 6457.0155 | 209066.0825 | 59.78 | 767.752
2016-07-14 05:00 | 41552 | 6510.9309 | 209066.0825 | 59.78 | 789.488
2016-07-14 06:00 | 43459 | 6218.8262 | 207770.4845 | 59.78 | 825.721
2016-07-14 07:00 | 44656 | 6638.0974 | 207770.4845 | 59.77 | 893.12
2016-07-14 08:00 | 46948 | 7323.4438 | 214483.2845 | 59.77 | 938.96
2016-07-14 09:00 | 50105 | 8504.381 | 229521.8749 | 59.77 | 1002.1
2016-07-14 10:00 | 53549 | 7895.4956 | 255951.8659 | 59.78 | 1017.431
2016-07-14 11:00 | 56703 | 8790.1218 | 269398.1338 | 59.76 | 1190.763
2016-07-14 12:00 | 59028 | 10249.9898 | 278712.5778 | 59.76 | 1239.588
2016-07-14 13:00 | 61666 | 10750.2123 | 298337.4666 | 59.76 | 1294.986
2016-07-14 14:00 | 63816 | 11053.1898 | 307551.682 | 59.75 | 1403.952
2016-07-14 15:00 | 65205 | 11154.7422 | 311114.4696 | 59.75 | 1434.51
2016-07-14 16:00 | 65742 | 9912.7369 | 311268.8863 | 59.75 | 1446.324
2016-07-14 17:00 | 65584 | 9751.1007 | 311203.0796 | 59.75 | 1442.848
2016-07-14 18:00 | 63812 | 10019.2759 | 309039.6342 | 59.75 | 1403.864
2016-07-14 19:00 | 62041 | 10465.1427 | 297596.5156 | 59.76 | 1302.861
2016-07-14 20:00 | 59667 | 10592.7315 | 284506.5621 | 59.76 | 1253.007
2016-07-14 21:00 | 58159 | 9271.334 | 275868.2761 | 59.76 | 1221.339
2016-07-14 22:00 | 54180 | 9710.5124 | 241368.4049 | 59.78 | 1029.42
2016-07-14 23:00 | 49795 | 9820.1589 | 215301.1969 | 59.77 | 995.9
2016-07-15 | 44977 | 9622.0806 | 203457.3901 | 59.78 | 854.563
2016-07-15 01:00 | 42481 | 8843.8344 | 201568.4401 | 59.78 | 807.139
2016-07-15 02:00 | 40880 | 8347.4821 | 201568.4401 | 59.78 | 776.72
2016-07-15 03:00 | 39750 | 7710.6751 | 201568.4401 | 59.77 | 795
2016-07-15 04:00 | 39413 | 6929.6146 | 201568.4401 | 59.77 | 788.26
2016-07-15 05:00 | 40247 | 6728.0454 | 201568.4401 | 59.78 | 764.693
2016-07-15 06:00 | 41714 | 6402.6036 | 202864.0381 | 59.78 | 792.566
2016-07-15 07:00 | 42783 | 4783.2442 | 204383.0381 | 59.77 | 855.66
2016-07-15 08:00 | 45547 | 3469.8064 | 230652.6015 | 59.77 | 910.94
2016-07-15 09:00 | 48948 | 2725.06 | 256533.669 | 59.78 | 930.012
2016-07-15 10:00 | 52508 | 2308.663 | 281979.5992 | 59.76 | 1102.668
2016-07-15 11:00 | 55534 | 4092.2063 | 291010.9132 | 59.76 | 1166.214
2016-07-15 12:00 | 58186 | 6245.7188 | 294992.9183 | 59.76 | 1221.906
2016-07-15 13:00 | 60831 | 7677.5285 | 298347.9903 | 59.75 | 1338.282
2016-07-15 14:00 | 62691 | 6818.7775 | 312343.8979 | 59.75 | 1379.202
2016-07-15 15:00 | 63828 | 6467.7489 | 316584.9925 | 59.75 | 1404.216
2016-07-15 16:00 | 64339 | 6359.3643 | 318879.3736 | 59.75 | 1415.458
2016-07-15 17:00 | 64059 | 5471.9301 | 318879.3736 | 59.75 | 1409.298
2016-07-15 18:00 | 62276 | 5687.9763 | 315236.685 | 59.75 | 1370.072
2016-07-15 19:00 | 60494 | 5076.0033 | 313815.403 | 59.75 | 1330.868
2016-07-15 20:00 | 58390 | 4550.5283 | 306880.6729 | 59.75 | 1284.58
2016-07-15 21:00 | 56768 | 3263.9131 | 303863.7309 | 59.75 | 1248.896
2016-07-15 22:00 | 52896 | 5160.1225 | 259743.7711 | 59.76 | 1110.816
2016-07-15 23:00 | 48564 | 5422.4618 | 239572.2457 | 59.78 | 922.716
2016-07-16 | 47047 | 4695.0818 | 228131.5007 | 59.77 | 940.94
2016-07-16 01:00 | 44260 | 5129.239 | 230020.4507 | 59.77 | 885.2
2016-07-16 02:00 | 42298 | 5512.2768 | 230020.4507 | 59.78 | 803.662
2016-07-16 03:00 | 40990 | 4737.5219 | 230020.4507 | 59.78 | 778.81
2016-07-16 04:00 | 40622 | 5270.3846 | 230020.4507 | 59.78 | 771.818
2016-07-16 05:00 | 41424 | 5038.3333 | 230020.4507 | 59.78 | 787.056
2016-07-16 06:00 | 42987 | 3728.5372 | 230020.4507 | 59.77 | 859.74
2016-07-16 07:00 | 44032 | 2660.0309 | 230020.4507 | 59.77 | 880.64
2016-07-16 08:00 | 46900 | 1910.2613 | 244626.9337 | 59.78 | 891.1
2016-07-16 09:00 | 50462 | 1953.8907 | 270214.1739 | 59.76 | 1059.702
2016-07-16 10:00 | 54525 | 3053.2949 | 285223.9013 | 59.76 | 1145.025
2016-07-16 11:00 | 57980 | 3080.5001 | 305780.8917 | 59.75 | 1275.56
2016-07-16 12:00 | 60858 | 3079.6974 | 331367.834 | 59.75 | 1338.876
2016-07-16 13:00 | 63742 | 2730.5847 | 337417.3577 | 59.75 | 1402.324
2016-07-16 14:00 | 65893 | 2413.8321 | 341026.0162 | 59.75 | 1449.646
2016-07-16 15:00 | 66481 | 2696.2228 | 342014.5261 | 59.75 | 1462.582
2016-07-16 16:00 | 66855 | 2364.0875 | 343404.7351 | 59.75 | 1470.81
2016-07-16 17:00 | 66458 | 2423.3241 | 343493.345 | 59.75 | 1462.076
2016-07-16 18:00 | 65069 | 2746.8416 | 341345.6775 | 59.75 | 1431.518
2016-07-16 19:00 | 62994 | 3269.1014 | 338615.9404 | 59.75 | 1385.868
2016-07-16 20:00 | 60722 | 3952.7616 | 320264.4215 | 59.75 | 1335.884
2016-07-16 21:00 | 58831 | 4010.2608 | 306264.3956 | 59.75 | 1294.282
2016-07-16 22:00 | 55061 | 4440.3062 | 274204.6662 | 59.76 | 1156.281
2016-07-16 23:00 | 50924 | 5316.9345 | 243467.1759 | 59.78 | 967.556
2016-07-17 | 49081 | 5750.9394 | 233290.6429 | 59.78 | 932.539
2016-07-17 01:00 | 46035 | 5836.8234 | 223488.6522 | 59.77 | 920.7
2016-07-17 02:00 | 43805 | 6291.4124 | 219946.5302 | 59.77 | 876.1
2016-07-17 03:00 | 42206 | 6477.4576 | 219946.5302 | 59.78 | 801.914
2016-07-17 04:00 | 41210 | 6269.6723 | 219946.5302 | 59.78 | 782.99
2016-07-17 05:00 | 41040 | 5849.3392 | 219946.5302 | 59.78 | 779.76
2016-07-17 06:00 | 41091 | 5294.6514 | 219327.1602 | 59.78 | 780.729
2016-07-17 07:00 | 41741 | 3281.5583 | 219327.1602 | 59.77 | 834.82
2016-07-17 08:00 | 45326 | 1681.2069 | 236219.8132 | 59.78 | 861.194
2016-07-17 09:00 | 49816 | 1302.9485 | 266267.5208 | 59.76 | 1046.136
2016-07-17 10:00 | 54397 | 1332.4773 | 297829.7712 | 59.75 | 1196.734
2016-07-17 11:00 | 58442 | 1016.0976 | 322499.5193 | 59.75 | 1285.724
2016-07-17 12:00 | 61858 | 1165.8672 | 334400.7788 | 59.75 | 1360.876
2016-07-17 13:00 | 64295 | 2165.3361 | 336139.3839 | 59.75 | 1414.49
2016-07-17 14:00 | 66143 | 2341.922 | 338280.1001 | 59.75 | 1455.146
2016-07-17 15:00 | 66826 | 2641.2006 | 338280.1001 | 59.75 | 1470.172
2016-07-17 16:00 | 67579 | 2475.5273 | 338280.1001 | 59.75 | 1486.738
2016-07-17 17:00 | 67058 | 2209.2873 | 338280.1001 | 59.75 | 1475.276
2016-07-17 18:00 | 65508 | 2705.8136 | 336314.4621 | 59.75 | 1441.176
2016-07-17 19:00 | 63270 | 3648.2963 | 331390.6886 | 59.75 | 1391.94
2016-07-17 20:00 | 60811 | 4735.2566 | 314237.9089 | 59.75 | 1337.842
2016-07-17 21:00 | 58851 | 5097.757 | 302151.9592 | 59.75 | 1294.722
2016-07-17 22:00 | 55206 | 7132.6026 | 262503.0186 | 59.76 | 1159.326
2016-07-17 23:00 | 51326 | 8160.2126 | 233022.4152 | 59.78 | 975.194
2016-07-18 | 50339 | 7140.764 | 228540.1702 | 59.78 | 956.441
2016-07-18 01:00 | 47559 | 6483.4756 | 223094.2718 | 59.77 | 951.18
2016-07-18 02:00 | 45251 | 6119.1185 | 225487.5018 | 59.77 | 905.02
2016-07-18 03:00 | 43604 | 6355.7794 | 225487.5018 | 59.78 | 828.476
2016-07-18 04:00 | 42585 | 7000.6505 | 225487.5018 | 59.78 | 809.115
2016-07-18 05:00 | 42201 | 6281.6012 | 225487.5018 | 59.78 | 801.819
2016-07-18 06:00 | 42005 | 5581.4556 | 226106.8718 | 59.78 | 798.095
2016-07-18 07:00 | 42475 | 4445.092 | 226106.8718 | 59.77 | 849.5
2016-07-18 08:00 | 46035 | 3500.2388 | 232368.1438 | 59.78 | 874.665
2016-07-18 09:00 | 50585 | 2526.1269 | 268295.2552 | 59.76 | 1062.285
2016-07-18 10:00 | 54803 | 2734.8986 | 286562.8936 | 59.76 | 1150.863
2016-07-18 11:00 | 58797 | 3340.0299 | 311143.168 | 59.75 | 1293.534
2016-07-18 12:00 | 62323 | 3594.7815 | 329723.479 | 59.75 | 1371.106
2016-07-18 13:00 | 64872 | 4248.5262 | 332232.168 | 59.75 | 1427.184
2016-07-18 14:00 | 66053 | 4723.4277 | 333699.8387 | 59.75 | 1453.166
2016-07-18 15:00 | 66814 | 4951.0402 | 333872.3286 | 59.75 | 1469.908
2016-07-18 16:00 | 66587 | 5072.4493 | 333699.8387 | 59.75 | 1464.914
2016-07-18 17:00 | 67018 | 5087.6838 | 333889.3385 | 59.75 | 1474.396
2016-07-18 18:00 | 65116 | 5954.7946 | 328090.777 | 59.75 | 1432.552
2016-07-18 19:00 | 63213 | 5903.2172 | 323091.0186 | 59.75 | 1390.686
2016-07-18 20:00 | 61282 | 6042.6864 | 309122.766 | 59.75 | 1348.204
2016-07-18 21:00 | 60202 | 6836.6872 | 297877.0896 | 59.75 | 1324.444
2016-07-18 22:00 | 56696 | 8273.0357 | 263388.2094 | 59.76 | 1190.616
2016-07-18 23:00 | 52536 | 8000.1037 | 241393.6499 | 59.78 | 998.184
2016-07-19 | 46074 | 8469.2079 | 222121.6765 | 59.77 | 921.48
2016-07-19 01:00 | 43708 | 7398.1819 | 220209.2765 | 59.78 | 830.452
2016-07-19 02:00 | 42044 | 6056.1729 | 220209.2765 | 59.78 | 798.836
2016-07-19 03:00 | 41068 | 6510.61 | 220209.2765 | 59.78 | 780.292
2016-07-19 04:00 | 40958 | 6608.5035 | 220209.2765 | 59.78 | 778.202
2016-07-19 05:00 | 42152 | 6132.2668 | 220209.2765 | 59.78 | 800.888
2016-07-19 06:00 | 44045 | 5208.9989 | 220209.2765 | 59.77 | 880.9
2016-07-19 07:00 | 45339 | 4036.9119 | 228062.9869 | 59.77 | 906.78
2016-07-19 08:00 | 47899 | 2998.6036 | 251713.4396 | 59.78 | 910.081
2016-07-19 09:00 | 50912 | 2325.4473 | 273211.5098 | 59.76 | 1069.152
2016-07-19 10:00 | 54539 | 2644.6915 | 296864.5512 | 59.76 | 1145.319
2016-07-19 11:00 | 57850 | 3786.606 | 311124.5471 | 59.75 | 1272.7
2016-07-19 12:00 | 60645 | 4389.5131 | 329990.201 | 59.75 | 1334.19
2016-07-19 13:00 | 62737 | 4409.0097 | 329550.1394 | 59.75 | 1380.214
2016-07-19 14:00 | 64247 | 3858.4684 | 332997.6457 | 59.75 | 1413.434
2016-07-19 15:00 | 65336 | 4260.3529 | 332880.7657 | 59.75 | 1437.392
2016-07-19 16:00 | 65657 | 4924.5205 | 332880.7657 | 59.75 | 1444.454
2016-07-19 17:00 | 65065 | 4848.7522 | 332880.7657 | 59.75 | 1431.43
2016-07-19 18:00 | 63337 | 5366.8874 | 329083.103 | 59.75 | 1393.414
2016-07-19 19:00 | 61609 | 7219.9816 | 320174.9015 | 59.75 | 1355.398
2016-07-19 20:00 | 59857 | 8933.8469 | 293493.9772 | 59.76 | 1256.997
2016-07-19 21:00 | 58784 | 8395.1109 | 285092.3332 | 59.76 | 1234.464
2016-07-19 22:00 | 55162 | 7547.748 | 263923.211 | 59.76 | 1158.402
2016-07-19 23:00 | 50905 | 7690.2001 | 239474.8776 | 59.78 | 967.195
2016-07-20 | 46125 | 8096.8023 | 221751.9926 | 59.77 | 922.5
2016-07-20 01:00 | 43678 | 6824.4296 | 221751.9926 | 59.78 | 829.882
2016-07-20 02:00 | 42056 | 5604.8775 | 221751.9926 | 59.78 | 799.064
2016-07-20 03:00 | 41071 | 5377.5465 | 221751.9926 | 59.78 | 780.349
2016-07-20 04:00 | 40903 | 4816.4507 | 221751.9926 | 59.78 | 777.157
2016-07-20 05:00 | 42007 | 5098.2443 | 221751.9926 | 59.78 | 798.133
2016-07-20 06:00 | 43878 | 5837.0745 | 221751.9926 | 59.77 | 877.56
2016-07-20 07:00 | 45136 | 5132.4975 | 224001.9926 | 59.77 | 902.72
2016-07-20 08:00 | 47676 | 4499.5369 | 241928.5259 | 59.78 | 905.844
2016-07-20 09:00 | 50928 | 5545.2694 | 255281.7339 | 59.78 | 967.632
2016-07-20 10:00 | 54370 | 5117.2594 | 277562.5478 | 59.76 | 1141.77
2016-07-20 11:00 | 57796 | 5728.9497 | 297297.27 | 59.76 | 1213.716
2016-07-20 12:00 | 60677 | 6257.6241 | 310794.688 | 59.75 | 1334.894
2016-07-20 13:00 | 63086 | 5315.294 | 318582.9046 | 59.75 | 1387.892
2016-07-20 14:00 | 64093 | 6735.2082 | 318582.9046 | 59.75 | 1410.046
2016-07-20 15:00 | 64484 | 8178.0173 | 317158.55 | 59.75 | 1418.648
2016-07-20 16:00 | 64696 | 8481.6375 | 317158.55 | 59.75 | 1423.312
2016-07-20 17:00 | 64347 | 8481.9941 | 313154.062 | 59.75 | 1415.634
2016-07-20 18:00 | 62725 | 9524.9639 | 303177.6216 | 59.75 | 1379.95
2016-07-20 19:00 | 61104 | 8755.4423 | 298677.0735 | 59.76 | 1283.184
2016-07-20 20:00 | 59170 | 7710.3385 | 291246.6295 | 59.76 | 1242.57
2016-07-20 21:00 | 57903 | 6945.7146 | 286595.3335 | 59.76 | 1215.963
2016-07-20 22:00 | 54252 | 6211.0131 | 264686.6633 | 59.76 | 1139.292
2016-07-20 23:00 | 49902 | 7039.4496 | 234072.0799 | 59.78 | 948.138
2016-07-21 | 44437 | 9047.7519 | 202579.0365 | 59.78 | 844.303
2016-07-21 01:00 | 42099 | 7439.8612 | 202579.0365 | 59.78 | 799.881
2016-07-21 02:00 | 40441 | 7505.3252 | 199420.6365 | 59.78 | 768.379
2016-07-21 03:00 | 39352 | 7593.1452 | 199420.6365 | 59.77 | 787.04
2016-07-21 04:00 | 39101 | 6572.6129 | 199420.6365 | 59.78 | 742.919
2016-07-21 05:00 | 40064 | 5969.4635 | 199420.6365 | 59.78 | 761.216
2016-07-21 06:00 | 42005 | 5647.9304 | 199420.6365 | 59.78 | 798.095
2016-07-21 07:00 | 43235 | 4729.5127 | 207655.3469 | 59.77 | 864.7
2016-07-21 08:00 | 45990 | 3637.4626 | 232438.2799 | 59.77 | 919.8
2016-07-21 09:00 | 49472 | 3923.0802 | 252164.0279 | 59.78 | 939.968
2016-07-21 10:00 | 53097 | 4610.562 | 271998.4773 | 59.76 | 1115.037
2016-07-21 11:00 | 56052 | 5704.8931 | 287150.8853 | 59.76 | 1177.092
2016-07-21 12:00 | 58525 | 7979.3678 | 288554.8853 | 59.76 | 1229.025
2016-07-21 13:00 | 60661 | 9262.3456 | 291314.3947 | 59.76 | 1273.881
2016-07-21 14:00 | 62191 | 9196.0905 | 297965.4265 | 59.75 | 1368.202
2016-07-21 15:00 | 63001 | 10044.3776 | 297965.4265 | 59.75 | 1386.022
2016-07-21 16:00 | 63152 | 10302.2846 | 296949.4265 | 59.75 | 1389.344
2016-07-21 17:00 | 62257 | 10172.0603 | 296457.7895 | 59.76 | 1307.397
2016-07-21 18:00 | 60242 | 10416.6118 | 280682.1481 | 59.76 | 1265.082
2016-07-21 19:00 | 58227 | 10035.1112 | 265971.4802 | 59.76 | 1222.767
2016-07-21 20:00 | 56577 | 9805.4205 | 263333.4802 | 59.78 | 1074.963
2016-07-21 21:00 | 55514 | 7378.6771 | 263333.4802 | 59.76 | 1165.794
2016-07-21 22:00 | 52159 | 8186.099 | 232326.7729 | 59.78 | 991.021
2016-07-21 23:00 | 48175 | 8738.6865 | 212274.4745 | 59.77 | 963.5
2016-07-22 | 45800 | 8720.032 | 208720.9481 | 59.78 | 870.2
2016-07-22 01:00 | 43643 | 9190.1533 | 208720.9481 | 59.78 | 829.217
2016-07-22 02:00 | 41976 | 8309.2476 | 208720.9481 | 59.78 | 797.544
2016-07-22 03:00 | 40969 | 7562.0783 | 208720.9481 | 59.78 | 778.411
2016-07-22 04:00 | 40728 | 6897.7812 | 206266.5481 | 59.78 | 773.832
2016-07-22 05:00 | 41721 | 6202.3457 | 209424.9481 | 59.78 | 792.699
2016-07-22 06:00 | 43456 | 5341.0316 | 209424.9481 | 59.77 | 869.12
2016-07-22 07:00 | 44615 | 4646.9114 | 214445.4361 | 59.77 | 892.3
2016-07-22 08:00 | 47095 | 4226.1964 | 232247.7345 | 59.78 | 894.805
2016-07-22 09:00 | 50280 | 4407.5247 | 250502.8175 | 59.78 | 955.32
2016-07-22 10:00 | 53720 | 5449.2311 | 264926.8164 | 59.76 | 1128.12
2016-07-22 11:00 | 56723 | 6065.3847 | 286987.6954 | 59.76 | 1191.183
2016-07-22 12:00 | 59144 | 4573.2378 | 310688.3246 | 59.75 | 1301.168
2016-07-22 13:00 | 61241 | 4753.9744 | 315600.8877 | 59.75 | 1347.302
2016-07-22 14:00 | 62547 | 4880.0605 | 316129.1502 | 59.75 | 1376.034
2016-07-22 15:00 | 63281 | 4705.3367 | 318379.1502 | 59.75 | 1392.182
2016-07-22 16:00 | 63365 | 5163.8902 | 318379.1502 | 59.75 | 1394.03
2016-07-22 17:00 | 62265 | 6857.74 | 313360.0341 | 59.75 | 1369.83
2016-07-22 18:00 | 60479 | 7036.4127 | 305260.8757 | 59.75 | 1330.538
2016-07-22 19:00 | 58694 | 8345.7794 | 280157.1887 | 59.76 | 1232.574
2016-07-22 20:00 | 57323 | 9806.4447 | 262160.5195 | 59.76 | 1203.783
2016-07-22 21:00 | 56070 | 8583.8635 | 259784.3795 | 59.78 | 1065.33
2016-07-22 22:00 | 52786 | 7654.2005 | 240423.417 | 59.78 | 1002.934
2016-07-22 23:00 | 48968 | 7380.1917 | 223975.1686 | 59.77 | 979.36
2016-07-23 | 48059 | 7190.2501 | 223975.1686 | 59.77 | 961.18
2016-07-23 01:00 | 45584 | 6723.613 | 223975.1686 | 59.77 | 911.68
2016-07-23 02:00 | 43909 | 6997.7152 | 223975.1686 | 59.78 | 834.271
2016-07-23 03:00 | 42843 | 7298.5605 | 220718.6386 | 59.78 | 814.017
2016-07-23 04:00 | 42616 | 7036.3321 | 223173.0386 | 59.78 | 809.704
2016-07-23 05:00 | 43822 | 7130.6339 | 223173.0386 | 59.78 | 832.618
2016-07-23 06:00 | 45837 | 6556.3655 | 223173.0386 | 59.77 | 916.74
2016-07-23 07:00 | 47114 | 7094.189 | 226913.765 | 59.77 | 942.28
2016-07-23 08:00 | 50001 | 7489.2801 | 239639.9984 | 59.78 | 950.019
2016-07-23 09:00 | 53459 | 7302.9745 | 256743.9528 | 59.78 | 1015.721
2016-07-23 10:00 | 56786 | 8336.4439 | 271391.0557 | 59.76 | 1192.506
2016-07-23 11:00 | 59945 | 10334.6775 | 282791.5917 | 59.76 | 1258.845
2016-07-23 12:00 | 62688 | 10427.6278 | 305828.2605 | 59.76 | 1316.448
2016-07-23 13:00 | 65088 | 10447.7446 | 313724.585 | 59.75 | 1431.936
2016-07-23 14:00 | 66736 | 11167.3961 | 316687.8891 | 59.75 | 1468.192
2016-07-23 15:00 | 66754 | 10306.8429 | 316942.1624 | 59.75 | 1468.588
2016-07-23 16:00 | 66957 | 10764.9951 | 316633.1225 | 59.75 | 1473.054
2016-07-23 17:00 | 64996 | 12152.3811 | 306568.4396 | 59.75 | 1429.912
2016-07-23 18:00 | 62439 | 12381.7272 | 289429.2162 | 59.76 | 1311.219
2016-07-23 19:00 | 59883 | 12141.0201 | 277012.6802 | 59.76 | 1257.543
2016-07-23 20:00 | 58251 | 11280.8504 | 265762.6914 | 59.78 | 1106.769
2016-07-23 21:00 | 56922 | 9956.5631 | 264252.3714 | 59.78 | 1081.518
2016-07-23 22:00 | 53477 | 8101.1192 | 252338.1039 | 59.78 | 1016.063
2016-07-23 23:00 | 50045 | 8198.2005 | 232482.5459 | 59.77 | 1000.9
2016-07-24 | 48732 | 7940.1363 | 225908.1129 | 59.77 | 974.64
2016-07-24 01:00 | 46195 | 7364.597 | 222098.3129 | 59.77 | 923.9
2016-07-24 02:00 | 44093 | 6992.7877 | 222098.3129 | 59.78 | 837.767
2016-07-24 03:00 | 42822 | 7237.6325 | 225354.8429 | 59.78 | 813.618
2016-07-24 04:00 | 42060 | 6630.477 | 225354.8429 | 59.78 | 799.14
2016-07-24 05:00 | 42081 | 5959.2368 | 225354.8429 | 59.78 | 799.539
2016-07-24 06:00 | 42562 | 5498.6941 | 225354.8429 | 59.78 | 808.678
2016-07-24 07:00 | 42889 | 5718.1899 | 225354.8429 | 59.78 | 814.891
2016-07-24 08:00 | 46069 | 6174.9065 | 227707.0029 | 59.77 | 921.38
2016-07-24 09:00 | 50304 | 4665.1961 | 256386.9939 | 59.78 | 955.776
2016-07-24 10:00 | 54532 | 4842.4943 | 278021.2507 | 59.76 | 1145.172
2016-07-24 11:00 | 58368 | 6328.162 | 292773.1031 | 59.76 | 1225.728
2016-07-24 12:00 | 61521 | 7203.5037 | 308949.9557 | 59.75 | 1353.462
2016-07-24 13:00 | 64243 | 7349.0366 | 316202.2674 | 59.75 | 1413.346
2016-07-24 14:00 | 66256 | 9464.021 | 316154.2674 | 59.75 | 1457.632
2016-07-24 15:00 | 66938 | 10109.5057 | 316154.2674 | 59.75 | 1472.636
2016-07-24 16:00 | 67637 | 8883.3626 | 317025.2105 | 59.75 | 1488.014
2016-07-24 17:00 | 66911 | 9276.5785 | 318881.8674 | 59.75 | 1472.042
2016-07-24 18:00 | 65045 | 9937.3054 | 312632.4726 | 59.75 | 1430.99
2016-07-24 19:00 | 62491 | 8925.7505 | 300130.6202 | 59.75 | 1374.802
2016-07-24 20:00 | 60281 | 7712.4763 | 294292.4476 | 59.75 | 1326.182
2016-07-24 21:00 | 58209 | 5513.1884 | 291722.9296 | 59.75 | 1280.598
2016-07-24 22:00 | 54432 | 5325.9288 | 267001.4014 | 59.76 | 1143.072
2016-07-24 23:00 | 50658 | 6063.391 | 241679.6259 | 59.78 | 962.502
2016-07-25 | 48086 | 4846.2233 | 229253.0929 | 59.78 | 913.634
2016-07-25 01:00 | 45486 | 4365.1777 | 229253.0929 | 59.77 | 909.72
2016-07-25 02:00 | 43491 | 4914.181 | 229253.0929 | 59.77 | 869.82
2016-07-25 03:00 | 41890 | 4463.4492 | 227744.7429 | 59.78 | 795.91
2016-07-25 04:00 | 40816 | 4065.563 | 227744.7429 | 59.78 | 775.504
2016-07-25 05:00 | 40429 | 4232.3231 | 226449.1449 | 59.78 | 768.151
2016-07-25 06:00 | 40265 | 3814.9988 | 226449.1449 | 59.78 | 765.035
2016-07-25 07:00 | 40610 | 2456.552 | 226449.1449 | 59.77 | 812.2
2016-07-25 08:00 | 44009 | 1541.4538 | 233023.5779 | 59.77 | 880.18
2016-07-25 09:00 | 48486 | 2178.0742 | 255129.1359 | 59.78 | 921.234
2016-07-25 10:00 | 53348 | 2913.0951 | 285509.3836 | 59.76 | 1120.308
2016-07-25 11:00 | 57990 | 3765.8611 | 306104.27 | 59.75 | 1275.78
2016-07-25 12:00 | 62295 | 5479.5111 | 323204.3961 | 59.75 | 1370.49
2016-07-25 13:00 | 65443 | 4853.6658 | 334303.8674 | 59.75 | 1439.746
2016-07-25 14:00 | 66974 | 5616.5203 | 335740.3161 | 59.75 | 1473.428
2016-07-25 15:00 | 68198 | 5885.7353 | 336904.4626 | 59.75 | 1500.356
2016-07-25 16:00 | 68581 | 4869.4909 | 336904.4626 | 59.75 | 1508.782
2016-07-25 17:00 | 68144 | 4492.8861 | 336619.8916 | 59.75 | 1499.168
2016-07-25 18:00 | 66680 | 5046.6517 | 335455.7451 | 59.75 | 1466.96
2016-07-25 19:00 | 64530 | 5672.2328 | 332175.9054 | 59.75 | 1419.66
2016-07-25 20:00 | 62598 | 6137.9485 | 320493.2626 | 59.75 | 1377.156
2016-07-25 21:00 | 60655 | 5201.0627 | 310888.929 | 59.75 | 1334.41
2016-07-25 22:00 | 56678 | 4456.4484 | 289994.8166 | 59.76 | 1190.238
2016-07-25 23:00 | 52019 | 4667.3872 | 261506.0784 | 59.78 | 988.361
2016-07-26 | 47478 | 5517.8617 | 236585.3059 | 59.77 | 949.56
2016-07-26 01:00 | 45044 | 4508.9658 | 236585.3059 | 59.77 | 900.88
2016-07-26 02:00 | 43401 | 4785.8518 | 236585.3059 | 59.77 | 868.02
2016-07-26 03:00 | 42453 | 5030.2183 | 238093.6559 | 59.78 | 806.607
2016-07-26 04:00 | 42407 | 4393.1546 | 238093.6559 | 59.77 | 848.14
2016-07-26 05:00 | 43648 | 4124.241 | 239389.2539 | 59.77 | 872.96
2016-07-26 06:00 | 45841 | 4060.5251 | 239389.2539 | 59.77 | 916.82
2016-07-26 07:00 | 47098 | 2257.4713 | 239389.2539 | 59.78 | 894.862
2016-07-26 08:00 | 49356 | 1115.168 | 264043.0244 | 59.76 | 1036.476
2016-07-26 09:00 | 52467 | 929.7112 | 285458.9715 | 59.76 | 1101.807
2016-07-26 10:00 | 56224 | 1074.5486 | 314064.5671 | 59.75 | 1236.928
2016-07-26 11:00 | 60094 | 2294.2459 | 326673.3974 | 59.75 | 1322.068
2016-07-26 12:00 | 63572 | 2424.0554 | 330983.6619 | 59.75 | 1398.584
2016-07-26 13:00 | 66374 | 2144.3779 | 337066.8067 | 59.75 | 1460.228
2016-07-26 14:00 | 66917 | 3261.5701 | 336483.8636 | 59.75 | 1472.174
2016-07-26 15:00 | 64888 | 3185.5419 | 333479.9019 | 59.75 | 1427.536
2016-07-26 16:00 | 62015 | 2743.8583 | 330576.1974 | 59.75 | 1364.33
2016-07-26 17:00 | 60129 | 3867.9484 | 319918.5265 | 59.75 | 1322.838
2016-07-26 18:00 | 58285 | 4667.0318 | 303003.4409 | 59.75 | 1282.27
2016-07-26 19:00 | 56440 | 4363.0226 | 289110.6776 | 59.76 | 1185.24
2016-07-26 20:00 | 55402 | 4587.4363 | 283824.8756 | 59.76 | 1163.442
2016-07-26 21:00 | 54143 | 5155.059 | 274221.0134 | 59.76 | 1137.003
2016-07-26 22:00 | 51000 | 3908.4149 | 256280.5879 | 59.78 | 969
2016-07-26 23:00 | 47034 | 3350.5012 | 239473.4199 | 59.78 | 893.646
2016-07-27 | 43176 | 3380.4787 | 234218.3749 | 59.77 | 863.52
2016-07-27 01:00 | 41130 | 3630.8639 | 234218.3749 | 59.78 | 781.47
2016-07-27 02:00 | 39746 | 3065.7389 | 231736.7749 | 59.78 | 755.174
2016-07-27 03:00 | 39019 | 2474.011 | 231736.7749 | 59.78 | 741.361
2016-07-27 04:00 | 39178 | 1998.8207 | 231736.7749 | 59.78 | 744.382
2016-07-27 05:00 | 40721 | 2068.5741 | 229743.2249 | 59.77 | 814.42
2016-07-27 06:00 | 43194 | 2232.216 | 229743.2249 | 59.77 | 863.88
2016-07-27 07:00 | 44478 | 1831.6155 | 232942.4509 | 59.78 | 845.082
2016-07-27 08:00 | 46264 | 1603.1486 | 248527.9039 | 59.78 | 879.016
2016-07-27 09:00 | 48612 | 2797.7354 | 257541.6739 | 59.78 | 923.628
2016-07-27 10:00 | 51854 | 2046.9228 | 283970.3326 | 59.76 | 1088.934
2016-07-27 11:00 | 55137 | 2152.2942 | 306389.1218 | 59.75 | 1213.014
2016-07-27 12:00 | 57819 | 3015.6467 | 315731.7892 | 59.75 | 1272.018
2016-07-27 13:00 | 60040 | 3539.401 | 318372.0807 | 59.75 | 1320.88
2016-07-27 14:00 | 61778 | 4062.9828 | 320324.8557 | 59.75 | 1359.116
2016-07-27 15:00 | 62843 | 5297.9892 | 320324.8557 | 59.75 | 1382.546
2016-07-27 16:00 | 63067 | 5424.8384 | 320460.8557 | 59.75 | 1387.474
2016-07-27 17:00 | 62347 | 5932.1991 | 316433.2453 | 59.75 | 1371.634
2016-07-27 18:00 | 60398 | 7302.1023 | 299711.4099 | 59.75 | 1328.756
2016-07-27 19:00 | 58450 | 8202.5068 | 279196.6207 | 59.76 | 1227.45
2016-07-27 20:00 | 57123 | 8221.5079 | 269853.9533 | 59.76 | 1199.583
2016-07-27 21:00 | 55952 | 8634.4808 | 256301.1234 | 59.78 | 1063.088
2016-07-27 22:00 | 52472 | 8261.8463 | 236324.1609 | 59.78 | 996.968
2016-07-27 23:00 | 48270 | 7792.6154 | 215709.3229 | 59.77 | 965.4
2016-07-28 | 42608 | 6853.2083 | 201275.5009 | 59.78 | 809.552
2016-07-28 01:00 | 40478 | 6018.8863 | 198998.7909 | 59.78 | 769.082
2016-07-28 02:00 | 39028 | 5800.8818 | 201480.3909 | 59.78 | 741.532
2016-07-28 03:00 | 38319 | 5872.7373 | 201480.3909 | 59.77 | 766.38
2016-07-28 04:00 | 38440 | 4400.6139 | 201480.3909 | 59.78 | 730.36
2016-07-28 05:00 | 39828 | 3934.2374 | 203473.9409 | 59.78 | 756.732
2016-07-28 06:00 | 42366 | 2961.5453 | 211330.3409 | 59.77 | 847.32
2016-07-28 07:00 | 43168 | 2752.4055 | 215830.3409 | 59.77 | 863.36
2016-07-28 08:00 | 45139 | 2758.284 | 231984.5039 | 59.77 | 902.78
2016-07-28 09:00 | 48150 | 4095.402 | 246724.3894 | 59.78 | 914.85
2016-07-28 10:00 | 51253 | 4286.7852 | 263922.66 | 59.78 | 973.807
2016-07-28 11:00 | 53718 | 4559.2733 | 275638.534 | 59.76 | 1128.078
2016-07-28 12:00 | 54872 | 3825.3245 | 293993.0792 | 59.76 | 1152.312
2016-07-28 13:00 | 56362 | 4350.955 | 296626.0263 | 59.76 | 1183.602
2016-07-28 14:00 | 57614 | 3095.4341 | 303058.3317 | 59.75 | 1267.508
2016-07-28 15:00 | 58621 | 3758.136 | 303058.3317 | 59.75 | 1289.662
2016-07-28 16:00 | 59186 | 3845.6924 | 302913.4557 | 59.75 | 1302.092
2016-07-28 17:00 | 58836 | 4558.1793 | 302756.8592 | 59.75 | 1294.392
2016-07-28 18:00 | 56845 | 6313.113 | 289197.9547 | 59.76 | 1193.745
2016-07-28 19:00 | 54854 | 6034.5209 | 277482.0807 | 59.76 | 1151.934
2016-07-28 20:00 | 53827 | 5763.6983 | 270275.4995 | 59.76 | 1130.367
2016-07-28 21:00 | 52996 | 6915.2384 | 249654.746 | 59.78 | 1006.924
2016-07-28 22:00 | 49338 | 6171.5753 | 232582.2787 | 59.78 | 937.422
2016-07-28 23:00 | 45437 | 6265.7738 | 209754.3877 | 59.77 | 908.74
2016-07-29 | 41810 | 7027.72 | 201819.7917 | 59.78 | 794.39
2016-07-29 01:00 | 39679 | 6653.1255 | 199820.0305 | 59.78 | 753.901
2016-07-29 02:00 | 38315 | 5784.9081 | 199820.0305 | 59.78 | 727.985
2016-07-29 03:00 | 37579 | 4965.64 | 199820.0305 | 59.78 | 714.001
2016-07-29 04:00 | 37655 | 4753.9673 | 199820.0305 | 59.78 | 715.445
2016-07-29 05:00 | 38925 | 4138.6969 | 199820.0305 | 59.78 | 739.575
2016-07-29 06:00 | 41064 | 3557.4858 | 200968.9225 | 59.77 | 821.28
2016-07-29 07:00 | 42262 | 2644.8246 | 214364.5955 | 59.77 | 845.24
2016-07-29 08:00 | 44337 | 2234.7026 | 232561.1615 | 59.77 | 886.74
2016-07-29 09:00 | 47595 | 2853.8982 | 249172.287 | 59.78 | 904.305
2016-07-29 10:00 | 51435 | 3306.5683 | 271165.1147 | 59.76 | 1080.135
2016-07-29 11:00 | 54925 | 4128.1279 | 287439.4599 | 59.76 | 1153.425
2016-07-29 12:00 | 57737 | 5238.3554 | 297700.2119 | 59.76 | 1212.477
2016-07-29 13:00 | 60363 | 6581.3494 | 303724.8879 | 59.75 | 1327.986
2016-07-29 14:00 | 62318 | 7555.3117 | 307318.9811 | 59.75 | 1370.996
2016-07-29 15:00 | 63509 | 8852.0786 | 306302.9811 | 59.75 | 1397.198
2016-07-29 16:00 | 63713 | 8440.7972 | 307379.9771 | 59.75 | 1401.686
2016-07-29 17:00 | 62763 | 7871.0374 | 305220.5771 | 59.75 | 1380.786
2016-07-29 18:00 | 60706 | 9226.0813 | 296997.8904 | 59.76 | 1274.826
2016-07-29 19:00 | 58650 | 9020.9455 | 285604.8232 | 59.76 | 1231.65
2016-07-29 20:00 | 56983 | 8430.9773 | 277781.2072 | 59.76 | 1196.643
2016-07-29 21:00 | 55504 | 9522.0601 | 261015.9318 | 59.78 | 1054.576
2016-07-29 22:00 | 51872 | 7665.4012 | 247215.3715 | 59.78 | 985.568
2016-07-29 23:00 | 47738 | 7997.6885 | 221655.8535 | 59.77 | 954.76
2016-07-30 | 45823 | 7724.6391 | 213824.5185 | 59.77 | 916.46
2016-07-30 01:00 | 43409 | 6405.1412 | 213824.5185 | 59.78 | 824.771
2016-07-30 02:00 | 41741 | 6217.8965 | 213824.5185 | 59.78 | 793.079
2016-07-30 03:00 | 40718 | 6425.9479 | 213824.5185 | 59.78 | 773.642
2016-07-30 04:00 | 40492 | 6763.3995 | 213824.5185 | 59.78 | 769.348
2016-07-30 05:00 | 41516 | 6485.4335 | 212247.7485 | 59.78 | 788.804
2016-07-30 06:00 | 43148 | 5899.8278 | 214566.9917 | 59.78 | 819.812
2016-07-30 07:00 | 44321 | 5735.9072 | 218766.9677 | 59.77 | 886.42
2016-07-30 08:00 | 47486 | 5597.3669 | 233805.2157 | 59.77 | 949.72
2016-07-30 09:00 | 51208 | 4970.3904 | 259018.2782 | 59.78 | 972.952
2016-07-30 10:00 | 55315 | 4277.5299 | 289262.5644 | 59.76 | 1161.615
2016-07-30 11:00 | 58848 | 4435.1111 | 309785.2855 | 59.75 | 1294.656
2016-07-30 12:00 | 61890 | 4337.8689 | 329599.6022 | 59.75 | 1361.58
2016-07-30 13:00 | 64814 | 4788.0218 | 332392.915 | 59.75 | 1425.908
2016-07-30 14:00 | 67004 | 5348.8646 | 335408.1849 | 59.75 | 1474.088
2016-07-30 15:00 | 67928 | 6138.2373 | 332829.2116 | 59.75 | 1494.416
2016-07-30 16:00 | 68628 | 5991.3344 | 331089.7372 | 59.75 | 1509.816
2016-07-30 17:00 | 68206 | 6019.5533 | 332764.9042 | 59.75 | 1500.532
2016-07-30 18:00 | 66455 | 6451.1572 | 331432.2114 | 59.75 | 1462.01
2016-07-30 19:00 | 64016 | 5268.0028 | 329907.6114 | 59.75 | 1408.352
2016-07-30 20:00 | 61658 | 4283.4832 | 318824.0027 | 59.75 | 1356.476
2016-07-30 21:00 | 59728 | 6595.4606 | 298819.7516 | 59.75 | 1314.016
2016-07-30 22:00 | 55860 | 7514.3478 | 264972.9534 | 59.76 | 1173.06
2016-07-30 23:00 | 51779 | 7819.1995 | 239508.62 | 59.78 | 983.801
2016-07-31 | 49902 | 8560.3692 | 220828.1266 | 59.77 | 998.04
2016-07-31 01:00 | 46997 | 8316.0095 | 220828.1266 | 59.77 | 939.94
2016-07-31 02:00 | 44845 | 7938.6746 | 220828.1266 | 59.78 | 852.055
2016-07-31 03:00 | 43299 | 7357.3539 | 220828.1266 | 59.78 | 822.681
2016-07-31 04:00 | 42450 | 6699.6415 | 220828.1266 | 59.78 | 806.55
2016-07-31 05:00 | 42305 | 5387.5329 | 221850.7066 | 59.78 | 803.795
2016-07-31 06:00 | 42495 | 4310.2346 | 221850.7066 | 59.77 | 849.9
2016-07-31 07:00 | 42990 | 4402.8137 | 221850.7066 | 59.77 | 859.8
2016-07-31 08:00 | 45999 | 4784.8614 | 225199.7966 | 59.77 | 919.98
2016-07-31 09:00 | 50043 | 3455.7924 | 260687.458 | 59.78 | 950.817
2016-07-31 10:00 | 54469 | 2092.3491 | 296494.8056 | 59.76 | 1143.849
2016-07-31 11:00 | 58621 | 1519.5329 | 319942.5387 | 59.75 | 1289.662
2016-07-31 12:00 | 62197 | 1378.9811 | 338987.6634 | 59.75 | 1368.334
2016-07-31 13:00 | 65184 | 1931.0612 | 341251.5031 | 59.75 | 1434.048
2016-07-31 14:00 | 67033 | 3031.5846 | 342785.3261 | 59.75 | 1474.726
2016-07-31 15:00 | 68802 | 3821.5413 | 345430.1061 | 59.75 | 1513.644
2016-07-31 16:00 | 69886 | 4159.8584 | 347686.7169 | 59.75 | 1537.492
2016-07-31 17:00 | 69803 | 4180.2721 | 347686.7169 | 59.75 | 1535.666
2016-07-31 18:00 | 67706 | 3995.6662 | 345802.7375 | 59.75 | 1489.532
2016-07-31 19:00 | 66296 | 4490.8658 | 339549.0007 | 59.75 | 1458.512
2016-07-31 20:00 | 63475 | 5376.1447 | 322176.822 | 59.75 | 1396.45
2016-07-31 21:00 | 61101 | 7788.0061 | 297652.0929 | 59.75 | 1344.222
2016-07-31 22:00 | 56999 | 9521.835 | 256871.7853 | 59.78 | 1082.981
2016-07-31 23:00 | 52864 | 8968.5318 | 238368.3273 | 59.78 | 1004.416
2016-08-01 | 50717 | 8812.8309 | 222588.0839 | 59.77 | 1014.34
2016-08-01 01:00 | 47784 | 8207.8783 | 220338.0839 | 59.77 | 955.68
2016-08-01 02:00 | 45400 | 7606.2418 | 220338.0839 | 59.77 | 908
2016-08-01 03:00 | 43675 | 7745.5912 | 220338.0839 | 59.78 | 829.825
2016-08-01 04:00 | 42473 | 7478.0767 | 217457.6879 | 59.78 | 806.987
2016-08-01 05:00 | 41917 | 6742.0708 | 218011.8779 | 59.78 | 796.423
2016-08-01 06:00 | 41604 | 6430.715 | 218011.8779 | 59.78 | 790.476
2016-08-01 07:00 | 41745 | 4240.8246 | 218011.8779 | 59.77 | 834.9
2016-08-01 08:00 | 45126 | 2547.8955 | 237838.6609 | 59.78 | 857.394
2016-08-01 09:00 | 49742 | 1818.95 | 263302.9943 | 59.76 | 1044.582
2016-08-01 10:00 | 54706 | 1686.4171 | 300153.4825 | 59.75 | 1203.532
2016-08-01 11:00 | 59662 | 1731.0386 | 327506.59 | 59.75 | 1312.564
2016-08-01 12:00 | 64295 | 2377.8577 | 344418.9321 | 59.75 | 1414.49
2016-08-01 13:00 | 68106 | 2926.9971 | 351037.9906 | 59.75 | 1498.332
2016-08-01 14:00 | 70267 | 2564.0114 | 352354.3636 | 59.75 | 1545.874
2016-08-01 15:00 | 72181 | 3376.5012 | 352354.3636 | 59.75 | 1587.982
2016-08-01 16:00 | 73304 | 3945.1303 | 352937.3067 | 59.75 | 1612.688
2016-08-01 17:00 | 73403 | 4151.418 | 352632.4734 | 59.75 | 1614.866
2016-08-01 18:00 | 71471 | 5065.1416 | 348941.9961 | 59.75 | 1572.362
2016-08-01 19:00 | 69538 | 6018.3337 | 344646.5037 | 59.75 | 1529.836
2016-08-01 20:00 | 67428 | 6879.3341 | 334902.5398 | 59.75 | 1483.416
2016-08-01 21:00 | 65292 | 8446.1738 | 318104.9051 | 59.75 | 1436.424
2016-08-01 22:00 | 60697 | 8620.7413 | 293436.654 | 59.76 | 1274.637
2016-08-01 23:00 | 55642 | 8887.933 | 259170.2978 | 59.78 | 1057.198
2016-08-02 | 48592 | 8510.7764 | 220629.1813 | 59.77 | 971.84
2016-08-02 01:00 | 45754 | 8471.1691 | 220629.1813 | 59.78 | 869.326
2016-08-02 02:00 | 43691 | 8349.4209 | 220629.1813 | 59.78 | 830.129
2016-08-02 03:00 | 42327 | 7281.4463 | 220629.1813 | 59.78 | 804.213
2016-08-02 04:00 | 41833 | 6757.8464 | 223509.5773 | 59.78 | 794.827
2016-08-02 05:00 | 42642 | 6580.3895 | 223509.5773 | 59.78 | 810.198
2016-08-02 06:00 | 44268 | 6096.4736 | 223509.5773 | 59.77 | 885.36
2016-08-02 07:00 | 45431 | 5197.4239 | 223509.5773 | 59.77 | 908.62
2016-08-02 08:00 | 48469 | 4137.6681 | 243856.8483 | 59.78 | 920.911
2016-08-02 09:00 | 52461 | 3573.195 | 271654.556 | 59.76 | 1101.681
2016-08-02 10:00 | 56996 | 3392.7987 | 302148.7024 | 59.75 | 1253.912
2016-08-02 11:00 | 61324 | 4325.223 | 320463.7318 | 59.75 | 1349.128
2016-08-02 12:00 | 65335 | 4762.3447 | 338071.6005 | 59.75 | 1437.37
2016-08-02 13:00 | 68814 | 4592.1004 | 342819.197 | 59.75 | 1513.908
2016-08-02 14:00 | 70769 | 4655.621 | 349726.0637 | 59.75 | 1556.918
2016-08-02 15:00 | 72311 | 4835.8908 | 349726.0637 | 59.75 | 1590.842
2016-08-02 16:00 | 72891 | 4725.16 | 350188.5268 | 59.75 | 1603.602
2016-08-02 17:00 | 72423 | 4707.7348 | 349726.0637 | 59.75 | 1593.306
2016-08-02 18:00 | 70314 | 5417.9064 | 346713.4913 | 59.75 | 1546.908
2016-08-02 19:00 | 68892 | 6592.4776 | 343446.641 | 59.75 | 1515.624
2016-08-02 20:00 | 66644 | 7997.9589 | 324120.4735 | 59.75 | 1466.168
2016-08-02 21:00 | 64457 | 9271.3411 | 309677.5095 | 59.75 | 1418.054
2016-08-02 22:00 | 59947 | 10084.3966 | 273886.814 | 59.76 | 1258.887
2016-08-02 23:00 | 54935 | 9756.7471 | 247277.6667 | 59.78 | 1043.765
2016-08-03 | 49532 | 10354.5541 | 225415.2637 | 59.77 | 990.64
2016-08-03 01:00 | 46611 | 9753.4385 | 223027.7637 | 59.78 | 885.609
2016-08-03 02:00 | 44518 | 8802.6049 | 223027.7637 | 59.78 | 845.842
2016-08-03 03:00 | 43268 | 8220.1704 | 223027.7637 | 59.78 | 822.092
2016-08-03 04:00 | 42690 | 7943.143 | 223027.7637 | 59.78 | 811.11
2016-08-03 05:00 | 43436 | 7288.2443 | 223027.7637 | 59.78 | 825.284
2016-08-03 06:00 | 44954 | 6939.747 | 223027.7637 | 59.77 | 899.08
2016-08-03 07:00 | 45983 | 4690.0004 | 226247.6837 | 59.77 | 919.66
2016-08-03 08:00 | 48749 | 2759.9249 | 259369.2332 | 59.78 | 926.231
2016-08-03 09:00 | 52660 | 2273.1843 | 286570.7114 | 59.76 | 1105.86
2016-08-03 10:00 | 57107 | 1571.0786 | 316582.3625 | 59.75 | 1256.354
2016-08-03 11:00 | 61276 | 2148.8889 | 337173.3432 | 59.75 | 1348.072
2016-08-03 12:00 | 64923 | 2571.1183 | 344566.0065 | 59.75 | 1428.306
2016-08-03 13:00 | 68270 | 3322.5339 | 346449.9859 | 59.75 | 1501.94
2016-08-03 14:00 | 69832 | 4538.0246 | 348699.9859 | 59.75 | 1536.304
2016-08-03 15:00 | 70989 | 4739.1664 | 348699.9859 | 59.75 | 1561.758
2016-08-03 16:00 | 71185 | 4341.6069 | 348699.9859 | 59.75 | 1566.07
2016-08-03 17:00 | 70586 | 4132.6896 | 348699.9859 | 59.75 | 1552.892
2016-08-03 18:00 | 69163 | 4639.9915 | 346705.9534 | 59.75 | 1521.586
2016-08-03 19:00 | 67053 | 6295.0943 | 339612.3712 | 59.75 | 1475.166
2016-08-03 20:00 | 65089 | 8240.1032 | 318758.7425 | 59.75 | 1431.958
2016-08-03 21:00 | 63112 | 8419.3961 | 305950.3014 | 59.75 | 1388.464
2016-08-03 22:00 | 58970 | 8470.7508 | 275943.365 | 59.76 | 1238.37
2016-08-03 23:00 | 54144 | 9067.5231 | 244313.7297 | 59.78 | 1028.736
2016-08-04 | 48084 | 8214.5082 | 228986.9467 | 59.77 | 961.68
2016-08-04 01:00 | 45456 | 7778.2233 | 227074.5467 | 59.77 | 909.12
2016-08-04 02:00 | 43600 | 7989.1312 | 227074.5467 | 59.78 | 828.4
2016-08-04 03:00 | 42471 | 7692.5054 | 227074.5467 | 59.78 | 806.949
2016-08-04 04:00 | 42112 | 7630.8482 | 227074.5467 | 59.78 | 800.128
2016-08-04 05:00 | 43087 | 6678.8959 | 226980.4467 | 59.78 | 818.653
2016-08-04 06:00 | 44901 | 4903.5906 | 226980.4467 | 59.77 | 898.02
2016-08-04 07:00 | 45980 | 3382.5361 | 232679.9547 | 59.78 | 873.62
2016-08-04 08:00 | 48453 | 2220.6562 | 259552.3287 | 59.78 | 920.607
2016-08-04 09:00 | 52000 | 2331.4903 | 277828.756 | 59.76 | 1092
2016-08-04 10:00 | 55935 | 3219.9349 | 300459.8904 | 59.75 | 1230.57
2016-08-04 11:00 | 59682 | 2589.1687 | 325847.2547 | 59.75 | 1313.004
2016-08-04 12:00 | 62917 | 2529.3319 | 345088.3214 | 59.75 | 1384.174
2016-08-04 13:00 | 65757 | 2569.3332 | 348327.7823 | 59.75 | 1446.654
2016-08-04 14:00 | 67931 | 2176.4991 | 352139.6209 | 59.75 | 1494.482
2016-08-04 15:00 | 68930 | 1986.6739 | 352139.6209 | 59.75 | 1516.46
2016-08-04 16:00 | 69292 | 1859.9719 | 352172.5242 | 59.75 | 1524.424
2016-08-04 17:00 | 68976 | 2399.6776 | 352139.6209 | 59.75 | 1517.472
2016-08-04 18:00 | 67060 | 3849.5118 | 347977.6259 | 59.75 | 1475.32
2016-08-04 19:00 | 65144 | 4475.7731 | 343327.3894 | 59.75 | 1433.168
2016-08-04 20:00 | 63143 | 5611.3823 | 322767.3707 | 59.75 | 1389.146
2016-08-04 21:00 | 61054 | 4834.0986 | 317431.6471 | 59.75 | 1343.188
2016-08-04 22:00 | 56561 | 4029.7626 | 292914.2356 | 59.75 | 1244.342
2016-08-04 23:00 | 52111 | 5006.3311 | 260242.5234 | 59.78 | 990.109
2016-08-05 | 48665 | 6831.079 | 235029.4609 | 59.77 | 973.3
2016-08-05 01:00 | 45906 | 5963.4222 | 235029.4609 | 59.77 | 918.12
2016-08-05 02:00 | 43871 | 5262.2294 | 235029.4609 | 59.77 | 877.42
2016-08-05 03:00 | 42597 | 4552.5479 | 235029.4609 | 59.77 | 851.94
2016-08-05 04:00 | 42090 | 4525.9712 | 235029.4609 | 59.77 | 841.8
2016-08-05 05:00 | 42967 | 4195.6764 | 237511.0609 | 59.77 | 859.34
2016-08-05 06:00 | 44822 | 3185.2096 | 237511.0609 | 59.77 | 896.44
2016-08-05 07:00 | 45576 | 3262.0288 | 236215.4629 | 59.77 | 911.52
2016-08-05 08:00 | 48276 | 3696.2602 | 246212.2079 | 59.78 | 917.244
2016-08-05 09:00 | 52053 | 1670.5525 | 280506.0736 | 59.76 | 1093.113
2016-08-05 10:00 | 56262 | 808.7242 | 310664.238 | 59.75 | 1237.764
2016-08-05 11:00 | 60185 | 438.7615 | 335719.6429 | 59.75 | 1324.07
2016-08-05 12:00 | 63605 | 742.0476 | 349185.8605 | 59.75 | 1399.31
2016-08-05 13:00 | 66556 | 953.4806 | 351762.2907 | 59.75 | 1464.232
2016-08-05 14:00 | 68522 | 1179.6546 | 353322.34 | 59.75 | 1507.484
2016-08-05 15:00 | 68783 | 1393.6828 | 353322.34 | 59.75 | 1513.226
2016-08-05 16:00 | 68976 | 1485.0262 | 353322.34 | 59.75 | 1517.472
2016-08-05 17:00 | 69197 | 1403.1177 | 353540.0132 | 59.75 | 1522.334
2016-08-05 18:00 | 67130 | 1737.7863 | 350824.1232 | 59.75 | 1476.86
2016-08-05 19:00 | 65062 | 1952.381 | 345538.001 | 59.75 | 1431.364
2016-08-05 20:00 | 63463 | 2639.7938 | 337145.3068 | 59.75 | 1396.186
2016-08-05 21:00 | 61518 | 4264.9282 | 321909.4829 | 59.75 | 1353.396
2016-08-05 22:00 | 57245 | 5071.573 | 294795.9969 | 59.76 | 1202.145
2016-08-05 23:00 | 52826 | 5186.3945 | 268182.9267 | 59.76 | 1109.346
2016-08-06 | 51794 | 4577.5314 | 268182.9267 | 59.78 | 984.086
2016-08-06 01:00 | 48840 | 4196.3061 | 268182.9267 | 59.78 | 927.96
2016-08-06 02:00 | 46892 | 4030.4769 | 266293.9767 | 59.78 | 890.948
2016-08-06 03:00 | 45358 | 3637.2994 | 266293.9767 | 59.77 | 907.16
2016-08-06 04:00 | 44871 | 4368.0371 | 266293.9767 | 59.77 | 897.42
2016-08-06 05:00 | 45815 | 2979.6725 | 266293.9767 | 59.78 | 870.485
2016-08-06 06:00 | 47480 | 2007.2565 | 266005.9767 | 59.78 | 902.12
2016-08-06 07:00 | 48206 | 1141.5803 | 270657.9747 | 59.78 | 915.914
2016-08-06 08:00 | 50953 | 731.4187 | 291093.9719 | 59.76 | 1070.013
2016-08-06 09:00 | 54708 | 834.8536 | 313596.1779 | 59.75 | 1203.576
2016-08-06 10:00 | 59127 | 1036.394 | 333064.9833 | 59.75 | 1300.794
2016-08-06 11:00 | 63234 | 1216.9418 | 348350.0021 | 59.75 | 1391.148
2016-08-06 12:00 | 66706 | 1097.9923 | 356589.9541 | 59.75 | 1467.532
2016-08-06 13:00 | 69167 | 1269.7969 | 360907.6287 | 59.75 | 1521.674
2016-08-06 14:00 | 71399 | 1645.909 | 362729.0312 | 59.75 | 1570.778
2016-08-06 15:00 | 72387 | 1891.3285 | 363311.9743 | 59.75 | 1592.514
2016-08-06 16:00 | 71838 | 1794.4474 | 362729.0312 | 59.75 | 1580.436
2016-08-06 17:00 | 69782 | 1890.2791 | 359286.1195 | 59.75 | 1535.204
2016-08-06 18:00 | 67311 | 2653.6844 | 351488.3936 | 59.75 | 1480.842
2016-08-06 19:00 | 64152 | 2589.3726 | 345853.7412 | 59.75 | 1411.344
2016-08-06 20:00 | 62195 | 2498.0601 | 333481.2685 | 59.75 | 1368.29
2016-08-06 21:00 | 60016 | 3514.8678 | 320116.353 | 59.75 | 1320.352
2016-08-06 22:00 | 56328 | 3952.0921 | 294803.3059 | 59.76 | 1182.888
2016-08-06 23:00 | 52319 | 4129.6668 | 268754.8017 | 59.76 | 1098.699
2016-08-07 | 51557 | 5766.6298 | 248904.8257 | 59.78 | 979.583
2016-08-07 01:00 | 48940 | 6025.1304 | 243180.8507 | 59.78 | 929.86
2016-08-07 02:00 | 46811 | 6003.2488 | 245069.8007 | 59.77 | 936.22
2016-08-07 03:00 | 45379 | 5385.415 | 245069.8007 | 59.77 | 907.58
2016-08-07 04:00 | 44630 | 5129.1723 | 244497.3007 | 59.77 | 892.6
2016-08-07 05:00 | 44626 | 4843.1834 | 244497.3007 | 59.77 | 892.52
2016-08-07 06:00 | 45129 | 4707.4349 | 243283.6507 | 59.77 | 902.58
2016-08-07 07:00 | 45551 | 4343.276 | 243283.6507 | 59.77 | 911.02
2016-08-07 08:00 | 48494 | 4156.339 | 247849.0207 | 59.78 | 921.386
2016-08-07 09:00 | 52619 | 3588.941 | 276206.749 | 59.76 | 1104.999
2016-08-07 10:00 | 57189 | 3541.0451 | 306611.0804 | 59.75 | 1258.158
2016-08-07 11:00 | 61521 | 4093.129 | 324358.9491 | 59.75 | 1353.462
2016-08-07 12:00 | 65299 | 2995.5986 | 347160.8141 | 59.75 | 1436.578
2016-08-07 13:00 | 68108 | 2270.9071 | 351218.0716 | 59.75 | 1498.376
2016-08-07 14:00 | 69404 | 3422.7604 | 352443.0316 | 59.75 | 1526.888
2016-08-07 15:00 | 70680 | 3959.8062 | 352443.0316 | 59.75 | 1554.96
2016-08-07 16:00 | 71105 | 3814.6444 | 350937.6213 | 59.75 | 1564.31
2016-08-07 17:00 | 70586 | 4534.8111 | 352193.0816 | 59.75 | 1552.892
2016-08-07 18:00 | 69389 | 5189.8271 | 348824.5474 | 59.75 | 1526.558
2016-08-07 19:00 | 67506 | 6564.6963 | 344080.0295 | 59.75 | 1485.132
2016-08-07 20:00 | 65717 | 7742.7628 | 326587.3345 | 59.75 | 1445.774
2016-08-07 21:00 | 63830 | 8454.7298 | 313580.1805 | 59.75 | 1404.26
2016-08-07 22:00 | 60345 | 8607.05 | 289537.7598 | 59.76 | 1267.245
2016-08-07 23:00 | 56385 | 8465.3816 | 267629.0896 | 59.76 | 1184.085
2016-08-08 | 52938 | 9167.5069 | 237682.5112 | 59.78 | 1005.822
2016-08-08 01:00 | 50069 | 8721.8142 | 234080.4112 | 59.77 | 1001.38
2016-08-08 02:00 | 47996 | 8367.8953 | 234080.4112 | 59.77 | 959.92
2016-08-08 03:00 | 46436 | 8407.8844 | 234080.4112 | 59.77 | 928.72
2016-08-08 04:00 | 45343 | 8458.034 | 234652.9112 | 59.78 | 861.517
2016-08-08 05:00 | 44878 | 8142.767 | 234652.9112 | 59.78 | 852.682
2016-08-08 06:00 | 44692 | 7045.2414 | 236154.5612 | 59.77 | 893.84
2016-08-08 07:00 | 44745 | 5679.0545 | 236154.5612 | 59.77 | 894.9
2016-08-08 08:00 | 48168 | 4635.27 | 243679.6142 | 59.78 | 915.192
2016-08-08 09:00 | 52587 | 4826.0979 | 265652.1616 | 59.76 | 1104.327
2016-08-08 10:00 | 57041 | 5188.627 | 292853.6398 | 59.76 | 1197.861
2016-08-08 11:00 | 61336 | 4655.9817 | 321777.7609 | 59.75 | 1349.392
2016-08-08 12:00 | 65021 | 5007.6091 | 347237.1196 | 59.75 | 1430.462
2016-08-08 13:00 | 67849 | 3539.0282 | 350967.0889 | 59.75 | 1492.678
2016-08-08 14:00 | 69134 | 3183.1123 | 353189.8851 | 59.75 | 1520.948
2016-08-08 15:00 | 70453 | 3242.2719 | 353189.8851 | 59.75 | 1549.966
2016-08-08 16:00 | 71075 | 3026.3378 | 353434.1503 | 59.75 | 1563.65
2016-08-08 17:00 | 70930 | 4187.8993 | 352591.9071 | 59.75 | 1560.46
2016-08-08 18:00 | 69134 | 5541.9184 | 348429.9121 | 59.75 | 1520.948
2016-08-08 19:00 | 68025 | 7127.2206 | 346783.9618 | 59.75 | 1496.55
2016-08-08 20:00 | 66401 | 9396.6444 | 318795.0651 | 59.75 | 1460.822
2016-08-08 21:00 | 64653 | 10067.7577 | 308482.2724 | 59.75 | 1422.366
2016-08-08 22:00 | 60558 | 8740.2443 | 291203.6684 | 59.76 | 1271.718
2016-08-08 23:00 | 55855 | 8326.7915 | 261616.2287 | 59.76 | 1172.955
2016-08-09 | 49215 | 7822.5625 | 239079.5857 | 59.77 | 984.3
2016-08-09 01:00 | 46621 | 6820.6052 | 239079.5857 | 59.77 | 932.42
2016-08-09 02:00 | 44893 | 6654.7033 | 239079.5857 | 59.77 | 897.86
2016-08-09 03:00 | 43881 | 6815.7192 | 239079.5857 | 59.78 | 833.739
2016-08-09 04:00 | 43627 | 6563.0587 | 239079.5857 | 59.78 | 828.913
2016-08-09 05:00 | 44597 | 5817.1685 | 239079.5857 | 59.77 | 891.94
2016-08-09 06:00 | 46768 | 5048.979 | 239079.5857 | 59.77 | 935.36
2016-08-09 07:00 | 47862 | 3837.0432 | 242681.6857 | 59.78 | 909.378
2016-08-09 08:00 | 50695 | 2765.3188 | 267335.4562 | 59.76 | 1064.595
2016-08-09 09:00 | 54463 | 2656.7056 | 291671.5524 | 59.76 | 1143.723
2016-08-09 10:00 | 58817 | 1897.0126 | 321453.4635 | 59.75 | 1293.974
2016-08-09 11:00 | 62770 | 1976.0512 | 341302.4345 | 59.75 | 1380.94
2016-08-09 12:00 | 66270 | 2453.4446 | 348203.715 | 59.75 | 1457.94
2016-08-09 13:00 | 69177 | 2883.4554 | 350448.769 | 59.75 | 1521.894
2016-08-09 14:00 | 70711 | 2994.5251 | 354048.2157 | 59.75 | 1555.642
2016-08-09 15:00 | 72135 | 2940.8242 | 354354.4989 | 59.75 | 1586.97
2016-08-09 16:00 | 72463 | 2911.8329 | 357091.0237 | 59.75 | 1594.186
2016-08-09 17:00 | 71563 | 3296.2545 | 359341.0237 | 59.75 | 1574.386
2016-08-09 18:00 | 69263 | 3923.412 | 353074.347 | 59.75 | 1523.786
2016-08-09 19:00 | 67651 | 4650.5418 | 344928.5522 | 59.75 | 1488.322
2016-08-09 20:00 | 65844 | 5936.5524 | 332616.1409 | 59.75 | 1448.568
2016-08-09 21:00 | 63638 | 5002.9178 | 325077.8104 | 59.75 | 1400.036
2016-08-09 22:00 | 59077 | 4697.9355 | 302168.2804 | 59.75 | 1299.694
2016-08-09 23:00 | 54161 | 4981.8443 | 271868.7542 | 59.76 | 1137.381
2016-08-10 | 48673 | 5163.7948 | 239546.0357 | 59.78 | 924.787
2016-08-10 01:00 | 46005 | 4806.323 | 239546.0357 | 59.77 | 920.1
2016-08-10 02:00 | 43993 | 5250.9673 | 236387.6357 | 59.77 | 879.86
2016-08-10 03:00 | 42778 | 5396.0458 | 236387.6357 | 59.78 | 812.782
2016-08-10 04:00 | 42470 | 5137.7276 | 236387.6357 | 59.78 | 806.93
2016-08-10 05:00 | 43402 | 5530.8547 | 236387.6357 | 59.77 | 868.04
2016-08-10 06:00 | 45727 | 5277.428 | 236387.6357 | 59.77 | 914.54
2016-08-10 07:00 | 46730 | 4610.386 | 236387.6357 | 59.77 | 934.6
2016-08-10 08:00 | 49520 | 4063.8561 | 253072.1787 | 59.78 | 940.88
2016-08-10 09:00 | 53319 | 2512.7385 | 289836.4264 | 59.76 | 1119.699
2016-08-10 10:00 | 57606 | 2266.1294 | 319319.0515 | 59.75 | 1267.332
2016-08-10 11:00 | 61733 | 1703.6504 | 344564.8125 | 59.75 | 1358.126
2016-08-10 12:00 | 65252 | 1714.3873 | 354886.6098 | 59.75 | 1435.544
2016-08-10 13:00 | 68091 | 1516.8659 | 358675.164 | 59.75 | 1498.002
2016-08-10 14:00 | 69516 | 1982.135 | 360040.2309 | 59.75 | 1529.352
2016-08-10 15:00 | 70558 | 2391.465 | 360040.2309 | 59.75 | 1552.276
2016-08-10 16:00 | 70820 | 2234.2385 | 360174.0242 | 59.75 | 1558.04
2016-08-10 17:00 | 70238 | 2969.086 | 360040.2309 | 59.75 | 1545.236
2016-08-10 18:00 | 68908 | 3792.2716 | 354463.2048 | 59.75 | 1515.976
2016-08-10 19:00 | 66892 | 4148.7238 | 348042.8987 | 59.75 | 1471.624
2016-08-10 20:00 | 65175 | 4879.9597 | 339503.7962 | 59.75 | 1433.85
2016-08-10 21:00 | 62780 | 4813.3767 | 331114.7278 | 59.75 | 1381.16
2016-08-10 22:00 | 58240 | 4920.5997 | 307765.2424 | 59.75 | 1281.28
2016-08-10 23:00 | 53444 | 5389.882 | 272217.5162 | 59.76 | 1122.324
2016-08-11 | 48130 | 7294.4326 | 236756.4377 | 59.77 | 962.6
2016-08-11 01:00 | 45651 | 6979.6711 | 236756.4377 | 59.77 | 913.02
2016-08-11 02:00 | 43879 | 6153.5448 | 236756.4377 | 59.77 | 877.58
2016-08-11 03:00 | 42755 | 5850.0399 | 236756.4377 | 59.78 | 812.345
2016-08-11 04:00 | 42264 | 5009.7511 | 236756.4377 | 59.78 | 803.016
2016-08-11 05:00 | 43164 | 3845.7435 | 239914.8377 | 59.77 | 863.28
2016-08-11 06:00 | 45053 | 3029.538 | 239914.8377 | 59.77 | 901.06
2016-08-11 07:00 | 45880 | 2291.2323 | 239914.8377 | 59.78 | 871.72
2016-08-11 08:00 | 48400 | 1689.2475 | 264806.3507 | 59.78 | 919.6
2016-08-11 09:00 | 52273 | 1247.9196 | 292329.3784 | 59.76 | 1097.733
2016-08-11 10:00 | 56757 | 877.4065 | 320582.7295 | 59.75 | 1248.654
2016-08-11 11:00 | 60978 | 742.0533 | 345389.1445 | 59.75 | 1341.516
2016-08-11 12:00 | 64211 | 832.4225 | 347987.726 | 59.75 | 1412.642
2016-08-11 13:00 | 66798 | 955.1613 | 351046.5151 | 59.75 | 1469.556
2016-08-11 14:00 | 68149 | 1242.0244 | 354238.3151 | 59.75 | 1499.278
2016-08-11 15:00 | 68693 | 1359.0994 | 354238.3151 | 59.75 | 1511.246
2016-08-11 16:00 | 68626 | 1612.0042 | 354238.3151 | 59.75 | 1509.772
2016-08-11 17:00 | 67877 | 2116.8091 | 353013.3551 | 59.75 | 1493.294
2016-08-11 18:00 | 65615 | 2132.3421 | 352033.5481 | 59.75 | 1443.53
2016-08-11 19:00 | 63354 | 3494.8698 | 336253.366 | 59.75 | 1393.788
2016-08-11 20:00 | 62007 | 5808.5033 | 318353.9459 | 59.75 | 1364.154
2016-08-11 21:00 | 59793 | 4913.6676 | 309802.1555 | 59.75 | 1315.446
2016-08-11 22:00 | 55658 | 3752.4028 | 283983.9895 | 59.76 | 1168.818
2016-08-11 23:00 | 51378 | 4343.5255 | 256979.0899 | 59.78 | 976.182
2016-08-12 | 48523 | 3461.9979 | 243874.2569 | 59.78 | 921.937
2016-08-12 01:00 | 46002 | 3140.9512 | 242363.9369 | 59.78 | 874.038
2016-08-12 02:00 | 44195 | 3460.2699 | 242363.9369 | 59.77 | 883.9
2016-08-12 03:00 | 43118 | 3913.0959 | 242363.9369 | 59.77 | 862.36
2016-08-12 04:00 | 42857 | 4220.3942 | 242363.9369 | 59.77 | 857.14
2016-08-12 05:00 | 44001 | 4664.3638 | 242363.9369 | 59.77 | 880.02
2016-08-12 06:00 | 45932 | 4754.0346 | 242363.9369 | 59.77 | 918.64
2016-08-12 07:00 | 46736 | 3242.7942 | 242363.9369 | 59.78 | 887.984
2016-08-12 08:00 | 48655 | 2071.4858 | 255468.7699 | 59.78 | 924.445
2016-08-12 09:00 | 52219 | 1881.7012 | 282968.4101 | 59.76 | 1096.599
2016-08-12 10:00 | 56457 | 1337.2233 | 314823.8135 | 59.75 | 1242.054
2016-08-12 11:00 | 60234 | 655.5934 | 339738.9406 | 59.75 | 1325.148
2016-08-12 12:00 | 63500 | 567.5767 | 355101.4993 | 59.75 | 1397
2016-08-12 13:00 | 66061 | 829.4107 | 352428.9779 | 59.75 | 1453.342
2016-08-12 14:00 | 67673 | 1094.5712 | 354919.6177 | 59.75 | 1488.806
2016-08-12 15:00 | 68766 | 979.5461 | 354919.6177 | 59.75 | 1512.852
2016-08-12 16:00 | 69060 | 1038.2545 | 354919.6177 | 59.75 | 1519.32
2016-08-12 17:00 | 68498 | 1176.0601 | 354919.6177 | 59.75 | 1506.956
2016-08-12 18:00 | 66462 | 1834.6389 | 351996.5087 | 59.75 | 1462.164
2016-08-12 19:00 | 64426 | 3141.8451 | 345574.1082 | 59.75 | 1417.372
2016-08-12 20:00 | 63032 | 5367.7953 | 323786.8355 | 59.75 | 1386.704
2016-08-12 21:00 | 60884 | 7477.8645 | 296905.6204 | 59.75 | 1339.448
2016-08-12 22:00 | 56672 | 7362.6103 | 265015.0802 | 59.76 | 1190.112
2016-08-12 23:00 | 52364 | 7322.9489 | 239802.0177 | 59.78 | 994.916
2016-08-13 | 51556 | 7606.7414 | 236565.3477 | 59.78 | 979.564
2016-08-13 01:00 | 48915 | 6835.9695 | 231544.8597 | 59.77 | 978.3
2016-08-13 02:00 | 46883 | 5701.1272 | 231544.8597 | 59.77 | 937.66
2016-08-13 03:00 | 45579 | 6029.2915 | 231544.8597 | 59.77 | 911.58
2016-08-13 04:00 | 45248 | 6913.0313 | 231544.8597 | 59.77 | 904.96
2016-08-13 05:00 | 46218 | 6762.7125 | 231544.8597 | 59.77 | 924.36
2016-08-13 06:00 | 48152 | 6850.3939 | 233055.1797 | 59.77 | 963.04
2016-08-13 07:00 | 48934 | 6037.6217 | 233055.1797 | 59.78 | 929.746
2016-08-13 08:00 | 51639 | 5345.9431 | 250981.5622 | 59.78 | 981.141
2016-08-13 09:00 | 55551 | 5699.0814 | 271186.44 | 59.76 | 1166.571
2016-08-13 10:00 | 59856 | 5447.5295 | 302768.1364 | 59.75 | 1316.832
2016-08-13 11:00 | 63840 | 4925.2433 | 330594.9218 | 59.75 | 1404.48
2016-08-13 12:00 | 67336 | 5457.6154 | 342057.9805 | 59.75 | 1481.392
2016-08-13 13:00 | 69745 | 4194.8546 | 350326.1478 | 59.75 | 1534.39
2016-08-13 14:00 | 71920 | 3423.033 | 355698.9419 | 59.75 | 1582.24
2016-08-13 15:00 | 72853 | 3679.5304 | 355698.9419 | 59.75 | 1602.766
2016-08-13 16:00 | 72840 | 3466.6522 | 354673.405 | 59.75 | 1602.48
2016-08-13 17:00 | 71746 | 4101.1811 | 354174.3419 | 59.75 | 1578.412
2016-08-13 18:00 | 69156 | 5637.3615 | 350754.141 | 59.75 | 1521.432
2016-08-13 19:00 | 67253 | 6130.3289 | 343303.5502 | 59.75 | 1479.566
2016-08-13 20:00 | 65551 | 6839.8061 | 331294.3215 | 59.75 | 1442.122
2016-08-13 21:00 | 63345 | 8562.364 | 308211.6771 | 59.75 | 1393.59
2016-08-13 22:00 | 59430 | 9437.3658 | 283652.3316 | 59.76 | 1248.03
2016-08-13 23:00 | 55444 | 9336.2288 | 261869.4387 | 59.78 | 1053.436
2016-08-14 | 52801 | 9891.7585 | 240810.6457 | 59.78 | 1003.219
2016-08-14 01:00 | 49948 | 8932.747 | 239291.6457 | 59.77 | 998.96
2016-08-14 02:00 | 47904 | 8015.1155 | 236559.5177 | 59.77 | 958.08
2016-08-14 03:00 | 46414 | 7012.9155 | 236559.5177 | 59.77 | 928.28
2016-08-14 04:00 | 45708 | 6429.5482 | 236559.5177 | 59.77 | 914.16
2016-08-14 05:00 | 45722 | 5916.2476 | 236559.5177 | 59.77 | 914.44
2016-08-14 06:00 | 46239 | 5953.802 | 236559.5177 | 59.77 | 924.78
2016-08-14 07:00 | 46564 | 4491.957 | 237581.4247 | 59.77 | 931.28
2016-08-14 08:00 | 49671 | 3424.2904 | 255706.7457 | 59.78 | 943.749
2016-08-14 09:00 | 54218 | 3999.3371 | 279589.1516 | 59.76 | 1138.578
2016-08-14 10:00 | 58893 | 4248.0859 | 309982.2876 | 59.75 | 1295.646
2016-08-14 11:00 | 63007 | 4426.3381 | 330519.9117 | 59.75 | 1386.154
2016-08-14 12:00 | 66397 | 5892.3264 | 343951.0534 | 59.75 | 1460.734
2016-08-14 13:00 | 68839 | 5056.4983 | 352244.7654 | 59.75 | 1514.458
2016-08-14 14:00 | 69977 | 4434.0327 | 352397.3686 | 59.75 | 1539.494
2016-08-14 15:00 | 71195 | 4157.391 | 353348.0229 | 59.75 | 1566.29
2016-08-14 16:00 | 71833 | 3574.7209 | 355107.5795 | 59.75 | 1580.326
2016-08-14 17:00 | 71473 | 3346.8595 | 354747.0396 | 59.75 | 1572.406
2016-08-14 18:00 | 69537 | 3236.0888 | 354183.8384 | 59.75 | 1529.814
2016-08-14 19:00 | 68287 | 4969.6976 | 350035.7694 | 59.75 | 1502.314
2016-08-14 20:00 | 66633 | 7405.5295 | 334221.9362 | 59.75 | 1465.926
2016-08-14 21:00 | 64442 | 8768.898 | 312681.1402 | 59.75 | 1417.724
2016-08-14 22:00 | 60710 | 7484.2427 | 300264.4778 | 59.75 | 1335.62
2016-08-14 23:00 | 56948 | 6730.4611 | 278821.9038 | 59.76 | 1195.908
2016-08-15 | 52498 | 7654.9216 | 247686.765 | 59.78 | 997.462
2016-08-15 01:00 | 49780 | 6847.4694 | 242553.0686 | 59.78 | 945.82
2016-08-15 02:00 | 47680 | 6286.0594 | 242553.0686 | 59.77 | 953.6
2016-08-15 03:00 | 46226 | 6159.328 | 241404.1766 | 59.77 | 924.52
2016-08-15 04:00 | 45111 | 5474.921 | 241404.1766 | 59.77 | 902.22
2016-08-15 05:00 | 44665 | 4969.4518 | 241404.1766 | 59.77 | 893.3
2016-08-15 06:00 | 44581 | 4197.5622 | 241404.1766 | 59.77 | 891.62
2016-08-15 07:00 | 44472 | 3198.9146 | 241404.1766 | 59.77 | 889.44
2016-08-15 08:00 | 47537 | 2388.7082 | 250906.9096 | 59.78 | 903.203
2016-08-15 09:00 | 51805 | 2076.3939 | 278013.1498 | 59.76 | 1087.905
2016-08-15 10:00 | 56273 | 2422.3169 | 307395.5742 | 59.75 | 1238.006
2016-08-15 11:00 | 60595 | 2502.2189 | 328722.0503 | 59.75 | 1333.09
2016-08-15 12:00 | 64400 | 2307.3485 | 347581.201 | 59.75 | 1416.8
2016-08-15 13:00 | 67304 | 2280.1091 | 349982.553 | 59.75 | 1480.688
2016-08-15 14:00 | 69226 | 1682.6765 | 352433.9173 | 59.75 | 1522.972
2016-08-15 15:00 | 69852 | 2130.9408 | 353171.4163 | 59.75 | 1536.744
2016-08-15 16:00 | 70510 | 2607.8694 | 353451.4163 | 59.75 | 1551.22
2016-08-15 17:00 | 70433 | 3353.8706 | 353451.4163 | 59.75 | 1549.526
2016-08-15 18:00 | 69316 | 4011.8609 | 351395.4043 | 59.75 | 1524.952
2016-08-15 19:00 | 67513 | 3678.7779 | 349340.5493 | 59.75 | 1485.286
2016-08-15 20:00 | 66092 | 4272.3548 | 339836.4473 | 59.75 | 1454.024
2016-08-15 21:00 | 63869 | 6281.8751 | 322333.0161 | 59.75 | 1405.118
2016-08-15 22:00 | 59639 | 4124.8258 | 315170.4454 | 59.75 | 1312.058
2016-08-15 23:00 | 55236 | 3284.8792 | 293442.5694 | 59.76 | 1159.956
2016-08-16 | 49859 | 3390.7292 | 266105.1298 | 59.78 | 947.321
2016-08-16 01:00 | 47196 | 2471.5667 | 266105.1298 | 59.78 | 896.724
2016-08-16 02:00 | 45480 | 2296.077 | 265978.6498 | 59.78 | 864.12
2016-08-16 03:00 | 44454 | 1625.1691 | 265978.6498 | 59.78 | 844.626
2016-08-16 04:00 | 44174 | 1174.7809 | 262935.8418 | 59.78 | 839.306
2016-08-16 05:00 | 45149 | 1097.2693 | 263465.3638 | 59.78 | 857.831
2016-08-16 06:00 | 47215 | 1428.0334 | 263465.3638 | 59.78 | 897.085
2016-08-16 07:00 | 47843 | 897.7988 | 263465.3638 | 59.78 | 909.017
2016-08-16 08:00 | 50065 | 634.7595 | 275095.8282 | 59.76 | 1051.365
2016-08-16 09:00 | 53723 | 1025.1011 | 300863.3078 | 59.75 | 1181.906
2016-08-16 10:00 | 57995 | 898.7713 | 325397.4742 | 59.75 | 1275.89
2016-08-16 11:00 | 62412 | 1986.4071 | 345707.2341 | 59.75 | 1373.064
2016-08-16 12:00 | 66441 | 1499.6911 | 362854.1609 | 59.75 | 1461.702
2016-08-16 13:00 | 69296 | 1309.0584 | 365896.2096 | 59.75 | 1524.512
2016-08-16 14:00 | 71563 | 982.4573 | 369199.7826 | 59.75 | 1574.386
2016-08-16 15:00 | 71921 | 858.9704 | 369484.1906 | 59.75 | 1582.262
2016-08-16 16:00 | 70429 | 1322.2469 | 367986.3512 | 59.75 | 1549.438
2016-08-16 17:00 | 68856 | 1952.8063 | 363506.9399 | 59.75 | 1514.832
2016-08-16 18:00 | 67066 | 2992.78 | 361676.2714 | 59.75 | 1475.452
2016-08-16 19:00 | 64589 | 3647.2103 | 350631.7451 | 59.75 | 1420.958
2016-08-16 20:00 | 63144 | 4582.4906 | 330601.5304 | 59.75 | 1389.168
2016-08-16 21:00 | 60679 | 4471.6093 | 318398.2424 | 59.75 | 1334.938
2016-08-16 22:00 | 56202 | 3211.9362 | 297837.8964 | 59.75 | 1236.444
2016-08-16 23:00 | 51744 | 2993.7015 | 270931.2052 | 59.76 | 1086.624
2016-08-17 | 47713 | 3707.2142 | 244941.9357 | 59.78 | 906.547
2016-08-17 01:00 | 45287 | 3437.7925 | 244941.9357 | 59.77 | 905.74
2016-08-17 02:00 | 43526 | 4178.9296 | 245068.4157 | 59.77 | 870.52
2016-08-17 03:00 | 42450 | 4596.5112 | 242675.1857 | 59.77 | 849
2016-08-17 04:00 | 42191 | 3846.7934 | 242675.1857 | 59.77 | 843.82
2016-08-17 05:00 | 43383 | 3358.0182 | 243294.5557 | 59.77 | 867.66
2016-08-17 06:00 | 45788 | 2249.2151 | 243294.5557 | 59.78 | 869.972
2016-08-17 07:00 | 46460 | 2502.9685 | 243294.5557 | 59.78 | 882.74
2016-08-17 08:00 | 48474 | 2984.7725 | 247776.8007 | 59.78 | 921.006
2016-08-17 09:00 | 51906 | 2948.0276 | 273241.1342 | 59.76 | 1090.026
2016-08-17 10:00 | 56068 | 4399.4144 | 292373.5564 | 59.76 | 1177.428
2016-08-17 11:00 | 60247 | 5595.4924 | 311103.2324 | 59.75 | 1325.434
2016-08-17 12:00 | 64145 | 3571.5572 | 347915.8891 | 59.75 | 1411.19
2016-08-17 13:00 | 67470 | 2796.4553 | 350950.0679 | 59.75 | 1484.34
2016-08-17 14:00 | 69120 | 3046.2282 | 355081.7197 | 59.75 | 1520.64
2016-08-17 15:00 | 70533 | 2778.1194 | 355239.8329 | 59.75 | 1551.726
2016-08-17 16:00 | 70621 | 3023.8204 | 355203.2329 | 59.75 | 1553.662
2016-08-17 17:00 | 69464 | 2821.7947 | 355081.7197 | 59.75 | 1528.208
2016-08-17 18:00 | 67487 | 3211.4867 | 352158.6107 | 59.75 | 1484.714
2016-08-17 19:00 | 64823 | 3928.6137 | 349081.8842 | 59.75 | 1426.106
2016-08-17 20:00 | 63512 | 5541.3598 | 326092.3415 | 59.75 | 1397.264
2016-08-17 21:00 | 61177 | 4980.7384 | 314872.1924 | 59.75 | 1345.894
2016-08-17 22:00 | 57010 | 5504.1453 | 283791.119 | 59.76 | 1197.21
2016-08-17 23:00 | 52650 | 5644.2096 | 258203.8787 | 59.78 | 1000.35
2016-08-18 | 47186 | 4795.6744 | 244544.8557 | 59.77 | 943.72
2016-08-18 01:00 | 44719 | 4252.0373 | 244544.8557 | 59.77 | 894.38
2016-08-18 02:00 | 43135 | 3541.0998 | 244544.8557 | 59.77 | 862.7
2016-08-18 03:00 | 42104 | 2741.6528 | 246938.0857 | 59.77 | 842.08
2016-08-18 04:00 | 41895 | 2348.8546 | 246938.0857 | 59.77 | 837.9
2016-08-18 05:00 | 43040 | 1954.5841 | 246938.0857 | 59.77 | 860.8
2016-08-18 06:00 | 45275 | 1504.5337 | 246938.0857 | 59.78 | 860.225
2016-08-18 07:00 | 46054 | 1046.817 | 246938.0857 | 59.78 | 875.026
2016-08-18 08:00 | 47662 | 828.9959 | 253896.5857 | 59.78 | 905.578
2016-08-18 09:00 | 50688 | 712.8604 | 275096.3962 | 59.76 | 1064.448
2016-08-18 10:00 | 54035 | 853.9156 | 298658.3264 | 59.75 | 1188.77
2016-08-18 11:00 | 57178 | 1480.4842 | 320260.1679 | 59.75 | 1257.916
2016-08-18 12:00 | 59860 | 2251.2884 | 336212.3036 | 59.75 | 1316.92
2016-08-18 13:00 | 62397 | 2096.0418 | 338789.8984 | 59.75 | 1372.734
2016-08-18 14:00 | 64480 | 1931.4662 | 341440.4343 | 59.75 | 1418.56
2016-08-18 15:00 | 65733 | 3022.6829 | 341440.4343 | 59.75 | 1446.126
2016-08-18 16:00 | 66226 | 3247.865 | 341440.4343 | 59.75 | 1456.972
2016-08-18 17:00 | 65582 | 3576.5871 | 341440.4343 | 59.75 | 1442.804
2016-08-18 18:00 | 63439 | 4123.2927 | 336581.2356 | 59.75 | 1395.658
2016-08-18 19:00 | 61295 | 4932.9408 | 329176.0401 | 59.75 | 1348.49
2016-08-18 20:00 | 60123 | 5980.7258 | 310409.8902 | 59.75 | 1322.706
2016-08-18 21:00 | 57743 | 5524.2701 | 297993.2278 | 59.76 | 1212.603
2016-08-18 22:00 | 53875 | 4923.224 | 273845.7344 | 59.76 | 1131.375
2016-08-18 23:00 | 49693 | 4245.223 | 258141.1742 | 59.78 | 944.167
2016-08-19 | 46554 | 4331.1177 | 248130.3992 | 59.77 | 931.08
2016-08-19 01:00 | 44205 | 4090.7161 | 248130.3992 | 59.77 | 884.1
2016-08-19 02:00 | 42580 | 3694.2114 | 248130.3992 | 59.77 | 851.6
2016-08-19 03:00 | 41614 | 4088.6062 | 248130.3992 | 59.77 | 832.28
2016-08-19 04:00 | 41448 | 4103.6478 | 248130.3992 | 59.78 | 787.512
2016-08-19 05:00 | 42615 | 4224.0524 | 246136.8492 | 59.77 | 852.3
2016-08-19 06:00 | 44815 | 3548.6408 | 244247.8992 | 59.77 | 896.3
2016-08-19 07:00 | 45518 | 2929.5524 | 244247.8992 | 59.78 | 864.842
2016-08-19 08:00 | 47693 | 2519.5596 | 260516.8242 | 59.78 | 906.167
2016-08-19 09:00 | 51255 | 2594.9058 | 280661.8518 | 59.76 | 1076.355
2016-08-19 10:00 | 55028 | 2592.926 | 305445.1822 | 59.76 | 1155.588
2016-08-19 11:00 | 58660 | 2188.5022 | 333183.9352 | 59.75 | 1290.52
2016-08-19 12:00 | 61506 | 2313.9976 | 339769.7318 | 59.75 | 1353.132
2016-08-19 13:00 | 63826 | 2016.142 | 341494.4109 | 59.75 | 1404.172
2016-08-19 14:00 | 65505 | 2009.2998 | 343731.1331 | 59.75 | 1441.11
2016-08-19 15:00 | 66850 | 2300.6702 | 341551.5996 | 59.75 | 1470.7
2016-08-19 16:00 | 66917 | 2204.9102 | 341551.5996 | 59.75 | 1472.174
2016-08-19 17:00 | 65280 | 2581.2684 | 341130.7028 | 59.75 | 1436.16
2016-08-19 18:00 | 62913 | 3320.8629 | 337957.2983 | 59.75 | 1384.086
2016-08-19 19:00 | 60546 | 5540.0791 | 310144.4633 | 59.75 | 1332.012
2016-08-19 20:00 | 59696 | 9023.7448 | 282368.3829 | 59.76 | 1253.616
2016-08-19 21:00 | 57716 | 9957.652 | 266357.3553 | 59.76 | 1212.036
2016-08-19 22:00 | 54161 | 9945.8983 | 240869.8923 | 59.78 | 1029.059
2016-08-19 23:00 | 50237 | 10043.2663 | 217568.6543 | 59.77 | 1004.74
2016-08-20 | 48697 | 9350.9521 | 214214.9439 | 59.77 | 973.94
2016-08-20 01:00 | 46417 | 9383.5205 | 211895.7007 | 59.78 | 881.923
2016-08-20 02:00 | 44844 | 9289.099 | 211895.7007 | 59.78 | 852.036
2016-08-20 03:00 | 43828 | 9668.0659 | 211895.7007 | 59.78 | 832.732
2016-08-20 04:00 | 43776 | 9968.8952 | 211611.2927 | 59.78 | 831.744
2016-08-20 05:00 | 45072 | 9796.4934 | 213604.8427 | 59.78 | 856.368
2016-08-20 06:00 | 47461 | 8825.5512 | 215023.9177 | 59.77 | 949.22
2016-08-20 07:00 | 48326 | 9223.023 | 215023.9177 | 59.77 | 966.52
2016-08-20 08:00 | 50477 | 9894.4612 | 215023.9177 | 59.77 | 1009.54
2016-08-20 09:00 | 54221 | 7914.6528 | 251667.2111 | 59.78 | 1030.199
2016-08-20 10:00 | 58228 | 7708.7966 | 280495.2705 | 59.76 | 1222.788
2016-08-20 11:00 | 61610 | 7373.1626 | 308042.9294 | 59.75 | 1355.42
2016-08-20 12:00 | 64287 | 6873.4627 | 334147.9297 | 59.75 | 1414.314
2016-08-20 13:00 | 66810 | 5644.1854 | 344311.5197 | 59.75 | 1469.82
2016-08-20 14:00 | 68495 | 4144.8215 | 348097.8428 | 59.75 | 1506.89
2016-08-20 15:00 | 69063 | 3472.0196 | 349726.6888 | 59.75 | 1519.386
2016-08-20 16:00 | 69073 | 3060.3236 | 349726.6888 | 59.75 | 1519.606
2016-08-20 17:00 | 68319 | 3147.8889 | 349726.6888 | 59.75 | 1503.018
2016-08-20 18:00 | 65839 | 4451.1527 | 345631.7167 | 59.75 | 1448.458
2016-08-20 19:00 | 63359 | 5652.9112 | 330904.5602 | 59.75 | 1393.898
2016-08-20 20:00 | 61970 | 7045.7061 | 307039.7859 | 59.75 | 1363.34
2016-08-20 21:00 | 59979 | 8098.8559 | 280582.6835 | 59.76 | 1259.559
2016-08-20 22:00 | 56429 | 9310.056 | 250564.9982 | 59.78 | 1072.151
2016-08-20 23:00 | 52638 | 8763.525 | 236314.4032 | 59.78 | 1000.122
2016-08-21 | 51511 | 8090.2119 | 236314.4032 | 59.78 | 978.709
2016-08-21 01:00 | 48799 | 6382.8643 | 236314.4032 | 59.77 | 975.98
2016-08-21 02:00 | 46928 | 5408.7422 | 236314.4032 | 59.77 | 938.56
2016-08-21 03:00 | 45452 | 5249.6717 | 234155.0032 | 59.77 | 909.04
2016-08-21 04:00 | 44635 | 6120.3092 | 234439.4112 | 59.77 | 892.7
2016-08-21 05:00 | 44756 | 5935.1294 | 234439.4112 | 59.77 | 895.12
2016-08-21 06:00 | 45397 | 5865.5372 | 234909.2862 | 59.77 | 907.94
2016-08-21 07:00 | 45787 | 5581.584 | 237228.5294 | 59.77 | 915.74
2016-08-21 08:00 | 49041 | 5558.9396 | 237228.5294 | 59.78 | 931.779
2016-08-21 09:00 | 53495 | 5843.7079 | 263466.4436 | 59.76 | 1123.395
2016-08-21 10:00 | 57751 | 4689.8881 | 295626.36 | 59.75 | 1270.522
2016-08-21 11:00 | 61436 | 4053.6766 | 324888.1855 | 59.75 | 1351.592
2016-08-21 12:00 | 64553 | 3485.5439 | 346789.1816 | 59.75 | 1420.166
2016-08-21 13:00 | 67206 | 2586.0351 | 357101.888 | 59.75 | 1478.532
2016-08-21 14:00 | 69355 | 2497.3087 | 359499.7624 | 59.75 | 1525.81
2016-08-21 15:00 | 70234 | 2970.0905 | 358793.8099 | 59.75 | 1545.148
2016-08-21 16:00 | 70985 | 2514.3651 | 359376.753 | 59.75 | 1561.67
2016-08-21 17:00 | 70672 | 2316.7264 | 359016.2131 | 59.75 | 1554.784
2016-08-21 18:00 | 69259 | 2719.0478 | 357568.8499 | 59.75 | 1523.698
2016-08-21 19:00 | 67158 | 3344.6312 | 354584.7449 | 59.75 | 1477.476
2016-08-21 20:00 | 65503 | 4088.9265 | 346795.6681 | 59.75 | 1441.066
2016-08-21 21:00 | 62962 | 5086.4113 | 328954.1514 | 59.75 | 1385.164
2016-08-21 22:00 | 59146 | 5426.5404 | 305797.3015 | 59.75 | 1301.212
2016-08-21 23:00 | 55250 | 5280.0164 | 282254.0375 | 59.76 | 1160.25
2016-08-22 | 52109 | 5832.9317 | 256893.5299 | 59.78 | 990.071
2016-08-22 01:00 | 49277 | 6244.8192 | 246559.1849 | 59.78 | 936.263
2016-08-22 02:00 | 47256 | 6295.8888 | 246559.1849 | 59.77 | 945.12
2016-08-22 03:00 | 45820 | 7071.0487 | 248718.5849 | 59.77 | 916.4
2016-08-22 04:00 | 44861 | 6209.6832 | 248718.5849 | 59.77 | 897.22
2016-08-22 05:00 | 44561 | 5767.06 | 248718.5849 | 59.77 | 891.22
2016-08-22 06:00 | 44594 | 5253.9759 | 248718.5849 | 59.77 | 891.88
2016-08-22 07:00 | 44528 | 4072.3184 | 247944.2549 | 59.77 | 890.56
2016-08-22 08:00 | 47424 | 3324.3493 | 247169.9249 | 59.78 | 901.056
2016-08-22 09:00 | 51926 | 2412.0212 | 276920.498 | 59.76 | 1090.446
2016-08-22 10:00 | 56525 | 1455.302 | 313795.0024 | 59.75 | 1243.55
2016-08-22 11:00 | 60729 | 879.4428 | 339427.6341 | 59.75 | 1336.038
2016-08-22 12:00 | 64859 | 1144.4604 | 354524.4522 | 59.75 | 1426.898
2016-08-22 13:00 | 68356 | 1690.0393 | 362068.2439 | 59.75 | 1503.832
2016-08-22 14:00 | 70258 | 1978.2288 | 363311.8342 | 59.75 | 1545.676
2016-08-22 15:00 | 72040 | 2033.0348 | 367270.7834 | 59.75 | 1584.88
2016-08-22 16:00 | 73048 | 1877.3605 | 366820.4664 | 59.75 | 1607.056
2016-08-22 17:00 | 73230 | 1413.6031 | 369869.6162 | 59.75 | 1611.06
2016-08-22 18:00 | 71541 | 2483.5771 | 364661.5604 | 59.75 | 1573.902
2016-08-22 19:00 | 69851 | 2663.4405 | 357756.8133 | 59.75 | 1536.722
2016-08-22 20:00 | 69219 | 3417.1116 | 352752.5649 | 59.75 | 1522.818
2016-08-22 21:00 | 66209 | 3155.3791 | 346577.7332 | 59.75 | 1456.598
2016-08-22 22:00 | 61172 | 3383.2555 | 325658.7924 | 59.75 | 1345.784
2016-08-22 23:00 | 55939 | 3927.996 | 297704.5324 | 59.76 | 1174.719
2016-08-23 | 50249 | 4448.5852 | 263428.0307 | 59.78 | 954.731
2016-08-23 01:00 | 47605 | 4484.0052 | 263428.0307 | 59.78 | 904.495
2016-08-23 02:00 | 45901 | 3689.7269 | 263428.0307 | 59.77 | 918.02
2016-08-23 03:00 | 44893 | 3573.8594 | 263428.0307 | 59.77 | 897.86
2016-08-23 04:00 | 44611 | 3882.4771 | 263428.0307 | 59.77 | 892.22
2016-08-23 05:00 | 45911 | 4488.9643 | 263428.0307 | 59.77 | 918.22
2016-08-23 06:00 | 48788 | 4352.1361 | 262837.0227 | 59.78 | 926.972
2016-08-23 07:00 | 48969 | 3307.0945 | 263611.3527 | 59.78 | 930.411
2016-08-23 08:00 | 50727 | 2587.656 | 271504.9827 | 59.76 | 1065.267
2016-08-23 09:00 | 54523 | 1814.0443 | 301881.2184 | 59.75 | 1199.506
2016-08-23 10:00 | 58962 | 1845.5582 | 327116.7779 | 59.75 | 1297.164
2016-08-23 11:00 | 63592 | 1261.4535 | 352065.6235 | 59.75 | 1399.024
2016-08-23 12:00 | 68055 | 996.3119 | 364111.8689 | 59.75 | 1497.21
2016-08-23 13:00 | 71086 | 830.129 | 365617.3602 | 59.75 | 1563.892
2016-08-23 14:00 | 73588 | 911.9371 | 375525.4702 | 59.75 | 1618.936
2016-08-23 15:00 | 74619 | 1569.4418 | 377693.1476 | 59.75 | 1641.618
2016-08-23 16:00 | 74700 | 1250.415 | 379334.1256 | 59.75 | 1643.4
2016-08-23 17:00 | 73004 | 1522.3792 | 368712.7382 | 59.75 | 1606.088
2016-08-23 18:00 | 70301 | 1769.4321 | 363677.3368 | 59.75 | 1546.622
2016-08-23 19:00 | 68285 | 2813.7301 | 355105.2555 | 59.75 | 1502.27
2016-08-23 20:00 | 66942 | 4704.8861 | 341441.5745 | 59.75 | 1472.724
2016-08-23 21:00 | 63721 | 4869.2341 | 330434.9572 | 59.75 | 1401.862
2016-08-23 22:00 | 58828 | 3709.0522 | 310138.7081 | 59.75 | 1294.216
2016-08-23 23:00 | 53959 | 4017.0404 | 277924.7371 | 59.76 | 1133.139
2016-08-24 | 50415 | 3706.899 | 257231.6564 | 59.78 | 957.885
2016-08-24 01:00 | 47791 | 3779.3159 | 253352.0306 | 59.78 | 908.029
2016-08-24 02:00 | 45949 | 4375.9001 | 253352.0306 | 59.77 | 918.98
2016-08-24 03:00 | 44726 | 5266.8494 | 253352.0306 | 59.77 | 894.52
2016-08-24 04:00 | 44472 | 4865.6737 | 253352.0306 | 59.77 | 889.44
2016-08-24 05:00 | 45775 | 4789.9647 | 253352.0306 | 59.77 | 915.5
2016-08-24 06:00 | 48825 | 5146.349 | 253079.7386 | 59.78 | 927.675
2016-08-24 07:00 | 49153 | 4279.0161 | 252488.7306 | 59.78 | 933.907
2016-08-24 08:00 | 50838 | 4054.0864 | 258514.2401 | 59.78 | 965.922
2016-08-24 09:00 | 54494 | 4008.5544 | 287558.5783 | 59.76 | 1144.374
2016-08-24 10:00 | 58641 | 5211.7992 | 305854.3378 | 59.75 | 1290.102
2016-08-24 11:00 | 62255 | 7689.4519 | 314108.1318 | 59.75 | 1369.61
2016-08-24 12:00 | 65515 | 9330.0296 | 317773.1662 | 59.75 | 1441.33
2016-08-24 13:00 | 68232 | 10325.9712 | 321387.3105 | 59.75 | 1501.104
2016-08-24 14:00 | 69102 | 10751.1839 | 323637.3105 | 59.75 | 1520.244
2016-08-24 15:00 | 68850 | 11549.3141 | 323637.3105 | 59.75 | 1514.7
2016-08-24 16:00 | 68793 | 11585.0426 | 322552.0759 | 59.75 | 1513.446
2016-08-24 17:00 | 66572 | 10417.2635 | 320989.5593 | 59.75 | 1464.584
2016-08-24 18:00 | 64106 | 9545.5371 | 310896.4418 | 59.75 | 1410.332
2016-08-24 19:00 | 61641 | 9433.6326 | 293244.9058 | 59.76 | 1294.461
2016-08-24 20:00 | 61034 | 8696.9554 | 294141.6746 | 59.76 | 1281.714
2016-08-24 21:00 | 58840 | 8777.2858 | 278068.6822 | 59.76 | 1235.64
2016-08-24 22:00 | 54496 | 8550.7165 | 251459.5349 | 59.78 | 1035.424
2016-08-24 23:00 | 50083 | 8155.0754 | 231112.2639 | 59.77 | 1001.66
2016-08-25 | 45095 | 7142.7208 | 227758.5535 | 59.77 | 901.9
2016-08-25 01:00 | 42999 | 7593.4281 | 226973.7293 | 59.78 | 816.981
2016-08-25 02:00 | 41476 | 7337.7469 | 225465.3793 | 59.78 | 788.044
2016-08-25 03:00 | 40552 | 7150.2088 | 225382.2543 | 59.78 | 770.488
2016-08-25 04:00 | 40401 | 6349.1801 | 225382.2543 | 59.78 | 767.619
2016-08-25 05:00 | 41967 | 4522.2605 | 225382.2543 | 59.78 | 797.373
2016-08-25 06:00 | 45086 | 3734.7645 | 228997.6043 | 59.77 | 901.72
2016-08-25 07:00 | 45670 | 3743.6986 | 229588.6123 | 59.77 | 913.4
2016-08-25 08:00 | 46272 | 3762.9335 | 232942.3227 | 59.78 | 879.168
2016-08-25 09:00 | 48195 | 3472.6053 | 243960.2702 | 59.78 | 915.705
2016-08-25 10:00 | 50458 | 6572.9558 | 246347.7702 | 59.78 | 958.702
2016-08-25 11:00 | 52464 | 6173.8078 | 249289.3702 | 59.78 | 996.816
2016-08-25 12:00 | 54428 | 5468.0459 | 267124.8232 | 59.76 | 1142.988
2016-08-25 13:00 | 56478 | 6600.4852 | 274350.6052 | 59.76 | 1186.038
2016-08-25 14:00 | 57933 | 6008.4598 | 293481.8204 | 59.76 | 1216.593
2016-08-25 15:00 | 59044 | 5699.9878 | 297546.5354 | 59.75 | 1298.968
2016-08-25 16:00 | 59601 | 5934.6585 | 298562.5354 | 59.75 | 1311.222
2016-08-25 17:00 | 59134 | 5958.8193 | 297546.5354 | 59.75 | 1300.948
2016-08-25 18:00 | 57626 | 5852.1485 | 293771.0259 | 59.76 | 1210.146
2016-08-25 19:00 | 56118 | 4650.208 | 291521.0259 | 59.76 | 1178.478
2016-08-25 20:00 | 55959 | 3690.9446 | 291521.0259 | 59.76 | 1175.139
2016-08-25 21:00 | 53961 | 3170.7351 | 282275.2539 | 59.76 | 1133.181
2016-08-25 22:00 | 50012 | 3434.6922 | 252040.8307 | 59.78 | 950.228
2016-08-25 23:00 | 45874 | 2290.9054 | 236251.4327 | 59.78 | 871.606
2016-08-26 | 41162 | 2174.0661 | 220498.8303 | 59.77 | 823.24
2016-08-26 01:00 | 39187 | 2362.6349 | 220498.8303 | 59.78 | 744.553
2016-08-26 02:00 | 37798 | 2013.0414 | 222007.1803 | 59.78 | 718.162
2016-08-26 03:00 | 36956 | 1871.5122 | 222090.3053 | 59.78 | 702.164
2016-08-26 04:00 | 36975 | 2198.9098 | 220794.7073 | 59.78 | 702.525
2016-08-26 05:00 | 38429 | 2454.4209 | 220794.7073 | 59.78 | 730.151
2016-08-26 06:00 | 41581 | 2194.6956 | 220794.7073 | 59.77 | 831.62
2016-08-26 07:00 | 42138 | 2023.0852 | 220794.7073 | 59.77 | 842.76
2016-08-26 08:00 | 43267 | 1914.9202 | 222707.1073 | 59.77 | 865.34
2016-08-26 09:00 | 45561 | 930.8467 | 240419.0057 | 59.78 | 865.659
2016-08-26 10:00 | 48407 | 1427.2699 | 257888.7087 | 59.78 | 919.733
2016-08-26 11:00 | 51378 | 1629.0302 | 275834.9766 | 59.76 | 1078.938
2016-08-26 12:00 | 54204 | 1861.8949 | 291175.8516 | 59.76 | 1138.284
2016-08-26 13:00 | 56925 | 2242.7562 | 312633.7024 | 59.75 | 1252.35
2016-08-26 14:00 | 59048 | 2785.3551 | 322150.8728 | 59.75 | 1299.056
2016-08-26 15:00 | 60435 | 2672.937 | 326880.041 | 59.75 | 1329.57
2016-08-26 16:00 | 61046 | 1930.9494 | 327160.041 | 59.75 | 1343.012
2016-08-26 17:00 | 60498 | 1618.7025 | 324705.641 | 59.75 | 1330.956
2016-08-26 18:00 | 58500 | 1827.2621 | 322316.5968 | 59.75 | 1287
2016-08-26 19:00 | 56502 | 2409.5741 | 312080.3049 | 59.75 | 1243.044
2016-08-26 20:00 | 55786 | 3358.3469 | 304120.3379 | 59.76 | 1171.506
2016-08-26 21:00 | 53121 | 3994.638 | 277440.0191 | 59.76 | 1115.541
2016-08-26 22:00 | 48759 | 3923.1629 | 246633.4357 | 59.78 | 926.421
2016-08-26 23:00 | 44413 | 3741.6866 | 222660.8573 | 59.77 | 888.26
2016-08-27 | 43054 | 3869.5586 | 222660.8573 | 59.77 | 861.08
2016-08-27 01:00 | 42140 | 4671.6152 | 222660.8573 | 59.78 | 800.66
2016-08-27 02:00 | 40494 | 4598.4689 | 222660.8573 | 59.78 | 769.386
2016-08-27 03:00 | 39423 | 4288.446 | 222660.8573 | 59.78 | 749.037
2016-08-27 04:00 | 39206 | 4994.1895 | 223956.4553 | 59.78 | 744.914
2016-08-27 05:00 | 40690 | 5228.5805 | 223956.4553 | 59.78 | 773.11
2016-08-27 06:00 | 43933 | 4910.0099 | 225105.3473 | 59.77 | 878.66
2016-08-27 07:00 | 44553 | 3601.0547 | 225105.3473 | 59.77 | 891.06
2016-08-27 08:00 | 45792 | 2397.5274 | 235209.0577 | 59.78 | 870.048
2016-08-27 09:00 | 48742 | 2044.7773 | 252785.8407 | 59.78 | 926.098
2016-08-27 10:00 | 52233 | 2788.4619 | 272957.3662 | 59.76 | 1096.893
2016-08-27 11:00 | 55663 | 3171.8033 | 294889.2912 | 59.76 | 1168.923
2016-08-27 12:00 | 58869 | 3627.9879 | 315808.3615 | 59.75 | 1295.118
2016-08-27 13:00 | 61897 | 3551.4614 | 330728.2412 | 59.75 | 1361.734
2016-08-27 14:00 | 64305 | 3690.2631 | 334976.4369 | 59.75 | 1414.71
2016-08-27 15:00 | 66176 | 3920.9858 | 336197.6694 | 59.75 | 1455.872
2016-08-27 16:00 | 67195 | 4373.673 | 336197.6694 | 59.75 | 1478.29
2016-08-27 17:00 | 66589 | 4352.0067 | 338652.0694 | 59.75 | 1464.958
2016-08-27 18:00 | 63632 | 5217.0989 | 328556.5012 | 59.75 | 1399.904
2016-08-27 19:00 | 60675 | 5764.4947 | 306624.5762 | 59.75 | 1334.85
2016-08-27 20:00 | 58580 | 6522.3126 | 285615.915 | 59.76 | 1230.18
2016-08-27 21:00 | 55441 | 8131.7336 | 251523.8399 | 59.78 | 1053.379
2016-08-27 22:00 | 51347 | 9235.3293 | 218822.8585 | 59.77 | 1026.94
2016-08-27 23:00 | 47205 | 9289.0996 | 196615.3225 | 59.77 | 944.1
2016-08-28 | 45194 | 9056.087 | 186734.5117 | 59.78 | 858.686
2016-08-28 01:00 | 42521 | 8414.8248 | 186734.5117 | 59.78 | 807.899
2016-08-28 02:00 | 40492 | 7870.6309 | 186734.5117 | 59.78 | 769.348
2016-08-28 03:00 | 39149 | 6853.7863 | 186734.5117 | 59.77 | 782.98
2016-08-28 04:00 | 38416 | 6418.0043 | 186734.5117 | 59.77 | 768.32
2016-08-28 05:00 | 38475 | 6600.3559 | 186734.5117 | 59.77 | 769.5
2016-08-28 06:00 | 39143 | 5941.2934 | 186734.5117 | 59.78 | 743.717
2016-08-28 07:00 | 39389 | 5301.2557 | 186734.5117 | 59.78 | 748.391
2016-08-28 08:00 | 42279 | 4800.3889 | 196803.3017 | 59.78 | 803.301
2016-08-28 09:00 | 46624 | 3952.6054 | 227634.5661 | 59.78 | 885.856
2016-08-28 10:00 | 51546 | 6417.2953 | 245889.6491 | 59.78 | 979.374
2016-08-28 11:00 | 56065 | 6003.6699 | 282787.4858 | 59.76 | 1177.365
2016-08-28 12:00 | 60006 | 4760.5033 | 319045.7217 | 59.75 | 1320.132
2016-08-28 13:00 | 63361 | 4801.3885 | 328246.5585 | 59.75 | 1393.942
2016-08-28 14:00 | 65847 | 5621.4545 | 330444.9803 | 59.75 | 1448.634
2016-08-28 15:00 | 67901 | 6038.6904 | 331694.0648 | 59.75 | 1493.822
2016-08-28 16:00 | 68993 | 6171.0667 | 332240.4079 | 59.75 | 1517.846
2016-08-28 17:00 | 68832 | 6651.5701 | 331694.0648 | 59.75 | 1514.304
2016-08-28 18:00 | 66554 | 7211.146 | 328596.7149 | 59.75 | 1464.188
2016-08-28 19:00 | 64276 | 8469.3827 | 325266.901 | 59.75 | 1414.072
2016-08-28 20:00 | 62924 | 9594.4454 | 305380.184 | 59.75 | 1384.328
2016-08-28 21:00 | 59964 | 9890.8742 | 279643.7156 | 59.76 | 1259.244
2016-08-28 22:00 | 56046 | 9938.6961 | 253428.728 | 59.78 | 1064.874
2016-08-28 23:00 | 52222 | 10452.3537 | 229248.737 | 59.77 | 1044.44
2016-08-29 | 48542 | 10791.2304 | 211626.2266 | 59.77 | 970.84
2016-08-29 01:00 | 46199 | 9812.8908 | 211626.2266 | 59.78 | 877.781
2016-08-29 02:00 | 44343 | 8592.6979 | 211626.2266 | 59.78 | 842.517
2016-08-29 03:00 | 43045 | 7776.8777 | 211626.2266 | 59.78 | 817.855
2016-08-29 04:00 | 42164 | 6400.2709 | 211626.2266 | 59.78 | 801.116
2016-08-29 05:00 | 41884 | 5980.4301 | 211626.2266 | 59.78 | 795.796
2016-08-29 06:00 | 42072 | 5795.7807 | 211626.2266 | 59.78 | 799.368
2016-08-29 07:00 | 41980 | 4584.9794 | 211626.2266 | 59.78 | 797.62
2016-08-29 08:00 | 44951 | 3826.1879 | 222836.337 | 59.77 | 899.02
2016-08-29 09:00 | 49317 | 3389.0819 | 252190.2187 | 59.78 | 937.023
2016-08-29 10:00 | 53881 | 5015.1303 | 272349.6562 | 59.76 | 1131.501
2016-08-29 11:00 | 58253 | 5504.3532 | 303080.4975 | 59.75 | 1281.566
2016-08-29 12:00 | 62071 | 5703.9345 | 325692.6458 | 59.75 | 1365.562
2016-08-29 13:00 | 65279 | 5678.986 | 338607.5458 | 59.75 | 1436.138
2016-08-29 14:00 | 67180 | 5385.9997 | 341942.5338 | 59.75 | 1477.96
2016-08-29 15:00 | 68472 | 5760.6591 | 342008.3405 | 59.75 | 1506.384
2016-08-29 16:00 | 69061 | 6050.0782 | 342044.9405 | 59.75 | 1519.342
2016-08-29 17:00 | 68745 | 6690.1273 | 342031.1437 | 59.75 | 1512.39
2016-08-29 18:00 | 66884 | 7757.4583 | 336913.2518 | 59.75 | 1471.448
2016-08-29 19:00 | 65024 | 8591.5768 | 323781.3547 | 59.75 | 1430.528
2016-08-29 20:00 | 64358 | 9568.7173 | 308493.4104 | 59.75 | 1415.876
2016-08-29 21:00 | 61797 | 10453.9352 | 280479.3874 | 59.76 | 1297.737
2016-08-29 22:00 | 57688 | 9989.5542 | 254892.1471 | 59.76 | 1211.448
2016-08-29 23:00 | 53176 | 9899.4157 | 234544.8761 | 59.78 | 1010.344
2016-08-30 | 48275 | 10112.9265 | 230950.9861 | 59.77 | 965.5
2016-08-30 01:00 | 46229 | 9326.4485 | 230950.9861 | 59.78 | 878.351
2016-08-30 02:00 | 44792 | 8105.1475 | 230950.9861 | 59.78 | 851.048
2016-08-30 03:00 | 44228 | 7134.0623 | 230950.9861 | 59.78 | 840.332
2016-08-30 04:00 | 44472 | 6083.5282 | 230950.9861 | 59.77 | 889.44
2016-08-30 05:00 | 46243 | 5819.8414 | 230950.9861 | 59.77 | 924.86
2016-08-30 06:00 | 49734 | 5290.7499 | 246277.7691 | 59.78 | 944.946
2016-08-30 07:00 | 50681 | 5628.6682 | 247293.7691 | 59.78 | 962.939
2016-08-30 08:00 | 51855 | 5942.4841 | 251298.2571 | 59.78 | 985.245
2016-08-30 09:00 | 54704 | 6060.9897 | 269492.1026 | 59.76 | 1148.784
2016-08-30 10:00 | 57965 | 6378.3949 | 290295.6328 | 59.76 | 1217.265
2016-08-30 11:00 | 60568 | 8701.1582 | 293267.1192 | 59.76 | 1271.928
2016-08-30 12:00 | 62412 | 8992.7664 | 302648.7912 | 59.75 | 1373.064
2016-08-30 13:00 | 64268 | 8300.3337 | 320625.4992 | 59.75 | 1413.896
2016-08-30 14:00 | 65867 | 9004.6174 | 323184.6272 | 59.75 | 1449.074
2016-08-30 15:00 | 67120 | 8904.4507 | 328004.6138 | 59.75 | 1476.64
2016-08-30 16:00 | 67925 | 8655.9456 | 326988.6138 | 59.75 | 1494.35
2016-08-30 17:00 | 67636 | 9300.6314 | 327548.6138 | 59.75 | 1487.992
2016-08-30 18:00 | 66009 | 10192.2623 | 323001.6392 | 59.75 | 1452.198
2016-08-30 19:00 | 64383 | 10708.7467 | 307926.3324 | 59.75 | 1416.426
2016-08-30 20:00 | 64015 | 10899.6904 | 301593.0604 | 59.75 | 1408.33
2016-08-30 21:00 | 61194 | 9571.1688 | 285551.966 | 59.76 | 1285.074
2016-08-30 22:00 | 56674 | 9162.3829 | 258942.8187 | 59.76 | 1190.154
2016-08-30 23:00 | 52043 | 9169.0135 | 236345.5477 | 59.78 | 988.817
2016-08-31 | 47987 | 9565.2939 | 235343.9973 | 59.77 | 959.74
2016-08-31 01:00 | 45797 | 9175.5865 | 235343.9973 | 59.78 | 870.143
2016-08-31 02:00 | 44350 | 9521.4893 | 235343.9973 | 59.78 | 842.65
2016-08-31 03:00 | 43484 | 8671.842 | 235343.9973 | 59.78 | 826.196
2016-08-31 04:00 | 43516 | 7775.8064 | 235343.9973 | 59.78 | 826.804
2016-08-31 05:00 | 45114 | 6598.4874 | 234480.6973 | 59.77 | 902.28
2016-08-31 06:00 | 48569 | 5679.9268 | 234480.6973 | 59.78 | 922.811
2016-08-31 07:00 | 49262 | 5632.1803 | 235722.4273 | 59.78 | 935.978
2016-08-31 08:00 | 50701 | 5971.4632 | 240064.6153 | 59.78 | 963.319
2016-08-31 09:00 | 53880 | 5505.1756 | 264402.4183 | 59.76 | 1131.48
2016-08-31 10:00 | 57148 | 4213.492 | 297032.666 | 59.75 | 1257.256
2016-08-31 11:00 | 60290 | 4052.8988 | 318250.7971 | 59.75 | 1326.38
2016-08-31 12:00 | 62853 | 4348.1633 | 333544.9184 | 59.75 | 1382.766
2016-08-31 13:00 | 65102 | 3321.9467 | 340530.7062 | 59.75 | 1432.244
2016-08-31 14:00 | 66677 | 3179.1474 | 343649.8925 | 59.75 | 1466.894
2016-08-31 15:00 | 67920 | 3524.113 | 343978.2125 | 59.75 | 1494.24
2016-08-31 16:00 | 68593 | 3002.0919 | 344465.2256 | 59.75 | 1509.046
2016-08-31 17:00 | 67972 | 2754.2717 | 344434.2125 | 59.75 | 1495.384
2016-08-31 18:00 | 66086 | 3690.8474 | 341835.9943 | 59.75 | 1453.892
2016-08-31 19:00 | 64201 | 5080.8692 | 337022.8894 | 59.75 | 1412.422
2016-08-31 20:00 | 63861 | 6597.192 | 323826.6181 | 59.75 | 1404.942
2016-08-31 21:00 | 61128 | 7925.8024 | 300809.24 | 59.75 | 1344.816
2016-08-31 22:00 | 56450 | 7225.273 | 271180.3358 | 59.76 | 1185.45
2016-08-31 23:00 | 51806 | 6539.4502 | 251008.8103 | 59.78 | 984.314
2016-09-01 | 46127 | 5329.3137 | 242924.4653 | 59.77 | 922.54
2016-09-01 01:00 | 43898 | 3603.4657 | 242924.4653 | 59.77 | 877.96
2016-09-01 02:00 | 42456 | 3017.7631 | 242924.4653 | 59.77 | 849.12
2016-09-01 03:00 | 41586 | 2673.3491 | 242924.4653 | 59.77 | 831.72
2016-09-01 04:00 | 41597 | 2293.4971 | 242924.4653 | 59.77 | 831.94
2016-09-01 05:00 | 43151 | 2479.0118 | 241599.235 | 59.77 | 863.02
2016-09-01 06:00 | 46491 | 3014.9879 | 241599.235 | 59.78 | 883.329
2016-09-01 07:00 | 47184 | 3410.9309 | 241599.235 | 59.78 | 896.496
2016-09-01 08:00 | 48057 | 4366.277 | 241599.235 | 59.78 | 913.083
2016-09-01 09:00 | 50698 | 4027.2701 | 258057.7784 | 59.78 | 963.262
2016-09-01 10:00 | 53867 | 3993.5131 | 278501.6238 | 59.76 | 1131.207
2016-09-01 11:00 | 57027 | 3654.5269 | 306279.8053 | 59.75 | 1254.594
2016-09-01 12:00 | 59257 | 2746.3831 | 329453.9284 | 59.75 | 1303.654
2016-09-01 13:00 | 61841 | 1640.0554 | 337269.8426 | 59.75 | 1360.502
2016-09-01 14:00 | 63316 | 947.2459 | 339406.0621 | 59.75 | 1392.952
2016-09-01 15:00 | 63677 | 940.4979 | 339406.0621 | 59.75 | 1400.894
2016-09-01 16:00 | 63418 | 931.8538 | 335798.7421 | 59.75 | 1395.196
2016-09-01 17:00 | 62047 | 1687.2021 | 333459.0931 | 59.75 | 1365.034
2016-09-01 18:00 | 59847 | 2174.2938 | 326941.8314 | 59.75 | 1316.634
2016-09-01 19:00 | 58334 | 3661.3958 | 306110.2448 | 59.75 | 1283.348
2016-09-01 20:00 | 57761 | 6848.9242 | 275542.7268 | 59.76 | 1212.981
2016-09-01 21:00 | 55289 | 9166.145 | 246699.4504 | 59.78 | 1050.491
2016-09-01 22:00 | 51290 | 7464.1335 | 231372.6674 | 59.78 | 974.51
2016-09-01 23:00 | 46881 | 5677.6193 | 219018.957 | 59.77 | 937.62
2016-09-02 | 43549 | 5738.9821 | 216642.477 | 59.77 | 870.98
2016-09-02 01:00 | 41525 | 6137.8693 | 216642.477 | 59.78 | 788.975
2016-09-02 02:00 | 40125 | 4859.8953 | 216642.477 | 59.78 | 762.375
2016-09-02 03:00 | 39356 | 4612.4671 | 216642.477 | 59.78 | 747.764
2016-09-02 04:00 | 39383 | 4189.9877 | 216642.477 | 59.78 | 748.277
2016-09-02 05:00 | 41047 | 3874.3808 | 218831.0073 | 59.78 | 779.893
2016-09-02 06:00 | 44259 | 3812.4189 | 218831.0073 | 59.77 | 885.18
2016-09-02 07:00 | 45117 | 2932.6307 | 221081.0073 | 59.77 | 902.34
2016-09-02 08:00 | 45969 | 2337.2904 | 233434.7177 | 59.78 | 873.411
2016-09-02 09:00 | 48273 | 2508.0795 | 246610.4727 | 59.78 | 917.187
2016-09-02 10:00 | 50686 | 3080.9119 | 263167.0826 | 59.76 | 1064.406
2016-09-02 11:00 | 53159 | 3070.7497 | 283725.7376 | 59.76 | 1116.339
2016-09-02 12:00 | 55026 | 2498.8084 | 297871.4244 | 59.75 | 1210.572
2016-09-02 13:00 | 56955 | 2810.1778 | 306598.9244 | 59.75 | 1253.01
2016-09-02 14:00 | 58576 | 2931.0144 | 311321.5974 | 59.75 | 1288.672
2016-09-02 15:00 | 59516 | 2845.9832 | 311321.5974 | 59.75 | 1309.352
2016-09-02 16:00 | 59470 | 3108.0357 | 314192.9174 | 59.75 | 1308.34
2016-09-02 17:00 | 59115 | 4117.0259 | 315454.4444 | 59.75 | 1300.53
2016-09-02 18:00 | 57481 | 6197.1837 | 296053.1945 | 59.76 | 1207.101
2016-09-02 19:00 | 55848 | 6944.284 | 282010.9955 | 59.76 | 1172.808
2016-09-02 20:00 | 55411 | 7959.1804 | 273008.7035 | 59.78 | 1052.809
2016-09-02 21:00 | 52959 | 6866.6964 | 256984.2327 | 59.78 | 1006.221
2016-09-02 22:00 | 49106 | 5398.665 | 237798.5657 | 59.78 | 933.014
2016-09-02 23:00 | 45196 | 6677.1166 | 205666.5273 | 59.77 | 903.92
2016-09-03 | 44499 | 10019.5636 | 201887.0573 | 59.78 | 845.481
2016-09-03 01:00 | 42392 | 10415.5728 | 198888.8573 | 59.77 | 847.84
2016-09-03 02:00 | 40946 | 9760.823 | 198888.8573 | 59.77 | 818.92
2016-09-03 03:00 | 40170 | 6850.3963 | 198888.8573 | 59.78 | 763.23
2016-09-03 04:00 | 40245 | 6577.1021 | 198888.8573 | 59.78 | 764.655
2016-09-03 05:00 | 41845 | 7716.7915 | 196729.4573 | 59.78 | 795.055
2016-09-03 06:00 | 45111 | 7128.9511 | 198979.4573 | 59.77 | 902.22
2016-09-03 07:00 | 45936 | 7774.851 | 198979.4573 | 59.77 | 918.72
2016-09-03 08:00 | 46179 | 8736.0332 | 198979.4573 | 59.78 | 877.401
2016-09-03 09:00 | 47370 | 9007.006 | 202333.1677 | 59.77 | 947.4
2016-09-03 10:00 | 49023 | 10277.9088 | 202333.1677 | 59.77 | 980.46
2016-09-03 11:00 | 50337 | 10331.3959 | 208926.2377 | 59.77 | 1006.74
2016-09-03 12:00 | 51709 | 10012.7177 | 224519.3077 | 59.77 | 1034.18
2016-09-03 13:00 | 53180 | 9620.948 | 239224.6157 | 59.78 | 1010.42
2016-09-03 14:00 | 54415 | 9848.2441 | 246624.8657 | 59.78 | 1033.885
2016-09-03 15:00 | 55665 | 9908.6485 | 248993.2657 | 59.78 | 1057.635
2016-09-03 16:00 | 56227 | 9344.0029 | 254035.5107 | 59.78 | 1068.313
2016-09-03 17:00 | 55519 | 8627.0848 | 254035.5107 | 59.78 | 1054.861
2016-09-03 18:00 | 53449 | 8437.0427 | 249665.8003 | 59.78 | 1015.531
2016-09-03 19:00 | 51379 | 6414.0699 | 249665.8003 | 59.78 | 976.201
2016-09-03 20:00 | 50947 | 4904.0123 | 249665.8003 | 59.78 | 967.993
2016-09-03 21:00 | 49021 | 5224.3215 | 234960.4923 | 59.78 | 931.399
2016-09-03 22:00 | 46094 | 5240.3077 | 212983.1723 | 59.77 | 921.88
2016-09-03 23:00 | 42931 | 5173.4071 | 202620.0459 | 59.77 | 858.62
2016-09-04 | 42357 | 5194.8123 | 197874.7402 | 59.78 | 804.783
2016-09-04 01:00 | 41895 | 5431.4653 | 197874.7402 | 59.78 | 796.005
2016-09-04 02:00 | 40241 | 6115.6933 | 196364.4202 | 59.78 | 764.579
2016-09-04 03:00 | 39253 | 6154.8143 | 196364.4202 | 59.78 | 745.807
2016-09-04 04:00 | 38756 | 6371.0688 | 196364.4202 | 59.77 | 775.12
2016-09-04 05:00 | 39047 | 6398.9147 | 198523.8202 | 59.78 | 741.893
2016-09-04 06:00 | 39873 | 5703.618 | 198523.8202 | 59.78 | 757.587
2016-09-04 07:00 | 40188 | 4564.7908 | 198523.8202 | 59.78 | 763.572
2016-09-04 08:00 | 42348 | 3902.2708 | 205502.4602 | 59.77 | 846.96
2016-09-04 09:00 | 45604 | 3142.772 | 230055.6406 | 59.77 | 912.08
2016-09-04 10:00 | 49137 | 3389.4514 | 250763.9616 | 59.78 | 933.603
2016-09-04 11:00 | 52551 | 3155.6044 | 279976.1222 | 59.76 | 1103.571
2016-09-04 12:00 | 55557 | 3760.6136 | 298938.7226 | 59.76 | 1166.697
2016-09-04 13:00 | 58115 | 3999.0417 | 315070.1566 | 59.75 | 1278.53
2016-09-04 14:00 | 59406 | 3257.35 | 319291.7859 | 59.75 | 1306.932
2016-09-04 15:00 | 60633 | 2733.2004 | 320079.0678 | 59.75 | 1333.926
2016-09-04 16:00 | 61013 | 2582.087 | 320114.151 | 59.75 | 1342.286
2016-09-04 17:00 | 60741 | 2255.5158 | 320198.031 | 59.75 | 1336.302
2016-09-04 18:00 | 59507 | 3159.2761 | 318670.5153 | 59.75 | 1309.154
2016-09-04 19:00 | 57586 | 5036.1666 | 301098.6873 | 59.75 | 1266.892
2016-09-04 20:00 | 57022 | 7282.008 | 279093.2789 | 59.76 | 1197.462
2016-09-04 21:00 | 54371 | 8859.2063 | 253596.2425 | 59.78 | 1033.049
2016-09-04 22:00 | 51072 | 9923.6581 | 223775.2674 | 59.77 | 1021.44
2016-09-04 23:00 | 47547 | 9034.239 | 206780.2014 | 59.77 | 950.94
2016-09-05 | 43672 | 9125.4807 | 177032.521 | 59.78 | 829.768
2016-09-05 01:00 | 41507 | 10782.2292 | 171900.601 | 59.77 | 830.14
2016-09-05 02:00 | 39818 | 9114.0717 | 171900.601 | 59.77 | 796.36
2016-09-05 03:00 | 38590 | 8427.0972 | 171900.601 | 59.77 | 771.8
2016-09-05 04:00 | 37871 | 9192.0898 | 171900.601 | 59.77 | 757.42
2016-09-05 05:00 | 37803 | 9089.794 | 171900.601 | 59.77 | 756.06
2016-09-05 06:00 | 38231 | 8780.8222 | 170323.831 | 59.77 | 764.62
2016-09-05 07:00 | 38178 | 7501.8007 | 170323.831 | 59.77 | 763.56
2016-09-05 08:00 | 40828 | 6529.4556 | 182654.4874 | 59.78 | 775.732
2016-09-05 09:00 | 44816 | 5814.751 | 210136.3534 | 59.77 | 896.32
2016-09-05 10:00 | 49090 | 7473.0982 | 221688.8252 | 59.77 | 981.8
2016-09-05 11:00 | 53263 | 7990.9852 | 245295.6472 | 59.78 | 1011.997
2016-09-05 12:00 | 57064 | 6888.8088 | 282231.1316 | 59.76 | 1198.344
2016-09-05 13:00 | 59515 | 6023.1427 | 302987.3418 | 59.75 | 1309.33
2016-09-05 14:00 | 62024 | 5794.128 | 311628.4634 | 59.75 | 1364.528
2016-09-05 15:00 | 63955 | 6797.4634 | 314431.6434 | 59.75 | 1407.01
2016-09-05 16:00 | 64922 | 8115.1963 | 314431.6434 | 59.75 | 1428.284
2016-09-05 17:00 | 64734 | 8445.9495 | 312937.2652 | 59.75 | 1424.148
2016-09-05 18:00 | 62365 | 9833.8987 | 299646.8199 | 59.75 | 1372.03
2016-09-05 19:00 | 59996 | 10616.3114 | 277416.6259 | 59.76 | 1259.916
2016-09-05 20:00 | 58928 | 11180.3275 | 257630.6651 | 59.76 | 1237.488
2016-09-05 21:00 | 57080 | 12293.1916 | 239460.5549 | 59.78 | 1084.52
2016-09-05 22:00 | 53709 | 12980.293 | 212866.0169 | 59.77 | 1074.18
2016-09-05 23:00 | 50214 | 12068.8826 | 198002.3769 | 59.77 | 1004.28
2016-09-06 | 45746 | 12426.7883 | 170507.1065 | 59.78 | 869.174
2016-09-06 01:00 | 43533 | 12391.3849 | 170507.1065 | 59.77 | 870.66
2016-09-06 02:00 | 41956 | 11974.2144 | 170507.1065 | 59.77 | 839.12
2016-09-06 03:00 | 40923 | 11497.8058 | 170507.1065 | 59.77 | 818.46
2016-09-06 04:00 | 40489 | 10997.9644 | 170507.1065 | 59.77 | 809.78
2016-09-06 05:00 | 40812 | 10465.5584 | 170507.1065 | 59.77 | 816.24
2016-09-06 06:00 | 41535 | 9158.9832 | 172083.8765 | 59.77 | 830.7
2016-09-06 07:00 | 41357 | 9350.0602 | 172083.8765 | 59.77 | 827.14
2016-09-06 08:00 | 43663 | 9758.6402 | 173602.8765 | 59.78 | 829.597
2016-09-06 09:00 | 48129 | 10066.0142 | 191450.2465 | 59.77 | 962.58
2016-09-06 10:00 | 52745 | 8860.2242 | 232171.2669 | 59.78 | 1002.155
2016-09-06 11:00 | 56047 | 9046.0414 | 253820.8304 | 59.78 | 1064.893
2016-09-06 12:00 | 58657 | 8386.6375 | 276858.1944 | 59.76 | 1231.797
2016-09-06 13:00 | 59980 | 7166.5961 | 295705.2112 | 59.75 | 1319.56
2016-09-06 14:00 | 60677 | 5898.9855 | 311052.5516 | 59.75 | 1334.894
2016-09-06 15:00 | 61255 | 4926.4581 | 315196.4032 | 59.75 | 1347.61
2016-09-06 16:00 | 61654 | 3850.4988 | 315196.4032 | 59.75 | 1356.388
2016-09-06 17:00 | 61606 | 4189.9534 | 316059.7032 | 59.75 | 1355.332
2016-09-06 18:00 | 60163 | 4981.7974 | 313131.952 | 59.75 | 1323.586
2016-09-06 19:00 | 59408 | 7162.1702 | 293342.9765 | 59.76 | 1247.568
2016-09-06 20:00 | 59167 | 9584.2257 | 272534.2373 | 59.76 | 1242.507
2016-09-06 21:00 | 57512 | 11144.7833 | 250579.0325 | 59.78 | 1092.728
2016-09-06 22:00 | 53656 | 9726.1535 | 235231.6921 | 59.78 | 1019.464
2016-09-06 23:00 | 49437 | 10514.231 | 212699.0813 | 59.77 | 988.74
2016-09-07 | 44517 | 10702.0897 | 211550.1893 | 59.78 | 845.823
2016-09-07 01:00 | 42761 | 10297.075 | 209370.6559 | 59.77 | 855.22
2016-09-07 02:00 | 41592 | 9831.9826 | 209370.6559 | 59.77 | 831.84
2016-09-07 03:00 | 41064 | 8129.5184 | 208982.8959 | 59.78 | 780.216
2016-09-07 04:00 | 41594 | 6040.5233 | 208982.8959 | 59.78 | 790.286
2016-09-07 05:00 | 43741 | 4983.0688 | 209304.4453 | 59.77 | 874.82
2016-09-07 06:00 | 47381 | 4795.0646 | 226732.6593 | 59.78 | 900.239
2016-09-07 07:00 | 48981 | 3321.1828 | 248525.4897 | 59.78 | 930.639
2016-09-07 08:00 | 49451 | 2597.0443 | 259221.8877 | 59.78 | 939.569
2016-09-07 09:00 | 50336 | 2909.015 | 259221.8877 | 59.78 | 956.384
2016-09-07 10:00 | 51213 | 2867.8869 | 264720.1327 | 59.76 | 1075.473
2016-09-07 11:00 | 51740 | 3292.2513 | 266185.7327 | 59.76 | 1086.54
2016-09-07 12:00 | 52477 | 4837.089 | 266185.7327 | 59.76 | 1102.017
2016-09-07 13:00 | 52807 | 5789.4616 | 265864.1833 | 59.78 | 1003.333
2016-09-07 14:00 | 52984 | 6971.6275 | 254991.5953 | 59.78 | 1006.696
2016-09-07 15:00 | 53132 | 7315.0467 | 248908.8753 | 59.78 | 1009.508
2016-09-07 16:00 | 53387 | 8397.1281 | 241108.4153 | 59.78 | 1014.353
2016-09-07 17:00 | 52797 | 9117.6149 | 241108.4153 | 59.78 | 1003.143
2016-09-07 18:00 | 52440 | 9230.8872 | 241108.4153 | 59.78 | 996.36
2016-09-07 19:00 | 52082 | 9100.0571 | 240921.2153 | 59.78 | 989.558
2016-09-07 20:00 | 52980 | 8880.7103 | 240921.2153 | 59.78 | 1006.62
2016-09-07 21:00 | 51532 | 6824.3803 | 240873.2153 | 59.78 | 979.108
2016-09-07 22:00 | 48526 | 6269.25 | 226898.5323 | 59.77 | 970.52
2016-09-07 23:00 | 45071 | 5662.3541 | 210082.0219 | 59.77 | 901.42
2016-09-08 | 39302 | 4757.7733 | 207649.0219 | 59.78 | 746.738
2016-09-08 01:00 | 37900 | 4280.4163 | 205328.0073 | 59.78 | 720.1
2016-09-08 02:00 | 37215 | 3944.7547 | 205328.0073 | 59.78 | 707.085
2016-09-08 03:00 | 36984 | 3094.0118 | 205715.7673 | 59.78 | 702.696
2016-09-08 04:00 | 37502 | 2674.0517 | 205715.7673 | 59.78 | 712.538
2016-09-08 05:00 | 39405 | 2334.7118 | 207895.3008 | 59.78 | 748.695
2016-09-08 06:00 | 43108 | 2775.3747 | 212400.5928 | 59.77 | 862.16
2016-09-08 07:00 | 44435 | 3050.5395 | 215756.9928 | 59.77 | 888.7
2016-09-08 08:00 | 44941 | 3765.0689 | 215756.9928 | 59.77 | 898.82
2016-09-08 09:00 | 46451 | 3705.7446 | 228110.7032 | 59.78 | 882.569
2016-09-08 10:00 | 48362 | 4528.3364 | 235024.4406 | 59.78 | 918.878
2016-09-08 11:00 | 49917 | 4230.0023 | 246026.7906 | 59.78 | 948.423
2016-09-08 12:00 | 51427 | 4335.0169 | 259224.7436 | 59.78 | 977.113
2016-09-08 13:00 | 52888 | 4407.6084 | 274786.544 | 59.76 | 1110.648
2016-09-08 14:00 | 54114 | 3535.4156 | 286374.5488 | 59.76 | 1136.394
2016-09-08 15:00 | 55279 | 3101.82 | 293222.4078 | 59.76 | 1160.859
2016-09-08 16:00 | 56204 | 2978.8662 | 297568.9078 | 59.75 | 1236.488
2016-09-08 17:00 | 55724 | 2995.041 | 297446.9158 | 59.75 | 1225.928
2016-09-08 18:00 | 54502 | 2895.0141 | 292508.4864 | 59.76 | 1144.542
2016-09-08 19:00 | 53280 | 2972.1571 | 287865.2564 | 59.76 | 1118.88
2016-09-08 20:00 | 53482 | 3429.104 | 285425.6564 | 59.76 | 1123.122
2016-09-08 21:00 | 51492 | 3608.8421 | 263829.136 | 59.76 | 1081.332
2016-09-08 22:00 | 48053 | 3046.9762 | 247220.6432 | 59.78 | 913.007
2016-09-08 23:00 | 44421 | 2780.0708 | 229510.1812 | 59.77 | 888.42
2016-09-09 | 40810 | 3303.9607 | 225297.2512 | 59.77 | 816.2
2016-09-09 01:00 | 39246 | 3811.7114 | 225297.2512 | 59.78 | 745.674
2016-09-09 02:00 | 38365 | 3333.561 | 225297.2512 | 59.78 | 728.935
2016-09-09 03:00 | 37919 | 3527.7429 | 225297.2512 | 59.78 | 720.461
2016-09-09 04:00 | 38171 | 3123.6345 | 225297.2512 | 59.78 | 725.249
2016-09-09 05:00 | 39859 | 2943.3252 | 227618.2657 | 59.78 | 757.321
2016-09-09 06:00 | 43280 | 2653.7845 | 227618.2657 | 59.77 | 865.6
2016-09-09 07:00 | 44268 | 3718.7442 | 227618.2657 | 59.77 | 885.36
2016-09-09 08:00 | 45064 | 5235.4842 | 227618.2657 | 59.77 | 901.28
2016-09-09 09:00 | 47268 | 5020.1683 | 236370.6157 | 59.77 | 945.36
2016-09-09 10:00 | 50169 | 5090.4146 | 253407.1407 | 59.78 | 953.211
2016-09-09 11:00 | 52900 | 6421.6879 | 261653.5407 | 59.78 | 1005.1
2016-09-09 12:00 | 55451 | 5777.0713 | 285671.4529 | 59.76 | 1164.471
2016-09-09 13:00 | 57984 | 4322.6433 | 311466.7964 | 59.75 | 1275.648
2016-09-09 14:00 | 59312 | 4920.8452 | 312682.8968 | 59.75 | 1304.864
2016-09-09 15:00 | 60326 | 4702.4275 | 315024.4174 | 59.75 | 1327.172
2016-09-09 16:00 | 60645 | 4859.8867 | 315024.4174 | 59.75 | 1334.19
2016-09-09 17:00 | 59969 | 4625.5498 | 314008.4174 | 59.75 | 1319.318
2016-09-09 18:00 | 58801 | 4916.3716 | 311348.7048 | 59.75 | 1293.622
2016-09-09 19:00 | 56947 | 6642.4103 | 286307.9818 | 59.76 | 1195.887
2016-09-09 20:00 | 56568 | 8890.2165 | 264399.9196 | 59.76 | 1187.928
2016-09-09 21:00 | 54022 | 8833.6621 | 239620.5761 | 59.78 | 1026.418
2016-09-09 22:00 | 49616 | 9601.8434 | 204761.4373 | 59.77 | 992.32
2016-09-09 23:00 | 45625 | 8384.6074 | 198089.9213 | 59.78 | 866.875
2016-09-10 | 44751 | 8181.0925 | 197498.9133 | 59.78 | 850.269
2016-09-10 01:00 | 42699 | 8980.4517 | 197498.9133 | 59.78 | 811.281
2016-09-10 02:00 | 41287 | 8904.8755 | 197498.9133 | 59.77 | 825.74
2016-09-10 03:00 | 40458 | 7959.4811 | 197498.9133 | 59.77 | 809.16
2016-09-10 04:00 | 40518 | 8083.2572 | 197498.9133 | 59.77 | 810.36
2016-09-10 05:00 | 42063 | 7378.4618 | 200657.3133 | 59.78 | 799.197
2016-09-10 06:00 | 45582 | 6665.7127 | 200657.3133 | 59.77 | 911.64
2016-09-10 07:00 | 46490 | 7579.8282 | 200657.3133 | 59.77 | 929.8
2016-09-10 08:00 | 47596 | 8712.4665 | 200657.3133 | 59.77 | 951.92
2016-09-10 09:00 | 50234 | 7528.5958 | 220770.0293 | 59.78 | 954.446
2016-09-10 10:00 | 53504 | 6382.6947 | 252623.3561 | 59.78 | 1016.576
2016-09-10 11:00 | 56641 | 6432.8099 | 274100.8791 | 59.76 | 1189.461
2016-09-10 12:00 | 59430 | 5606.4468 | 299313.9416 | 59.75 | 1307.46
2016-09-10 13:00 | 61496 | 5145.9029 | 318621.8064 | 59.75 | 1352.912
2016-09-10 14:00 | 63506 | 5162.6542 | 325128.184 | 59.75 | 1397.132
2016-09-10 15:00 | 64906 | 4953.726 | 325235.258 | 59.75 | 1427.932
2016-09-10 16:00 | 65481 | 4843.9668 | 325301.0647 | 59.75 | 1440.582
2016-09-10 17:00 | 64604 | 5435.2472 | 325235.258 | 59.75 | 1421.288
2016-09-10 18:00 | 61871 | 6443.0242 | 310265.7484 | 59.75 | 1361.162
2016-09-10 19:00 | 59138 | 6067.148 | 293938.4754 | 59.75 | 1301.036
2016-09-10 20:00 | 58469 | 5849.4373 | 292034.4754 | 59.75 | 1286.318
2016-09-10 21:00 | 55793 | 5215.3864 | 275769.4186 | 59.76 | 1171.653
2016-09-10 22:00 | 52369 | 4626.3748 | 259924.8207 | 59.76 | 1099.749
2016-09-10 23:00 | 48967 | 4636.5211 | 243832.7395 | 59.78 | 930.373
2016-09-11 | 47116 | 6426.4648 | 216669.2841 | 59.77 | 942.32
2016-09-11 01:00 | 44738 | 6322.9221 | 216669.2841 | 59.77 | 894.76
2016-09-11 02:00 | 42956 | 6121.2341 | 216669.2841 | 59.78 | 816.164
2016-09-11 03:00 | 41862 | 5680.1296 | 216669.2841 | 59.78 | 795.378
2016-09-11 04:00 | 41246 | 6120.0803 | 216669.2841 | 59.78 | 783.674
2016-09-11 05:00 | 41462 | 6611.6316 | 216669.2841 | 59.78 | 787.778
2016-09-11 06:00 | 42332 | 6131.5244 | 216669.2841 | 59.78 | 804.308
2016-09-11 07:00 | 42805 | 4673.9226 | 216669.2841 | 59.77 | 856.1
2016-09-11 08:00 | 45083 | 3516.7459 | 224525.6841 | 59.77 | 901.66
2016-09-11 09:00 | 48643 | 2875.0183 | 252726.6655 | 59.78 | 924.217
2016-09-11 10:00 | 52403 | 2795.7422 | 273170.511 | 59.76 | 1100.463
2016-09-11 11:00 | 56253 | 2105.7261 | 306277.2932 | 59.75 | 1237.566
2016-09-11 12:00 | 59132 | 1748.5734 | 331216.9895 | 59.75 | 1300.904
2016-09-11 13:00 | 62114 | 1523.5385 | 337105.1034 | 59.75 | 1366.508
2016-09-11 14:00 | 64401 | 1867.3329 | 338726.8847 | 59.75 | 1416.822
2016-09-11 15:00 | 65933 | 2552.8137 | 338671.1782 | 59.75 | 1450.526
2016-09-11 16:00 | 66548 | 3232.7498 | 338759.7881 | 59.75 | 1464.056
2016-09-11 17:00 | 66040 | 4238.0475 | 337576.2598 | 59.75 | 1452.88
2016-09-11 18:00 | 63730 | 5573.6979 | 334527.5086 | 59.75 | 1402.06
2016-09-11 19:00 | 61421 | 5559.0343 | 320953.2566 | 59.75 | 1351.262
2016-09-11 20:00 | 60049 | 5777.7475 | 304805.3263 | 59.75 | 1321.078
2016-09-11 21:00 | 57640 | 6908.9945 | 275507.2728 | 59.76 | 1210.44
2016-09-11 22:00 | 53816 | 5912.6717 | 260684.8055 | 59.76 | 1130.136
2016-09-11 23:00 | 50073 | 4513.0862 | 248898.1255 | 59.78 | 951.387
2016-09-12 | 47775 | 4476.5731 | 235793.2925 | 59.78 | 907.725
2016-09-12 01:00 | 45222 | 4446.1653 | 234227.4225 | 59.77 | 904.44
2016-09-12 02:00 | 43361 | 3737.6133 | 234227.4225 | 59.77 | 867.22
2016-09-12 03:00 | 42082 | 3976.257 | 229918.0345 | 59.77 | 841.64
2016-09-12 04:00 | 41240 | 4735.8266 | 229918.0345 | 59.78 | 783.56
2016-09-12 05:00 | 41042 | 4383.4146 | 229918.0345 | 59.78 | 779.798
2016-09-12 06:00 | 41405 | 3766.35 | 228525.7045 | 59.77 | 828.1
2016-09-12 07:00 | 41545 | 2072.2124 | 229549.3497 | 59.77 | 830.9
2016-09-12 08:00 | 44151 | 1079.1013 | 237251.5147 | 59.78 | 838.869
2016-09-12 09:00 | 48390 | 1250.5403 | 260235.2282 | 59.78 | 919.41
2016-09-12 10:00 | 52808 | 965.6869 | 292685.6644 | 59.76 | 1108.968
2016-09-12 11:00 | 57415 | 1298.1592 | 316920.1435 | 59.75 | 1263.13
2016-09-12 12:00 | 60619 | 2929.8155 | 326606.8615 | 59.75 | 1333.618
2016-09-12 13:00 | 63491 | 3996.7532 | 333056.2902 | 59.75 | 1396.802
2016-09-12 14:00 | 65417 | 4099.3111 | 336242.9789 | 59.75 | 1439.174
2016-09-12 15:00 | 66589 | 3935.5709 | 336242.9789 | 59.75 | 1464.958
2016-09-12 16:00 | 66845 | 4493.2887 | 336242.9789 | 59.75 | 1470.59
2016-09-12 17:00 | 66216 | 5220.9608 | 335145.0517 | 59.75 | 1456.752
2016-09-12 18:00 | 64148 | 5049.3211 | 333056.2902 | 59.75 | 1411.256
2016-09-12 19:00 | 62081 | 3878.6104 | 331422.9922 | 59.75 | 1365.782
2016-09-12 20:00 | 61161 | 3620.3728 | 324881.5222 | 59.75 | 1345.542
2016-09-12 21:00 | 58984 | 3934.5861 | 312874.4708 | 59.75 | 1297.648
2016-09-12 22:00 | 54632 | 2858.6708 | 292634.1924 | 59.76 | 1147.272
2016-09-12 23:00 | 50192 | 1940.2067 | 274222.663 | 59.76 | 1054.032
2016-09-13 | 44384 | 2603.6403 | 237450.9097 | 59.77 | 887.68
2016-09-13 01:00 | 42128 | 3361.8849 | 237450.9097 | 59.77 | 842.56
2016-09-13 02:00 | 40644 | 2982.5071 | 237450.9097 | 59.77 | 812.88
2016-09-13 03:00 | 39927 | 3265.9061 | 239803.0697 | 59.78 | 758.613
2016-09-13 04:00 | 40035 | 4549.1658 | 239248.8797 | 59.78 | 760.665
2016-09-13 05:00 | 41795 | 3587.5809 | 238813.9997 | 59.77 | 835.9
2016-09-13 06:00 | 45347 | 2501.2674 | 242163.5577 | 59.78 | 861.593
2016-09-13 07:00 | 46329 | 2074.796 | 243459.1557 | 59.78 | 880.251
2016-09-13 08:00 | 47384 | 1995.5405 | 248381.4257 | 59.78 | 900.296
2016-09-13 09:00 | 50181 | 2073.5104 | 261486.2587 | 59.76 | 1053.801
2016-09-13 10:00 | 53682 | 3135.1568 | 276637.2962 | 59.76 | 1127.322
2016-09-13 11:00 | 57095 | 1889.2538 | 313199.6141 | 59.75 | 1256.09
2016-09-13 12:00 | 59712 | 1733.6568 | 333399.7054 | 59.75 | 1313.664
2016-09-13 13:00 | 62767 | 2061.2109 | 339658.3338 | 59.75 | 1380.874
2016-09-13 14:00 | 65028 | 1855.6793 | 343032.3424 | 59.75 | 1430.616
2016-09-13 15:00 | 65963 | 2027.3946 | 343156.0356 | 59.75 | 1451.186
2016-09-13 16:00 | 66292 | 2686.1712 | 342999.4391 | 59.75 | 1458.424
2016-09-13 17:00 | 65510 | 3010.1595 | 342845.0225 | 59.75 | 1441.22
2016-09-13 18:00 | 63363 | 4090.4591 | 338061.0518 | 59.75 | 1393.986
2016-09-13 19:00 | 61216 | 4823.1875 | 322710.6121 | 59.75 | 1346.752
2016-09-13 20:00 | 60295 | 5807.2354 | 305801.2468 | 59.75 | 1326.49
2016-09-13 21:00 | 57712 | 7470.7235 | 276803.8042 | 59.76 | 1211.952
2016-09-13 22:00 | 53054 | 7325.2285 | 249832.3102 | 59.78 | 1008.026
2016-09-13 23:00 | 48429 | 6024.4576 | 227755.5272 | 59.77 | 968.58
2016-09-14 | 44466 | 5715.1613 | 219901.8168 | 59.77 | 889.32
2016-09-14 01:00 | 42157 | 5712.0344 | 219901.8168 | 59.78 | 800.983
2016-09-14 02:00 | 40541 | 5318.7513 | 219283.8168 | 59.78 | 770.279
2016-09-14 03:00 | 39592 | 4769.3901 | 219283.8168 | 59.78 | 752.248
2016-09-14 04:00 | 39480 | 5299.2435 | 219838.0068 | 59.78 | 750.12
2016-09-14 05:00 | 41137 | 4822.3793 | 220272.8868 | 59.78 | 781.603
2016-09-14 06:00 | 44679 | 4747.4036 | 220272.8868 | 59.77 | 893.58
2016-09-14 07:00 | 45743 | 4398.812 | 220272.8868 | 59.77 | 914.86
2016-09-14 08:00 | 46829 | 4040.4821 | 228126.5972 | 59.78 | 889.751
2016-09-14 09:00 | 49927 | 3484.6879 | 250203.3802 | 59.78 | 948.613
2016-09-14 10:00 | 53424 | 3893.4043 | 273417.7136 | 59.76 | 1121.904
2016-09-14 11:00 | 56835 | 3754.8818 | 298280.6352 | 59.75 | 1250.37
2016-09-14 12:00 | 59246 | 3239.6067 | 323170.1822 | 59.75 | 1303.412
2016-09-14 13:00 | 62109 | 3412.1297 | 328352.0833 | 59.75 | 1366.398
2016-09-14 14:00 | 64294 | 3696.1419 | 331241.0949 | 59.75 | 1414.468
2016-09-14 15:00 | 65537 | 3222.2557 | 331241.0949 | 59.75 | 1441.814
2016-09-14 16:00 | 65938 | 3555.1119 | 331241.0949 | 59.75 | 1450.636
2016-09-14 17:00 | 65097 | 4182.7586 | 331159.0149 | 59.75 | 1432.134
2016-09-14 18:00 | 62614 | 4781.1875 | 326200.8633 | 59.75 | 1377.508
2016-09-14 19:00 | 60131 | 6212.7349 | 306710.9635 | 59.75 | 1322.882
2016-09-14 20:00 | 59466 | 8186.4744 | 281736.9235 | 59.76 | 1248.786
2016-09-14 21:00 | 55916 | 7724.3378 | 260331.8772 | 59.76 | 1174.236
2016-09-14 22:00 | 51556 | 7511.8383 | 235075.2347 | 59.78 | 979.564
2016-09-14 23:00 | 46840 | 7906.5639 | 203100.3703 | 59.77 | 936.8
2016-09-15 | 42150 | 8707.4284 | 199628.0803 | 59.78 | 800.85
2016-09-15 01:00 | 39854 | 8376.9141 | 199628.0803 | 59.77 | 797.08
2016-09-15 02:00 | 38581 | 7345.6781 | 198357.1303 | 59.77 | 771.62
2016-09-15 03:00 | 37732 | 6851.4538 | 195875.5303 | 59.77 | 754.64
2016-09-15 04:00 | 37842 | 6556.7792 | 195279.5803 | 59.77 | 756.84
2016-09-15 05:00 | 39436 | 6874.8249 | 195279.5803 | 59.78 | 749.284
2016-09-15 06:00 | 42809 | 6826.7012 | 195279.5803 | 59.78 | 813.371
2016-09-15 07:00 | 43526 | 6415.1104 | 195279.5803 | 59.78 | 826.994
2016-09-15 08:00 | 44579 | 6073.2596 | 204201.0963 | 59.77 | 891.58
2016-09-15 09:00 | 47413 | 5167.5277 | 228476.7347 | 59.77 | 948.26
2016-09-15 10:00 | 50919 | 6048.5158 | 244145.1157 | 59.78 | 967.461
2016-09-15 11:00 | 54069 | 5738.5854 | 271174.9849 | 59.76 | 1135.449
2016-09-15 12:00 | 57032 | 5267.6465 | 295702.7634 | 59.76 | 1197.672
2016-09-15 13:00 | 59047 | 4369.6256 | 314090.9318 | 59.75 | 1299.034
2016-09-15 14:00 | 61058 | 4034.0737 | 320630.0284 | 59.75 | 1343.276
2016-09-15 15:00 | 62421 | 4215.5609 | 320630.0284 | 59.75 | 1373.262
2016-09-15 16:00 | 62940 | 4284.6687 | 320630.0284 | 59.75 | 1384.68
2016-09-15 17:00 | 61914 | 4262.118 | 320630.0284 | 59.75 | 1362.108
2016-09-15 18:00 | 59270 | 4303.2042 | 313805.1088 | 59.75 | 1303.94
2016-09-15 19:00 | 57312 | 5371.7699 | 291795.7276 | 59.76 | 1203.552
2016-09-15 20:00 | 56022 | 7268.8528 | 267267.9491 | 59.76 | 1176.462
2016-09-15 21:00 | 52951 | 8898.2141 | 235774.9477 | 59.78 | 1006.069
2016-09-15 22:00 | 48617 | 8837.5554 | 207335.7293 | 59.77 | 972.34
2016-09-15 23:00 | 44259 | 7835.4837 | 197427.5433 | 59.78 | 840.921
2016-09-16 | 40872 | 7541.4059 | 192205.3333 | 59.78 | 776.568
2016-09-16 01:00 | 38789 | 7143.5307 | 190695.0133 | 59.77 | 775.78
2016-09-16 02:00 | 37358 | 6311.5533 | 192583.9633 | 59.77 | 747.16
2016-09-16 03:00 | 36538 | 5976.2396 | 195065.5633 | 59.77 | 730.76
2016-09-16 04:00 | 36465 | 4986.0084 | 195661.5133 | 59.77 | 729.3
2016-09-16 05:00 | 38118 | 4031.0279 | 195661.5133 | 59.78 | 724.242
2016-09-16 06:00 | 41488 | 2905.47 | 203006.2593 | 59.77 | 829.76
2016-09-16 07:00 | 42291 | 2138.1416 | 211849.3293 | 59.77 | 845.82
2016-09-16 08:00 | 43290 | 1583.3467 | 225160.1097 | 59.77 | 865.8
2016-09-16 09:00 | 45890 | 1641.7748 | 242967.5127 | 59.78 | 871.91
2016-09-16 10:00 | 49326 | 1980.1211 | 258901.5062 | 59.78 | 937.194
2016-09-16 11:00 | 52643 | 2367.6242 | 279064.0037 | 59.76 | 1105.503
2016-09-16 12:00 | 55796 | 1474.8862 | 312680.3661 | 59.75 | 1227.512
2016-09-16 13:00 | 58812 | 1862.6108 | 320819.4461 | 59.75 | 1293.864
2016-09-16 14:00 | 60434 | 2162.825 | 325378.5747 | 59.75 | 1329.548
2016-09-16 15:00 | 62000 | 2366.7877 | 322438.2438 | 59.75 | 1364
2016-09-16 16:00 | 62683 | 3995.2347 | 321855.3007 | 59.75 | 1379.026
2016-09-16 17:00 | 61714 | 5449.4537 | 316434.8901 | 59.75 | 1357.708
2016-09-16 18:00 | 59330 | 5764.093 | 314661.3926 | 59.75 | 1305.26
2016-09-16 19:00 | 57634 | 5989.0477 | 307570.3206 | 59.76 | 1210.314
2016-09-16 20:00 | 56484 | 6402.7499 | 286841.6594 | 59.76 | 1186.164
2016-09-16 21:00 | 53270 | 5472.9933 | 269099.574 | 59.76 | 1118.67
2016-09-16 22:00 | 49066 | 5960.803 | 240741.8457 | 59.78 | 932.254
2016-09-16 23:00 | 44588 | 3942.3739 | 236133.1207 | 59.77 | 891.76
2016-09-17 | 44428 | 3865.2922 | 231506.9807 | 59.77 | 888.56
2016-09-17 01:00 | 42180 | 3426.1092 | 231506.9807 | 59.77 | 843.6
2016-09-17 02:00 | 40654 | 4367.3964 | 231506.9807 | 59.78 | 772.426
2016-09-17 03:00 | 39804 | 3662.07 | 231506.9807 | 59.78 | 756.276
2016-09-17 04:00 | 39867 | 2727.8165 | 231506.9807 | 59.78 | 757.473
2016-09-17 05:00 | 41566 | 1990.0346 | 232426.2927 | 59.77 | 831.32
2016-09-17 06:00 | 44994 | 1099.2305 | 237312.8727 | 59.78 | 854.886
2016-09-17 07:00 | 46064 | 664.2274 | 246815.6057 | 59.78 | 875.216
2016-09-17 08:00 | 47054 | 688.7122 | 256352.2857 | 59.78 | 894.026
2016-09-17 09:00 | 50230 | 605.8409 | 275938.7731 | 59.76 | 1054.83
2016-09-17 10:00 | 54050 | 448.7378 | 305933.9212 | 59.75 | 1189.1
2016-09-17 11:00 | 57404 | 913.4399 | 318237.0976 | 59.75 | 1262.888
2016-09-17 12:00 | 59600 | 1497.0743 | 323123.4952 | 59.75 | 1311.2
2016-09-17 13:00 | 61545 | 1607.1654 | 324150.5142 | 59.75 | 1353.99
2016-09-17 14:00 | 62887 | 2822.4242 | 324289.4089 | 59.75 | 1383.514
2016-09-17 15:00 | 63450 | 3638.2353 | 327962.2889 | 59.75 | 1395.9
2016-09-17 16:00 | 63036 | 4175.3057 | 326882.8434 | 59.75 | 1386.792
2016-09-17 17:00 | 60015 | 5304.9169 | 312610.5947 | 59.75 | 1320.33
2016-09-17 18:00 | 58102 | 5471.0878 | 295936.9219 | 59.75 | 1278.244
2016-09-17 19:00 | 55501 | 5523.1131 | 274643.4195 | 59.76 | 1165.521
2016-09-17 20:00 | 54545 | 6077.8284 | 262789.5573 | 59.76 | 1145.445
2016-09-17 21:00 | 52228 | 6355.0215 | 246845.7119 | 59.78 | 992.332
2016-09-17 22:00 | 49334 | 6328.6267 | 228590.6289 | 59.78 | 937.346
2016-09-17 23:00 | 46124 | 5704.5848 | 221313.9825 | 59.77 | 922.48
2016-09-18 | 45360 | 5524.8641 | 218926.4825 | 59.77 | 907.2
2016-09-18 01:00 | 44049 | 6178.7889 | 218926.4825 | 59.77 | 880.98
2016-09-18 02:00 | 42394 | 5905.9299 | 218926.4825 | 59.78 | 805.486
2016-09-18 03:00 | 41305 | 5270.612 | 217418.1325 | 59.78 | 784.795
2016-09-18 04:00 | 40769 | 4973.4556 | 217418.1325 | 59.78 | 774.611
2016-09-18 05:00 | 41106 | 4400.0506 | 217418.1325 | 59.78 | 781.014
2016-09-18 06:00 | 42176 | 3723.4815 | 217418.1325 | 59.77 | 843.52
2016-09-18 07:00 | 42925 | 2875.6559 | 219668.1325 | 59.77 | 858.5
2016-09-18 08:00 | 45428 | 2151.9949 | 239364.6259 | 59.78 | 863.132
2016-09-18 09:00 | 49221 | 2440.5383 | 261562.9593 | 59.78 | 935.199
2016-09-18 10:00 | 52957 | 2806.949 | 280203.1139 | 59.76 | 1112.097
2016-09-18 11:00 | 55981 | 2865.5343 | 307787.1794 | 59.75 | 1231.582
2016-09-18 12:00 | 58152 | 2448.0846 | 319091.2965 | 59.75 | 1279.344
2016-09-18 13:00 | 59004 | 2442.4541 | 320540.7782 | 59.75 | 1298.088
2016-09-18 14:00 | 59916 | 3504.4907 | 320540.7782 | 59.75 | 1318.152
2016-09-18 15:00 | 60376 | 3731.918 | 320540.7782 | 59.75 | 1328.272
2016-09-18 16:00 | 60149 | 3600.3063 | 320540.7782 | 59.75 | 1323.278
2016-09-18 17:00 | 59040 | 4176.3054 | 316399.6565 | 59.75 | 1298.88
2016-09-18 18:00 | 58311 | 5827.2455 | 306842.8226 | 59.76 | 1224.531
2016-09-18 19:00 | 56896 | 7708.0223 | 279258.7572 | 59.76 | 1194.816
2016-09-18 20:00 | 56235 | 9673.8038 | 259242.4179 | 59.78 | 1068.465
2016-09-18 21:00 | 54135 | 8605.5417 | 252920.6907 | 59.78 | 1028.565
2016-09-18 22:00 | 51231 | 6323.9426 | 252599.1413 | 59.78 | 973.389
2016-09-18 23:00 | 48026 | 6102.7305 | 236230.2013 | 59.77 | 960.52
2016-09-19 | 45526 | 4184.5495 | 236458.3013 | 59.77 | 910.52
2016-09-19 01:00 | 43305 | 3639.8255 | 232489.8413 | 59.77 | 866.1
2016-09-19 02:00 | 41700 | 3600.8457 | 230742.0362 | 59.77 | 834
2016-09-19 03:00 | 40592 | 3523.9131 | 232250.3862 | 59.78 | 771.248
2016-09-19 04:00 | 39958 | 2903.432 | 232250.3862 | 59.78 | 759.202
2016-09-19 05:00 | 39940 | 1918.4202 | 232250.3862 | 59.77 | 798.8
2016-09-19 06:00 | 40515 | 1702.7914 | 232250.3862 | 59.77 | 810.3
2016-09-19 07:00 | 41087 | 1584.7598 | 232250.3862 | 59.77 | 821.74
2016-09-19 08:00 | 43169 | 1589.6827 | 236060.1862 | 59.77 | 863.38
2016-09-19 09:00 | 46595 | 1134.9733 | 254873.5542 | 59.78 | 885.305
2016-09-19 10:00 | 50269 | 1534.4933 | 276523.7876 | 59.76 | 1055.649
2016-09-19 11:00 | 53768 | 3512.3185 | 282831.8068 | 59.76 | 1129.128
2016-09-19 12:00 | 56959 | 4284.4723 | 304024.9258 | 59.75 | 1253.098
2016-09-19 13:00 | 59166 | 5641.8577 | 305841.2118 | 59.75 | 1301.652
2016-09-19 14:00 | 59009 | 5456.6601 | 305841.2118 | 59.75 | 1298.198
2016-09-19 15:00 | 59051 | 5837.9787 | 305841.2118 | 59.75 | 1299.122
2016-09-19 16:00 | 59057 | 7226.2536 | 304024.9258 | 59.76 | 1240.197
2016-09-19 17:00 | 59127 | 8597.6578 | 291248.0458 | 59.76 | 1241.667
2016-09-19 18:00 | 58309 | 9734.3556 | 281239.9133 | 59.76 | 1224.489
2016-09-19 19:00 | 57491 | 8617.1473 | 281239.9133 | 59.76 | 1207.311
2016-09-19 20:00 | 57139 | 7181.9149 | 281239.9133 | 59.76 | 1199.919
2016-09-19 21:00 | 54317 | 5815.5588 | 269136.0929 | 59.76 | 1140.657
2016-09-19 22:00 | 50453 | 5401.3331 | 251832.0256 | 59.78 | 958.607
2016-09-19 23:00 | 46332 | 4444.0087 | 238141.3456 | 59.77 | 926.64
2016-09-20 | 39993 | 2758.6378 | 223584.9962 | 59.78 | 759.867
2016-09-20 01:00 | 38177 | 3636.0173 | 221883.3517 | 59.78 | 725.363
2016-09-20 02:00 | 37107 | 3760.961 | 223072.0125 | 59.78 | 705.033
2016-09-20 03:00 | 36693 | 3631.7503 | 223072.0125 | 59.78 | 697.167
2016-09-20 04:00 | 37148 | 3635.1531 | 223072.0125 | 59.78 | 705.812
2016-09-20 05:00 | 39130 | 3296.7019 | 223072.0125 | 59.78 | 743.47
2016-09-20 06:00 | 42860 | 2931.4786 | 224591.0125 | 59.77 | 857.2
2016-09-20 07:00 | 44218 | 2471.5306 | 228956.1025 | 59.77 | 884.36
2016-09-20 08:00 | 44735 | 2302.2399 | 233438.3475 | 59.77 | 894.7
2016-09-20 09:00 | 46555 | 1755.6034 | 249229.5155 | 59.78 | 884.545
2016-09-20 10:00 | 48949 | 2158.3805 | 263030.0757 | 59.78 | 930.031
2016-09-20 11:00 | 51637 | 3253.2698 | 274743.8837 | 59.76 | 1084.377
2016-09-20 12:00 | 54267 | 4571.0826 | 285606.4671 | 59.76 | 1139.607
2016-09-20 13:00 | 56827 | 6370.0508 | 294798.0651 | 59.76 | 1193.367
2016-09-20 14:00 | 57908 | 8017.519 | 293782.0651 | 59.76 | 1216.068
2016-09-20 15:00 | 58197 | 7825.051 | 293007.7351 | 59.76 | 1222.137
2016-09-20 16:00 | 58806 | 7480.9076 | 294084.7311 | 59.76 | 1234.926
2016-09-20 17:00 | 58081 | 7279.7892 | 294084.7311 | 59.76 | 1219.701
2016-09-20 18:00 | 57064 | 7430.6893 | 292233.4051 | 59.76 | 1198.344
2016-09-20 19:00 | 56047 | 7608.8732 | 280519.5971 | 59.76 | 1176.987
2016-09-20 20:00 | 55331 | 7915.4534 | 271381.8311 | 59.78 | 1051.289
2016-09-20 21:00 | 52431 | 8562.0538 | 242471.4669 | 59.78 | 996.189
2016-09-20 22:00 | 48297 | 7656.7115 | 219740.0045 | 59.77 | 965.94
2016-09-20 23:00 | 44079 | 6842.356 | 199795.1665 | 59.78 | 837.501
2016-09-21 | 39560 | 6737.7552 | 195199.7261 | 59.78 | 751.64
2016-09-21 01:00 | 37696 | 6591.9751 | 193617.1361 | 59.77 | 753.92
2016-09-21 02:00 | 36520 | 5931.1424 | 193617.1361 | 59.77 | 730.4
2016-09-21 03:00 | 35936 | 5375.1305 | 193617.1361 | 59.77 | 718.72
2016-09-21 04:00 | 36210 | 4920.846 | 193617.1361 | 59.77 | 724.2
2016-09-21 05:00 | 38046 | 4489.2374 | 193617.1361 | 59.78 | 722.874
2016-09-21 06:00 | 41755 | 4248.102 | 202915.547 | 59.77 | 835.1
2016-09-21 07:00 | 42952 | 4191.1922 | 208882.997 | 59.77 | 859.04
2016-09-21 08:00 | 43327 | 4306.9615 | 215485.6474 | 59.77 | 866.54
2016-09-21 09:00 | 45031 | 5173.4203 | 219985.6474 | 59.77 | 900.62
2016-09-21 10:00 | 47394 | 5132.8475 | 237178.3578 | 59.77 | 947.88
2016-09-21 11:00 | 49415 | 6653.6473 | 237178.3578 | 59.78 | 938.885
2016-09-21 12:00 | 50960 | 6774.9306 | 250729.2006 | 59.78 | 968.24
2016-09-21 13:00 | 52837 | 5372.8864 | 269604.7476 | 59.78 | 1003.903
2016-09-21 14:00 | 54445 | 5858.7004 | 277880.8321 | 59.76 | 1143.345
2016-09-21 15:00 | 55916 | 6117.0046 | 280532.4441 | 59.76 | 1174.236
2016-09-21 16:00 | 56914 | 7051.7454 | 280532.4441 | 59.76 | 1195.194
2016-09-21 17:00 | 56448 | 8613.0816 | 272242.7621 | 59.76 | 1185.408
2016-09-21 18:00 | 54911 | 9932.8152 | 253384.7817 | 59.78 | 1043.309
2016-09-21 19:00 | 53374 | 11184.5698 | 234318.2713 | 59.77 | 1067.48
2016-09-21 20:00 | 52900 | 11911.4926 | 219032.4085 | 59.77 | 1058
2016-09-21 21:00 | 50487 | 11248.885 | 207452.1495 | 59.77 | 1009.74
2016-09-21 22:00 | 46638 | 10195.1511 | 193895.685 | 59.78 | 886.122
2016-09-21 23:00 | 42576 | 8841.1873 | 185792.487 | 59.78 | 808.944
2016-09-22 | 37336 | 7981.3533 | 185792.487 | 59.77 | 746.72
2016-09-22 01:00 | 35805 | 6569.241 | 185562.477 | 59.77 | 716.1
2016-09-22 02:00 | 34781 | 5306.004 | 185562.477 | 59.77 | 695.62
2016-09-22 03:00 | 34274 | 4621.6296 | 185562.477 | 59.77 | 685.48
2016-09-22 04:00 | 34555 | 3832.2053 | 185562.477 | 59.77 | 691.1
2016-09-22 05:00 | 36319 | 2906.6529 | 185562.477 | 59.78 | 690.061
2016-09-22 06:00 | 39885 | 2655.18 | 199971.6474 | 59.78 | 757.815
2016-09-22 07:00 | 41044 | 3496.9379 | 201391.6474 | 59.77 | 820.88
2016-09-22 08:00 | 41695 | 4714.0268 | 202642.7074 | 59.78 | 792.205
2016-09-22 09:00 | 43728 | 5534.5244 | 202642.7074 | 59.77 | 874.56
2016-09-22 10:00 | 46249 | 8085.6416 | 205082.3074 | 59.77 | 924.98
2016-09-22 11:00 | 48748 | 10808.3388 | 205082.3074 | 59.77 | 974.96
2016-09-22 12:00 | 50967 | 12369.2569 | 205082.3074 | 59.77 | 1019.34
2016-09-22 13:00 | 52888 | 12468.6093 | 214180.4374 | 59.77 | 1057.76
2016-09-22 14:00 | 54203 | 12667.6496 | 221917.1074 | 59.77 | 1084.06
2016-09-22 15:00 | 55303 | 13183.259 | 221447.2324 | 59.77 | 1106.06
2016-09-22 16:00 | 56024 | 13558.2482 | 221727.2324 | 59.77 | 1120.48
2016-09-22 17:00 | 55317 | 13650.718 | 221447.2324 | 59.77 | 1106.34
2016-09-22 18:00 | 53586 | 14091.047 | 221447.2324 | 59.77 | 1071.72
2016-09-22 19:00 | 51855 | 12678.1248 | 221447.2324 | 59.77 | 1037.1
2016-09-22 20:00 | 51203 | 9893.0582 | 218248.0064 | 59.77 | 1024.06
2016-09-22 21:00 | 48804 | 9990.7406 | 207039.0464 | 59.77 | 976.08
2016-09-22 22:00 | 45251 | 10263.25 | 179788.9164 | 59.78 | 859.769
2016-09-22 23:00 | 41598 | 10700.2934 | 167095.024 | 59.77 | 831.96
2016-09-23 | 39014 | 11271.7446 | 160508.666 | 59.77 | 780.28
2016-09-23 01:00 | 37300 | 10214.4163 | 160796.666 | 59.79 | 671.4
2016-09-23 02:00 | 36365 | 10448.3906 | 160796.666 | 59.79 | 654.57
2016-09-23 03:00 | 35866 | 9863.6957 | 160796.666 | 59.79 | 645.588
2016-09-23 04:00 | 36106 | 8743.8178 | 160796.666 | 59.79 | 649.908
2016-09-23 05:00 | 37968 | 7763.298 | 160796.666 | 59.77 | 759.36
2016-09-23 06:00 | 41583 | 7441.8771 | 166833.154 | 59.78 | 790.077
2016-09-23 07:00 | 42780 | 9288.7006 | 167810.704 | 59.78 | 812.82
2016-09-23 08:00 | 43329 | 11175.6309 | 167810.704 | 59.77 | 866.58
2016-09-23 09:00 | 45477 | 12054.1419 | 167810.704 | 59.78 | 864.063
2016-09-23 10:00 | 48120 | 12717.2799 | 175393.844 | 59.78 | 914.28
2016-09-23 11:00 | 50597 | 12520.6307 | 190811.724 | 59.77 | 1011.94
2016-09-23 12:00 | 52602 | 12465.3957 | 208883.5345 | 59.77 | 1052.04
2016-09-23 13:00 | 54558 | 11921.1955 | 221832.8845 | 59.78 | 1036.602
2016-09-23 14:00 | 56128 | 10806.9868 | 240916.3925 | 59.78 | 1066.432
2016-09-23 15:00 | 57189 | 9213.8126 | 259869.6555 | 59.76 | 1200.969
2016-09-23 16:00 | 57817 | 8045.7278 | 269973.3659 | 59.76 | 1214.157
2016-09-23 17:00 | 57113 | 7941.9159 | 268957.3659 | 59.76 | 1199.373
2016-09-23 18:00 | 55400 | 6204.1309 | 267162.2924 | 59.76 | 1163.4
2016-09-23 19:00 | 53687 | 5701.3552 | 265903.2659 | 59.76 | 1127.427
2016-09-23 20:00 | 53144 | 5401.1579 | 261099.4714 | 59.76 | 1116.024
2016-09-23 21:00 | 50518 | 4864.9313 | 251562.7914 | 59.78 | 959.842
2016-09-23 22:00 | 46969 | 4058.9582 | 235539.9534 | 59.78 | 892.411
2016-09-23 23:00 | 43062 | 3511.6089 | 231197.7654 | 59.77 | 861.24
2016-09-24 | 42769 | 4215.9568 | 226493.3654 | 59.77 | 855.38
2016-09-24 01:00 | 41784 | 4636.1643 | 226493.3654 | 59.78 | 793.896
2016-09-24 02:00 | 40410 | 4837.3554 | 226493.3654 | 59.78 | 767.79
2016-09-24 03:00 | 39724 | 4440.4643 | 226493.3654 | 59.78 | 754.756
2016-09-24 04:00 | 40022 | 3128.4552 | 226493.3654 | 59.78 | 760.418
2016-09-24 05:00 | 41813 | 2360.3341 | 226493.3654 | 59.77 | 836.26
2016-09-24 06:00 | 45353 | 2005.3544 | 241820.1484 | 59.78 | 861.707
2016-09-24 07:00 | 46577 | 1586.6601 | 250673.3564 | 59.78 | 884.963
2016-09-24 08:00 | 47407 | 1434.4062 | 258627.3164 | 59.78 | 900.733
2016-09-24 09:00 | 49699 | 1085.7679 | 271744.9493 | 59.76 | 1043.679
2016-09-24 10:00 | 52309 | 1581.058 | 287184.2304 | 59.76 | 1098.489
2016-09-24 11:00 | 54600 | 2759.5761 | 297570.025 | 59.76 | 1146.6
2016-09-24 12:00 | 56530 | 2099.6013 | 313989.2234 | 59.75 | 1243.66
2016-09-24 13:00 | 58563 | 2395.3222 | 317983.6182 | 59.75 | 1288.386
2016-09-24 14:00 | 59656 | 3128.193 | 319533.2191 | 59.75 | 1312.432
2016-09-24 15:00 | 60627 | 3099.55 | 318185.5313 | 59.75 | 1333.794
2016-09-24 16:00 | 60424 | 2966.5905 | 318185.5313 | 59.75 | 1329.328
2016-09-24 17:00 | 59358 | 3347.7611 | 313051.8349 | 59.75 | 1305.876
2016-09-24 18:00 | 57261 | 3746.5272 | 309009.0971 | 59.75 | 1259.742
2016-09-24 19:00 | 55164 | 4294.7535 | 284672.2405 | 59.76 | 1158.444
2016-09-24 20:00 | 54278 | 5048.837 | 269615.3341 | 59.76 | 1139.838
2016-09-24 21:00 | 51919 | 4699.7114 | 261940.8947 | 59.78 | 986.461
2016-09-24 22:00 | 48904 | 3141.6543 | 253605.2787 | 59.78 | 929.176
2016-09-24 23:00 | 45529 | 3068.8408 | 231326.3113 | 59.77 | 910.58
2016-09-25 | 44884 | 2726.3283 | 233780.7113 | 59.77 | 897.68
2016-09-25 01:00 | 42622 | 1984.568 | 230560.7913 | 59.77 | 852.44
2016-09-25 02:00 | 41070 | 1898.476 | 230560.7913 | 59.77 | 821.4
2016-09-25 03:00 | 40026 | 1814.5293 | 230560.7913 | 59.77 | 800.52
2016-09-25 04:00 | 39457 | 2132.775 | 230276.3833 | 59.78 | 749.683
2016-09-25 05:00 | 39779 | 1774.8007 | 230276.3833 | 59.77 | 795.58
2016-09-25 06:00 | 40965 | 1462.5749 | 230276.3833 | 59.77 | 819.3
2016-09-25 07:00 | 41771 | 1286.007 | 230276.3833 | 59.77 | 835.42
2016-09-25 08:00 | 43908 | 1347.3168 | 232526.3833 | 59.78 | 834.252
2016-09-25 09:00 | 47100 | 856.7498 | 259689.9893 | 59.78 | 894.9
2016-09-25 10:00 | 50105 | 1262.8599 | 273473.4487 | 59.76 | 1052.205
2016-09-25 11:00 | 52499 | 1962.2376 | 283909.6515 | 59.76 | 1102.479
2016-09-25 12:00 | 54409 | 2776.0656 | 291847.8069 | 59.76 | 1142.589
2016-09-25 13:00 | 55375 | 4655.6893 | 291847.8069 | 59.76 | 1162.875
2016-09-25 14:00 | 56133 | 2958.1679 | 300383.5569 | 59.75 | 1234.926
2016-09-25 15:00 | 56393 | 2218.3553 | 302640.1677 | 59.75 | 1240.646
2016-09-25 16:00 | 56270 | 2799.3374 | 300849.8377 | 59.75 | 1237.94
2016-09-25 17:00 | 55625 | 4345.5587 | 295276.4457 | 59.76 | 1168.125
2016-09-25 18:00 | 54539 | 6128.5979 | 286611.1857 | 59.76 | 1145.319
2016-09-25 19:00 | 53453 | 3328.9772 | 286611.1857 | 59.76 | 1122.513
2016-09-25 20:00 | 52706 | 1763.0996 | 281923.7909 | 59.76 | 1106.826
2016-09-25 21:00 | 50529 | 1803.8031 | 277007.3235 | 59.76 | 1061.109
2016-09-25 22:00 | 47782 | 1456.0212 | 257852.9195 | 59.78 | 907.858
2016-09-25 23:00 | 44746 | 1242.2758 | 242701.882 | 59.78 | 850.174
2016-09-26 | 42730 | 1147.0978 | 220104.611 | 59.77 | 854.6
2016-09-26 01:00 | 40613 | 1645.0767 | 204514.2306 | 59.77 | 812.26
2016-09-26 02:00 | 39029 | 2847.9397 | 196276.8306 | 59.78 | 741.551
2016-09-26 03:00 | 38121 | 3332.1673 | 196276.8306 | 59.78 | 724.299
2016-09-26 04:00 | 37606 | 3174.1967 | 193088.9486 | 59.78 | 714.514
2016-09-26 05:00 | 37599 | 4768.7838 | 193088.9486 | 59.78 | 714.381
2016-09-26 06:00 | 38267 | 5602.3516 | 193088.9486 | 59.78 | 727.073
2016-09-26 07:00 | 38865 | 5934.7951 | 193088.9486 | 59.78 | 738.435
2016-09-26 08:00 | 40746 | 6194.8486 | 193088.9486 | 59.78 | 774.174
2016-09-26 09:00 | 43297 | 8779.9198 | 193088.9486 | 59.78 | 822.643
2016-09-26 10:00 | 45556 | 8408.6956 | 196308.8686 | 59.78 | 865.564
2016-09-26 11:00 | 47759 | 8029.8163 | 208271.255 | 59.77 | 955.18
2016-09-26 12:00 | 49640 | 7168.5504 | 228206.513 | 59.77 | 992.8
2016-09-26 13:00 | 50989 | 7425.9836 | 236958.863 | 59.78 | 968.791
2016-09-26 14:00 | 51934 | 8094.4483 | 236958.863 | 59.78 | 986.746
2016-09-26 15:00 | 52758 | 9477.1677 | 236958.863 | 59.78 | 1002.402
2016-09-26 16:00 | 53223 | 9011.1778 | 238749.193 | 59.78 | 1011.237
2016-09-26 17:00 | 52739 | 8679.6021 | 238749.193 | 59.78 | 1002.041
2016-09-26 18:00 | 51831 | 8330.9002 | 246048.158 | 59.78 | 984.789
2016-09-26 19:00 | 50923 | 6067.5022 | 247064.158 | 59.78 | 967.537
2016-09-26 20:00 | 50614 | 4092.994 | 247647.1012 | 59.78 | 961.666
2016-09-26 21:00 | 48111 | 5204.1418 | 246726.458 | 59.78 | 914.109
2016-09-26 22:00 | 44280 | 4821.5321 | 216774.638 | 59.77 | 885.6
2016-09-26 23:00 | 40326 | 4304.0882 | 202519.952 | 59.78 | 766.194
2016-09-27 | 37557 | 4877.2393 | 191430.9462 | 59.78 | 713.583
2016-09-27 01:00 | 35730 | 5494.7371 | 191430.9462 | 59.77 | 714.6
2016-09-27 02:00 | 34636 | 5057.8189 | 187598.2262 | 59.77 | 692.72
2016-09-27 03:00 | 34132 | 4640.7789 | 187598.2262 | 59.77 | 682.64
2016-09-27 04:00 | 34568 | 4731.08 | 187598.2262 | 59.77 | 691.36
2016-09-27 05:00 | 36430 | 4282.9412 | 187598.2262 | 59.77 | 728.6
2016-09-27 06:00 | 40000 | 3722.3054 | 187598.2262 | 59.78 | 760
2016-09-27 07:00 | 40984 | 3434.0895 | 196317.9262 | 59.77 | 819.68
2016-09-27 08:00 | 41286 | 3485.6109 | 197333.9262 | 59.77 | 825.72
2016-09-27 09:00 | 42583 | 2730.1829 | 210634.0819 | 59.77 | 851.66
2016-09-27 10:00 | 44120 | 2870.2155 | 218871.4819 | 59.77 | 882.4
2016-09-27 11:00 | 45358 | 2433.6168 | 229874.1519 | 59.78 | 861.802
2016-09-27 12:00 | 46478 | 1847.4671 | 242093.5469 | 59.78 | 883.082
2016-09-27 13:00 | 47898 | 1636.9889 | 252387.1917 | 59.78 | 910.062
2016-09-27 14:00 | 49169 | 1649.9054 | 263721.5002 | 59.76 | 1032.549
2016-09-27 15:00 | 50464 | 1487.3202 | 273894.01 | 59.76 | 1059.744
2016-09-27 16:00 | 51431 | 1479.3407 | 275092.998 | 59.76 | 1080.051
2016-09-27 17:00 | 51308 | 1315.447 | 275092.998 | 59.76 | 1077.468
2016-09-27 18:00 | 50291 | 1225.2118 | 273894.01 | 59.76 | 1056.111
2016-09-27 19:00 | 49274 | 2147.6856 | 262478.877 | 59.78 | 936.206
2016-09-27 20:00 | 49015 | 4222.4272 | 246993.482 | 59.78 | 931.285
2016-09-27 21:00 | 46367 | 3958.2571 | 235180.8372 | 59.77 | 927.34
2016-09-27 22:00 | 42463 | 3981.0543 | 206596.3712 | 59.77 | 849.26
2016-09-27 23:00 | 38523 | 3544.5487 | 184081.5754 | 59.78 | 731.937
2016-09-28 | 35853 | 3847.0251 | 185209.1512 | 59.77 | 717.06
2016-09-28 01:00 | 34367 | 3799.7958 | 185209.1512 | 59.77 | 687.34
2016-09-28 02:00 | 33496 | 4227.6257 | 185209.1512 | 59.77 | 669.92
2016-09-28 03:00 | 33058 | 3742.7494 | 185209.1512 | 59.77 | 661.16
2016-09-28 04:00 | 33403 | 3902.0759 | 185209.1512 | 59.77 | 668.06
2016-09-28 05:00 | 35417 | 4803.2907 | 184345.8512 | 59.77 | 708.34
2016-09-28 06:00 | 39350 | 5302.1409 | 182844.2012 | 59.78 | 747.65
2016-09-28 07:00 | 40346 | 5124.1745 | 184085.9312 | 59.78 | 766.574
2016-09-28 08:00 | 40688 | 5178.8468 | 184085.9312 | 59.78 | 773.072
2016-09-28 09:00 | 42363 | 2441.8718 | 213991.9475 | 59.77 | 847.26
2016-09-28 10:00 | 44162 | 1645.0532 | 230160.5159 | 59.78 | 839.078
2016-09-28 11:00 | 45734 | 2068.0913 | 238498.4154 | 59.78 | 868.946
2016-09-28 12:00 | 47336 | 2769.0157 | 243716.6604 | 59.78 | 899.384
2016-09-28 13:00 | 49540 | 2936.9743 | 258750.9884 | 59.78 | 941.26
2016-09-28 14:00 | 51786 | 2358.9046 | 283667.2807 | 59.76 | 1087.506
2016-09-28 15:00 | 53925 | 2373.5007 | 296094.4681 | 59.76 | 1132.425
2016-09-28 16:00 | 55505 | 3034.0642 | 297383.1011 | 59.76 | 1165.605
2016-09-28 17:00 | 55807 | 2916.9972 | 297383.1011 | 59.75 | 1227.754
2016-09-28 18:00 | 54578 | 2972.3063 | 296094.4681 | 59.76 | 1146.138
2016-09-28 19:00 | 53349 | 2755.5123 | 295772.9186 | 59.76 | 1120.329
2016-09-28 20:00 | 52436 | 2777.8567 | 288364.9306 | 59.76 | 1101.156
2016-09-28 21:00 | 49407 | 2972.122 | 268848.3576 | 59.78 | 938.733
2016-09-28 22:00 | 45204 | 3817.1098 | 230652.2148 | 59.77 | 904.08
2016-09-28 23:00 | 40896 | 3391.1776 | 202751.6874 | 59.77 | 817.92
2016-09-29 | 34784 | 3086.1337 | 186962.887 | 59.77 | 695.68
2016-09-29 01:00 | 33130 | 3227.1108 | 186188.557 | 59.77 | 662.6
2016-09-29 02:00 | 32134 | 3317.5679 | 186188.557 | 59.77 | 642.68
2016-09-29 03:00 | 31570 | 2708.6136 | 186188.557 | 59.77 | 631.4
2016-09-29 04:00 | 31898 | 2457.2275 | 186188.557 | 59.77 | 637.96
2016-09-29 05:00 | 33703 | 2643.7348 | 187051.857 | 59.77 | 674.06
2016-09-29 06:00 | 37323 | 2378.0416 | 190483.257 | 59.78 | 709.137
2016-09-29 07:00 | 38279 | 2627.179 | 190483.257 | 59.78 | 727.301
2016-09-29 08:00 | 38715 | 3289.4319 | 190483.257 | 59.78 | 735.585
2016-09-29 09:00 | 40570 | 942.17 | 218244.3578 | 59.77 | 811.4
2016-09-29 10:00 | 42799 | 657.7668 | 235751.8976 | 59.77 | 855.98
2016-09-29 11:00 | 44961 | 600.8664 | 247976.9931 | 59.78 | 854.259
2016-09-29 12:00 | 47193 | 268.6003 | 268914.5439 | 59.78 | 896.667
2016-09-29 13:00 | 49640 | 310.6464 | 290063.5639 | 59.76 | 1042.44
2016-09-29 14:00 | 51862 | 333.8756 | 304780.1309 | 59.76 | 1089.102
2016-09-29 15:00 | 53725 | 490.6173 | 309593.1795 | 59.75 | 1181.95
2016-09-29 16:00 | 54990 | 746.6705 | 308753.1795 | 59.75 | 1209.78
2016-09-29 17:00 | 54872 | 703.5468 | 306056.2691 | 59.75 | 1207.184
2016-09-29 18:00 | 53070 | 724.1746 | 306056.2691 | 59.76 | 1114.47
2016-09-29 19:00 | 51268 | 2140.2009 | 295200.1625 | 59.76 | 1076.628
2016-09-29 20:00 | 49970 | 4541.1049 | 275758.2317 | 59.78 | 949.43
2016-09-29 21:00 | 46892 | 5119.6029 | 256574.8037 | 59.77 | 937.84
2016-09-29 22:00 | 42719 | 4946.6241 | 207713.0258 | 59.77 | 854.38
2016-09-29 23:00 | 38516 | 5169.1839 | 185104.0658 | 59.78 | 731.804
2016-09-30 | 34978 | 5121.824 | 185104.0658 | 59.77 | 699.56
2016-09-30 01:00 | 33263 | 4998.8512 | 185104.0658 | 59.77 | 665.26
2016-09-30 02:00 | 32135 | 4074.5109 | 185104.0658 | 59.77 | 642.7
2016-09-30 03:00 | 31659 | 3231.5221 | 185104.0658 | 59.77 | 633.18
2016-09-30 04:00 | 31849 | 1966.3193 | 185104.0658 | 59.77 | 636.98
2016-09-30 05:00 | 33616 | 1295.3839 | 184609.0658 | 59.77 | 672.32
2016-09-30 06:00 | 37267 | 1205.3826 | 193101.8438 | 59.78 | 708.073
2016-09-30 07:00 | 38240 | 1110.7397 | 202064.6438 | 59.78 | 726.56
2016-09-30 08:00 | 38630 | 1492.3608 | 202064.6438 | 59.78 | 733.97
2016-09-30 09:00 | 40479 | 1054.9629 | 215594.6242 | 59.77 | 809.58
2016-09-30 10:00 | 42718 | 638.0527 | 232461.1387 | 59.77 | 854.36
2016-09-30 11:00 | 44984 | 1114.5688 | 242464.6424 | 59.78 | 854.696
2016-09-30 12:00 | 47331 | 1751.764 | 254542.4904 | 59.78 | 899.289
2016-09-30 13:00 | 50062 | 2406.5231 | 273531.6772 | 59.76 | 1051.302
2016-09-30 14:00 | 52200 | 2793.3479 | 284778.7452 | 59.76 | 1096.2
2016-09-30 15:00 | 53959 | 2461.9267 | 293133.3727 | 59.76 | 1133.139
2016-09-30 16:00 | 55128 | 2117.5259 | 294458.0217 | 59.75 | 1212.816
2016-09-30 17:00 | 54512 | 2009.188 | 294950.3717 | 59.75 | 1199.264
2016-09-30 18:00 | 52842 | 2126.3181 | 289589.0897 | 59.76 | 1109.682
2016-09-30 19:00 | 51173 | 2748.8322 | 277304.3147 | 59.76 | 1074.633
2016-09-30 20:00 | 50059 | 3643.3564 | 263127.4867 | 59.78 | 951.121
2016-09-30 21:00 | 47167 | 3634.0694 | 240272.3279 | 59.78 | 896.173
2016-09-30 22:00 | 43196 | 4365.591 | 206824.2395 | 59.77 | 863.92
2016-09-30 23:00 | 39127 | 4214.802 | 192500.755 | 59.78 | 743.413
2016-10-01 | 37392 | 4011.0124 | 190019.155 | 59.78 | 710.448
2016-10-01 01:00 | 35432 | 4584.0148 | 188442.385 | 59.77 | 708.64
2016-10-01 02:00 | 34116 | 4417.1828 | 188442.385 | 59.77 | 682.32
2016-10-01 03:00 | 33438 | 3976.066 | 188442.385 | 59.77 | 668.76
2016-10-01 04:00 | 33565 | 3597.3606 | 188442.385 | 59.77 | 671.3
2016-10-01 05:00 | 35184 | 2689.6913 | 188937.385 | 59.77 | 703.68
2016-10-01 06:00 | 38730 | 1897.005 | 194659.675 | 59.78 | 735.87
2016-10-01 07:00 | 39749 | 2031.3692 | 198771.145 | 59.77 | 794.98
2016-10-01 08:00 | 40219 | 2408.8228 | 198771.145 | 59.77 | 804.38
2016-10-01 09:00 | 42075 | 1441.8442 | 219839.4434 | 59.77 | 841.5
2016-10-01 10:00 | 44222 | 1509.134 | 234874.6138 | 59.78 | 840.218
2016-10-01 11:00 | 46434 | 1449.1423 | 248914.4985 | 59.78 | 882.246
2016-10-01 12:00 | 48689 | 1612.8133 | 265926.945 | 59.78 | 925.091
2016-10-01 13:00 | 51113 | 1501.5946 | 281242.7678 | 59.76 | 1073.373
2016-10-01 14:00 | 53258 | 1397.8419 | 298617.0162 | 59.76 | 1118.418
2016-10-01 15:00 | 54848 | 1200.5355 | 298378.3152 | 59.75 | 1206.656
2016-10-01 16:00 | 55608 | 1216.0298 | 299394.3152 | 59.75 | 1223.376
2016-10-01 17:00 | 54625 | 1232.9979 | 298378.3152 | 59.75 | 1201.75
2016-10-01 18:00 | 52254 | 1409.0287 | 295007.6858 | 59.76 | 1097.334
2016-10-01 19:00 | 49884 | 2739.1669 | 268774.7584 | 59.78 | 947.796
2016-10-01 20:00 | 48273 | 4842.3737 | 243768.8004 | 59.78 | 917.187
2016-10-01 21:00 | 45616 | 5819.0937 | 216790.8672 | 59.77 | 912.32
2016-10-01 22:00 | 42531 | 5404.8916 | 199416.6188 | 59.78 | 808.089
2016-10-01 23:00 | 39262 | 5443.2914 | 190453.8188 | 59.78 | 745.978
2016-10-02 | 38713 | 5142.4545 | 190453.8188 | 59.78 | 735.547
2016-10-02 01:00 | 37505 | 4559.782 | 192030.5888 | 59.78 | 712.595
2016-10-02 02:00 | 36024 | 4678.9384 | 192030.5888 | 59.77 | 720.48
2016-10-02 03:00 | 35014 | 4160.4815 | 192030.5888 | 59.77 | 700.28
2016-10-02 04:00 | 34548 | 3773.7326 | 192030.5888 | 59.77 | 690.96
2016-10-02 05:00 | 34888 | 3139.4669 | 192030.5888 | 59.77 | 697.76
2016-10-02 06:00 | 36039 | 2510.3299 | 192030.5888 | 59.78 | 684.741
2016-10-02 07:00 | 36757 | 2045.8133 | 194512.1888 | 59.78 | 698.383
2016-10-02 08:00 | 38466 | 2134.7548 | 194512.1888 | 59.78 | 730.854
2016-10-02 09:00 | 40952 | 1297.5403 | 214715.1286 | 59.77 | 819.04
2016-10-02 10:00 | 43272 | 1224.6822 | 233547.3346 | 59.77 | 865.44
2016-10-02 11:00 | 45272 | 1490.8008 | 240612.0594 | 59.78 | 860.168
2016-10-02 12:00 | 47313 | 1910.9594 | 248828.0809 | 59.78 | 898.947
2016-10-02 13:00 | 49176 | 2382.1758 | 256409.4357 | 59.78 | 934.344
2016-10-02 14:00 | 50931 | 3426.3101 | 260242.1557 | 59.76 | 1069.551
2016-10-02 15:00 | 52540 | 3766.4232 | 263962.3988 | 59.76 | 1103.34
2016-10-02 16:00 | 53526 | 4476.7326 | 264234.3288 | 59.76 | 1124.046
2016-10-02 17:00 | 53126 | 5648.2056 | 257813.8362 | 59.78 | 1009.394
2016-10-02 18:00 | 51751 | 5980.4516 | 247240.0682 | 59.78 | 983.269
2016-10-02 19:00 | 50377 | 5552.9935 | 241360.2902 | 59.78 | 957.163
2016-10-02 20:00 | 49298 | 5320.9057 | 237203.1022 | 59.78 | 936.662
2016-10-02 21:00 | 46975 | 6590.4995 | 215511.2094 | 59.77 | 939.5
2016-10-02 22:00 | 44038 | 5866.5052 | 199324.779 | 59.77 | 880.76
2016-10-02 23:00 | 40833 | 6534.2185 | 179467.123 | 59.78 | 775.827
2016-10-03 | 39570 | 6991.103 | 172870.623 | 59.78 | 751.83
2016-10-03 01:00 | 37373 | 7799.4906 | 172870.623 | 59.77 | 747.46
2016-10-03 02:00 | 36050 | 6500.9749 | 172870.623 | 59.77 | 721
2016-10-03 03:00 | 35182 | 5354.8308 | 172870.623 | 59.77 | 703.64
2016-10-03 04:00 | 34770 | 4398.3462 | 172870.623 | 59.77 | 695.4
2016-10-03 05:00 | 34846 | 4356.956 | 172870.623 | 59.77 | 696.92
2016-10-03 06:00 | 35489 | 4665.9334 | 172870.623 | 59.77 | 709.78
2016-10-03 07:00 | 35799 | 4719.9377 | 172870.623 | 59.77 | 715.98
2016-10-03 08:00 | 37508 | 5002.9528 | 172274.673 | 59.78 | 712.652
2016-10-03 09:00 | 39818 | 4003.0628 | 184645.689 | 59.78 | 756.542
2016-10-03 10:00 | 41640 | 3169.2009 | 202567.449 | 59.77 | 832.8
2016-10-03 11:00 | 43197 | 3121.8817 | 213785.5169 | 59.77 | 863.94
2016-10-03 12:00 | 44752 | 3572.0027 | 221869.8619 | 59.77 | 895.04
2016-10-03 13:00 | 46181 | 3738.3019 | 227020.1119 | 59.77 | 923.62
2016-10-03 14:00 | 47492 | 3753.1283 | 235494.5599 | 59.78 | 902.348
2016-10-03 15:00 | 48527 | 2913.0098 | 248157.2759 | 59.78 | 922.013
2016-10-03 16:00 | 49093 | 2849.6069 | 249395.6791 | 59.78 | 932.767
2016-10-03 17:00 | 49080 | 2997.2105 | 249173.2759 | 59.78 | 932.52
2016-10-03 18:00 | 48830 | 3475.0203 | 248157.2759 | 59.78 | 927.77
2016-10-03 19:00 | 48581 | 4095.4416 | 241643.608 | 59.78 | 923.039
2016-10-03 20:00 | 48446 | 4769.567 | 233559.263 | 59.78 | 920.474
2016-10-03 21:00 | 46143 | 5559.4812 | 211473.923 | 59.77 | 922.86
2016-10-03 22:00 | 42701 | 6314.5009 | 187454.589 | 59.78 | 811.319
2016-10-03 23:00 | 39053 | 6042.3799 | 171736.873 | 59.78 | 742.007
2016-10-04 | 34829 | 6042.3934 | 171736.873 | 59.77 | 696.58
2016-10-04 01:00 | 33492 | 6377.3792 | 171736.873 | 59.79 | 602.856
2016-10-04 02:00 | 32703 | 6230.6345 | 171736.873 | 59.79 | 588.654
2016-10-04 03:00 | 32501 | 5600.3026 | 171736.873 | 59.79 | 585.018
2016-10-04 04:00 | 33060 | 5208.2493 | 170962.543 | 59.77 | 661.2
2016-10-04 05:00 | 35258 | 5422.2204 | 170962.543 | 59.77 | 705.16
2016-10-04 06:00 | 39312 | 5327.4687 | 174758.119 | 59.78 | 746.928
2016-10-04 07:00 | 40697 | 4805.6251 | 184618.305 | 59.78 | 773.243
2016-10-04 08:00 | 40818 | 4446.2214 | 188570.655 | 59.78 | 775.542
2016-10-04 09:00 | 41877 | 3840.5414 | 199663.725 | 59.77 | 837.54
2016-10-04 10:00 | 43140 | 5225.9515 | 199663.725 | 59.77 | 862.8
2016-10-04 11:00 | 44166 | 6005.4489 | 201913.725 | 59.77 | 883.32
2016-10-04 12:00 | 45213 | 5427.7937 | 213010.225 | 59.77 | 904.26
2016-10-04 13:00 | 46279 | 4794.8673 | 223854.763 | 59.77 | 925.58
2016-10-04 14:00 | 47129 | 4400.5046 | 228775.1609 | 59.78 | 895.451
2016-10-04 15:00 | 48007 | 4486.4606 | 232019.6608 | 59.78 | 912.133
2016-10-04 16:00 | 48825 | 5173.617 | 232413.1041 | 59.78 | 927.675
2016-10-04 17:00 | 48613 | 6123.9573 | 227206.8409 | 59.77 | 972.26
2016-10-04 18:00 | 48255 | 7122.9764 | 219350.4409 | 59.77 | 965.1
2016-10-04 19:00 | 47897 | 8030.4571 | 210271.7509 | 59.77 | 957.94
2016-10-04 20:00 | 47570 | 8931.3457 | 200285.0809 | 59.77 | 951.4
2016-10-04 21:00 | 45208 | 9131.1753 | 189440.5429 | 59.78 | 858.952
2016-10-04 22:00 | 41309 | 8781.9123 | 171097.2085 | 59.78 | 784.871
2016-10-04 23:00 | 37751 | 9164.4422 | 171097.2085 | 59.77 | 755.02
2016-10-05 | 35735 | 8329.7985 | 165753.3085 | 59.79 | 643.23
2016-10-05 01:00 | 34379 | 7885.9595 | 165753.3085 | 59.79 | 618.822
2016-10-05 02:00 | 33661 | 7475.8012 | 165753.3085 | 59.79 | 605.898
2016-10-05 03:00 | 33360 | 6931.2542 | 165753.3085 | 59.79 | 600.48
2016-10-05 04:00 | 33799 | 7141.9385 | 166527.6385 | 59.79 | 608.382
2016-10-05 05:00 | 35914 | 6859.5116 | 166527.6385 | 59.77 | 718.28
2016-10-05 06:00 | 40004 | 6285.6009 | 176655.8585 | 59.78 | 760.076
2016-10-05 07:00 | 41391 | 5838.123 | 185389.7545 | 59.78 | 786.429
2016-10-05 08:00 | 41315 | 5585.8923 | 188862.0445 | 59.78 | 784.985
2016-10-05 09:00 | 42324 | 4515.5985 | 198811.5145 | 59.77 | 846.48
2016-10-05 10:00 | 43495 | 4037.5975 | 211165.2249 | 59.77 | 869.9
2016-10-05 11:00 | 44626 | 5104.8419 | 216185.7129 | 59.77 | 892.52
2016-10-05 12:00 | 45381 | 5839.4484 | 216185.7129 | 59.77 | 907.62
2016-10-05 13:00 | 46499 | 6047.0188 | 221335.9629 | 59.77 | 929.98
2016-10-05 14:00 | 47515 | 6760.2733 | 223428.1509 | 59.77 | 950.3
2016-10-05 15:00 | 48530 | 6792.6201 | 227030.2509 | 59.77 | 970.6
2016-10-05 16:00 | 49415 | 6740.8907 | 230016.2509 | 59.78 | 938.885
2016-10-05 17:00 | 49075 | 6617.1869 | 229280.2509 | 59.77 | 981.5
2016-10-05 18:00 | 48615 | 6675.4133 | 229280.2509 | 59.77 | 972.3
2016-10-05 19:00 | 48156 | 7934.8389 | 213570.1405 | 59.77 | 963.12
2016-10-05 20:00 | 47951 | 9146.0438 | 210213.7405 | 59.77 | 959.02
2016-10-05 21:00 | 45254 | 8757.9893 | 200316.5005 | 59.78 | 859.826
2016-10-05 22:00 | 41716 | 8752.0477 | 173350.0485 | 59.78 | 792.604
2016-10-05 23:00 | 38102 | 8664.4169 | 151132.2941 | 59.77 | 762.04
2016-10-06 | 32139 | 7976.9029 | 148882.2941 | 59.79 | 578.502
2016-10-06 01:00 | 30963 | 8065.4182 | 146427.8941 | 59.79 | 557.334
2016-10-06 02:00 | 30287 | 7641.8093 | 146427.8941 | 59.79 | 545.166
2016-10-06 03:00 | 29905 | 6657.4946 | 146427.8941 | 59.79 | 538.29
2016-10-06 04:00 | 30260 | 6305.043 | 143946.2941 | 59.79 | 544.68
2016-10-06 05:00 | 32250 | 6744.3933 | 145903.5221 | 59.79 | 580.5
2016-10-06 06:00 | 35916 | 5884.0473 | 159665.0265 | 59.77 | 718.32
2016-10-06 07:00 | 37230 | 5447.5069 | 168126.4965 | 59.77 | 744.6
2016-10-06 08:00 | 36824 | 5177.9912 | 168126.4965 | 59.77 | 736.48
2016-10-06 09:00 | 37733 | 3327.3659 | 184507.9825 | 59.78 | 716.927
2016-10-06 10:00 | 38863 | 2158.4442 | 196823.3425 | 59.78 | 738.397
2016-10-06 11:00 | 39861 | 1866.8082 | 207406.0625 | 59.77 | 797.22
2016-10-06 12:00 | 40772 | 1446.1644 | 214806.3125 | 59.77 | 815.44
2016-10-06 13:00 | 41886 | 1688.9124 | 223428.9005 | 59.77 | 837.72
2016-10-06 14:00 | 42965 | 2378.7351 | 225678.9005 | 59.77 | 859.3
2016-10-06 15:00 | 44160 | 2636.9253 | 231124.7989 | 59.77 | 883.2
2016-10-06 16:00 | 45292 | 2790.6207 | 232140.7989 | 59.78 | 860.548
2016-10-06 17:00 | 45329 | 2409.519 | 232619.5721 | 59.78 | 861.251
2016-10-06 18:00 | 44649 | 2900.1581 | 231124.7989 | 59.77 | 892.98
2016-10-06 19:00 | 43969 | 4610.8106 | 211463.3889 | 59.77 | 879.38
2016-10-06 20:00 | 43236 | 6593.3453 | 195339.7989 | 59.78 | 821.484
2016-10-06 21:00 | 41036 | 7557.2238 | 177282.5349 | 59.78 | 779.684
2016-10-06 22:00 | 37547 | 7854.5116 | 154594.1669 | 59.77 | 750.94
2016-10-06 23:00 | 34291 | 8185.4557 | 144014.5721 | 59.79 | 617.238
2016-10-07 | 31640 | 7718.0255 | 142865.6801 | 59.79 | 569.52
2016-10-07 01:00 | 30499 | 7555.9625 | 145320.0801 | 59.79 | 548.982
2016-10-07 02:00 | 29832 | 7377.4343 | 145320.0801 | 59.79 | 536.976
2016-10-07 03:00 | 29549 | 6112.9315 | 145320.0801 | 59.79 | 531.882
2016-10-07 04:00 | 29898 | 5501.6691 | 147801.6801 | 59.79 | 538.164
2016-10-07 05:00 | 31696 | 4989.4038 | 147801.6801 | 59.79 | 570.528
2016-10-07 06:00 | 35314 | 4542.2042 | 159466.1845 | 59.77 | 706.28
2016-10-07 07:00 | 36444 | 4119.6942 | 168185.8845 | 59.77 | 728.88
2016-10-07 08:00 | 36462 | 3910.5988 | 168185.8845 | 59.78 | 692.778
2016-10-07 09:00 | 37535 | 2235.3177 | 185666.4605 | 59.78 | 713.165
2016-10-07 10:00 | 38797 | 878.5456 | 199877.4569 | 59.77 | 775.94
2016-10-07 11:00 | 40076 | 612.5046 | 212539.9169 | 59.77 | 801.52
2016-10-07 12:00 | 41270 | 533.947 | 223176.8369 | 59.77 | 825.4
2016-10-07 13:00 | 42831 | 998.2953 | 228197.3249 | 59.77 | 856.62
2016-10-07 14:00 | 44399 | 1525.998 | 243280.0449 | 59.78 | 843.581
2016-10-07 15:00 | 45876 | 1692.4431 | 246636.4449 | 59.78 | 871.644
2016-10-07 16:00 | 47022 | 1791.7936 | 245485.847 | 59.78 | 893.418
2016-10-07 17:00 | 46850 | 1771.3293 | 245331.4304 | 59.78 | 890.15
2016-10-07 18:00 | 45803 | 2467.3398 | 235826.724 | 59.78 | 870.257
2016-10-07 19:00 | 44755 | 3969.4429 | 218001.974 | 59.77 | 895.1
2016-10-07 20:00 | 43849 | 5577.6707 | 202590.834 | 59.77 | 876.98
2016-10-07 21:00 | 41279 | 6917.7911 | 181608.07 | 59.78 | 784.301
2016-10-07 22:00 | 38090 | 8845.4218 | 150242.7856 | 59.77 | 761.8
2016-10-07 23:00 | 34674 | 9464.1249 | 146886.3856 | 59.79 | 624.132
2016-10-08 | 34522 | 9096.6677 | 144973.9856 | 59.79 | 621.396
2016-10-08 01:00 | 33176 | 8409.064 | 144973.9856 | 59.79 | 597.168
2016-10-08 02:00 | 32406 | 7924.0468 | 144973.9856 | 59.79 | 583.308
2016-10-08 03:00 | 31975 | 7514.6736 | 144973.9856 | 59.79 | 575.55
2016-10-08 04:00 | 32316 | 7142.1418 | 144973.9856 | 59.79 | 581.688
2016-10-08 05:00 | 34078 | 7041.8584 | 144973.9856 | 59.79 | 613.404
2016-10-08 06:00 | 37767 | 6347.2159 | 163847.87 | 59.77 | 755.34
2016-10-08 07:00 | 39197 | 5470.7655 | 178091.776 | 59.78 | 744.743
2016-10-08 08:00 | 39183 | 4845.2153 | 181594.9391 | 59.78 | 744.477
2016-10-08 09:00 | 40475 | 3058.7701 | 201766.6991 | 59.78 | 769.025
2016-10-08 10:00 | 42158 | 2315.0457 | 217682.9769 | 59.77 | 843.16
2016-10-08 11:00 | 43696 | 2440.1787 | 226157.4249 | 59.77 | 873.92
2016-10-08 12:00 | 45129 | 2029.5073 | 239972.9349 | 59.78 | 857.451
2016-10-08 13:00 | 46752 | 2399.9907 | 250077.6219 | 59.78 | 888.288
2016-10-08 14:00 | 48475 | 2254.014 | 266982.5059 | 59.78 | 921.025
2016-10-08 15:00 | 49925 | 2287.3037 | 267883.5019 | 59.76 | 1048.425
2016-10-08 16:00 | 50957 | 2466.1513 | 270204.5165 | 59.76 | 1070.097
2016-10-08 17:00 | 50472 | 2706.0448 | 269303.5205 | 59.76 | 1059.912
2016-10-08 18:00 | 48687 | 3172.6372 | 255637.2427 | 59.78 | 925.053
2016-10-08 19:00 | 46903 | 4594.6199 | 231449.9947 | 59.77 | 938.06
2016-10-08 20:00 | 45457 | 6098.5814 | 210669.0747 | 59.77 | 909.14
2016-10-08 21:00 | 43054 | 7459.6472 | 186174.6717 | 59.78 | 818.026
2016-10-08 22:00 | 40415 | 9596.7118 | 155940.2277 | 59.77 | 808.3
2016-10-08 23:00 | 37548 | 10987.4235 | 145786.0433 | 59.79 | 675.864
2016-10-09 | 36769 | 10386.5066 | 145786.0433 | 59.79 | 661.842
2016-10-09 01:00 | 35141 | 9284.5281 | 145786.0433 | 59.79 | 632.538
2016-10-09 02:00 | 34228 | 8717.3649 | 145786.0433 | 59.79 | 616.104
2016-10-09 03:00 | 33452 | 8395.4531 | 145786.0433 | 59.79 | 602.136
2016-10-09 04:00 | 33234 | 8216.7409 | 145786.0433 | 59.79 | 598.212
2016-10-09 05:00 | 33709 | 8243.8503 | 145786.0433 | 59.79 | 606.762
2016-10-09 06:00 | 34998 | 7721.6416 | 145786.0433 | 59.79 | 629.964
2016-10-09 07:00 | 35983 | 6393.9676 | 150919.7397 | 59.77 | 719.66
2016-10-09 08:00 | 37569 | 5337.8848 | 167792.3265 | 59.77 | 751.38
2016-10-09 09:00 | 39762 | 2877.8693 | 194351.5925 | 59.78 | 755.478
2016-10-09 10:00 | 41889 | 1941.7682 | 217640.5609 | 59.77 | 837.78
2016-10-09 11:00 | 43764 | 1953.4877 | 230476.1769 | 59.77 | 875.28
2016-10-09 12:00 | 45513 | 1234.8469 | 247745.6469 | 59.78 | 864.747
2016-10-09 13:00 | 47491 | 848.5091 | 266020.1459 | 59.78 | 902.329
2016-10-09 14:00 | 49417 | 1416.1006 | 275923.2628 | 59.76 | 1037.757
2016-10-09 15:00 | 51294 | 1489.0421 | 281511.5308 | 59.76 | 1077.174
2016-10-09 16:00 | 52381 | 1393.8459 | 280934.5868 | 59.76 | 1100.001
2016-10-09 17:00 | 52121 | 1878.333 | 279918.5868 | 59.76 | 1094.541
2016-10-09 18:00 | 50746 | 2768.6919 | 276063.3008 | 59.76 | 1065.666
2016-10-09 19:00 | 49372 | 4070.9898 | 253281.7864 | 59.78 | 938.068
2016-10-09 20:00 | 48054 | 6418.0152 | 225905.9164 | 59.77 | 961.08
2016-10-09 21:00 | 45710 | 8130.566 | 197566.0574 | 59.77 | 914.2
2016-10-09 22:00 | 43036 | 8698.4371 | 180496.0445 | 59.78 | 817.684
2016-10-09 23:00 | 40168 | 8938.9457 | 163097.2165 | 59.77 | 803.36
2016-10-10 | 37938 | 9025.0956 | 155143.3965 | 59.77 | 758.76
2016-10-10 01:00 | 35980 | 8163.5799 | 155143.3965 | 59.77 | 719.6
2016-10-10 02:00 | 34820 | 7890.4084 | 155143.3965 | 59.79 | 626.76
2016-10-10 03:00 | 34124 | 7349.6938 | 155143.3965 | 59.79 | 614.232
2016-10-10 04:00 | 33777 | 6960.4864 | 155143.3965 | 59.79 | 607.986
2016-10-10 05:00 | 33891 | 6874.0931 | 155143.3965 | 59.79 | 610.038
2016-10-10 06:00 | 34601 | 5926.2456 | 155143.3965 | 59.77 | 692.02
2016-10-10 07:00 | 35155 | 6495.0399 | 155143.3965 | 59.77 | 703.1
2016-10-10 08:00 | 37004 | 7169.3955 | 155143.3965 | 59.77 | 740.08
2016-10-10 09:00 | 39538 | 6275.0139 | 174907.7765 | 59.78 | 751.222
2016-10-10 10:00 | 42027 | 6407.7359 | 187065.9625 | 59.78 | 798.513
2016-10-10 11:00 | 44452 | 6480.9143 | 200287.3395 | 59.77 | 889.04
2016-10-10 12:00 | 46967 | 6212.3787 | 217786.693 | 59.77 | 939.34
2016-10-10 13:00 | 49358 | 6265.9342 | 238280.1114 | 59.78 | 937.802
2016-10-10 14:00 | 51388 | 6677.8867 | 247912.6064 | 59.78 | 976.372
2016-10-10 15:00 | 52989 | 6546.5006 | 262097.4264 | 59.78 | 1006.791
2016-10-10 16:00 | 53927 | 6166.1416 | 264490.6564 | 59.76 | 1132.467
2016-10-10 17:00 | 53794 | 6314.0682 | 264490.6564 | 59.78 | 1022.086
2016-10-10 18:00 | 53051 | 5792.1712 | 265106.0564 | 59.78 | 1007.969
2016-10-10 19:00 | 52308 | 5708.9323 | 264084.1494 | 59.78 | 993.852
2016-10-10 20:00 | 51216 | 6123.7918 | 255526.8059 | 59.78 | 973.104
2016-10-10 21:00 | 48748 | 5846.9136 | 238387.0979 | 59.78 | 926.212
2016-10-10 22:00 | 45430 | 5098.1604 | 225400.8925 | 59.77 | 908.6
2016-10-10 23:00 | 41758 | 4791.1006 | 196609.6725 | 59.78 | 793.402
2016-10-11 | 35611 | 4710.7738 | 190203.8025 | 59.77 | 712.22
2016-10-11 01:00 | 34127 | 3960.0674 | 187947.1918 | 59.77 | 682.54
2016-10-11 02:00 | 33248 | 3044.2188 | 187947.1918 | 59.77 | 664.96
2016-10-11 03:00 | 32790 | 2674.2486 | 187947.1918 | 59.77 | 655.8
2016-10-11 04:00 | 33154 | 2690.2084 | 187947.1918 | 59.77 | 663.08
2016-10-11 05:00 | 34845 | 3049.1294 | 187947.1918 | 59.77 | 696.9
2016-10-11 06:00 | 37833 | 3281.2784 | 187947.1918 | 59.78 | 718.827
2016-10-11 07:00 | 39215 | 3205.125 | 191303.5918 | 59.78 | 745.085
2016-10-11 08:00 | 40112 | 3248.9432 | 199159.9918 | 59.78 | 762.128
2016-10-11 09:00 | 42251 | 2610.3378 | 216506.1402 | 59.77 | 845.02
2016-10-11 10:00 | 44580 | 1710.1314 | 237161.0792 | 59.78 | 847.02
2016-10-11 11:00 | 46719 | 1483.4188 | 253769.128 | 59.78 | 887.661
2016-10-11 12:00 | 48649 | 1048.7063 | 274620.8054 | 59.76 | 1021.629
2016-10-11 13:00 | 50653 | 1016.1446 | 286153.9054 | 59.76 | 1063.713
2016-10-11 14:00 | 52368 | 1270.2944 | 287354.6124 | 59.76 | 1099.728
2016-10-11 15:00 | 53673 | 1501.4151 | 289702.8366 | 59.76 | 1127.133
2016-10-11 16:00 | 54399 | 1714.9151 | 289702.8366 | 59.75 | 1196.778
2016-10-11 17:00 | 53518 | 2209.263 | 288492.6044 | 59.76 | 1123.878
2016-10-11 18:00 | 52547 | 2099.7203 | 287977.8304 | 59.76 | 1103.487
2016-10-11 19:00 | 51576 | 1759.7988 | 280116.5496 | 59.76 | 1083.096
2016-10-11 20:00 | 50335 | 1884.3932 | 265953.2196 | 59.76 | 1057.035
2016-10-11 21:00 | 47507 | 1728.3201 | 249969.2702 | 59.78 | 902.633
2016-10-11 22:00 | 43703 | 1515.8232 | 229677.3422 | 59.77 | 874.06
2016-10-11 23:00 | 39719 | 1721.9983 | 204375.8858 | 59.77 | 794.38
2016-10-12 | 36625 | 1866.1025 | 204375.8858 | 59.78 | 695.875
2016-10-12 01:00 | 34875 | 1698.3805 | 202865.5658 | 59.78 | 662.625
2016-10-12 02:00 | 33733 | 1523.8897 | 201357.2158 | 59.77 | 674.66
2016-10-12 03:00 | 33122 | 1370.076 | 201357.2158 | 59.77 | 662.44
2016-10-12 04:00 | 33309 | 1479.1359 | 201357.2158 | 59.77 | 666.18
2016-10-12 05:00 | 35003 | 1502.444 | 201357.2158 | 59.78 | 665.057
2016-10-12 06:00 | 38639 | 1873.9484 | 201357.2158 | 59.78 | 734.141
2016-10-12 07:00 | 39921 | 2170.2267 | 206850.4965 | 59.77 | 798.42
2016-10-12 08:00 | 39927 | 2853.2143 | 206850.4965 | 59.78 | 758.613
2016-10-12 09:00 | 41677 | 1219.593 | 220274.4149 | 59.77 | 833.54
2016-10-12 10:00 | 43838 | 628.9639 | 236419.3709 | 59.78 | 832.922
2016-10-12 11:00 | 45880 | 520.57 | 251996.5063 | 59.78 | 871.72
2016-10-12 12:00 | 47774 | 713.2838 | 264401.4623 | 59.78 | 907.706
2016-10-12 13:00 | 49910 | 1082.3146 | 275246.2648 | 59.76 | 1048.11
2016-10-12 14:00 | 51544 | 1448.5536 | 278713.7232 | 59.76 | 1082.424
2016-10-12 15:00 | 52791 | 1920.8649 | 279704.6574 | 59.76 | 1108.611
2016-10-12 16:00 | 53403 | 2589.378 | 279269.7774 | 59.76 | 1121.463
2016-10-12 17:00 | 52547 | 3162.5619 | 276777.4322 | 59.76 | 1103.487
2016-10-12 18:00 | 51277 | 3342.6864 | 272023.6842 | 59.76 | 1076.817
2016-10-12 19:00 | 50007 | 3515.5584 | 259604.9488 | 59.78 | 950.133
2016-10-12 20:00 | 48668 | 4124.3118 | 243367.2728 | 59.78 | 924.692
2016-10-12 21:00 | 45745 | 4280.4114 | 222846.7419 | 59.77 | 914.9
2016-10-12 22:00 | 41868 | 4810.7829 | 192478.6315 | 59.78 | 795.492
2016-10-12 23:00 | 38021 | 4414.5559 | 174681.7775 | 59.78 | 722.399
2016-10-13 | 33977 | 4044.592 | 167319.3975 | 59.77 | 679.54
2016-10-13 01:00 | 32181 | 4523.8845 | 167319.3975 | 59.77 | 643.62
2016-10-13 02:00 | 31183 | 4391.294 | 168710.8675 | 59.79 | 561.294
2016-10-13 03:00 | 30739 | 4605.2152 | 168215.8675 | 59.79 | 553.302
2016-10-13 04:00 | 30979 | 4808.5972 | 167624.8595 | 59.79 | 557.622
2016-10-13 05:00 | 32604 | 4959.8144 | 167624.8595 | 59.77 | 652.08
2016-10-13 06:00 | 36236 | 4237.7345 | 169135.1795 | 59.77 | 724.72
2016-10-13 07:00 | 37574 | 4251.9956 | 167422.4095 | 59.78 | 713.906
2016-10-13 08:00 | 37590 | 4697.4265 | 167422.4095 | 59.78 | 714.21
2016-10-13 09:00 | 38865 | 2632.0075 | 186947.9955 | 59.78 | 738.435
2016-10-13 10:00 | 40681 | 2583.8293 | 206342.4335 | 59.77 | 813.62
2016-10-13 11:00 | 42281 | 2646.0694 | 217579.4995 | 59.77 | 845.62
2016-10-13 12:00 | 43765 | 2803.1581 | 232609.93 | 59.77 | 875.3
2016-10-13 13:00 | 45476 | 3186.0182 | 234943.397 | 59.77 | 909.52
2016-10-13 14:00 | 46766 | 4467.1201 | 235009.2037 | 59.77 | 935.32
2016-10-13 15:00 | 47696 | 5209.6565 | 235530.7935 | 59.77 | 953.92
2016-10-13 16:00 | 48183 | 5282.4537 | 236392.0201 | 59.78 | 915.477
2016-10-13 17:00 | 47387 | 5665.5767 | 234876.202 | 59.77 | 947.74
2016-10-13 18:00 | 46519 | 4943.6395 | 233499.2119 | 59.77 | 930.38
2016-10-13 19:00 | 45651 | 4673.253 | 229351.794 | 59.77 | 913.02
2016-10-13 20:00 | 44703 | 4610.8181 | 222503.4365 | 59.77 | 894.06
2016-10-13 21:00 | 42341 | 5050.0456 | 208062.5209 | 59.78 | 804.479
2016-10-13 22:00 | 38877 | 4586.8607 | 189393.3049 | 59.78 | 738.663
2016-10-13 23:00 | 35368 | 3873.0638 | 176082.5029 | 59.77 | 707.36
2016-10-14 | 34002 | 4467.0863 | 167667.1729 | 59.77 | 680.04
2016-10-14 01:00 | 32481 | 4842.279 | 167667.1729 | 59.77 | 649.62
2016-10-14 02:00 | 31526 | 4930.441 | 167784.0529 | 59.79 | 567.468
2016-10-14 03:00 | 31109 | 4058.9129 | 167784.0529 | 59.79 | 559.962
2016-10-14 04:00 | 31349 | 3576.665 | 168375.0609 | 59.77 | 626.98
2016-10-14 05:00 | 33096 | 2763.7148 | 168375.0609 | 59.77 | 661.92
2016-10-14 06:00 | 36702 | 2428.7064 | 188427.3593 | 59.78 | 697.338
2016-10-14 07:00 | 37963 | 2658.107 | 191156.1293 | 59.78 | 721.297
2016-10-14 08:00 | 37727 | 3108.7735 | 190140.1293 | 59.78 | 716.813
2016-10-14 09:00 | 38720 | 2875.1375 | 198892.4793 | 59.78 | 735.68
2016-10-14 10:00 | 40055 | 2340.1859 | 211678.6793 | 59.77 | 801.1
2016-10-14 11:00 | 41103 | 2200.262 | 216625.4873 | 59.77 | 822.06
2016-10-14 12:00 | 42129 | 2179.987 | 220079.4473 | 59.77 | 842.58
2016-10-14 13:00 | 43370 | 1843.3241 | 228258.3353 | 59.77 | 867.4
2016-10-14 14:00 | 44478 | 1646.9457 | 241626.8448 | 59.78 | 845.082
2016-10-14 15:00 | 45488 | 1630.5285 | 241626.8448 | 59.78 | 864.272
2016-10-14 16:00 | 46145 | 1424.2282 | 243233.8528 | 59.78 | 876.755
2016-10-14 17:00 | 45637 | 1067.5106 | 243233.8528 | 59.78 | 867.103
2016-10-14 18:00 | 45044 | 728.5685 | 240866.7328 | 59.78 | 855.836
2016-10-14 19:00 | 44451 | 1362.7616 | 231971.8248 | 59.78 | 844.569
2016-10-14 20:00 | 43576 | 2750.776 | 217921.7164 | 59.77 | 871.52
2016-10-14 21:00 | 41036 | 4573.0584 | 191457.8385 | 59.78 | 779.684
2016-10-14 22:00 | 37749 | 7571.3826 | 150070.0431 | 59.77 | 754.98
2016-10-14 23:00 | 34672 | 8794.9851 | 145049.5551 | 59.79 | 624.096
2016-10-15 | 34631 | 9314.4109 | 142342.5519 | 59.79 | 623.358
2016-10-15 01:00 | 34595 | 9717.9639 | 142342.5519 | 59.79 | 622.71
2016-10-15 02:00 | 33701 | 9135.1386 | 142342.5519 | 59.79 | 606.618
2016-10-15 03:00 | 33432 | 8377.7277 | 142342.5519 | 59.79 | 601.776
2016-10-15 04:00 | 33799 | 7750.6137 | 142342.5519 | 59.79 | 608.382
2016-10-15 05:00 | 35850 | 6999.6561 | 147408.7919 | 59.77 | 717
2016-10-15 06:00 | 39860 | 6544.7002 | 172043.7959 | 59.78 | 757.34
2016-10-15 07:00 | 41372 | 6262.4931 | 184359.1559 | 59.78 | 786.068
2016-10-15 08:00 | 41219 | 6201.7783 | 184359.1559 | 59.78 | 783.161
2016-10-15 09:00 | 42189 | 3990.0987 | 205555.9363 | 59.77 | 843.78
2016-10-15 10:00 | 43472 | 2416.5047 | 225596.4943 | 59.77 | 869.44
2016-10-15 11:00 | 44748 | 1796.3961 | 238765.7893 | 59.78 | 850.212
2016-10-15 12:00 | 45912 | 1599.5022 | 254735.7913 | 59.78 | 872.328
2016-10-15 13:00 | 47548 | 2174.5244 | 259756.2793 | 59.78 | 903.412
2016-10-15 14:00 | 49275 | 1814.3288 | 272873.9121 | 59.78 | 936.225
2016-10-15 15:00 | 50838 | 1511.9774 | 276319.3201 | 59.76 | 1067.598
2016-10-15 16:00 | 52068 | 1458.4865 | 278728.5403 | 59.76 | 1093.428
2016-10-15 17:00 | 51694 | 1306.3306 | 278728.5403 | 59.76 | 1085.574
2016-10-15 18:00 | 50260 | 2191.5449 | 270236.6001 | 59.76 | 1055.46
2016-10-15 19:00 | 48826 | 4752.809 | 244677.0771 | 59.78 | 927.694
2016-10-15 20:00 | 47156 | 7845.9864 | 203918.2747 | 59.77 | 943.12
2016-10-15 21:00 | 44884 | 9248.6466 | 182027.5407 | 59.78 | 852.796
2016-10-15 22:00 | 42067 | 10444.8405 | 161214.3179 | 59.77 | 841.34
2016-10-15 23:00 | 39163 | 10757.1675 | 147902.5153 | 59.77 | 783.26
2016-10-16 | 37228 | 10130.912 | 143828.6253 | 59.79 | 670.104
2016-10-16 01:00 | 35504 | 9489.3863 | 143209.2553 | 59.79 | 639.072
2016-10-16 02:00 | 34278 | 9040.6738 | 142739.3803 | 59.79 | 617.004
2016-10-16 03:00 | 33622 | 8342.3784 | 142739.3803 | 59.79 | 605.196
2016-10-16 04:00 | 33489 | 7466.3702 | 142739.3803 | 59.79 | 602.802
2016-10-16 05:00 | 34037 | 7704.4231 | 142739.3803 | 59.79 | 612.666
2016-10-16 06:00 | 35332 | 6569.8495 | 147238.157 | 59.77 | 706.64
2016-10-16 07:00 | 36404 | 5870.8087 | 153834.657 | 59.77 | 728.08
2016-10-16 08:00 | 37946 | 5416.9068 | 169124.817 | 59.78 | 720.974
2016-10-16 09:00 | 39955 | 5690.2707 | 178917.113 | 59.78 | 759.145
2016-10-16 10:00 | 41659 | 3035.703 | 207602.0314 | 59.77 | 833.18
2016-10-16 11:00 | 43321 | 3907.9298 | 211666.7464 | 59.77 | 866.42
2016-10-16 12:00 | 44728 | 5342.9481 | 216908.2584 | 59.77 | 894.56
2016-10-16 13:00 | 46130 | 5188.1264 | 228594.5064 | 59.77 | 922.6
2016-10-16 14:00 | 47726 | 4571.4194 | 247935.9918 | 59.78 | 906.794
2016-10-16 15:00 | 49424 | 4382.5862 | 255305.8972 | 59.78 | 939.056
2016-10-16 16:00 | 50516 | 4040.7907 | 257756.6248 | 59.78 | 959.804
2016-10-16 17:00 | 50271 | 3292.0828 | 257756.6248 | 59.78 | 955.149
2016-10-16 18:00 | 49352 | 4123.2406 | 255305.8972 | 59.78 | 937.688
2016-10-16 19:00 | 48432 | 6523.7299 | 234792.9338 | 59.77 | 968.64
2016-10-16 20:00 | 47078 | 9175.1668 | 207129.6618 | 59.77 | 941.56
2016-10-16 21:00 | 44927 | 10540.2854 | 184370.0178 | 59.78 | 853.613
2016-10-16 22:00 | 42254 | 11093.4654 | 161679.4424 | 59.77 | 845.08
2016-10-16 23:00 | 39469 | 10838.018 | 145848.067 | 59.77 | 789.38
2016-10-17 | 35824 | 10805.122 | 137894.247 | 59.79 | 644.832
2016-10-17 01:00 | 34259 | 10015.0697 | 138513.617 | 59.79 | 616.662
2016-10-17 02:00 | 33173 | 9277.0601 | 138983.492 | 59.79 | 597.114
2016-10-17 03:00 | 32656 | 8752.299 | 138983.492 | 59.79 | 587.808
2016-10-17 04:00 | 32390 | 8660.3705 | 138983.492 | 59.79 | 583.02
2016-10-17 05:00 | 32571 | 8749.1309 | 136631.332 | 59.79 | 586.278
2016-10-17 06:00 | 33389 | 7630.127 | 138952.3465 | 59.79 | 601.002
2016-10-17 07:00 | 34035 | 6463.6387 | 138952.3465 | 59.77 | 680.7
2016-10-17 08:00 | 35445 | 5638.4994 | 154103.8465 | 59.77 | 708.9
2016-10-17 09:00 | 37642 | 4684.0373 | 175942.3225 | 59.78 | 715.198
2016-10-17 10:00 | 39546 | 2694.7495 | 202131.5409 | 59.78 | 751.374
2016-10-17 11:00 | 41554 | 3079.2232 | 212140.8064 | 59.77 | 831.08
2016-10-17 12:00 | 43513 | 3511.8777 | 220488.7744 | 59.77 | 870.26
2016-10-17 13:00 | 45174 | 3552.8663 | 230578.4394 | 59.77 | 903.48
2016-10-17 14:00 | 46724 | 3319.8789 | 242183.0664 | 59.78 | 887.756
2016-10-17 15:00 | 47818 | 3678.1609 | 241431.2464 | 59.78 | 908.542
2016-10-17 16:00 | 48495 | 4055.1409 | 242167.2464 | 59.78 | 921.405
2016-10-17 17:00 | 48312 | 4170.2846 | 241431.2464 | 59.78 | 917.928
2016-10-17 18:00 | 48785 | 4986.617 | 241431.2464 | 59.78 | 926.915
2016-10-17 19:00 | 49257 | 7089.227 | 231421.9809 | 59.77 | 985.14
2016-10-17 20:00 | 48280 | 9532.9305 | 210101.3845 | 59.77 | 965.6
2016-10-17 21:00 | 46132 | 11471.8317 | 179998.1535 | 59.78 | 876.508
2016-10-17 22:00 | 42679 | 11163.0011 | 160697.9365 | 59.77 | 853.58
2016-10-17 23:00 | 39283 | 10431.913 | 143608.6585 | 59.77 | 785.66
2016-10-18 | 32456 | 10257.1848 | 138474.9621 | 59.79 | 584.208
2016-10-18 01:00 | 31107 | 9480.278 | 138474.9621 | 59.79 | 559.926
2016-10-18 02:00 | 30322 | 9041.4622 | 138474.9621 | 59.79 | 545.796
2016-10-18 03:00 | 30107 | 9077.5009 | 138474.9621 | 59.79 | 541.926
2016-10-18 04:00 | 30650 | 8382.1527 | 138474.9621 | 59.79 | 551.7
2016-10-18 05:00 | 32569 | 8067.6983 | 140827.1221 | 59.79 | 586.242
2016-10-18 06:00 | 36221 | 7249.3668 | 145960.8185 | 59.77 | 724.42
2016-10-18 07:00 | 37718 | 7217.9362 | 150981.3065 | 59.77 | 754.36
2016-10-18 08:00 | 37705 | 7367.2744 | 150981.3065 | 59.77 | 754.1
2016-10-18 09:00 | 39157 | 5599.9347 | 170745.6865 | 59.78 | 743.983
2016-10-18 10:00 | 41275 | 5903.3175 | 179870.1724 | 59.78 | 784.225
2016-10-18 11:00 | 43152 | 5224.6832 | 197171.9834 | 59.77 | 863.04
2016-10-18 12:00 | 44794 | 3603.1817 | 222063.9314 | 59.77 | 895.88
2016-10-18 13:00 | 46717 | 2952.8863 | 240029.1464 | 59.78 | 887.623
2016-10-18 14:00 | 48358 | 2686.6862 | 253372.2164 | 59.78 | 918.802
2016-10-18 15:00 | 49461 | 2733.0737 | 255365.7664 | 59.78 | 939.759
2016-10-18 16:00 | 50067 | 2980.8143 | 255365.7664 | 59.78 | 951.273
2016-10-18 17:00 | 49214 | 2927.8052 | 255365.7664 | 59.78 | 935.066
2016-10-18 18:00 | 48502 | 3581.3132 | 249440.5065 | 59.78 | 921.538
2016-10-18 19:00 | 47791 | 4722.757 | 234388.6955 | 59.78 | 908.029
2016-10-18 20:00 | 46457 | 6081.2202 | 213892.5875 | 59.77 | 929.14
2016-10-18 21:00 | 43960 | 6551.2383 | 192690.7025 | 59.78 | 835.24
2016-10-18 22:00 | 40480 | 6219.1871 | 175875.3425 | 59.78 | 769.12
2016-10-18 23:00 | 36870 | 5788.0951 | 165671.5225 | 59.77 | 737.4
2016-10-19 | 33108 | 6510.1517 | 165671.5225 | 59.79 | 595.944
2016-10-19 01:00 | 31480 | 4987.6467 | 165671.5225 | 59.79 | 566.64
2016-10-19 02:00 | 30616 | 2987.5881 | 165671.5225 | 59.77 | 612.32
2016-10-19 03:00 | 30107 | 2809.6952 | 165671.5225 | 59.79 | 541.926
2016-10-19 04:00 | 30397 | 2664.4107 | 165671.5225 | 59.77 | 607.94
2016-10-19 05:00 | 32082 | 2436.9154 | 165671.5225 | 59.77 | 641.64
2016-10-19 06:00 | 35690 | 2091.5982 | 173625.3425 | 59.78 | 678.11
2016-10-19 07:00 | 37271 | 2282.0471 | 181988.3525 | 59.78 | 708.149
2016-10-19 08:00 | 37234 | 3008.5174 | 181988.3525 | 59.78 | 707.446
2016-10-19 09:00 | 38639 | 1791.5603 | 193693.3705 | 59.78 | 734.141
2016-10-19 10:00 | 40625 | 1440.0417 | 213589.8889 | 59.77 | 812.5
2016-10-19 11:00 | 42476 | 983.5065 | 229540.2913 | 59.77 | 849.52
2016-10-19 12:00 | 44485 | 696.8858 | 245665.6393 | 59.78 | 845.215
2016-10-19 13:00 | 46307 | 553.4951 | 254383.0163 | 59.78 | 879.833
2016-10-19 14:00 | 47941 | 554.844 | 261019.2808 | 59.78 | 910.879
2016-10-19 15:00 | 49203 | 769.8184 | 262279.2648 | 59.76 | 1033.263
2016-10-19 16:00 | 49871 | 1222.0509 | 262279.2648 | 59.76 | 1047.291
2016-10-19 17:00 | 49215 | 1873.6437 | 259263.7328 | 59.78 | 935.085
2016-10-19 18:00 | 48296 | 2160.4423 | 251720.9248 | 59.78 | 917.624
2016-10-19 19:00 | 47376 | 3055.4197 | 240084.0444 | 59.78 | 900.144
2016-10-19 20:00 | 45960 | 4354.0028 | 222796.1964 | 59.77 | 919.2
2016-10-19 21:00 | 43603 | 3357.2887 | 214078.8194 | 59.77 | 872.06
2016-10-19 22:00 | 40100 | 2069.0367 | 202292.3049 | 59.77 | 802
2016-10-19 23:00 | 36530 | 2433.2894 | 179989.1245 | 59.78 | 694.07
2016-10-20 | 32002 | 2747.5971 | 171030.1645 | 59.77 | 640.04
2016-10-20 01:00 | 30461 | 2623.8303 | 171030.1645 | 59.77 | 609.22
2016-10-20 02:00 | 29398 | 2856.7207 | 171030.1645 | 59.79 | 529.164
2016-10-20 03:00 | 28897 | 2374.9871 | 171030.1645 | 59.79 | 520.146
2016-10-20 04:00 | 29079 | 1656.8644 | 171030.1645 | 59.79 | 523.422
2016-10-20 05:00 | 30609 | 1532.7016 | 171030.1645 | 59.77 | 612.18
2016-10-20 06:00 | 33962 | 1262.48 | 171030.1645 | 59.78 | 645.278
2016-10-20 07:00 | 35443 | 1312.388 | 177112.7845 | 59.78 | 673.417
2016-10-20 08:00 | 35277 | 1680.1968 | 175924.1237 | 59.78 | 670.263
2016-10-20 09:00 | 36800 | 1145.832 | 187571.6736 | 59.78 | 699.2
2016-10-20 10:00 | 38608 | 814.4917 | 202813.0696 | 59.77 | 772.16
2016-10-20 11:00 | 40444 | 742.0481 | 211460.9276 | 59.77 | 808.88
2016-10-20 12:00 | 42259 | 652.247 | 226113.9106 | 59.77 | 845.18
2016-10-20 13:00 | 44217 | 790.7148 | 236591.5386 | 59.78 | 840.123
2016-10-20 14:00 | 45650 | 1051.2977 | 244447.9386 | 59.78 | 867.35
2016-10-20 15:00 | 47062 | 1404.6678 | 245463.9386 | 59.78 | 894.178
2016-10-20 16:00 | 47659 | 2381.0606 | 244447.9386 | 59.78 | 905.521
2016-10-20 17:00 | 47167 | 3649.7734 | 236272.6787 | 59.78 | 896.173
2016-10-20 18:00 | 46075 | 4066.0831 | 224387.6827 | 59.77 | 921.5
2016-10-20 19:00 | 44983 | 5105.7985 | 211099.9627 | 59.77 | 899.66
2016-10-20 20:00 | 43618 | 6345.5444 | 190011.0837 | 59.78 | 828.742
2016-10-20 21:00 | 41188 | 7724.9114 | 168230.5457 | 59.78 | 782.572
2016-10-20 22:00 | 37939 | 7252.4933 | 149739.1547 | 59.77 | 758.78
2016-10-20 23:00 | 34439 | 6936.1788 | 144718.6667 | 59.77 | 688.78
2016-10-21 | 32934 | 6820.7331 | 144718.6667 | 59.79 | 592.812
2016-10-21 01:00 | 31407 | 6467.3649 | 144718.6667 | 59.79 | 565.326
2016-10-21 02:00 | 30366 | 5418.3361 | 144100.6667 | 59.79 | 546.588
2016-10-21 03:00 | 29812 | 4845.2194 | 144100.6667 | 59.79 | 536.616
2016-10-21 04:00 | 29985 | 4719.97 | 141619.0667 | 59.79 | 539.73
2016-10-21 05:00 | 31633 | 3785.9278 | 141619.0667 | 59.77 | 632.66
2016-10-21 06:00 | 35024 | 2758.5875 | 162057.4347 | 59.77 | 700.48
2016-10-21 07:00 | 36442 | 3422.9769 | 171853.1607 | 59.78 | 692.398
2016-10-21 08:00 | 36407 | 4606.0129 | 170882.4215 | 59.77 | 728.14
2016-10-21 09:00 | 37805 | 5851.5617 | 170882.4215 | 59.77 | 756.1
2016-10-21 10:00 | 39730 | 4258.756 | 190894.5619 | 59.78 | 754.87
2016-10-21 11:00 | 41857 | 5778.1666 | 195394.5619 | 59.78 | 795.283
2016-10-21 12:00 | 43639 | 8212.8713 | 195394.5619 | 59.78 | 829.141
2016-10-21 13:00 | 45516 | 7218.8398 | 207136.9999 | 59.77 | 910.32
2016-10-21 14:00 | 47111 | 7028.1163 | 208396.0265 | 59.77 | 942.22
2016-10-21 15:00 | 48180 | 9252.1105 | 208152.9999 | 59.77 | 963.6
2016-10-21 16:00 | 48580 | 10215.2589 | 207136.9999 | 59.77 | 971.6
2016-10-21 17:00 | 47689 | 9076.5389 | 207136.9999 | 59.77 | 953.78
2016-10-21 18:00 | 46894 | 9627.5027 | 200426.8895 | 59.78 | 890.986
2016-10-21 19:00 | 46099 | 11379.9332 | 178191.6335 | 59.78 | 875.881
2016-10-21 20:00 | 44967 | 12512.6326 | 165872.7235 | 59.77 | 899.34
2016-10-21 21:00 | 42777 | 11794.8401 | 155146.2855 | 59.77 | 855.54
2016-10-21 22:00 | 39746 | 10829.6396 | 147842.3365 | 59.77 | 794.92
2016-10-21 23:00 | 36364 | 10061.8597 | 147842.3365 | 59.79 | 654.552
2016-10-22 | 35379 | 10362.1268 | 144075.4058 | 59.79 | 636.822
2016-10-22 01:00 | 34677 | 8952.005 | 140917.0058 | 59.79 | 624.186
2016-10-22 02:00 | 33581 | 8210.9059 | 141535.0058 | 59.79 | 604.458
2016-10-22 03:00 | 32939 | 8023.2651 | 141535.0058 | 59.79 | 592.902
2016-10-22 04:00 | 33195 | 7015.4862 | 144016.6058 | 59.79 | 597.51
2016-10-22 05:00 | 34961 | 5992.9508 | 149873.9258 | 59.77 | 699.22
2016-10-22 06:00 | 38822 | 5444.2501 | 175939.1718 | 59.78 | 737.618
2016-10-22 07:00 | 40665 | 5835.5917 | 185888.6418 | 59.78 | 772.635
2016-10-22 08:00 | 40633 | 6753.0382 | 188048.0418 | 59.78 | 772.027
2016-10-22 09:00 | 41921 | 7477.9006 | 188048.0418 | 59.78 | 796.499
2016-10-22 10:00 | 43756 | 8537.0213 | 189981.9929 | 59.78 | 831.364
2016-10-22 11:00 | 45177 | 9207.4962 | 196731.9929 | 59.78 | 858.363
2016-10-22 12:00 | 46309 | 10255.3165 | 196731.9929 | 59.78 | 879.871
2016-10-22 13:00 | 47673 | 10603.8446 | 206902.7309 | 59.78 | 905.787
2016-10-22 14:00 | 48619 | 10718.6537 | 213615.1409 | 59.77 | 972.38
2016-10-22 15:00 | 49002 | 10006.4877 | 216968.8513 | 59.77 | 980.04
2016-10-22 16:00 | 48984 | 9536.0564 | 218050.658 | 59.77 | 979.68
2016-10-22 17:00 | 47996 | 9199.5131 | 216968.8513 | 59.77 | 959.92
2016-10-22 18:00 | 47484 | 9015.8929 | 216968.8513 | 59.77 | 949.68
2016-10-22 19:00 | 46972 | 9801.782 | 206392.0813 | 59.78 | 892.468
2016-10-22 20:00 | 45977 | 10090.8064 | 197429.2813 | 59.78 | 873.563
2016-10-22 21:00 | 44174 | 10757.1752 | 178299.5833 | 59.78 | 839.306
2016-10-22 22:00 | 42211 | 11001.9861 | 165535.9053 | 59.77 | 844.22
2016-10-22 23:00 | 39713 | 10843.5638 | 157835.6949 | 59.77 | 794.26
2016-10-23 | 39694 | 10038.8583 | 157835.6949 | 59.77 | 793.88
2016-10-23 01:00 | 37769 | 8939.0638 | 157835.6949 | 59.77 | 755.38
2016-10-23 02:00 | 36458 | 8539.9783 | 157835.6949 | 59.77 | 729.16
2016-10-23 03:00 | 35532 | 8524.3937 | 157835.6949 | 59.79 | 639.576
2016-10-23 04:00 | 35201 | 8803.617 | 157835.6949 | 59.79 | 633.618
2016-10-23 05:00 | 35578 | 8900.6061 | 160994.0949 | 59.79 | 640.404
2016-10-23 06:00 | 36815 | 8437.8636 | 160994.0949 | 59.77 | 736.3
2016-10-23 07:00 | 38080 | 8927.1641 | 160994.0949 | 59.77 | 761.6
2016-10-23 08:00 | 39594 | 9661.6048 | 162504.4149 | 59.77 | 791.88
2016-10-23 09:00 | 42030 | 9454.3986 | 175809.8749 | 59.78 | 798.57
2016-10-23 10:00 | 43952 | 10353.8026 | 178375.9238 | 59.78 | 835.088
2016-10-23 11:00 | 45192 | 11684.4648 | 177825.2363 | 59.78 | 858.648
2016-10-23 12:00 | 45974 | 12128.9548 | 177825.2363 | 59.78 | 873.506
2016-10-23 13:00 | 46090 | 11991.9527 | 178001.2363 | 59.78 | 875.71
2016-10-23 14:00 | 46198 | 12849.3506 | 177440.6083 | 59.78 | 877.762
2016-10-23 15:00 | 46266 | 12627.1691 | 173833.2883 | 59.78 | 879.054
2016-10-23 16:00 | 46027 | 12900.2881 | 173833.2883 | 59.78 | 874.513
2016-10-23 17:00 | 45215 | 12986.3308 | 164874.3283 | 59.77 | 904.3
2016-10-23 18:00 | 45269 | 12605.9339 | 164874.3283 | 59.78 | 860.111
2016-10-23 19:00 | 45322 | 12065.2332 | 166451.0983 | 59.78 | 861.118
2016-10-23 20:00 | 44594 | 11113.1586 | 166451.0983 | 59.78 | 847.286
2016-10-23 21:00 | 43167 | 11126.7194 | 158755.5083 | 59.77 | 863.34
2016-10-23 22:00 | 41067 | 10794.4885 | 150294.0383 | 59.77 | 821.34
2016-10-23 23:00 | 38619 | 10920.8759 | 135073.6139 | 59.77 | 772.38
2016-10-24 | 36660 | 11019.1654 | 135073.6139 | 59.79 | 659.88
2016-10-24 01:00 | 35219 | 9513.5834 | 132885.0835 | 59.79 | 633.942
2016-10-24 02:00 | 34085 | 9879.5108 | 132885.0835 | 59.79 | 613.53
2016-10-24 03:00 | 33340 | 9825.7313 | 132885.0835 | 59.79 | 600.12
2016-10-24 04:00 | 32948 | 9267.1443 | 132885.0835 | 59.79 | 593.064
2016-10-24 05:00 | 33098 | 9227.5799 | 132885.0835 | 59.79 | 595.764
2016-10-24 06:00 | 33860 | 8566.656 | 134386.7335 | 59.79 | 609.48
2016-10-24 07:00 | 34645 | 8519.4027 | 134386.7335 | 59.79 | 623.61
2016-10-24 08:00 | 36200 | 8744.8402 | 134386.7335 | 59.79 | 651.6
2016-10-24 09:00 | 38977 | 7322.8563 | 157560.9779 | 59.77 | 779.54
2016-10-24 10:00 | 41447 | 6904.3443 | 174858.2079 | 59.78 | 787.493
2016-10-24 11:00 | 43810 | 7586.4766 | 183253.5854 | 59.78 | 832.39
2016-10-24 12:00 | 46098 | 8797.8508 | 194474.2554 | 59.78 | 875.862
2016-10-24 13:00 | 48161 | 9000.0483 | 204982.6934 | 59.77 | 963.22
2016-10-24 14:00 | 50032 | 9707.4855 | 214733.0566 | 59.77 | 1000.64
2016-10-24 15:00 | 51369 | 9876.1962 | 221285.993 | 59.77 | 1027.38
2016-10-24 16:00 | 51916 | 9917.5287 | 222301.993 | 59.77 | 1038.32
2016-10-24 17:00 | 51406 | 9652.4378 | 221285.993 | 59.77 | 1028.12
2016-10-24 18:00 | 50914 | 8782.4905 | 222301.993 | 59.77 | 1018.28
2016-10-24 19:00 | 50421 | 8478.4826 | 224166.389 | 59.77 | 1008.42
2016-10-24 20:00 | 49123 | 8127.1254 | 215166.389 | 59.77 | 982.46
2016-10-24 21:00 | 46773 | 8354.3996 | 199080.881 | 59.77 | 935.46
2016-10-24 22:00 | 43591 | 9605.0418 | 170162.935 | 59.78 | 828.229
2016-10-24 23:00 | 39949 | 10292.794 | 144994.3442 | 59.77 | 798.98
2016-10-25 | 34434 | 10006.0757 | 136708.1842 | 59.79 | 619.812
2016-10-25 01:00 | 32988 | 9960.9589 | 138896.7146 | 59.79 | 593.784
2016-10-25 02:00 | 32145 | 10199.8013 | 138305.7066 | 59.79 | 578.61
2016-10-25 03:00 | 31881 | 10473.3707 | 138305.7066 | 59.79 | 573.858
2016-10-25 04:00 | 32381 | 10913.2732 | 138305.7066 | 59.79 | 582.858
2016-10-25 05:00 | 34389 | 10797.5935 | 137442.4066 | 59.79 | 619.002
2016-10-25 06:00 | 38235 | 10739.0904 | 137442.4066 | 59.79 | 688.23
2016-10-25 07:00 | 40096 | 12146.5507 | 137442.4066 | 59.77 | 801.92
2016-10-25 08:00 | 40114 | 13306.8615 | 137442.4066 | 59.79 | 722.052
2016-10-25 09:00 | 41719 | 13595.4058 | 145249.113 | 59.77 | 834.38
2016-10-25 10:00 | 43530 | 13348.1538 | 150269.601 | 59.77 | 870.6
2016-10-25 11:00 | 45560 | 13808.5055 | 162782.231 | 59.77 | 911.2
2016-10-25 12:00 | 47398 | 13970.6419 | 173315.403 | 59.78 | 900.562
2016-10-25 13:00 | 49681 | 13825.6763 | 189693.459 | 59.78 | 943.939
2016-10-25 14:00 | 51267 | 13497.908 | 203108.9838 | 59.77 | 1025.34
2016-10-25 15:00 | 52417 | 13475.9237 | 206462.6942 | 59.77 | 1048.34
2016-10-25 16:00 | 52864 | 13304.9473 | 207420.7042 | 59.77 | 1057.28
2016-10-25 17:00 | 51897 | 13294.0613 | 206404.7042 | 59.77 | 1037.94
2016-10-25 18:00 | 51627 | 13446.8856 | 202252.7942 | 59.77 | 1032.54
2016-10-25 19:00 | 51357 | 14333.0365 | 194852.5442 | 59.78 | 975.783
2016-10-25 20:00 | 50223 | 15034.9821 | 181203.7962 | 59.78 | 954.237
2016-10-25 21:00 | 48191 | 15146.5403 | 168174.8302 | 59.78 | 915.629
2016-10-25 22:00 | 44938 | 14719.0761 | 148792.2782 | 59.77 | 898.76
2016-10-25 23:00 | 41532 | 14677.5649 | 136071.5798 | 59.79 | 747.576
2016-10-26 | 37068 | 13806.4031 | 136071.5798 | 59.79 | 667.224
2016-10-26 01:00 | 35483 | 13297.7375 | 136071.5798 | 59.79 | 638.694
2016-10-26 02:00 | 34440 | 12936.4849 | 136662.5878 | 59.79 | 619.92
2016-10-26 03:00 | 33492 | 12442.2266 | 136662.5878 | 59.79 | 602.856
2016-10-26 04:00 | 33329 | 12026.5993 | 136662.5878 | 59.79 | 599.922
2016-10-26 05:00 | 34806 | 9535.5863 | 137525.8878 | 59.79 | 626.508
2016-10-26 06:00 | 38278 | 7851.3189 | 150158.8758 | 59.77 | 765.56
2016-10-26 07:00 | 39414 | 6100.6867 | 168640.9518 | 59.78 | 748.866
2016-10-26 08:00 | 38940 | 5161.1813 | 171997.3518 | 59.78 | 739.86
2016-10-26 09:00 | 39942 | 5055.9602 | 178867.8625 | 59.78 | 758.898
2016-10-26 10:00 | 41407 | 3224.9849 | 199906.8309 | 59.77 | 828.14
2016-10-26 11:00 | 42843 | 2040.6494 | 216654.7839 | 59.77 | 856.86
2016-10-26 12:00 | 44186 | 2095.1635 | 223771.0999 | 59.77 | 883.72
2016-10-26 13:00 | 45827 | 4537.2469 | 222755.0999 | 59.77 | 916.54
2016-10-26 14:00 | 47061 | 6985.6042 | 221513.3699 | 59.77 | 941.22
2016-10-26 15:00 | 47962 | 7655.6003 | 221513.3699 | 59.77 | 959.24
2016-10-26 16:00 | 48453 | 7738.7762 | 221571.3599 | 59.77 | 969.06
2016-10-26 17:00 | 47634 | 7225.5535 | 221571.3599 | 59.77 | 952.68
2016-10-26 18:00 | 46779 | 6476.7092 | 220797.0299 | 59.77 | 935.58
2016-10-26 19:00 | 45923 | 4353.1429 | 220797.0299 | 59.77 | 918.46
2016-10-26 20:00 | 44564 | 3074.093 | 220797.0299 | 59.77 | 891.28
2016-10-26 21:00 | 42149 | 3477.1634 | 201609.4769 | 59.77 | 842.98
2016-10-26 22:00 | 38936 | 4839.71 | 173977.4385 | 59.78 | 739.784
2016-10-26 23:00 | 35545 | 6788.0159 | 140994.6781 | 59.77 | 710.9
2016-10-27 | 31376 | 8163.9267 | 138744.6781 | 59.79 | 564.768
2016-10-27 01:00 | 30061 | 7814.2384 | 136357.1781 | 59.79 | 541.098
2016-10-27 02:00 | 29301 | 7505.8841 | 136357.1781 | 59.79 | 527.418
2016-10-27 03:00 | 28979 | 6535.6273 | 136357.1781 | 59.79 | 521.622
2016-10-27 04:00 | 29326 | 6335.8969 | 136357.1781 | 59.79 | 527.868
2016-10-27 05:00 | 30979 | 6356.3536 | 136357.1781 | 59.79 | 557.622
2016-10-27 06:00 | 34482 | 4728.3173 | 150095.6325 | 59.77 | 689.64
2016-10-27 07:00 | 36005 | 4243.5892 | 162903.6025 | 59.77 | 720.1
2016-10-27 08:00 | 35786 | 4181.5521 | 162903.6025 | 59.77 | 715.72
2016-10-27 09:00 | 36916 | 4336.4121 | 170757.3129 | 59.78 | 701.404
2016-10-27 10:00 | 38437 | 2663.4556 | 188486.5869 | 59.78 | 730.303
2016-10-27 11:00 | 40082 | 1793.3654 | 205473.7919 | 59.77 | 801.64
2016-10-27 12:00 | 42026 | 1515.2129 | 220049.9924 | 59.77 | 840.52
2016-10-27 13:00 | 43862 | 1798.5116 | 225200.2424 | 59.77 | 877.24
2016-10-27 14:00 | 45471 | 2981.8106 | 228654.2024 | 59.77 | 909.42
2016-10-27 15:00 | 46862 | 4089.1836 | 227350.9592 | 59.78 | 890.378
2016-10-27 16:00 | 47432 | 4458.6619 | 227724.8124 | 59.78 | 901.208
2016-10-27 17:00 | 46736 | 5607.8295 | 218481.2488 | 59.77 | 934.72
2016-10-27 18:00 | 46070 | 5771.5129 | 213561.2908 | 59.77 | 921.4
2016-10-27 19:00 | 45404 | 5516.3424 | 209079.0458 | 59.77 | 908.08
2016-10-27 20:00 | 43987 | 5152.6844 | 202620.1578 | 59.77 | 879.74
2016-10-27 21:00 | 41804 | 6284.943 | 183110.8378 | 59.78 | 794.276
2016-10-27 22:00 | 38243 | 8481.0866 | 148201.923 | 59.77 | 764.86
2016-10-27 23:00 | 34835 | 7461.6827 | 148201.923 | 59.79 | 627.03
2016-10-28 | 34687 | 6032.611 | 148201.923 | 59.77 | 693.74
2016-10-28 01:00 | 33914 | 6321.465 | 144892.113 | 59.77 | 678.28
2016-10-28 02:00 | 32838 | 6587.2379 | 142712.5795 | 59.79 | 591.084
2016-10-28 03:00 | 32031 | 7128.9334 | 142712.5795 | 59.79 | 576.558
2016-10-28 04:00 | 31845 | 8044.128 | 142712.5795 | 59.79 | 573.21
2016-10-28 05:00 | 33252 | 7520.8362 | 145100.0795 | 59.79 | 598.536
2016-10-28 06:00 | 36674 | 7016.0802 | 150688.3095 | 59.77 | 733.48
2016-10-28 07:00 | 37926 | 6632.725 | 159149.7795 | 59.77 | 758.52
2016-10-28 08:00 | 37144 | 6522.3501 | 159149.7795 | 59.77 | 742.88
2016-10-28 09:00 | 37778 | 6478.4046 | 159149.7795 | 59.77 | 755.56
2016-10-28 10:00 | 38713 | 5202.0597 | 172414.3655 | 59.78 | 735.547
2016-10-28 11:00 | 39724 | 5864.0291 | 173430.3655 | 59.78 | 754.756
2016-10-28 12:00 | 40218 | 7128.2911 | 172965.053 | 59.78 | 764.142
2016-10-28 13:00 | 40781 | 8426.5162 | 171463.403 | 59.77 | 815.62
2016-10-28 14:00 | 41205 | 7493.0396 | 183315.7466 | 59.78 | 782.895
2016-10-28 15:00 | 41403 | 6728.0107 | 185634.9898 | 59.78 | 786.657
2016-10-28 16:00 | 41445 | 6026.4003 | 187884.9898 | 59.78 | 787.455
2016-10-28 17:00 | 40694 | 5042.1039 | 187884.9898 | 59.78 | 773.186
2016-10-28 18:00 | 40679 | 4638.0687 | 189128.4613 | 59.78 | 772.901
2016-10-28 19:00 | 40664 | 4698.8552 | 188817.8648 | 59.78 | 772.616
2016-10-28 20:00 | 39944 | 5052.7295 | 183427.5748 | 59.78 | 758.936
2016-10-28 21:00 | 38043 | 5165.0354 | 169296.0888 | 59.78 | 722.817
2016-10-28 22:00 | 35431 | 6663.9033 | 148373.9477 | 59.77 | 708.62
2016-10-28 23:00 | 32537 | 6580.7034 | 148373.9477 | 59.79 | 585.666
2016-10-29 | 32331 | 6653.0928 | 148373.9477 | 59.79 | 581.958
2016-10-29 01:00 | 32131 | 6554.825 | 148373.9477 | 59.79 | 578.358
2016-10-29 02:00 | 31944 | 6242.2541 | 148373.9477 | 59.79 | 574.992
2016-10-29 03:00 | 31784 | 6168.7401 | 148373.9477 | 59.79 | 572.112
2016-10-29 04:00 | 32326 | 6159.9521 | 148373.9477 | 59.79 | 581.868
2016-10-29 05:00 | 34403 | 6270.4532 | 148373.9477 | 59.77 | 688.06
2016-10-29 06:00 | 38780 | 6681.918 | 163322.1711 | 59.77 | 775.6
2016-10-29 07:00 | 40816 | 6659.0648 | 173342.7771 | 59.78 | 775.504
2016-10-29 08:00 | 40241 | 6814.6887 | 173342.7771 | 59.78 | 764.579
2016-10-29 09:00 | 40693 | 5894.1361 | 178829.4471 | 59.78 | 773.167
2016-10-29 10:00 | 41046 | 5125.9731 | 185542.2471 | 59.78 | 779.874
2016-10-29 11:00 | 41228 | 4952.6643 | 191028.9171 | 59.78 | 783.332
2016-10-29 12:00 | 41258 | 5163.4477 | 193152.4371 | 59.78 | 783.902
2016-10-29 13:00 | 41657 | 4512.6867 | 196904.0871 | 59.78 | 791.483
2016-10-29 14:00 | 41871 | 3628.4287 | 200644.8135 | 59.77 | 837.42
2016-10-29 15:00 | 42216 | 3623.4951 | 200644.8135 | 59.77 | 844.32
2016-10-29 16:00 | 42509 | 3663.8258 | 201882.8002 | 59.77 | 850.18
2016-10-29 17:00 | 42089 | 4439.0152 | 198394.8135 | 59.77 | 841.78
2016-10-29 18:00 | 42095 | 4777.4144 | 195121.5385 | 59.78 | 799.805
2016-10-29 19:00 | 42100 | 7577.2937 | 174120.2825 | 59.78 | 799.9
2016-10-29 20:00 | 41276 | 10418.034 | 150138.032 | 59.77 | 825.52
2016-10-29 21:00 | 39915 | 11735.8219 | 135574.4476 | 59.77 | 798.3
2016-10-29 22:00 | 37947 | 11987.1433 | 135574.4476 | 59.79 | 683.046
2016-10-29 23:00 | 35794 | 11957.9027 | 135574.4476 | 59.79 | 644.292
2016-10-30 | 35531 | 11876.4899 | 131745.083 | 59.79 | 639.558
2016-10-30 01:00 | 35508 | 11813.8573 | 131745.083 | 59.79 | 639.144
2016-10-30 02:00 | 34834 | 11346.7077 | 131745.083 | 59.79 | 627.012
2016-10-30 03:00 | 34518 | 11064.4968 | 129841.083 | 59.79 | 621.324
2016-10-30 04:00 | 34639 | 10754.0667 | 133448.403 | 59.79 | 623.502
2016-10-30 05:00 | 35541 | 9850.5773 | 135698.403 | 59.79 | 639.738
2016-10-30 06:00 | 37208 | 9511.3281 | 140832.0994 | 59.77 | 744.16
2016-10-30 07:00 | 39019 | 10016.1301 | 150199.0874 | 59.77 | 780.38
2016-10-30 08:00 | 40689 | 10767.0169 | 158376.1494 | 59.77 | 813.78
2016-10-30 09:00 | 41640 | 9812.533 | 168396.7554 | 59.77 | 832.8
2016-10-30 10:00 | 42274 | 8261.1906 | 185570.6674 | 59.78 | 803.206
2016-10-30 11:00 | 42531 | 5696.1179 | 201156.5728 | 59.78 | 808.089
2016-10-30 12:00 | 42553 | 3848.6152 | 219774.8256 | 59.77 | 851.06
2016-10-30 13:00 | 42662 | 2962.06 | 224257.0706 | 59.77 | 853.24
2016-10-30 14:00 | 43074 | 2328.7036 | 234175.4066 | 59.77 | 861.48
2016-10-30 15:00 | 43823 | 2122.9305 | 237613.967 | 59.77 | 876.46
2016-10-30 16:00 | 44490 | 2208.9817 | 238173.967 | 59.77 | 889.8
2016-10-30 17:00 | 44470 | 2150.4662 | 238629.967 | 59.77 | 889.4
2016-10-30 18:00 | 44946 | 2690.3799 | 238629.967 | 59.77 | 898.92
2016-10-30 19:00 | 45422 | 5096.8017 | 228489.96 | 59.77 | 908.44
2016-10-30 20:00 | 44675 | 8048.7184 | 202669.8294 | 59.78 | 848.825
2016-10-30 21:00 | 43203 | 9202.1259 | 184753.9144 | 59.78 | 820.857
2016-10-30 22:00 | 41178 | 10374.3125 | 161570.9924 | 59.77 | 823.56
2016-10-30 23:00 | 38830 | 11138.2396 | 146321.872 | 59.77 | 776.6
2016-10-31 | 36963 | 11792.5567 | 141233.722 | 59.79 | 665.334
2016-10-31 01:00 | 35519 | 11297.6012 | 138914.4788 | 59.79 | 639.342
2016-10-31 02:00 | 34612 | 11104.3282 | 138914.4788 | 59.79 | 623.016
2016-10-31 03:00 | 34147 | 10859.1114 | 140818.4788 | 59.79 | 614.646
2016-10-31 04:00 | 33986 | 10173.9225 | 140818.4788 | 59.79 | 611.748
2016-10-31 05:00 | 34414 | 9671.5483 | 140818.4788 | 59.79 | 619.452
2016-10-31 06:00 | 35404 | 9497.0477 | 140818.4788 | 59.79 | 637.272
2016-10-31 07:00 | 36584 | 9588.5994 | 140787.3333 | 59.79 | 658.512
2016-10-31 08:00 | 37785 | 9963.5426 | 144881.5413 | 59.77 | 755.7
2016-10-31 09:00 | 39456 | 8541.9148 | 161161.8013 | 59.77 | 789.12
2016-10-31 10:00 | 40948 | 5390.4432 | 187012.5527 | 59.78 | 778.012
2016-10-31 11:00 | 42372 | 3752.7794 | 208647.5711 | 59.77 | 847.44
2016-10-31 12:00 | 43972 | 3024.0063 | 219366.9491 | 59.77 | 879.44
2016-10-31 13:00 | 45679 | 2416.3286 | 234486.9541 | 59.78 | 867.901
2016-10-31 14:00 | 47563 | 2439.2577 | 244730.5629 | 59.78 | 903.697
2016-10-31 15:00 | 49559 | 2714.0246 | 253662.9189 | 59.78 | 941.621
2016-10-31 16:00 | 51022 | 3315.2696 | 254739.9149 | 59.76 | 1071.462
2016-10-31 17:00 | 51006 | 3973.4117 | 254739.9149 | 59.78 | 969.114
2016-10-31 18:00 | 50349 | 4994.5436 | 249202.4515 | 59.78 | 956.631
2016-10-31 19:00 | 49691 | 4401.041 | 245369.7315 | 59.78 | 944.129
2016-10-31 20:00 | 48768 | 4242.8561 | 243190.2235 | 59.78 | 926.592
2016-10-31 21:00 | 48026 | 4126.0036 | 237926.8065 | 59.78 | 912.494
2016-10-31 22:00 | 45734 | 4280.5947 | 222662.7097 | 59.77 | 914.68
2016-10-31 23:00 | 42142 | 4335.4053 | 200635.8157 | 59.77 | 842.84
2016-11-01 | 35153 | 5281.1213 | 155358.2493 | 59.77 | 703.06
2016-11-01 01:00 | 32347 | 7193.4774 | 155358.2493 | 59.79 | 582.246
2016-11-01 02:00 | 31768 | 6217.1978 | 155358.2493 | 59.79 | 571.824
2016-11-01 03:00 | 31578 | 6372.2415 | 155358.2493 | 59.79 | 568.404
2016-11-01 04:00 | 32163 | 6335.6554 | 155358.2493 | 59.79 | 578.934
2016-11-01 05:00 | 34216 | 6770.127 | 155358.2493 | 59.79 | 615.888
2016-11-01 06:00 | 37989 | 5966.9885 | 161284.8125 | 59.77 | 759.78
2016-11-01 07:00 | 40042 | 6208.7633 | 173095.8525 | 59.78 | 760.798
2016-11-01 08:00 | 40111 | 6496.1471 | 173095.8525 | 59.78 | 762.109
2016-11-01 09:00 | 41011 | 5062.6331 | 184554.3525 | 59.78 | 779.209
2016-11-01 10:00 | 42378 | 3970.8152 | 198390.4985 | 59.77 | 847.56
2016-11-01 11:00 | 43737 | 4849.4333 | 201627.1685 | 59.77 | 874.74
2016-11-01 12:00 | 44994 | 5181.6132 | 204983.5685 | 59.77 | 899.88
2016-11-01 13:00 | 46394 | 4590.3738 | 220651.7569 | 59.77 | 927.88
2016-11-01 14:00 | 47435 | 4361.4472 | 222214.1001 | 59.78 | 901.265
2016-11-01 15:00 | 48083 | 5445.6043 | 221667.7569 | 59.78 | 913.577
2016-11-01 16:00 | 48469 | 5887.0028 | 221766.467 | 59.78 | 920.911
2016-11-01 17:00 | 47848 | 7501.0864 | 209193.2569 | 59.77 | 956.96
2016-11-01 18:00 | 47998 | 9732.591 | 198556.3369 | 59.77 | 959.96
2016-11-01 19:00 | 48149 | 9929.7519 | 198268.3369 | 59.77 | 962.98
2016-11-01 20:00 | 46789 | 9511.0241 | 191675.2669 | 59.78 | 888.991
2016-11-01 21:00 | 44557 | 10793.3418 | 165112.2625 | 59.78 | 846.583
2016-11-01 22:00 | 41183 | 10006.7423 | 148022.9845 | 59.77 | 823.66
2016-11-01 23:00 | 37349 | 7970.7292 | 142501.5281 | 59.77 | 746.98
2016-11-02 | 36757 | 7305.8428 | 141205.9301 | 59.77 | 735.14
2016-11-02 01:00 | 34981 | 7973.5946 | 141205.9301 | 59.79 | 629.658
2016-11-02 02:00 | 33946 | 7909.2915 | 141205.9301 | 59.79 | 611.028
2016-11-02 03:00 | 33246 | 8433.3169 | 141205.9301 | 59.79 | 598.428
2016-11-02 04:00 | 33401 | 8950.9789 | 141205.9301 | 59.79 | 601.218
2016-11-02 05:00 | 35066 | 10208.8601 | 141205.9301 | 59.79 | 631.188
2016-11-02 06:00 | 38873 | 10120.5761 | 141205.9301 | 59.77 | 777.46
2016-11-02 07:00 | 41016 | 11172.4642 | 145720.2565 | 59.77 | 820.32
2016-11-02 08:00 | 40526 | 12283.4253 | 145720.2565 | 59.77 | 810.52
2016-11-02 09:00 | 40727 | 11778.8897 | 143238.6565 | 59.77 | 814.54
2016-11-02 10:00 | 41301 | 11834.3016 | 148259.1445 | 59.77 | 826.02
2016-11-02 11:00 | 41662 | 11711.5035 | 148259.1445 | 59.77 | 833.24
2016-11-02 12:00 | 41913 | 12601.221 | 147789.2695 | 59.77 | 838.26
2016-11-02 13:00 | 42294 | 13722.9039 | 147789.2695 | 59.77 | 845.88
2016-11-02 14:00 | 42536 | 14056.3733 | 147789.2695 | 59.77 | 850.72
2016-11-02 15:00 | 42513 | 14591.9649 | 147789.2695 | 59.77 | 850.26
2016-11-02 16:00 | 42617 | 14587.9607 | 145795.7195 | 59.77 | 852.34
2016-11-02 17:00 | 42625 | 14323.7205 | 145795.7195 | 59.77 | 852.5
2016-11-02 18:00 | 43371 | 13432.5026 | 161952.7795 | 59.77 | 867.42
2016-11-02 19:00 | 44118 | 12396.6906 | 162240.7795 | 59.77 | 882.36
2016-11-02 20:00 | 43379 | 10894.6504 | 163256.7795 | 59.77 | 867.58
2016-11-02 21:00 | 41436 | 9508.0809 | 162240.7795 | 59.77 | 828.72
2016-11-02 22:00 | 38436 | 6765.9941 | 162240.7795 | 59.77 | 768.72
2016-11-02 23:00 | 35505 | 6325.6488 | 147408.1151 | 59.77 | 710.1
2016-11-03 | 31630 | 6113.1755 | 148703.7131 | 59.79 | 569.34
2016-11-03 01:00 | 30630 | 4595.4597 | 148703.7131 | 59.79 | 551.34
2016-11-03 02:00 | 30202 | 4715.8742 | 142122.4131 | 59.79 | 543.636
2016-11-03 03:00 | 30052 | 5569.84 | 142122.4131 | 59.79 | 540.936
2016-11-03 04:00 | 30483 | 6104.2942 | 139682.8131 | 59.79 | 548.694
2016-11-03 05:00 | 32538 | 7475.0203 | 139682.8131 | 59.79 | 585.684
2016-11-03 06:00 | 36533 | 8644.4772 | 139091.8051 | 59.77 | 730.66
2016-11-03 07:00 | 38843 | 10609.5219 | 139711.1751 | 59.77 | 776.86
2016-11-03 08:00 | 38592 | 12846.5942 | 139711.1751 | 59.79 | 694.656
2016-11-03 09:00 | 38782 | 12412.4825 | 142192.7751 | 59.79 | 698.076
2016-11-03 10:00 | 38543 | 9435.2883 | 142192.7751 | 59.77 | 770.86
2016-11-03 11:00 | 38401 | 10135.8785 | 137080.3951 | 59.77 | 768.02
2016-11-03 12:00 | 38880 | 11851.9746 | 133203.7701 | 59.79 | 699.84
2016-11-03 13:00 | 39082 | 13857.3799 | 133203.7701 | 59.79 | 703.476
2016-11-03 14:00 | 39002 | 15715.6177 | 133203.7701 | 59.79 | 702.036
2016-11-03 15:00 | 38862 | 15831.1277 | 133203.7701 | 59.79 | 699.516
2016-11-03 16:00 | 38953 | 15645.1015 | 135197.3201 | 59.79 | 701.154
2016-11-03 17:00 | 39158 | 15283.9174 | 135197.3201 | 59.79 | 704.844
2016-11-03 18:00 | 40147 | 14439.866 | 135197.3201 | 59.79 | 722.646
2016-11-03 19:00 | 41137 | 13130.4403 | 135197.3201 | 59.77 | 822.74
2016-11-03 20:00 | 40549 | 10996.1591 | 138870.4866 | 59.77 | 810.98
2016-11-03 21:00 | 38993 | 9855.192 | 137630.3201 | 59.77 | 779.86
2016-11-03 22:00 | 36237 | 9886.3182 | 125288.5701 | 59.79 | 652.266
2016-11-03 23:00 | 33602 | 10277.0105 | 125288.5701 | 59.79 | 604.836
2016-11-04 | 31497 | 10515.519 | 123769.5701 | 59.79 | 566.946
2016-11-04 01:00 | 30509 | 10927.6211 | 120611.1701 | 59.79 | 549.162
2016-11-04 02:00 | 30017 | 10532.582 | 120611.1701 | 59.79 | 540.306
2016-11-04 03:00 | 29982 | 10003.0708 | 120611.1701 | 59.79 | 539.676
2016-11-04 04:00 | 30533 | 9653.3994 | 138898.9601 | 59.79 | 549.594
2016-11-04 05:00 | 32670 | 9425.4681 | 138898.9601 | 59.79 | 588.06
2016-11-04 06:00 | 36722 | 9808.2767 | 139489.9681 | 59.79 | 660.996
2016-11-04 07:00 | 38613 | 9910.414 | 143299.7681 | 59.77 | 772.26
2016-11-04 08:00 | 38027 | 10241.3297 | 143299.7681 | 59.77 | 760.54
2016-11-04 09:00 | 37976 | 9852.8829 | 143299.7681 | 59.77 | 759.52
2016-11-04 10:00 | 38353 | 9503.8261 | 146040.2345 | 59.77 | 767.06
2016-11-04 11:00 | 38434 | 9812.2873 | 144529.9145 | 59.77 | 768.68
2016-11-04 12:00 | 38273 | 9611.0278 | 144529.9145 | 59.77 | 765.46
2016-11-04 13:00 | 38179 | 9420.6653 | 144529.9145 | 59.77 | 763.58
2016-11-04 14:00 | 37899 | 9703.9576 | 144529.9145 | 59.77 | 757.98
2016-11-04 15:00 | 37719 | 9666.8835 | 144529.9145 | 59.77 | 754.38
2016-11-04 16:00 | 37712 | 10038.2593 | 144529.9145 | 59.77 | 754.24
2016-11-04 17:00 | 37420 | 9486.0049 | 144529.9145 | 59.77 | 748.4
2016-11-04 18:00 | 38606 | 7520.0317 | 163610.9625 | 59.77 | 772.12
2016-11-04 19:00 | 39791 | 5600.2204 | 183352.3185 | 59.78 | 756.029
2016-11-04 20:00 | 39609 | 3979.4107 | 184368.3185 | 59.78 | 752.571
2016-11-04 21:00 | 38262 | 4537.2001 | 188502.5685 | 59.78 | 726.978
2016-11-04 22:00 | 36042 | 4553.9664 | 188502.5685 | 59.77 | 720.84
2016-11-04 23:00 | 33578 | 3430.4519 | 188502.5685 | 59.77 | 671.56
2016-11-05 | 34153 | 2269.501 | 188502.5685 | 59.77 | 683.06
2016-11-05 01:00 | 34221 | 1992.2794 | 188502.5685 | 59.77 | 684.42
2016-11-05 02:00 | 33934 | 2161.1362 | 188502.5685 | 59.77 | 678.68
2016-11-05 03:00 | 34048 | 2332.0567 | 188502.5685 | 59.77 | 680.96
2016-11-05 04:00 | 35004 | 2662.1729 | 188502.5685 | 59.77 | 700.08
2016-11-05 05:00 | 37772 | 3222.3788 | 191660.9685 | 59.78 | 717.668
2016-11-05 06:00 | 42640 | 3401.4794 | 210569.6669 | 59.77 | 852.8
2016-11-05 07:00 | 45048 | 3557.0484 | 217289.7101 | 59.77 | 900.96
2016-11-05 08:00 | 44145 | 3918.907 | 211594.3869 | 59.77 | 882.9
2016-11-05 09:00 | 43733 | 3894.4568 | 210578.3869 | 59.77 | 874.66
2016-11-05 10:00 | 43366 | 2704.6052 | 214055.6035 | 59.77 | 867.32
2016-11-05 11:00 | 42848 | 2856.5429 | 209331.6869 | 59.77 | 856.96
2016-11-05 12:00 | 42081 | 3244.2678 | 204831.6869 | 59.77 | 841.62
2016-11-05 13:00 | 41732 | 3777.8047 | 202942.7369 | 59.77 | 834.64
2016-11-05 14:00 | 41372 | 3193.775 | 200692.7369 | 59.77 | 827.44
2016-11-05 15:00 | 41028 | 2882.6632 | 200692.7369 | 59.77 | 820.56
2016-11-05 16:00 | 40806 | 2623.0609 | 200692.7369 | 59.77 | 816.12
2016-11-05 17:00 | 40590 | 2518.2681 | 200692.7369 | 59.77 | 811.8
2016-11-05 18:00 | 41544 | 3149.0294 | 199565.1611 | 59.77 | 830.88
2016-11-05 19:00 | 42498 | 4932.4874 | 193870.8731 | 59.77 | 849.96
2016-11-05 20:00 | 41977 | 6825.5048 | 176067.6927 | 59.78 | 797.563
2016-11-05 21:00 | 41177 | 7697.6298 | 163909.5067 | 59.78 | 782.363
2016-11-05 22:00 | 39778 | 9711.2625 | 142664.8903 | 59.77 | 795.56
2016-11-05 23:00 | 38063 | 10891.3201 | 142664.8903 | 59.79 | 685.134
2016-11-06 | 37859 | 10321.4561 | 140408.2796 | 59.77 | 757.18
2016-11-06 01:00 | 36879 | 10749.2745 | 140408.2796 | 59.79 | 663.822
2016-11-06 02:00 | 36405 | 10440.1504 | 136377.1096 | 59.79 | 655.29
2016-11-06 03:00 | 36405 | 10079.2848 | 136377.1096 | 59.79 | 655.29
2016-11-06 04:00 | 36855 | 10419.513 | 136377.1096 | 59.79 | 663.39
2016-11-06 05:00 | 38063 | 10307.6206 | 141983.5096 | 59.77 | 761.26
2016-11-06 06:00 | 40258 | 9585.7452 | 156957.9356 | 59.77 | 805.16
2016-11-06 07:00 | 42488 | 9775.3734 | 168789.812 | 59.78 | 807.272
2016-11-06 08:00 | 43642 | 10215.0798 | 173902.192 | 59.78 | 829.198
2016-11-06 09:00 | 43799 | 9751.7328 | 178248.692 | 59.78 | 832.181
2016-11-06 10:00 | 43222 | 7835.5759 | 179597.475 | 59.78 | 821.218
2016-11-06 11:00 | 42215 | 7825.5232 | 178248.692 | 59.78 | 802.085
2016-11-06 12:00 | 41173 | 7588.7116 | 178248.692 | 59.78 | 782.287
2016-11-06 13:00 | 40190 | 7602.9921 | 174531.242 | 59.78 | 763.61
2016-11-06 14:00 | 39502 | 7546.0629 | 164623.056 | 59.77 | 790.04
2016-11-06 15:00 | 39274 | 7590.2721 | 164623.056 | 59.77 | 785.48
2016-11-06 16:00 | 39272 | 7204.8663 | 164623.056 | 59.77 | 785.44
2016-11-06 17:00 | 39351 | 7417.3736 | 164623.056 | 59.77 | 787.02
2016-11-06 18:00 | 40737 | 9056.3101 | 163398.4718 | 59.77 | 814.74
2016-11-06 19:00 | 42123 | 11299.5959 | 159051.9718 | 59.77 | 842.46
2016-11-06 20:00 | 41837 | 12434.0174 | 147241.4118 | 59.77 | 836.74
2016-11-06 21:00 | 40942 | 12421.8803 | 143084.2238 | 59.77 | 818.84
2016-11-06 22:00 | 39470 | 12287.9548 | 132884.2874 | 59.79 | 710.46
2016-11-06 23:00 | 37695 | 11791.6555 | 132884.2874 | 59.79 | 678.51
2016-11-07 | 37162 | 11466.0731 | 138228.1874 | 59.79 | 668.916
2016-11-07 01:00 | 35635 | 12046.9241 | 138228.1874 | 59.79 | 641.43
2016-11-07 02:00 | 35550 | 12217.3028 | 139804.9574 | 59.79 | 639.9
2016-11-07 03:00 | 35868 | 11938.8328 | 139804.9574 | 59.79 | 645.624
2016-11-07 04:00 | 36437 | 11623.4194 | 138018.8994 | 59.79 | 655.866
2016-11-07 05:00 | 37571 | 11518.5127 | 138018.8994 | 59.79 | 676.278
2016-11-07 06:00 | 39062 | 10899.8094 | 138018.8994 | 59.77 | 781.24
2016-11-07 07:00 | 40531 | 10974.7985 | 148218.8358 | 59.77 | 810.62
2016-11-07 08:00 | 41742 | 11013.1636 | 153239.3238 | 59.77 | 834.84
2016-11-07 09:00 | 41806 | 11153.81 | 153239.3238 | 59.77 | 836.12
2016-11-07 10:00 | 41249 | 10308.5984 | 152643.3738 | 59.77 | 824.98
2016-11-07 11:00 | 40665 | 9863.7813 | 151135.0238 | 59.77 | 813.3
2016-11-07 12:00 | 40659 | 9384.2629 | 159596.4938 | 59.77 | 813.18
2016-11-07 13:00 | 40570 | 8989.557 | 159596.4938 | 59.77 | 811.4
2016-11-07 14:00 | 40550 | 9895.8602 | 159596.4938 | 59.77 | 811
2016-11-07 15:00 | 40697 | 10239.7398 | 159596.4938 | 59.77 | 813.94
2016-11-07 16:00 | 41071 | 10483.0411 | 159596.4938 | 59.77 | 821.42
2016-11-07 17:00 | 42428 | 10921.5424 | 159596.4938 | 59.77 | 848.56
2016-11-07 18:00 | 43531 | 11538.1402 | 161948.6538 | 59.77 | 870.62
2016-11-07 19:00 | 44633 | 12866.1933 | 160706.9238 | 59.77 | 892.66
2016-11-07 20:00 | 43633 | 13353.1583 | 152245.4538 | 59.77 | 872.66
2016-11-07 21:00 | 41898 | 13508.1692 | 138161.0294 | 59.77 | 837.96
2016-11-07 22:00 | 39387 | 13350.251 | 134351.2294 | 59.79 | 708.966
2016-11-07 23:00 | 36806 | 13031.0991 | 134351.2294 | 59.79 | 662.508
2016-11-08 | 32351 | 12671.7655 | 129403.5494 | 59.79 | 582.318
2016-11-08 01:00 | 31794 | 12247.2935 | 129403.5494 | 59.79 | 572.292
2016-11-08 02:00 | 31720 | 12222.9046 | 129403.5494 | 59.79 | 570.96
2016-11-08 03:00 | 32049 | 11847.2727 | 129403.5494 | 59.79 | 576.882
2016-11-08 04:00 | 33283 | 11701.7011 | 137906.5956 | 59.79 | 599.094
2016-11-08 05:00 | 36253 | 11670.1912 | 142865.2138 | 59.79 | 652.554
2016-11-08 06:00 | 40677 | 11361.9625 | 151622.6938 | 59.77 | 813.54
2016-11-08 07:00 | 41449 | 11735.205 | 151622.6938 | 59.77 | 828.98
2016-11-08 08:00 | 41385 | 12377.0921 | 151622.6938 | 59.77 | 827.7
2016-11-08 09:00 | 41626 | 11924.9418 | 154161.5818 | 59.77 | 832.52
2016-11-08 10:00 | 41934 | 10679.3194 | 163219.0018 | 59.77 | 838.68
2016-11-08 11:00 | 42139 | 9836.3105 | 171275.6678 | 59.77 | 842.78
2016-11-08 12:00 | 42335 | 9203.602 | 171275.6678 | 59.78 | 804.365
2016-11-08 13:00 | 42843 | 8321.2755 | 179094.4578 | 59.78 | 814.017
2016-11-08 14:00 | 42938 | 8191.6062 | 179094.4578 | 59.78 | 815.822
2016-11-08 15:00 | 42986 | 8512.0785 | 179094.4578 | 59.78 | 816.734
2016-11-08 16:00 | 42943 | 8684.5566 | 178231.1578 | 59.78 | 815.917
2016-11-08 17:00 | 43481 | 8967.3863 | 178231.1578 | 59.78 | 826.139
2016-11-08 18:00 | 43883 | 10506.6218 | 169769.6878 | 59.78 | 833.777
2016-11-08 19:00 | 44285 | 12737.6465 | 160971.3718 | 59.77 | 885.7
2016-11-08 20:00 | 43053 | 13601.8594 | 145750.9474 | 59.77 | 861.06
2016-11-08 21:00 | 41057 | 13730.9412 | 136456.7674 | 59.79 | 739.026
2016-11-08 22:00 | 37874 | 13708.6242 | 132646.9674 | 59.79 | 681.732
2016-11-08 23:00 | 35220 | 13512.2982 | 132646.9674 | 59.79 | 633.96
2016-11-09 | 33023 | 13304.7866 | 129174.6774 | 59.79 | 594.414
2016-11-09 01:00 | 32164 | 13121.2235 | 129174.6774 | 59.79 | 578.952
2016-11-09 02:00 | 31628 | 13145.5563 | 129174.6774 | 59.79 | 569.304
2016-11-09 03:00 | 31578 | 12576.8511 | 129248.4965 | 59.79 | 568.404
2016-11-09 04:00 | 32369 | 12317.3399 | 140097.7425 | 59.79 | 582.642
2016-11-09 05:00 | 34780 | 12227.2641 | 140097.7425 | 59.79 | 626.04
2016-11-09 06:00 | 38846 | 11821.6188 | 140036.7465 | 59.79 | 699.228
2016-11-09 07:00 | 39676 | 12034.9108 | 140036.7465 | 59.77 | 793.52
2016-11-09 08:00 | 39953 | 12636.4666 | 140036.7465 | 59.79 | 719.154
2016-11-09 09:00 | 40693 | 12009.143 | 146328.1465 | 59.77 | 813.86
2016-11-09 10:00 | 41675 | 12363.0339 | 151461.8429 | 59.77 | 833.5
2016-11-09 11:00 | 42217 | 12432.5866 | 156408.5118 | 59.77 | 844.34
2016-11-09 12:00 | 42620 | 11878.5101 | 161520.8918 | 59.77 | 852.4
2016-11-09 13:00 | 43143 | 12037.0464 | 161520.8918 | 59.77 | 862.86
2016-11-09 14:00 | 43269 | 12467.9201 | 159201.6486 | 59.77 | 865.38
2016-11-09 15:00 | 43183 | 12315.3388 | 159201.6486 | 59.77 | 863.66
2016-11-09 16:00 | 42940 | 12099.7962 | 162321.5593 | 59.77 | 858.8
2016-11-09 17:00 | 43452 | 11345.7977 | 162614.3313 | 59.77 | 869.04
2016-11-09 18:00 | 44014 | 11718.0892 | 163630.3313 | 59.77 | 880.28
2016-11-09 19:00 | 44577 | 12718.547 | 162614.3313 | 59.77 | 891.54
2016-11-09 20:00 | 43591 | 13109.5909 | 162614.3313 | 59.77 | 871.82
2016-11-09 21:00 | 41439 | 13214.6727 | 152554.2713 | 59.77 | 828.78
2016-11-09 22:00 | 38433 | 12600.3458 | 138590.2869 | 59.79 | 691.794
2016-11-09 23:00 | 35470 | 11464.886 | 138590.2869 | 59.79 | 638.46
2016-11-10 | 31718 | 10342.3314 | 137079.9669 | 59.79 | 570.924
2016-11-10 01:00 | 30707 | 9642.6881 | 137079.9669 | 59.79 | 552.726
2016-11-10 02:00 | 30152 | 8663.1456 | 137079.9669 | 59.79 | 542.736
2016-11-10 03:00 | 30066 | 7108.3359 | 137079.9669 | 59.79 | 541.188
2016-11-10 04:00 | 30609 | 6715.7195 | 139329.9669 | 59.79 | 550.962
2016-11-10 05:00 | 32706 | 6400.158 | 139329.9669 | 59.79 | 588.708
2016-11-10 06:00 | 36537 | 5658.1449 | 158241.6313 | 59.77 | 730.74
2016-11-10 07:00 | 37434 | 5353.4532 | 161590.7213 | 59.77 | 748.68
2016-11-10 08:00 | 37989 | 5361.0917 | 164939.8113 | 59.78 | 721.791
2016-11-10 09:00 | 39050 | 4651.1581 | 177549.9173 | 59.78 | 741.95
2016-11-10 10:00 | 40166 | 3597.4491 | 191075.9485 | 59.78 | 763.154
2016-11-10 11:00 | 41056 | 2533.9327 | 205258.1365 | 59.77 | 821.12
2016-11-10 12:00 | 41521 | 1952.9479 | 213170.4865 | 59.77 | 830.42
2016-11-10 13:00 | 42005 | 1670.339 | 214377.5031 | 59.77 | 840.1
2016-11-10 14:00 | 42257 | 1731.2096 | 216505.7297 | 59.77 | 845.14
2016-11-10 15:00 | 42238 | 1690.0299 | 216505.7297 | 59.77 | 844.76
2016-11-10 16:00 | 42006 | 1883.6155 | 216505.7297 | 59.77 | 840.12
2016-11-10 17:00 | 42349 | 2017.7083 | 216283.4242 | 59.77 | 846.98
2016-11-10 18:00 | 42502 | 2547.7967 | 215267.4242 | 59.77 | 850.04
2016-11-10 19:00 | 42656 | 3416.4739 | 210577.8242 | 59.77 | 853.12
2016-11-10 20:00 | 41552 | 4744.4103 | 192983.2862 | 59.78 | 789.488
2016-11-10 21:00 | 39673 | 4964.8177 | 180304.0073 | 59.78 | 753.787
2016-11-10 22:00 | 37129 | 7042.2147 | 150728.8613 | 59.77 | 742.58
2016-11-10 23:00 | 34398 | 7922.4049 | 136228.1769 | 59.79 | 619.164
2016-11-11 | 32194 | 7842.3999 | 132643.9069 | 59.79 | 579.492
2016-11-11 01:00 | 31166 | 8572.1088 | 132643.9069 | 59.79 | 560.988
2016-11-11 02:00 | 30654 | 8925.7117 | 132643.9069 | 59.79 | 551.772
2016-11-11 03:00 | 30449 | 9036.34 | 132643.9069 | 59.79 | 548.082
2016-11-11 04:00 | 30913 | 9222.1265 | 136754.3833 | 59.79 | 556.434
2016-11-11 05:00 | 32791 | 9052.6237 | 136754.3833 | 59.79 | 590.238
2016-11-11 06:00 | 36530 | 8227.5424 | 141253.3523 | 59.77 | 730.6
2016-11-11 07:00 | 37846 | 8748.4837 | 141253.3523 | 59.77 | 756.92
2016-11-11 08:00 | 38390 | 9510.7702 | 141253.3523 | 59.77 | 767.8
2016-11-11 09:00 | 39399 | 9042.5898 | 151434.2203 | 59.77 | 787.98
2016-11-11 10:00 | 40445 | 10630.3196 | 154566.6192 | 59.77 | 808.9
2016-11-11 11:00 | 41051 | 11424.9213 | 154566.6192 | 59.77 | 821.02
2016-11-11 12:00 | 41596 | 11608.4077 | 154566.6192 | 59.77 | 831.92
2016-11-11 13:00 | 42267 | 10860.2788 | 160646.7992 | 59.77 | 845.34
2016-11-11 14:00 | 42568 | 10879.4433 | 164993.2992 | 59.77 | 851.36
2016-11-11 15:00 | 42524 | 10377.5314 | 164993.2992 | 59.77 | 850.48
2016-11-11 16:00 | 42389 | 9318.703 | 166009.2992 | 59.78 | 805.391
2016-11-11 17:00 | 42772 | 9196.1945 | 167628.8327 | 59.78 | 812.668
2016-11-11 18:00 | 43029 | 8766.3559 | 168771.7758 | 59.78 | 817.551
2016-11-11 19:00 | 43287 | 9972.8952 | 168630.7827 | 59.78 | 822.453
2016-11-11 20:00 | 42299 | 10441.4645 | 160729.8987 | 59.77 | 845.98
2016-11-11 21:00 | 40407 | 10272.6092 | 146690.4511 | 59.77 | 808.14
2016-11-11 22:00 | 37603 | 9905.2434 | 142343.9511 | 59.77 | 752.06
2016-11-11 23:00 | 34845 | 9791.0018 | 140093.9511 | 59.79 | 627.21
2016-11-12 | 33578 | 8501.2696 | 140093.9511 | 59.79 | 604.404
2016-11-12 01:00 | 32481 | 8303.0839 | 140093.9511 | 59.79 | 584.658
2016-11-12 02:00 | 31839 | 7676.0328 | 140093.9511 | 59.79 | 573.102
2016-11-12 03:00 | 31566 | 7707.1212 | 140093.9511 | 59.79 | 568.188
2016-11-12 04:00 | 31998 | 7563.3358 | 140093.9511 | 59.79 | 575.964
2016-11-12 05:00 | 33885 | 7102.3904 | 140093.9511 | 59.79 | 609.93
2016-11-12 06:00 | 37670 | 7191.1743 | 145628.6711 | 59.77 | 753.4
2016-11-12 07:00 | 39010 | 8516.503 | 145628.6711 | 59.77 | 780.2
2016-11-12 08:00 | 39970 | 10019.962 | 145628.6711 | 59.77 | 799.4
2016-11-12 09:00 | 41264 | 10385.5254 | 149212.9411 | 59.77 | 825.28
2016-11-12 10:00 | 42379 | 11528.3421 | 149212.9411 | 59.77 | 847.58
2016-11-12 11:00 | 43165 | 12283.4165 | 148825.1811 | 59.77 | 863.3
2016-11-12 12:00 | 43678 | 13190.5674 | 148825.1811 | 59.77 | 873.56
2016-11-12 13:00 | 44212 | 12746.9736 | 149443.1811 | 59.77 | 884.24
2016-11-12 14:00 | 44541 | 11168.5589 | 160659.1175 | 59.78 | 846.279
2016-11-12 15:00 | 43955 | 10605.3807 | 160379.1175 | 59.78 | 835.145
2016-11-12 16:00 | 42979 | 10724.9043 | 159643.1175 | 59.77 | 859.58
2016-11-12 17:00 | 42918 | 9501.7193 | 164663.6055 | 59.78 | 815.442
2016-11-12 18:00 | 42416 | 9047.5092 | 164663.6055 | 59.78 | 805.904
2016-11-12 19:00 | 41915 | 7902.1115 | 164663.6055 | 59.78 | 796.385
2016-11-12 20:00 | 40667 | 6880.0456 | 167544.0015 | 59.78 | 772.673
2016-11-12 21:00 | 39027 | 4385.4651 | 168560.0015 | 59.78 | 741.513
2016-11-12 22:00 | 36996 | 3307.1435 | 164187.6015 | 59.78 | 702.924
2016-11-12 23:00 | 34754 | 2868.4342 | 164187.6015 | 59.77 | 695.08
2016-11-13 | 34869 | 3172.8373 | 162621.7315 | 59.77 | 697.38
2016-11-13 01:00 | 35442 | 3880.0353 | 160234.2315 | 59.77 | 708.84
2016-11-13 02:00 | 34479 | 3615.0095 | 160234.2315 | 59.77 | 689.58
2016-11-13 03:00 | 34105 | 3051.4714 | 160234.2315 | 59.77 | 682.1
2016-11-13 04:00 | 34289 | 3071.3952 | 160234.2315 | 59.77 | 685.78
2016-11-13 05:00 | 35154 | 3793.4601 | 160234.2315 | 59.77 | 703.08
2016-11-13 06:00 | 36892 | 3643.8144 | 169498.5215 | 59.78 | 700.948
2016-11-13 07:00 | 38497 | 3533.4256 | 180543.2015 | 59.78 | 731.443
2016-11-13 08:00 | 40490 | 3640.6395 | 192701.3875 | 59.78 | 769.31
2016-11-13 09:00 | 41766 | 3573.3235 | 202650.8575 | 59.77 | 835.32
2016-11-13 10:00 | 42425 | 3367.6619 | 210850.5679 | 59.77 | 848.5
2016-11-13 11:00 | 41801 | 2940.174 | 211238.3279 | 59.77 | 836.02
2016-11-13 12:00 | 41188 | 2027.8609 | 211238.3279 | 59.77 | 823.76
2016-11-13 13:00 | 40481 | 1760.1275 | 211238.3279 | 59.77 | 809.62
2016-11-13 14:00 | 40007 | 1539.2939 | 208845.0979 | 59.77 | 800.14
2016-11-13 15:00 | 39769 | 1108.6637 | 216087.5359 | 59.77 | 795.38
2016-11-13 16:00 | 39871 | 1133.2819 | 216087.5359 | 59.77 | 797.42
2016-11-13 17:00 | 41213 | 1066.7127 | 221100.0379 | 59.77 | 824.26
2016-11-13 18:00 | 42016 | 1426.3721 | 225664.5259 | 59.77 | 840.32
2016-11-13 19:00 | 42819 | 1764.8101 | 225664.5259 | 59.77 | 856.38
2016-11-13 20:00 | 42267 | 2859.7749 | 219877.8155 | 59.77 | 845.34
2016-11-13 21:00 | 41295 | 3339.3849 | 209771.4155 | 59.77 | 825.9
2016-11-13 22:00 | 39735 | 4776.487 | 191020.1595 | 59.78 | 754.965
2016-11-13 23:00 | 37964 | 5167.6988 | 170969.7515 | 59.78 | 721.316
2016-11-14 | 36989 | 6267.9982 | 170969.7515 | 59.77 | 739.78
2016-11-14 01:00 | 36099 | 6682.2278 | 167505.1515 | 59.77 | 721.98
2016-11-14 02:00 | 35622 | 6662.2052 | 162484.6635 | 59.77 | 712.44
2016-11-14 03:00 | 35456 | 7341.9331 | 162484.6635 | 59.77 | 709.12
2016-11-14 04:00 | 35737 | 7837.8669 | 162200.2555 | 59.77 | 714.74
2016-11-14 05:00 | 36566 | 8166.7368 | 162200.2555 | 59.77 | 731.32
2016-11-14 06:00 | 37792 | 8304.7781 | 161028.0655 | 59.77 | 755.84
2016-11-14 07:00 | 39002 | 8938.7459 | 161028.0655 | 59.77 | 780.04
2016-11-14 08:00 | 40520 | 9524.1455 | 161028.0655 | 59.77 | 810.4
2016-11-14 09:00 | 41190 | 9587.377 | 162593.9355 | 59.77 | 823.8
2016-11-14 10:00 | 41279 | 7294.3319 | 177305.9055 | 59.78 | 784.301
2016-11-14 11:00 | 41031 | 6215.0506 | 180505.1315 | 59.78 | 779.589
2016-11-14 12:00 | 40895 | 6462.2027 | 180505.1315 | 59.78 | 777.005
2016-11-14 13:00 | 40576 | 5477.7958 | 180505.1315 | 59.78 | 770.944
2016-11-14 14:00 | 40272 | 4714.9159 | 186135.0315 | 59.78 | 765.168
2016-11-14 15:00 | 40218 | 4291.6611 | 194502.9835 | 59.78 | 764.142
2016-11-14 16:00 | 40869 | 4442.1055 | 193639.6835 | 59.78 | 776.511
2016-11-14 17:00 | 43250 | 4579.6114 | 201648.0815 | 59.77 | 865
2016-11-14 18:00 | 44205 | 5005.8479 | 210648.0815 | 59.77 | 884.1
2016-11-14 19:00 | 45159 | 4109.0488 | 211664.0815 | 59.77 | 903.18
2016-11-14 20:00 | 44322 | 4108.8721 | 210648.0815 | 59.77 | 886.44
2016-11-14 21:00 | 42725 | 5163.5641 | 199753.2655 | 59.77 | 854.5
2016-11-14 22:00 | 40192 | 6393.6322 | 172834.7011 | 59.78 | 763.648
2016-11-14 23:00 | 37623 | 6125.2125 | 163875.7411 | 59.77 | 752.46
2016-11-15 | 33264 | 6871.3786 | 158334.2431 | 59.79 | 598.752
2016-11-15 01:00 | 32471 | 7685.9896 | 151621.4431 | 59.79 | 584.478
2016-11-15 02:00 | 32201 | 7773.5589 | 151621.4431 | 59.79 | 579.618
2016-11-15 03:00 | 32445 | 7862.1995 | 151621.4431 | 59.79 | 584.01
2016-11-15 04:00 | 33419 | 8048.0459 | 151905.8511 | 59.79 | 601.542
2016-11-15 05:00 | 36102 | 8449.2869 | 151905.8511 | 59.77 | 722.04
2016-11-15 06:00 | 40676 | 8421.2524 | 169295.2475 | 59.77 | 813.52
2016-11-15 07:00 | 41832 | 7913.5831 | 172156.3355 | 59.78 | 794.808
2016-11-15 08:00 | 41553 | 7497.4256 | 175505.4255 | 59.78 | 789.507
2016-11-15 09:00 | 41627 | 8078.9491 | 173616.4755 | 59.78 | 790.913
2016-11-15 10:00 | 41748 | 6967.1884 | 184398.8715 | 59.78 | 793.212
2016-11-15 11:00 | 41640 | 6714.8259 | 184398.8715 | 59.78 | 791.16
2016-11-15 12:00 | 41351 | 7904.9006 | 184398.8715 | 59.78 | 785.669
2016-11-15 13:00 | 41442 | 9634.2676 | 182486.4715 | 59.77 | 828.84
2016-11-15 14:00 | 41282 | 9923.2337 | 182486.4715 | 59.77 | 825.64
2016-11-15 15:00 | 41337 | 9737.4478 | 183077.4795 | 59.77 | 826.74
2016-11-15 16:00 | 41962 | 10254.0024 | 181553.2795 | 59.77 | 839.24
2016-11-15 17:00 | 43433 | 9629.6386 | 186665.6595 | 59.78 | 825.227
2016-11-15 18:00 | 43694 | 9114.4888 | 195624.6195 | 59.78 | 830.186
2016-11-15 19:00 | 43956 | 7458.0744 | 198856.8295 | 59.78 | 835.164
2016-11-15 20:00 | 43030 | 5557.7401 | 199312.8295 | 59.78 | 817.57
2016-11-15 21:00 | 41248 | 5568.853 | 192106.8295 | 59.78 | 783.712
2016-11-15 22:00 | 38192 | 4885.1996 | 176181.3435 | 59.78 | 725.648
2016-11-15 23:00 | 35571 | 4253.8724 | 165571.1591 | 59.77 | 711.42
2016-11-16 | 33110 | 4563.5159 | 165571.1591 | 59.77 | 662.2
2016-11-16 01:00 | 32202 | 5484.4009 | 163218.9991 | 59.79 | 579.636
2016-11-16 02:00 | 31917 | 6502.9039 | 163218.9991 | 59.79 | 574.506
2016-11-16 03:00 | 32048 | 7253.8062 | 163218.9991 | 59.79 | 576.864
2016-11-16 04:00 | 32959 | 7898.173 | 163218.9991 | 59.79 | 593.262
2016-11-16 05:00 | 35681 | 8760.9387 | 165176.2271 | 59.79 | 642.258
2016-11-16 06:00 | 40100 | 8212.054 | 171458.8155 | 59.77 | 802
2016-11-16 07:00 | 41014 | 8461.8591 | 173618.2155 | 59.78 | 779.266
2016-11-16 08:00 | 40527 | 8838.0176 | 173618.2155 | 59.77 | 810.54
2016-11-16 09:00 | 40493 | 7581.3014 | 175507.1655 | 59.78 | 769.367
2016-11-16 10:00 | 40448 | 5072.3797 | 183876.7435 | 59.78 | 768.512
2016-11-16 11:00 | 40203 | 4762.5767 | 183876.7435 | 59.78 | 763.857
2016-11-16 12:00 | 39921 | 4946.5617 | 183876.7435 | 59.78 | 758.499
2016-11-16 13:00 | 39888 | 5081.8255 | 180640.0735 | 59.78 | 757.872
2016-11-16 14:00 | 39837 | 6370.101 | 174917.7835 | 59.78 | 756.903
2016-11-16 15:00 | 39826 | 7533.2257 | 166456.3135 | 59.77 | 796.52
2016-11-16 16:00 | 40000 | 8322.9767 | 168843.8135 | 59.77 | 800
2016-11-16 17:00 | 41103 | 8285.8658 | 168843.8135 | 59.78 | 780.957
2016-11-16 18:00 | 41860 | 9013.0641 | 168843.8135 | 59.78 | 795.34
2016-11-16 19:00 | 42617 | 11264.1095 | 155457.4191 | 59.77 | 852.34
2016-11-16 20:00 | 41883 | 12913.8414 | 148134.5684 | 59.77 | 837.66
2016-11-16 21:00 | 40359 | 13293.3131 | 136747.0484 | 59.79 | 726.462
2016-11-16 22:00 | 37973 | 13559.1852 | 132937.2484 | 59.79 | 683.514
2016-11-16 23:00 | 35370 | 13720.2657 | 133011.0675 | 59.79 | 636.66
2016-11-17 | 31790 | 13215.8446 | 131502.7175 | 59.79 | 572.22
2016-11-17 01:00 | 31100 | 12598.6444 | 131502.7175 | 59.79 | 559.8
2016-11-17 02:00 | 30884 | 12693.4051 | 131502.7175 | 59.79 | 555.912
2016-11-17 03:00 | 30973 | 12408.5074 | 130911.7095 | 59.79 | 557.514
2016-11-17 04:00 | 31797 | 12151.9521 | 133816.5025 | 59.79 | 572.346
2016-11-17 05:00 | 34150 | 11996.9468 | 133816.5025 | 59.79 | 614.7
2016-11-17 06:00 | 38279 | 11446.0431 | 133263.8695 | 59.79 | 689.022
2016-11-17 07:00 | 38765 | 11594.4964 | 133263.8695 | 59.79 | 697.77
2016-11-17 08:00 | 38137 | 11931.1293 | 133190.0504 | 59.79 | 686.466
2016-11-17 09:00 | 37986 | 11754.7962 | 133190.0504 | 59.79 | 683.748
2016-11-17 10:00 | 38015 | 12594.0114 | 133190.0504 | 59.79 | 684.27
2016-11-17 11:00 | 38141 | 13051.3902 | 133190.0504 | 59.79 | 686.538
2016-11-17 12:00 | 38167 | 12693.3967 | 133190.0504 | 59.79 | 687.006
2016-11-17 13:00 | 38773 | 13231.7279 | 133190.0504 | 59.79 | 697.914
2016-11-17 14:00 | 38873 | 13085.6303 | 133190.0504 | 59.79 | 699.714
2016-11-17 15:00 | 38947 | 12990.4286 | 133190.0504 | 59.79 | 701.046
2016-11-17 16:00 | 38953 | 12608.3126 | 136409.9704 | 59.79 | 701.154
2016-11-17 17:00 | 39780 | 11408.1839 | 142132.1704 | 59.77 | 795.6
2016-11-17 18:00 | 40108 | 10618.2459 | 142132.1704 | 59.77 | 802.16
2016-11-17 19:00 | 40436 | 11171.2479 | 142132.1704 | 59.77 | 808.72
2016-11-17 20:00 | 39704 | 11154.5795 | 142132.1704 | 59.77 | 794.08
2016-11-17 21:00 | 38294 | 9020.0283 | 142132.1704 | 59.77 | 765.88
2016-11-17 22:00 | 35763 | 7968.3075 | 142132.1704 | 59.77 | 715.26
2016-11-17 23:00 | 33150 | 5493.169 | 142132.1704 | 59.77 | 663
2016-11-18 | 32202 | 5932.4241 | 142132.1704 | 59.79 | 579.636
2016-11-18 01:00 | 31426 | 6783.3086 | 142132.1704 | 59.79 | 565.668
2016-11-18 02:00 | 31177 | 6737.3907 | 142132.1704 | 59.79 | 561.186
2016-11-18 03:00 | 31368 | 6698.1461 | 140787.5647 | 59.79 | 564.624
2016-11-18 04:00 | 32408 | 6524.5727 | 142295.9147 | 59.79 | 583.344
2016-11-18 05:00 | 35291 | 5628.2627 | 145515.8347 | 59.77 | 705.82
2016-11-18 06:00 | 39764 | 4733.3685 | 174145.4091 | 59.78 | 755.516
2016-11-18 07:00 | 40716 | 4527.7591 | 181840.9991 | 59.78 | 773.604
2016-11-18 08:00 | 40237 | 4502.7786 | 180704.9991 | 59.78 | 764.503
2016-11-18 09:00 | 40173 | 4695.8352 | 180704.9991 | 59.78 | 763.287
2016-11-18 10:00 | 39813 | 4202.7888 | 180704.9991 | 59.78 | 756.447
2016-11-18 11:00 | 39147 | 3572.4634 | 180704.9991 | 59.78 | 743.793
2016-11-18 12:00 | 38930 | 3502.482 | 180704.9991 | 59.78 | 739.67
2016-11-18 13:00 | 38739 | 2959.2808 | 183672.6251 | 59.78 | 736.041
2016-11-18 14:00 | 38398 | 2772.2787 | 183672.6251 | 59.78 | 729.562
2016-11-18 15:00 | 38234 | 2624.6886 | 182165.4646 | 59.78 | 726.446
2016-11-18 16:00 | 38387 | 2803.1244 | 181569.5146 | 59.78 | 729.353
2016-11-18 17:00 | 39754 | 3204.3551 | 182895.4944 | 59.78 | 755.326
2016-11-18 18:00 | 40695 | 4474.2319 | 182585.5146 | 59.78 | 773.205
2016-11-18 19:00 | 41636 | 7052.614 | 171540.8346 | 59.78 | 791.084
2016-11-18 20:00 | 41301 | 10521.7714 | 147759.0302 | 59.77 | 826.02
2016-11-18 21:00 | 40137 | 11546.0226 | 133537.3442 | 59.77 | 802.74
2016-11-18 22:00 | 37743 | 12109.8132 | 133537.3442 | 59.79 | 679.374
2016-11-18 23:00 | 35542 | 12212.9632 | 133537.3442 | 59.79 | 639.756
2016-11-19 | 35331 | 12272.828 | 133537.3442 | 59.79 | 635.958
2016-11-19 01:00 | 35135 | 12412.307 | 131055.7442 | 59.79 | 632.43
2016-11-19 02:00 | 35081 | 11921.3651 | 131055.7442 | 59.79 | 631.458
2016-11-19 03:00 | 35379 | 12095.5874 | 132991.3578 | 59.79 | 636.822
2016-11-19 04:00 | 36470 | 12148.5676 | 135424.3578 | 59.79 | 656.46
2016-11-19 05:00 | 39471 | 12403.3431 | 136990.2278 | 59.79 | 710.478
2016-11-19 06:00 | 44143 | 12206.0554 | 159182.0622 | 59.77 | 882.86
2016-11-19 07:00 | 44907 | 12057.639 | 165310.4422 | 59.78 | 853.233
2016-11-19 08:00 | 43621 | 12121.8901 | 165430.4422 | 59.77 | 872.42
2016-11-19 09:00 | 42759 | 11690.1933 | 165430.4422 | 59.77 | 855.18
2016-11-19 10:00 | 42316 | 11000.0655 | 165430.4422 | 59.77 | 846.32
2016-11-19 11:00 | 41442 | 10150.5926 | 165430.4422 | 59.77 | 828.84
2016-11-19 12:00 | 40706 | 8473.8233 | 165430.4422 | 59.77 | 814.12
2016-11-19 13:00 | 40488 | 6886.3842 | 170030.7122 | 59.78 | 769.272
2016-11-19 14:00 | 40162 | 6715.7673 | 170030.7122 | 59.78 | 763.078
2016-11-19 15:00 | 39976 | 7302.9753 | 167172.7828 | 59.78 | 759.544
2016-11-19 16:00 | 39832 | 8129.6385 | 162656.3528 | 59.77 | 796.64
2016-11-19 17:00 | 40793 | 9009.6137 | 161154.7028 | 59.77 | 815.86
2016-11-19 18:00 | 40995 | 10214.616 | 161154.7028 | 59.77 | 819.9
2016-11-19 19:00 | 41197 | 11787.9941 | 145934.2784 | 59.77 | 823.94
2016-11-19 20:00 | 40549 | 12737.3217 | 144368.4084 | 59.77 | 810.98
2016-11-19 21:00 | 39489 | 13357.7602 | 140496.1384 | 59.79 | 710.802
2016-11-19 22:00 | 37838 | 13601.1019 | 138175.1238 | 59.79 | 681.084
2016-11-19 23:00 | 35877 | 13788.8817 | 135016.7238 | 59.79 | 645.786
2016-11-20 | 35731 | 13535.5377 | 135016.7238 | 59.79 | 643.158
2016-11-20 01:00 | 35642 | 13150.0118 | 137498.3238 | 59.79 | 641.556
2016-11-20 02:00 | 35104 | 12874.0526 | 137498.3238 | 59.79 | 631.872
2016-11-20 03:00 | 34964 | 12309.3362 | 137213.9158 | 59.79 | 629.352
2016-11-20 04:00 | 35289 | 11559.6027 | 137213.9158 | 59.79 | 635.202
2016-11-20 05:00 | 36373 | 11072.14 | 137213.9158 | 59.79 | 654.714
2016-11-20 06:00 | 38080 | 10746.0532 | 137213.9158 | 59.79 | 685.44
2016-11-20 07:00 | 39206 | 11153.0178 | 142364.0558 | 59.77 | 784.12
2016-11-20 08:00 | 40742 | 11719.1718 | 151776.7958 | 59.77 | 814.84
2016-11-20 09:00 | 41663 | 11493.5363 | 156910.4922 | 59.77 | 833.26
2016-11-20 10:00 | 41937 | 9549.6706 | 166845.3422 | 59.77 | 838.74
2016-11-20 11:00 | 41904 | 8449.2325 | 180177.4362 | 59.78 | 796.176
2016-11-20 12:00 | 41485 | 7540.6704 | 178800.2062 | 59.78 | 788.215
2016-11-20 13:00 | 41117 | 7224.5621 | 178472.2062 | 59.78 | 781.223
2016-11-20 14:00 | 40747 | 7208.8364 | 177736.2062 | 59.78 | 774.193
2016-11-20 15:00 | 40638 | 7739.5396 | 177736.2062 | 59.78 | 772.122
2016-11-20 16:00 | 40580 | 8366.1587 | 173389.7062 | 59.77 | 811.6
2016-11-20 17:00 | 42108 | 9515.1708 | 174891.3562 | 59.78 | 800.052
2016-11-20 18:00 | 42570 | 11731.7442 | 164956.5062 | 59.77 | 851.4
2016-11-20 19:00 | 43033 | 13900.3105 | 151624.4122 | 59.77 | 860.66
2016-11-20 20:00 | 42198 | 14659.1471 | 138991.4758 | 59.77 | 843.96
2016-11-20 21:00 | 41126 | 14612.2222 | 134129.3358 | 59.79 | 740.268
2016-11-20 22:00 | 39262 | 14047.037 | 129181.6558 | 59.79 | 706.716
2016-11-20 23:00 | 37170 | 13275.6648 | 129181.6558 | 59.79 | 669.06
2016-11-21 | 36365 | 12572.7834 | 129181.6558 | 59.79 | 654.57
2016-11-21 01:00 | 35275 | 12474.0972 | 129181.6558 | 59.79 | 634.95
2016-11-21 02:00 | 34525 | 12723.8924 | 129181.6558 | 59.79 | 621.45
2016-11-21 03:00 | 34101 | 11942.6789 | 129466.0638 | 59.79 | 613.818
2016-11-21 04:00 | 34024 | 11403.6074 | 135128.4664 | 59.79 | 612.432
2016-11-21 05:00 | 34497 | 11275.1602 | 135128.4664 | 59.79 | 620.946
2016-11-21 06:00 | 35293 | 10685.6346 | 132626.2352 | 59.79 | 635.274
2016-11-21 07:00 | 36050 | 11944.0784 | 132626.2352 | 59.79 | 648.9
2016-11-21 08:00 | 38456 | 13068.2797 | 132626.2352 | 59.79 | 692.208
2016-11-21 09:00 | 40314 | 13527.037 | 137573.9152 | 59.79 | 725.652
2016-11-21 10:00 | 41682 | 13369.6493 | 142640.1552 | 59.77 | 833.64
2016-11-21 11:00 | 42803 | 13645.6503 | 147773.8516 | 59.77 | 856.06
2016-11-21 12:00 | 43534 | 12403.9252 | 160299.9496 | 59.77 | 870.68
2016-11-21 13:00 | 44009 | 12315.1647 | 160347.9496 | 59.77 | 880.18
2016-11-21 14:00 | 44380 | 12334.4842 | 167046.1296 | 59.77 | 887.6
2016-11-21 15:00 | 44521 | 12297.9145 | 171392.6296 | 59.77 | 890.42
2016-11-21 16:00 | 44360 | 12217.3216 | 168747.8496 | 59.77 | 887.2
2016-11-21 17:00 | 45751 | 11613.0007 | 176330.9896 | 59.78 | 869.269
2016-11-21 18:00 | 46446 | 11379.5569 | 179596.9896 | 59.78 | 882.474
2016-11-21 19:00 | 47141 | 11551.0739 | 179911.6993 | 59.78 | 895.679
2016-11-21 20:00 | 46111 | 11003.063 | 179140.9896 | 59.78 | 876.109
2016-11-21 21:00 | 44524 | 13269.6389 | 164629.9372 | 59.77 | 890.48
2016-11-21 22:00 | 41993 | 13245.7376 | 152984.0772 | 59.77 | 839.86
2016-11-21 23:00 | 39192 | 13852.2698 | 144153.7892 | 59.79 | 705.456
2016-11-22 | 31947 | 13991.453 | 127808.9192 | 59.79 | 575.046
2016-11-22 01:00 | 30852 | 12483.4965 | 127808.9192 | 59.79 | 555.336
2016-11-22 02:00 | 30173 | 11515.9345 | 127808.9192 | 59.79 | 543.114
2016-11-22 03:00 | 30045 | 10287.0014 | 127808.9192 | 59.79 | 540.81
2016-11-22 04:00 | 30515 | 9356.4148 | 139735.3192 | 59.79 | 549.27
2016-11-22 05:00 | 32361 | 8517.8669 | 139735.3192 | 59.79 | 582.498
2016-11-22 06:00 | 35568 | 8235.584 | 139735.3192 | 59.79 | 640.224
2016-11-22 07:00 | 37141 | 9050.0476 | 138226.9692 | 59.77 | 742.82
2016-11-22 08:00 | 38206 | 10008.7039 | 142036.7692 | 59.77 | 764.12
2016-11-22 09:00 | 39678 | 10116.2569 | 147103.0092 | 59.77 | 793.56
2016-11-22 10:00 | 40950 | 8503.4786 | 163385.0795 | 59.77 | 819
2016-11-22 11:00 | 41996 | 8276.3441 | 166975.8395 | 59.78 | 797.924
2016-11-22 12:00 | 42548 | 9861.4583 | 165959.8395 | 59.78 | 808.412
2016-11-22 13:00 | 43410 | 10563.1151 | 165959.8395 | 59.78 | 824.79
2016-11-22 14:00 | 43972 | 10296.7459 | 172395.7355 | 59.78 | 835.468
2016-11-22 15:00 | 43985 | 9844.4223 | 176742.2355 | 59.78 | 835.715
2016-11-22 16:00 | 43683 | 9587.88 | 179387.0155 | 59.78 | 829.977
2016-11-22 17:00 | 43905 | 8959.9928 | 179387.0155 | 59.78 | 834.195
2016-11-22 18:00 | 44031 | 9135.4841 | 182859.3055 | 59.78 | 836.589
2016-11-22 19:00 | 44157 | 7919.9495 | 183875.3055 | 59.78 | 838.983
2016-11-22 20:00 | 43178 | 6714.6789 | 184199.662 | 59.78 | 820.382
2016-11-22 21:00 | 41469 | 8170.5245 | 170554.7255 | 59.78 | 787.911
2016-11-22 22:00 | 38938 | 9014.8725 | 145222.2431 | 59.77 | 778.76
2016-11-22 23:00 | 35926 | 9049.6317 | 140487.9831 | 59.79 | 646.668
2016-11-23 | 32126 | 8394.9299 | 137056.5831 | 59.79 | 578.268
2016-11-23 01:00 | 30809 | 7486.888 | 137056.5831 | 59.79 | 554.562
2016-11-23 02:00 | 30071 | 7054.7139 | 137056.5831 | 59.79 | 541.278
2016-11-23 03:00 | 29803 | 5676.4098 | 137056.5831 | 59.79 | 536.454
2016-11-23 04:00 | 30156 | 5947.0087 | 137056.5831 | 59.79 | 542.808
2016-11-23 05:00 | 31736 | 5757.707 | 137056.5831 | 59.79 | 571.248
2016-11-23 06:00 | 34726 | 4238.4588 | 159658.1455 | 59.77 | 694.52
2016-11-23 07:00 | 35905 | 3669.6846 | 167864.6755 | 59.77 | 718.1
2016-11-23 08:00 | 36701 | 3686.5243 | 174528.1959 | 59.78 | 697.319
2016-11-23 09:00 | 37874 | 1944.2271 | 192060.5919 | 59.78 | 719.606
2016-11-23 10:00 | 39192 | 1085.1309 | 204906.6119 | 59.77 | 783.84
2016-11-23 11:00 | 40102 | 853.3526 | 211287.3419 | 59.77 | 802.04
2016-11-23 12:00 | 40803 | 1353.2007 | 210424.0419 | 59.77 | 816.06
2016-11-23 13:00 | 41616 | 1766.9887 | 211440.0419 | 59.77 | 832.32
2016-11-23 14:00 | 42067 | 2229.8438 | 210424.0419 | 59.77 | 841.34
2016-11-23 15:00 | 41963 | 3028.9517 | 206951.7519 | 59.77 | 839.26
2016-11-23 16:00 | 41311 | 3814.8608 | 203598.0415 | 59.78 | 784.909
2016-11-23 17:00 | 41467 | 4346.205 | 197587.7215 | 59.78 | 787.873
2016-11-23 18:00 | 41488 | 5500.6609 | 192097.9415 | 59.78 | 788.272
2016-11-23 19:00 | 41508 | 6142.0783 | 186491.5415 | 59.78 | 788.652
2016-11-23 20:00 | 40492 | 6902.3205 | 175166.8715 | 59.78 | 769.348
2016-11-23 21:00 | 39082 | 7914.5358 | 161035.3855 | 59.77 | 781.64
2016-11-23 22:00 | 37228 | 9612.9692 | 136835.2911 | 59.77 | 744.56
2016-11-23 23:00 | 34712 | 10517.5901 | 133413.2511 | 59.79 | 624.816
2016-11-24 | 33703 | 11318.5655 | 133413.2511 | 59.79 | 606.654
2016-11-24 01:00 | 32508 | 11418.3749 | 133413.2511 | 59.79 | 585.144
2016-11-24 02:00 | 31885 | 11018.8104 | 133413.2511 | 59.79 | 573.93
2016-11-24 03:00 | 31545 | 11632.7811 | 133413.2511 | 59.79 | 567.81
2016-11-24 04:00 | 31820 | 11858.1029 | 133596.2391 | 59.79 | 572.76
2016-11-24 05:00 | 33272 | 11810.144 | 133596.2391 | 59.79 | 598.896
2016-11-24 06:00 | 35585 | 11534.0416 | 133296.3711 | 59.79 | 640.53
2016-11-24 07:00 | 36989 | 11840.6556 | 133296.3711 | 59.79 | 665.802
2016-11-24 08:00 | 38529 | 12153.0822 | 134815.3711 | 59.79 | 693.522
2016-11-24 09:00 | 40505 | 12274.6178 | 140537.5711 | 59.77 | 810.1
2016-11-24 10:00 | 42255 | 12706.3038 | 145621.2511 | 59.77 | 845.1
2016-11-24 11:00 | 43319 | 12077.522 | 154626.5435 | 59.77 | 866.38
2016-11-24 12:00 | 43854 | 11901.2737 | 158838.9335 | 59.77 | 877.08
2016-11-24 13:00 | 44494 | 12300.7754 | 162188.0235 | 59.77 | 889.88
2016-11-24 14:00 | 44620 | 11724.8784 | 167254.2635 | 59.78 | 847.78
2016-11-24 15:00 | 44479 | 11222.4577 | 168094.2635 | 59.78 | 845.101
2016-11-24 16:00 | 43669 | 11082.4142 | 167254.2635 | 59.78 | 829.711
2016-11-24 17:00 | 43933 | 11106.2156 | 168764.5835 | 59.78 | 834.727
2016-11-24 18:00 | 43811 | 11120.3673 | 167321.3635 | 59.78 | 832.409
2016-11-24 19:00 | 43689 | 11255.7061 | 167321.3635 | 59.77 | 873.78
2016-11-24 20:00 | 42586 | 10726.5248 | 161433.3855 | 59.77 | 851.72
2016-11-24 21:00 | 41129 | 10749.9914 | 152950.5991 | 59.77 | 822.58
2016-11-24 22:00 | 39084 | 10649.2284 | 139011.3071 | 59.77 | 781.68
2016-11-24 23:00 | 36552 | 10841.6638 | 139011.3071 | 59.79 | 657.936
2016-11-25 | 36531 | 9900.4646 | 139011.3071 | 59.79 | 657.558
2016-11-25 01:00 | 36512 | 9956.8845 | 136851.9071 | 59.79 | 657.216
2016-11-25 02:00 | 35331 | 9230.0402 | 136851.9071 | 59.79 | 635.958
2016-11-25 03:00 | 34677 | 8687.0825 | 136851.9071 | 59.79 | 624.186
2016-11-25 04:00 | 34541 | 8465.1157 | 138417.7771 | 59.79 | 621.738
2016-11-25 05:00 | 35116 | 8630.9758 | 138417.7771 | 59.79 | 632.088
2016-11-25 06:00 | 35999 | 10896.601 | 139107.1571 | 59.79 | 647.982
2016-11-25 07:00 | 36869 | 12081.9041 | 139107.1571 | 59.79 | 663.642
2016-11-25 08:00 | 39504 | 12882.6123 | 139107.1571 | 59.79 | 711.072
2016-11-25 09:00 | 42648 | 13521.5932 | 148746.7471 | 59.77 | 852.96
2016-11-25 10:00 | 45026 | 12268.4595 | 165531.6551 | 59.78 | 855.494
2016-11-25 11:00 | 46154 | 11756.3168 | 171361.9329 | 59.78 | 876.926
2016-11-25 12:00 | 45598 | 12828.3008 | 169879.7731 | 59.78 | 866.362
2016-11-25 13:00 | 44289 | 12876.6357 | 169879.7731 | 59.77 | 885.78
2016-11-25 14:00 | 43000 | 12294.5963 | 169879.7731 | 59.77 | 860
2016-11-25 15:00 | 41926 | 10848.2738 | 169879.7731 | 59.77 | 838.52
2016-11-25 16:00 | 40974 | 9776.5691 | 169879.7731 | 59.77 | 819.48
2016-11-25 17:00 | 41354 | 8399.9838 | 169879.7731 | 59.78 | 785.726
2016-11-25 18:00 | 41393 | 7475.9105 | 172232.7231 | 59.78 | 786.467
2016-11-25 19:00 | 41431 | 8030.8113 | 172232.7231 | 59.78 | 787.189
2016-11-25 20:00 | 41086 | 8189.5567 | 172232.7231 | 59.78 | 780.634
2016-11-25 21:00 | 40568 | 5174.5049 | 183004.7531 | 59.78 | 770.792
2016-11-25 22:00 | 39745 | 5870.8513 | 182680.3531 | 59.78 | 755.155
2016-11-25 23:00 | 38633 | 5449.9751 | 182680.3531 | 59.78 | 734.027
2016-11-26 | 38931 | 4350.543 | 182867.5531 | 59.78 | 739.689
2016-11-26 01:00 | 39523 | 4133.7731 | 185026.9531 | 59.78 | 750.937
2016-11-26 02:00 | 39288 | 5287.8228 | 181827.7271 | 59.78 | 746.472
2016-11-26 03:00 | 39487 | 5044.8817 | 181613.8383 | 59.78 | 750.253
2016-11-26 04:00 | 40273 | 5109.1836 | 184970.2383 | 59.78 | 765.187
2016-11-26 05:00 | 41812 | 4915.633 | 197326.6383 | 59.78 | 794.428
2016-11-26 06:00 | 43886 | 4915.9514 | 208541.5117 | 59.77 | 877.72
2016-11-26 07:00 | 45249 | 5077.0555 | 217394.7197 | 59.77 | 904.98
2016-11-26 08:00 | 46174 | 5442.754 | 218410.7197 | 59.77 | 923.48
2016-11-26 09:00 | 46603 | 6161.749 | 217394.7197 | 59.77 | 932.06
2016-11-26 10:00 | 46313 | 6419.5084 | 218169.0497 | 59.77 | 926.26
2016-11-26 11:00 | 45334 | 4897.7416 | 216867.5197 | 59.77 | 906.68
2016-11-26 12:00 | 43966 | 5140.4973 | 216867.5197 | 59.77 | 879.32
2016-11-26 13:00 | 42649 | 4127.3976 | 216867.5197 | 59.77 | 852.98
2016-11-26 14:00 | 41589 | 3033.1436 | 216867.5197 | 59.77 | 831.78
2016-11-26 15:00 | 41113 | 2299.3218 | 216867.5197 | 59.77 | 822.26
2016-11-26 16:00 | 41426 | 2131.6975 | 216867.5197 | 59.77 | 828.52
2016-11-26 17:00 | 44133 | 2118.751 | 230090.7811 | 59.77 | 882.66
2016-11-26 18:00 | 45812 | 1771.5027 | 249156.7983 | 59.78 | 870.428
2016-11-26 19:00 | 47491 | 1438.5413 | 249156.7983 | 59.78 | 902.329
2016-11-26 20:00 | 47661 | 1442.6367 | 250172.7983 | 59.78 | 905.559
2016-11-26 21:00 | 47318 | 1725.712 | 251161.5183 | 59.78 | 899.042
2016-11-26 22:00 | 46291 | 2558.4916 | 237878.7768 | 59.78 | 879.529
2016-11-26 23:00 | 44815 | 4106.6675 | 219830.7784 | 59.77 | 896.3
2016-11-27 | 41954 | 4819.5077 | 219830.7784 | 59.78 | 797.126
2016-11-27 01:00 | 41424 | 6372.6538 | 215348.5334 | 59.78 | 787.056
2016-11-27 02:00 | 41282 | 6405.3054 | 206611.6822 | 59.78 | 784.358
2016-11-27 03:00 | 41550 | 6612.086 | 206825.5711 | 59.78 | 789.45
2016-11-27 04:00 | 42195 | 7542.2707 | 205529.9731 | 59.78 | 801.705
2016-11-27 05:00 | 43511 | 8051.7756 | 205529.9731 | 59.78 | 826.709
2016-11-27 06:00 | 45333 | 8188.4979 | 205613.0981 | 59.78 | 861.327
2016-11-27 07:00 | 46426 | 7495.2867 | 209485.5541 | 59.77 | 928.52
2016-11-27 08:00 | 46598 | 7098.8413 | 210501.5541 | 59.77 | 931.96
2016-11-27 09:00 | 45659 | 7280.8875 | 209485.5541 | 59.77 | 913.18
2016-11-27 10:00 | 44155 | 6951.9636 | 209485.5541 | 59.78 | 838.945
2016-11-27 11:00 | 42413 | 2402.5 | 211803.0841 | 59.77 | 848.26
2016-11-27 12:00 | 40721 | 2196.4545 | 204701.4681 | 59.77 | 814.42
2016-11-27 13:00 | 39264 | 2486.6929 | 192032.1231 | 59.78 | 746.016
2016-11-27 14:00 | 38266 | 3651.5906 | 178726.6631 | 59.78 | 727.054
2016-11-27 15:00 | 37949 | 5592.6496 | 176476.6631 | 59.77 | 758.98
2016-11-27 16:00 | 38213 | 6026.9127 | 176476.6631 | 59.77 | 764.26
2016-11-27 17:00 | 40778 | 6864.0657 | 176476.6631 | 59.78 | 774.782
2016-11-27 18:00 | 42303 | 8717.2616 | 174572.6631 | 59.78 | 803.757
2016-11-27 19:00 | 43828 | 11265.3518 | 167766.1171 | 59.78 | 832.732
2016-11-27 20:00 | 43908 | 12605.2243 | 161067.9371 | 59.77 | 878.16
2016-11-27 21:00 | 43453 | 13154.6343 | 156482.3291 | 59.77 | 869.06
2016-11-27 22:00 | 42383 | 13137.3202 | 148746.4971 | 59.77 | 847.66
2016-11-27 23:00 | 40770 | 13279.4494 | 142905.6164 | 59.79 | 733.86
2016-11-28 | 39143 | 13047.2373 | 137957.9364 | 59.79 | 704.574
2016-11-28 01:00 | 38241 | 12653.6835 | 137957.9364 | 59.79 | 688.338
2016-11-28 02:00 | 37876 | 12503.6527 | 137957.9364 | 59.79 | 681.768
2016-11-28 03:00 | 37866 | 12777.6499 | 137957.9364 | 59.79 | 681.588
2016-11-28 04:00 | 38313 | 13195.0742 | 139253.5344 | 59.79 | 689.634
2016-11-28 05:00 | 39187 | 13356.8407 | 139253.5344 | 59.79 | 705.366
2016-11-28 06:00 | 40441 | 13166.3361 | 136820.5344 | 59.79 | 727.938
2016-11-28 07:00 | 41284 | 13994.2472 | 136831.4344 | 59.79 | 743.112
2016-11-28 08:00 | 41943 | 14993.3582 | 136831.4344 | 59.79 | 754.974
2016-11-28 09:00 | 41861 | 14950.2249 | 136831.4344 | 59.79 | 753.498
2016-11-28 10:00 | 41020 | 15489.594 | 136831.4344 | 59.79 | 738.36
2016-11-28 11:00 | 40209 | 15365.1422 | 136831.4344 | 59.79 | 723.762
2016-11-28 12:00 | 39743 | 14728.1358 | 136831.4344 | 59.79 | 715.374
2016-11-28 13:00 | 39256 | 14487.3468 | 137301.3094 | 59.79 | 706.608
2016-11-28 14:00 | 38865 | 14261.5185 | 137301.3094 | 59.79 | 699.57
2016-11-28 15:00 | 38812 | 13474.2904 | 137301.3094 | 59.79 | 698.616
2016-11-28 16:00 | 39458 | 13618.6565 | 137301.3094 | 59.79 | 710.244
2016-11-28 17:00 | 42064 | 13176.0522 | 144884.4494 | 59.77 | 841.28
2016-11-28 18:00 | 43138 | 13244.358 | 146788.4494 | 59.77 | 862.76
2016-11-28 19:00 | 44213 | 14914.841 | 146788.4494 | 59.77 | 884.26
2016-11-28 20:00 | 43383 | 15562.6391 | 136538.8094 | 59.77 | 867.66
2016-11-28 21:00 | 41659 | 15715.3501 | 136538.8094 | 59.79 | 749.862
2016-11-28 22:00 | 39163 | 15381.551 | 136538.8094 | 59.79 | 704.934
2016-11-28 23:00 | 36265 | 14332.0125 | 132853.6894 | 59.79 | 652.77
2016-11-29 | 32024 | 13275.4014 | 132853.6894 | 59.79 | 576.432
2016-11-29 01:00 | 31096 | 12794.3629 | 132853.6894 | 59.79 | 559.728
2016-11-29 02:00 | 30749 | 12536.0088 | 132853.6894 | 59.79 | 553.482
2016-11-29 03:00 | 30797 | 11510.5024 | 132303.0019 | 59.79 | 554.346
2016-11-29 04:00 | 31497 | 10935.9694 | 141380.2419 | 59.79 | 566.946
2016-11-29 05:00 | 33848 | 11067.3482 | 141380.2419 | 59.79 | 609.264
2016-11-29 06:00 | 37525 | 10670.7334 | 141380.2419 | 59.79 | 675.45
2016-11-29 07:00 | 38884 | 10380.1584 | 145190.0419 | 59.77 | 777.68
2016-11-29 08:00 | 39062 | 10023.4797 | 145190.0419 | 59.77 | 781.24
2016-11-29 09:00 | 39879 | 9659.8886 | 153476.2019 | 59.77 | 797.58
2016-11-29 10:00 | 40633 | 7593.358 | 164940.4763 | 59.78 | 772.027
2016-11-29 11:00 | 41404 | 7067.0987 | 168872.5094 | 59.78 | 786.676
2016-11-29 12:00 | 41776 | 8053.0864 | 167273.5663 | 59.78 | 793.744
2016-11-29 13:00 | 42322 | 8394.8611 | 168289.5663 | 59.78 | 804.118
2016-11-29 14:00 | 42481 | 10054.2732 | 167273.5663 | 59.77 | 849.62
2016-11-29 15:00 | 42452 | 11784.5587 | 167572.949 | 59.77 | 849.04
2016-11-29 16:00 | 41991 | 10304.8832 | 167572.949 | 59.77 | 839.82
2016-11-29 17:00 | 43155 | 10225.6413 | 167572.949 | 59.78 | 819.945
2016-11-29 18:00 | 43853 | 10559.4026 | 171919.449 | 59.78 | 833.207
2016-11-29 19:00 | 44551 | 10198.0344 | 171919.449 | 59.78 | 846.469
2016-11-29 20:00 | 43538 | 8329.4408 | 172935.449 | 59.78 | 827.222
2016-11-29 21:00 | 41740 | 7790.8163 | 171919.449 | 59.78 | 793.06
2016-11-29 22:00 | 38835 | 8381.8015 | 156593.461 | 59.77 | 776.7
2016-11-29 23:00 | 35793 | 8190.9505 | 146494.3746 | 59.77 | 715.86
2016-11-30 | 33634 | 9582.7982 | 140434.5746 | 59.79 | 605.412
2016-11-30 01:00 | 32598 | 10887.7183 | 140434.5746 | 59.79 | 586.764
2016-11-30 02:00 | 32158 | 12025.8738 | 140434.5746 | 59.79 | 578.844
2016-11-30 03:00 | 32272 | 11276.1368 | 140985.2621 | 59.79 | 580.896
2016-11-30 04:00 | 33249 | 11835.3571 | 140985.2621 | 59.79 | 598.482
2016-11-30 05:00 | 36131 | 11928.6813 | 140985.2621 | 59.79 | 650.358
2016-11-30 06:00 | 40994 | 11079.1009 | 149742.7421 | 59.77 | 819.88
2016-11-30 07:00 | 42747 | 10693.3865 | 163526.9485 | 59.77 | 854.94
2016-11-30 08:00 | 42328 | 10693.7599 | 163526.9485 | 59.77 | 846.56
2016-11-30 09:00 | 42564 | 11081.1064 | 163526.9485 | 59.77 | 851.28
2016-11-30 10:00 | 42473 | 9735.1488 | 166581.9485 | 59.78 | 806.987
2016-11-30 11:00 | 42540 | 7864.1876 | 176737.5845 | 59.78 | 808.26
2016-11-30 12:00 | 41965 | 8496.9577 | 176737.5845 | 59.78 | 797.335
2016-11-30 13:00 | 41503 | 8018.2138 | 176737.5845 | 59.78 | 788.557
2016-11-30 14:00 | 40869 | 6910.3749 | 176737.5845 | 59.78 | 776.511
2016-11-30 15:00 | 40527 | 7015.3933 | 178694.8125 | 59.78 | 770.013
2016-11-30 16:00 | 41003 | 6258.9657 | 178694.8125 | 59.78 | 779.057
2016-11-30 17:00 | 43444 | 4745.8833 | 199243.0705 | 59.77 | 868.88
2016-11-30 18:00 | 45293 | 4144.0264 | 217811.5569 | 59.77 | 905.86
2016-11-30 19:00 | 47141 | 3086.9785 | 233483.3169 | 59.78 | 895.679
2016-11-30 20:00 | 47237 | 2719.2116 | 234499.3169 | 59.78 | 897.503
2016-11-30 21:00 | 46152 | 3795.4419 | 225529.4969 | 59.77 | 923.04
2016-11-30 22:00 | 43851 | 4994.4121 | 205135.6197 | 59.77 | 877.02
2016-11-30 23:00 | 41403 | 6491.7719 | 196363.1597 | 59.78 | 786.657
2016-12-01 | 37923 | 8177.5684 | 196363.1597 | 59.77 | 758.46
2016-12-01 01:00 | 37439 | 9017.2379 | 187363.1597 | 59.77 | 748.78
2016-12-01 02:00 | 37432 | 8425.7031 | 187363.1597 | 59.77 | 748.64
2016-12-01 03:00 | 37887 | 8357.4372 | 186235.5839 | 59.77 | 757.74
2016-12-01 04:00 | 39108 | 8076.5456 | 186235.5839 | 59.77 | 782.16
2016-12-01 05:00 | 42335 | 7000.5474 | 186235.5839 | 59.78 | 804.365
2016-12-01 06:00 | 47046 | 5971.4535 | 212006.0703 | 59.77 | 940.92
2016-12-01 07:00 | 47644 | 6834.74 | 210990.0703 | 59.77 | 952.88
2016-12-01 08:00 | 45306 | 7836.7858 | 190081.1839 | 59.78 | 860.814
2016-12-01 09:00 | 43198 | 7897.2573 | 189065.1839 | 59.78 | 820.762
2016-12-01 10:00 | 41545 | 5615.0638 | 189065.1839 | 59.78 | 789.355
2016-12-01 11:00 | 40050 | 3790.1704 | 189065.1839 | 59.78 | 760.95
2016-12-01 12:00 | 38738 | 2478.2859 | 189065.1839 | 59.78 | 736.022
2016-12-01 13:00 | 37834 | 2059.484 | 189065.1839 | 59.78 | 718.846
2016-12-01 14:00 | 37387 | 2094.4647 | 187556.8339 | 59.78 | 710.353
2016-12-01 15:00 | 37029 | 2063.8921 | 187556.8339 | 59.78 | 703.551
2016-12-01 16:00 | 37405 | 2097.9979 | 187556.8339 | 59.78 | 710.695
2016-12-01 17:00 | 39432 | 2537 | 188630.8239 | 59.78 | 749.208
2016-12-01 18:00 | 40964 | 3960.5703 | 188630.8239 | 59.78 | 778.316
2016-12-01 19:00 | 42496 | 5470.6239 | 188630.8239 | 59.78 | 807.424
2016-12-01 20:00 | 42451 | 7140.9724 | 177549.4639 | 59.78 | 806.569
2016-12-01 21:00 | 41452 | 6158.5828 | 178565.4639 | 59.78 | 787.588
2016-12-01 22:00 | 39124 | 7514.258 | 156423.0543 | 59.77 | 782.48
2016-12-01 23:00 | 36626 | 9055.1368 | 156423.0543 | 59.77 | 732.52
2016-12-02 | 36168 | 9155.5621 | 156423.0543 | 59.79 | 651.024
2016-12-02 01:00 | 35540 | 8756.1021 | 156423.0543 | 59.79 | 639.72
2016-12-02 02:00 | 35391 | 7756.8392 | 156423.0543 | 59.77 | 707.82
2016-12-02 03:00 | 35750 | 7301.3819 | 156931.2601 | 59.77 | 715
2016-12-02 04:00 | 36976 | 7261.6875 | 156931.2601 | 59.77 | 739.52
2016-12-02 05:00 | 39966 | 7489.6925 | 167584.6765 | 59.77 | 799.32
2016-12-02 06:00 | 44678 | 7490.9725 | 189372.1345 | 59.78 | 848.882
2016-12-02 07:00 | 45284 | 8226.889 | 189372.1345 | 59.78 | 860.396
2016-12-02 08:00 | 43325 | 9272.7077 | 189372.1345 | 59.78 | 823.175
2016-12-02 09:00 | 41657 | 9577.322 | 189372.1345 | 59.77 | 833.14
2016-12-02 10:00 | 40565 | 5477.2324 | 189372.1345 | 59.78 | 770.735
2016-12-02 11:00 | 39458 | 2827.9865 | 189372.1345 | 59.78 | 749.702
2016-12-02 12:00 | 38710 | 1739.0616 | 189372.1345 | 59.78 | 735.49
2016-12-02 13:00 | 38313 | 1624.7094 | 189372.1345 | 59.78 | 727.947
2016-12-02 14:00 | 37990 | 1318.2086 | 190880.4845 | 59.78 | 721.81
2016-12-02 15:00 | 37902 | 1406.9949 | 199843.2845 | 59.78 | 720.138
2016-12-02 16:00 | 38109 | 1270.2754 | 197491.1245 | 59.78 | 724.071
2016-12-02 17:00 | 39741 | 972.775 | 202738.3597 | 59.77 | 794.82
2016-12-02 18:00 | 40755 | 1349.9323 | 207057.9297 | 59.77 | 815.1
2016-12-02 19:00 | 41769 | 1613.8153 | 207235.1496 | 59.77 | 835.38
2016-12-02 20:00 | 41299 | 2224.6779 | 202569.6397 | 59.77 | 825.98
2016-12-02 21:00 | 39992 | 2543.7204 | 192365.8197 | 59.78 | 759.848
2016-12-02 22:00 | 37588 | 2704.8898 | 183346.6252 | 59.78 | 714.172
2016-12-02 23:00 | 34931 | 3172.584 | 174383.8252 | 59.77 | 698.62
2016-12-03 | 35231 | 3585.1023 | 172471.4252 | 59.77 | 704.62
2016-12-03 01:00 | 35538 | 4048.8754 | 172471.4252 | 59.77 | 710.76
2016-12-03 02:00 | 35269 | 4126.4028 | 172471.4252 | 59.77 | 705.38
2016-12-03 03:00 | 35536 | 4497.8042 | 173090.7952 | 59.77 | 710.72
2016-12-03 04:00 | 36603 | 5525.1391 | 173090.7952 | 59.77 | 732.06
2016-12-03 05:00 | 39690 | 6646.1658 | 176698.1152 | 59.78 | 754.11
2016-12-03 06:00 | 44681 | 7976.5541 | 193465.0852 | 59.78 | 848.939
2016-12-03 07:00 | 45702 | 7840.4349 | 194481.0852 | 59.77 | 914.04
2016-12-03 08:00 | 44538 | 8175.9141 | 190228.4152 | 59.78 | 846.222
2016-12-03 09:00 | 43727 | 8558.7778 | 186991.7452 | 59.78 | 830.813
2016-12-03 10:00 | 43188 | 8687.7878 | 186991.7452 | 59.78 | 820.572
2016-12-03 11:00 | 42742 | 7628.7593 | 186991.7452 | 59.78 | 812.098
2016-12-03 12:00 | 42424 | 6847.0411 | 186419.2452 | 59.78 | 806.056
2016-12-03 13:00 | 42475 | 6619.5059 | 186419.2452 | 59.78 | 807.025
2016-12-03 14:00 | 42448 | 7076.8302 | 180696.9552 | 59.78 | 806.512
2016-12-03 15:00 | 42218 | 8288.735 | 173151.2292 | 59.78 | 802.142
2016-12-03 16:00 | 42088 | 9028.792 | 171896.0692 | 59.78 | 799.672
2016-12-03 17:00 | 43368 | 9634.1262 | 173084.73 | 59.78 | 823.992
2016-12-03 18:00 | 43689 | 11006.2813 | 163753.562 | 59.78 | 830.091
2016-12-03 19:00 | 44009 | 12735.9526 | 153553.6256 | 59.77 | 880.18
2016-12-03 20:00 | 43024 | 13732.6739 | 145172.1367 | 59.77 | 860.48
2016-12-03 21:00 | 41813 | 13879.6847 | 141952.2167 | 59.77 | 836.26
2016-12-03 22:00 | 39825 | 13811.5965 | 138142.4167 | 59.79 | 716.85
2016-12-03 23:00 | 37345 | 13741.5137 | 138142.4167 | 59.79 | 672.21
2016-12-04 | 36517 | 12957.2309 | 138142.4167 | 59.79 | 657.306
2016-12-04 01:00 | 35002 | 12198.368 | 138142.4167 | 59.79 | 630.036
2016-12-04 02:00 | 34157 | 11269.2578 | 138142.4167 | 59.79 | 614.826
2016-12-04 03:00 | 33842 | 10813.4014 | 138142.4167 | 59.79 | 609.156
2016-12-04 04:00 | 34066 | 10066.378 | 140463.4313 | 59.79 | 613.188
2016-12-04 05:00 | 34886 | 9887.3851 | 140707.4153 | 59.79 | 627.948
2016-12-04 06:00 | 36662 | 9851.7045 | 140463.4313 | 59.79 | 659.916
2016-12-04 07:00 | 37866 | 11570.1946 | 140463.4313 | 59.79 | 681.588
2016-12-04 08:00 | 39729 | 12567.6027 | 140463.4313 | 59.79 | 715.122
2016-12-04 09:00 | 41211 | 12524.0229 | 142375.8313 | 59.77 | 824.22
2016-12-04 10:00 | 42139 | 12558.505 | 142375.8313 | 59.77 | 842.78
2016-12-04 11:00 | 42466 | 12338.5624 | 146185.6313 | 59.77 | 849.32
2016-12-04 12:00 | 42569 | 11216.1569 | 152913.5633 | 59.77 | 851.38
2016-12-04 13:00 | 42531 | 9785.2096 | 157861.2433 | 59.78 | 808.089
2016-12-04 14:00 | 42547 | 9144.1347 | 162927.4833 | 59.78 | 808.393
2016-12-04 15:00 | 42377 | 8424.5018 | 163943.4833 | 59.78 | 805.163
2016-12-04 16:00 | 42347 | 7220.2138 | 173081.6677 | 59.78 | 804.593
2016-12-04 17:00 | 43965 | 7531.2507 | 178278.1977 | 59.78 | 835.335
2016-12-04 18:00 | 44702 | 8824.5439 | 178090.9977 | 59.78 | 849.338
2016-12-04 19:00 | 45439 | 8743.4105 | 179106.9977 | 59.78 | 863.341
2016-12-04 20:00 | 44900 | 8512.7374 | 178304.8865 | 59.78 | 853.1
2016-12-04 21:00 | 43981 | 7767.3077 | 178304.8865 | 59.78 | 835.639
2016-12-04 22:00 | 42387 | 5804.7235 | 179320.8865 | 59.78 | 805.353
2016-12-04 23:00 | 40307 | 5466.8927 | 178304.8865 | 59.78 | 765.833
2016-12-05 | 37761 | 5985.9736 | 176392.4865 | 59.77 | 755.22
2016-12-05 01:00 | 36752 | 5877.6646 | 176392.4865 | 59.77 | 735.04
2016-12-05 02:00 | 36292 | 6286.4387 | 173910.8865 | 59.77 | 725.84
2016-12-05 03:00 | 36286 | 6877.1873 | 173910.8865 | 59.77 | 725.72
2016-12-05 04:00 | 36775 | 6579.896 | 173910.8865 | 59.77 | 735.5
2016-12-05 05:00 | 37912 | 6497.2807 | 171917.3365 | 59.77 | 758.24
2016-12-05 06:00 | 39645 | 5881.1518 | 171917.3365 | 59.78 | 753.255
2016-12-05 07:00 | 41073 | 5989.4396 | 179871.1565 | 59.78 | 780.387
2016-12-05 08:00 | 43035 | 6226.8878 | 192029.3425 | 59.78 | 817.665
2016-12-05 09:00 | 43975 | 6140.4189 | 199473.1425 | 59.77 | 879.5
2016-12-05 10:00 | 43836 | 4145.5769 | 211826.8529 | 59.77 | 876.72
2016-12-05 11:00 | 43039 | 3179.5199 | 211826.8529 | 59.77 | 860.78
2016-12-05 12:00 | 42302 | 2613.0433 | 212111.2609 | 59.77 | 846.04
2016-12-05 13:00 | 41557 | 1974.3601 | 212111.2609 | 59.77 | 831.14
2016-12-05 14:00 | 40788 | 1663.8861 | 212111.2609 | 59.77 | 815.76
2016-12-05 15:00 | 40623 | 1562.3137 | 211994.3809 | 59.77 | 812.46
2016-12-05 16:00 | 41446 | 1549.5651 | 215231.0509 | 59.77 | 828.92
2016-12-05 17:00 | 44778 | 1654.8885 | 238963.0619 | 59.78 | 850.782
2016-12-05 18:00 | 46918 | 2363.2855 | 244077.7794 | 59.78 | 891.442
2016-12-05 19:00 | 49058 | 3968.7976 | 244479.2927 | 59.78 | 932.102
2016-12-05 20:00 | 49082 | 6167.779 | 233238.069 | 59.78 | 932.558
2016-12-05 21:00 | 48099 | 5965.4961 | 225381.669 | 59.77 | 961.98
2016-12-05 22:00 | 45745 | 5565.0942 | 215439.679 | 59.77 | 914.9
2016-12-05 23:00 | 43079 | 4341.6813 | 215439.679 | 59.77 | 861.58
2016-12-06 | 38527 | 4315.3984 | 215626.879 | 59.78 | 732.013
2016-12-06 01:00 | 38112 | 4441.2591 | 215626.879 | 59.78 | 724.128
2016-12-06 02:00 | 38258 | 4221.3964 | 218108.479 | 59.78 | 726.902
2016-12-06 03:00 | 38898 | 4173.4192 | 218108.479 | 59.78 | 739.062
2016-12-06 04:00 | 40452 | 3757.4803 | 218108.479 | 59.78 | 768.588
2016-12-06 05:00 | 43929 | 3562.1175 | 220102.029 | 59.77 | 878.58
2016-12-06 06:00 | 49280 | 3300.9573 | 249233.0174 | 59.78 | 936.32
2016-12-06 07:00 | 50549 | 3367.9454 | 250249.0174 | 59.78 | 960.431
2016-12-06 08:00 | 49014 | 3906.1937 | 242414.6999 | 59.78 | 931.266
2016-12-06 09:00 | 47409 | 4087.3254 | 232575.9269 | 59.78 | 900.771
2016-12-06 10:00 | 46009 | 2991.5194 | 225305.4389 | 59.78 | 874.171
2016-12-06 11:00 | 44527 | 1972.0604 | 225305.4389 | 59.78 | 846.013
2016-12-06 12:00 | 43156 | 1674.3951 | 225305.4389 | 59.77 | 863.12
2016-12-06 13:00 | 42237 | 1192.3506 | 225305.4389 | 59.77 | 844.74
2016-12-06 14:00 | 41222 | 1096.7207 | 225305.4389 | 59.77 | 824.44
2016-12-06 15:00 | 40837 | 1191.7963 | 225422.3189 | 59.77 | 816.74
2016-12-06 16:00 | 41617 | 1423.7961 | 225422.3189 | 59.77 | 832.34
2016-12-06 17:00 | 45141 | 1961.3155 | 226158.3189 | 59.78 | 857.679
2016-12-06 18:00 | 47237 | 3234.2495 | 229092.9189 | 59.78 | 897.503
2016-12-06 19:00 | 49334 | 4485.001 | 229555.3821 | 59.78 | 937.346
2016-12-06 20:00 | 49364 | 5784.733 | 224754.8189 | 59.78 | 937.916
2016-12-06 21:00 | 48150 | 5883.1421 | 217058.9205 | 59.77 | 963
2016-12-06 22:00 | 45359 | 7631.9268 | 190013.7905 | 59.77 | 907.18
2016-12-06 23:00 | 42535 | 9215.6129 | 168776.0961 | 59.78 | 808.165
2016-12-07 | 40362 | 9368.6313 | 168776.0961 | 59.77 | 807.24
2016-12-07 01:00 | 39911 | 9036.808 | 168776.0961 | 59.77 | 798.22
2016-12-07 02:00 | 39773 | 8985.1513 | 168776.0961 | 59.77 | 795.46
2016-12-07 03:00 | 40327 | 8767.8701 | 168776.0961 | 59.77 | 806.54
2016-12-07 04:00 | 41583 | 8240.4051 | 168776.0961 | 59.78 | 790.077
2016-12-07 05:00 | 44880 | 9109.4829 | 181772.0061 | 59.78 | 852.72
2016-12-07 06:00 | 49505 | 9731.7572 | 192194.1437 | 59.77 | 990.1
2016-12-07 07:00 | 50076 | 10522.6102 | 191887.8605 | 59.77 | 1001.52
2016-12-07 08:00 | 48129 | 10979.2188 | 179998.8145 | 59.78 | 914.451
2016-12-07 09:00 | 46228 | 11351.7302 | 176649.7245 | 59.78 | 878.332
2016-12-07 10:00 | 44901 | 9237.1147 | 176649.7245 | 59.78 | 853.119
2016-12-07 11:00 | 43438 | 8079.0242 | 174262.2245 | 59.78 | 825.322
2016-12-07 12:00 | 42166 | 6522.1215 | 174262.2245 | 59.78 | 801.154
2016-12-07 13:00 | 41414 | 6737.3131 | 174262.2245 | 59.78 | 786.866
2016-12-07 14:00 | 40798 | 6647.8081 | 173398.9245 | 59.78 | 775.162
2016-12-07 15:00 | 40901 | 7164.4666 | 173398.9245 | 59.78 | 777.119
2016-12-07 16:00 | 42021 | 7712.4281 | 173398.9245 | 59.78 | 798.399
2016-12-07 17:00 | 44747 | 8745.9228 | 174414.9245 | 59.78 | 850.193
2016-12-07 18:00 | 45670 | 11742.6178 | 173398.9245 | 59.78 | 867.73
2016-12-07 19:00 | 46593 | 11380.2144 | 173114.5165 | 59.78 | 885.267
2016-12-07 20:00 | 46121 | 10526.4529 | 173114.5165 | 59.78 | 876.299
2016-12-07 21:00 | 44301 | 9297.9828 | 168962.6065 | 59.78 | 841.719
2016-12-07 22:00 | 41463 | 8516.7265 | 168962.6065 | 59.78 | 787.797
2016-12-07 23:00 | 38578 | 6957.6861 | 168962.6065 | 59.77 | 771.56
2016-12-08 | 36471 | 6258.9976 | 168962.6065 | 59.77 | 729.42
2016-12-08 01:00 | 35727 | 6156.1934 | 168962.6065 | 59.77 | 714.54
2016-12-08 02:00 | 35576 | 5533.6243 | 168962.6065 | 59.77 | 711.52
2016-12-08 03:00 | 36031 | 4733.6882 | 165804.2065 | 59.77 | 720.62
2016-12-08 04:00 | 37356 | 4371.3499 | 169411.5265 | 59.78 | 709.764
2016-12-08 05:00 | 40650 | 5304.8539 | 179480.3165 | 59.78 | 772.35
2016-12-08 06:00 | 45562 | 5668.2621 | 210469.3929 | 59.77 | 911.24
2016-12-08 07:00 | 46982 | 5924.3093 | 213577.5809 | 59.77 | 939.64
2016-12-08 08:00 | 45734 | 6584.7199 | 207495.3409 | 59.77 | 914.68
2016-12-08 09:00 | 44583 | 7682.6045 | 204157.9186 | 59.78 | 847.077
2016-12-08 10:00 | 43614 | 6006.8851 | 204157.9186 | 59.77 | 872.28
2016-12-08 11:00 | 42631 | 3690.2072 | 206545.4186 | 59.77 | 852.62
2016-12-08 12:00 | 41654 | 3443.9898 | 206545.4186 | 59.77 | 833.08
2016-12-08 13:00 | 40951 | 2871.8731 | 206545.4186 | 59.77 | 819.02
2016-12-08 14:00 | 40408 | 2565.2137 | 207408.7186 | 59.77 | 808.16
2016-12-08 15:00 | 40182 | 2151.1036 | 207408.7186 | 59.77 | 803.64
2016-12-08 16:00 | 40598 | 1992.5759 | 207408.7186 | 59.77 | 811.96
2016-12-08 17:00 | 43544 | 2016.4684 | 218281.3066 | 59.77 | 870.88
2016-12-08 18:00 | 45325 | 2988.5168 | 220736.7966 | 59.77 | 906.5
2016-12-08 19:00 | 47107 | 5390.3313 | 220005.2046 | 59.77 | 942.14
2016-12-08 20:00 | 47144 | 8404.5155 | 199952.9062 | 59.77 | 942.88
2016-12-08 21:00 | 46212 | 10040.76 | 184400.8762 | 59.78 | 878.028
2016-12-08 22:00 | 43775 | 10673.4455 | 166588.9302 | 59.78 | 831.725
2016-12-08 23:00 | 41131 | 11624.2672 | 155298.7458 | 59.77 | 822.62
2016-12-09 | 37545 | 11923.0083 | 155298.7458 | 59.79 | 675.81
2016-12-09 01:00 | 37235 | 11802.8963 | 150278.2578 | 59.79 | 670.23
2016-12-09 02:00 | 37318 | 11428.5552 | 150278.2578 | 59.79 | 671.724
2016-12-09 03:00 | 37801 | 11491.2449 | 153436.6578 | 59.79 | 680.418
2016-12-09 04:00 | 39147 | 11848.6573 | 153436.6578 | 59.79 | 704.646
2016-12-09 05:00 | 42215 | 12275.5505 | 153436.6578 | 59.77 | 844.3
2016-12-09 06:00 | 47057 | 11666.0506 | 174699.1622 | 59.78 | 894.083
2016-12-09 07:00 | 47601 | 12144.2552 | 174699.1622 | 59.78 | 904.419
2016-12-09 08:00 | 45460 | 12611.1995 | 165014.3422 | 59.78 | 863.74
2016-12-09 09:00 | 43728 | 12781.5575 | 164883.6293 | 59.77 | 874.56
2016-12-09 10:00 | 42210 | 11824.0934 | 164883.6293 | 59.77 | 844.2
2016-12-09 11:00 | 40639 | 11462.4904 | 164883.6293 | 59.77 | 812.78
2016-12-09 12:00 | 39202 | 10326.775 | 164883.6293 | 59.77 | 784.04
2016-12-09 13:00 | 38295 | 7298.9665 | 166032.5213 | 59.77 | 765.9
2016-12-09 14:00 | 37526 | 5639.6277 | 166032.5213 | 59.77 | 750.52
2016-12-09 15:00 | 37163 | 4507.7627 | 166032.5213 | 59.78 | 706.097
2016-12-09 16:00 | 37443 | 3496.9606 | 166032.5213 | 59.78 | 711.417
2016-12-09 17:00 | 39691 | 2897.16 | 184243.5773 | 59.78 | 754.129
2016-12-09 18:00 | 40965 | 3257.8961 | 190109.0973 | 59.77 | 819.3
2016-12-09 19:00 | 42239 | 3658.0828 | 191125.0973 | 59.77 | 844.78
2016-12-09 20:00 | 42012 | 4527.5092 | 190109.0973 | 59.78 | 798.228
2016-12-09 21:00 | 40821 | 4702.5275 | 184975.4009 | 59.78 | 775.599
2016-12-09 22:00 | 38427 | 5102.6296 | 182542.4009 | 59.78 | 730.113
2016-12-09 23:00 | 35792 | 5137.978 | 183678.4009 | 59.77 | 715.84
2016-12-10 | 36531 | 4567.4867 | 183678.4009 | 59.77 | 730.62
2016-12-10 01:00 | 36933 | 4542.2754 | 183678.4009 | 59.77 | 738.66
2016-12-10 02:00 | 36733 | 4701.4572 | 183678.4009 | 59.77 | 734.66
2016-12-10 03:00 | 37041 | 4449.727 | 183678.4009 | 59.78 | 703.779
2016-12-10 04:00 | 38285 | 4599.1792 | 183678.4009 | 59.78 | 727.415
2016-12-10 05:00 | 41310 | 4056.9781 | 192774.9213 | 59.78 | 784.89
2016-12-10 06:00 | 46094 | 3279.2416 | 222344.7577 | 59.78 | 875.786
2016-12-10 07:00 | 47129 | 3592.6784 | 223360.7577 | 59.78 | 895.451
2016-12-10 08:00 | 45688 | 3980.055 | 218872.4677 | 59.77 | 913.76
2016-12-10 09:00 | 44481 | 3997.1472 | 213423.2417 | 59.77 | 889.62
2016-12-10 10:00 | 43405 | 3644.1036 | 207788.6649 | 59.77 | 868.1
2016-12-10 11:00 | 42353 | 3996.0422 | 205307.0649 | 59.77 | 847.06
2016-12-10 12:00 | 41423 | 4347.2504 | 203394.6649 | 59.78 | 787.037
2016-12-10 13:00 | 40947 | 4076.1685 | 200040.9545 | 59.78 | 777.993
2016-12-10 14:00 | 40524 | 4034.0037 | 197582.7645 | 59.78 | 769.956
2016-12-10 15:00 | 40235 | 3824.7412 | 197582.7645 | 59.78 | 764.465
2016-12-10 16:00 | 40405 | 4103.8491 | 197582.7645 | 59.78 | 767.695
2016-12-10 17:00 | 42323 | 4437.5722 | 197582.7645 | 59.77 | 846.46
2016-12-10 18:00 | 42822 | 6332.5141 | 186332.7645 | 59.78 | 813.618
2016-12-10 19:00 | 43321 | 8745.1057 | 173146.6245 | 59.78 | 823.099
2016-12-10 20:00 | 42570 | 10679.9473 | 156294.2601 | 59.77 | 851.4
2016-12-10 21:00 | 41496 | 11205.4464 | 148795.0201 | 59.77 | 829.92
2016-12-10 22:00 | 39657 | 11574.9677 | 138697.2001 | 59.77 | 793.14
2016-12-10 23:00 | 37383 | 12160.8613 | 136242.8001 | 59.79 | 672.894
2016-12-11 | 36731 | 13188.5175 | 134732.4801 | 59.79 | 661.158
2016-12-11 01:00 | 36496 | 13298.3679 | 134732.4801 | 59.79 | 656.928
2016-12-11 02:00 | 35673 | 13279.1114 | 134732.4801 | 59.79 | 642.114
2016-12-11 03:00 | 35351 | 13981.8856 | 134732.4801 | 59.79 | 636.318
2016-12-11 04:00 | 35684 | 14389.9047 | 137540.0801 | 59.79 | 642.312
2016-12-11 05:00 | 36808 | 13780.4119 | 139973.0801 | 59.79 | 662.544
2016-12-11 06:00 | 38497 | 12877.6088 | 139973.0801 | 59.79 | 692.946
2016-12-11 07:00 | 40014 | 12419.6988 | 139889.9551 | 59.77 | 800.28
2016-12-11 08:00 | 41736 | 11751.233 | 153488.1451 | 59.77 | 834.72
2016-12-11 09:00 | 43239 | 12082.4125 | 162346.7315 | 59.77 | 864.78
2016-12-11 10:00 | 43402 | 11501.4663 | 165695.8215 | 59.77 | 868.04
2016-12-11 11:00 | 43314 | 10111.3978 | 176848.8675 | 59.78 | 822.966
2016-12-11 12:00 | 42737 | 8637.4406 | 184483.5575 | 59.78 | 812.003
2016-12-11 13:00 | 42063 | 6786.0568 | 187720.2275 | 59.78 | 799.197
2016-12-11 14:00 | 41494 | 5787.962 | 190178.4175 | 59.78 | 788.386
2016-12-11 15:00 | 41250 | 6322.6045 | 190178.4175 | 59.78 | 783.75
2016-12-11 16:00 | 41538 | 6726.2564 | 190178.4175 | 59.78 | 789.222
2016-12-11 17:00 | 43875 | 6661.475 | 193983.5075 | 59.78 | 833.625
2016-12-11 18:00 | 44992 | 7443.647 | 194543.5075 | 59.77 | 899.84
2016-12-11 19:00 | 46109 | 8933.7157 | 190733.7075 | 59.78 | 876.071
2016-12-11 20:00 | 45814 | 10433.5411 | 180796.1915 | 59.78 | 870.466
2016-12-11 21:00 | 45339 | 11235.9122 | 177559.5215 | 59.78 | 861.441
2016-12-11 22:00 | 43788 | 11621.8217 | 166256.6115 | 59.77 | 875.76
2016-12-11 23:00 | 42155 | 11206.3722 | 168711.0115 | 59.77 | 843.1
2016-12-12 | 39115 | 9993.2144 | 165491.0915 | 59.77 | 782.3
2016-12-12 01:00 | 38454 | 9624.2569 | 165491.0915 | 59.77 | 769.08
2016-12-12 02:00 | 38402 | 8432.5824 | 165491.0915 | 59.77 | 768.04
2016-12-12 03:00 | 38871 | 8430.2108 | 167001.4115 | 59.77 | 777.42
2016-12-12 04:00 | 39811 | 8135.3397 | 167001.4115 | 59.77 | 796.22
2016-12-12 05:00 | 41317 | 8233.5644 | 170608.7315 | 59.78 | 785.023
2016-12-12 06:00 | 43241 | 7904.0283 | 178304.3215 | 59.78 | 821.579
2016-12-12 07:00 | 44915 | 7685.2063 | 188295.6325 | 59.78 | 853.385
2016-12-12 08:00 | 46487 | 7658.4825 | 200495.1025 | 59.77 | 929.74
2016-12-12 09:00 | 46876 | 8840.48 | 201790.7005 | 59.77 | 937.52
2016-12-12 10:00 | 46177 | 6653.0284 | 201790.7005 | 59.77 | 923.54
2016-12-12 11:00 | 45137 | 5188.7694 | 206853.6051 | 59.77 | 902.74
2016-12-12 12:00 | 44118 | 6063.4485 | 206853.6051 | 59.77 | 882.36
2016-12-12 13:00 | 43034 | 4488.1271 | 206853.6051 | 59.77 | 860.68
2016-12-12 14:00 | 42088 | 2305.5698 | 206853.6051 | 59.77 | 841.76
2016-12-12 15:00 | 41751 | 2102.4422 | 212705.7051 | 59.77 | 835.02
2016-12-12 16:00 | 42585 | 1696.6091 | 217818.0851 | 59.77 | 851.7
2016-12-12 17:00 | 46220 | 1226.654 | 246550.0565 | 59.78 | 878.18
2016-12-12 18:00 | 48842 | 1562.1653 | 258740.8677 | 59.78 | 927.998
2016-12-12 19:00 | 51464 | 1773.3612 | 263869.6108 | 59.76 | 1080.744
2016-12-12 20:00 | 51757 | 2352.1484 | 263496.7909 | 59.76 | 1086.897
2016-12-12 21:00 | 51059 | 2159.7861 | 263286.6677 | 59.76 | 1072.239
2016-12-12 22:00 | 48826 | 3081.5365 | 245242.8697 | 59.78 | 927.694
2016-12-12 23:00 | 46331 | 5420.0995 | 227641.7737 | 59.77 | 926.62
2016-12-13 | 41200 | 7072.6623 | 218798.7037 | 59.78 | 782.8
2016-12-13 01:00 | 40802 | 7646.4679 | 202420.4427 | 59.78 | 775.238
2016-12-13 02:00 | 40994 | 9451.269 | 200531.4927 | 59.77 | 819.88
2016-12-13 03:00 | 41706 | 10399.8527 | 200531.4927 | 59.77 | 834.12
2016-12-13 04:00 | 43309 | 10443.9645 | 200414.6127 | 59.78 | 822.871
2016-12-13 05:00 | 46879 | 10761.6862 | 200414.6127 | 59.78 | 890.701
2016-12-13 06:00 | 52208 | 10350.6192 | 221513.2887 | 59.77 | 1044.16
2016-12-13 07:00 | 53467 | 10288.6704 | 227544.6807 | 59.78 | 1015.873
2016-12-13 08:00 | 51134 | 10591.7844 | 217791.8295 | 59.77 | 1022.68
2016-12-13 09:00 | 48836 | 10905.3467 | 206484.1591 | 59.77 | 976.72
2016-12-13 10:00 | 46824 | 8603.8195 | 206484.1591 | 59.77 | 936.48
2016-12-13 11:00 | 44616 | 7187.7708 | 208663.6925 | 59.78 | 847.704
2016-12-13 12:00 | 42788 | 6558.5442 | 208663.6925 | 59.78 | 812.972
2016-12-13 13:00 | 41421 | 4710.1703 | 208663.6925 | 59.78 | 786.999
2016-12-13 14:00 | 40368 | 3294.7494 | 207800.3925 | 59.78 | 766.992
2016-12-13 15:00 | 39903 | 2621.9848 | 207800.3925 | 59.78 | 758.157
2016-12-13 16:00 | 40321 | 2666.5354 | 207800.3925 | 59.77 | 806.42
2016-12-13 17:00 | 43420 | 3120.7627 | 211020.3125 | 59.77 | 868.4
2016-12-13 18:00 | 45637 | 5208.7363 | 211020.3125 | 59.77 | 912.74
2016-12-13 19:00 | 47854 | 8164.4275 | 206520.3125 | 59.77 | 957.08
2016-12-13 20:00 | 47887 | 10317.7661 | 190968.2825 | 59.77 | 957.74
2016-12-13 21:00 | 46809 | 10298.582 | 187381.2965 | 59.78 | 889.371
2016-12-13 22:00 | 43988 | 10879.3003 | 168495.2465 | 59.78 | 835.772
2016-12-13 23:00 | 41239 | 10500.7262 | 165468.8765 | 59.77 | 824.78
2016-12-14 | 39320 | 10134.6063 | 165468.8765 | 59.77 | 786.4
2016-12-14 01:00 | 38682 | 10579.6905 | 163960.5265 | 59.77 | 773.64
2016-12-14 02:00 | 38690 | 10345.251 | 165849.4765 | 59.77 | 773.8
2016-12-14 03:00 | 39074 | 9813.7997 | 165849.4765 | 59.77 | 781.48
2016-12-14 04:00 | 40434 | 9893.8306 | 165849.4765 | 59.77 | 808.68
2016-12-14 05:00 | 43517 | 10076.3563 | 173470.6665 | 59.78 | 826.823
2016-12-14 06:00 | 48316 | 10393.8066 | 186607.6997 | 59.77 | 966.32
2016-12-14 07:00 | 48969 | 11878.3084 | 186615.7645 | 59.78 | 930.411
2016-12-14 08:00 | 46527 | 13214.167 | 170135.3361 | 59.78 | 884.013
2016-12-14 09:00 | 44485 | 13500.1951 | 161849.1761 | 59.77 | 889.7
2016-12-14 10:00 | 42752 | 11750.829 | 161231.1761 | 59.77 | 855.04
2016-12-14 11:00 | 41362 | 8972.3543 | 161231.1761 | 59.77 | 827.24
2016-12-14 12:00 | 40120 | 7199.9964 | 160456.8461 | 59.78 | 762.28
2016-12-14 13:00 | 39472 | 6699.777 | 162938.4461 | 59.78 | 749.968
2016-12-14 14:00 | 38839 | 6987.2446 | 163801.7461 | 59.77 | 776.78
2016-12-14 15:00 | 38575 | 6538.383 | 163801.7461 | 59.77 | 771.5
2016-12-14 16:00 | 38754 | 6215.4209 | 163801.7461 | 59.78 | 736.326
2016-12-14 17:00 | 40837 | 7090.5493 | 163801.7461 | 59.78 | 775.903
2016-12-14 18:00 | 42154 | 10147.4383 | 156256.0201 | 59.77 | 843.08
2016-12-14 19:00 | 43472 | 11965.998 | 152648.7001 | 59.77 | 869.44
2016-12-14 20:00 | 43024 | 12997.454 | 147113.9801 | 59.77 | 860.48
2016-12-14 21:00 | 41719 | 13146.5215 | 142554.0601 | 59.77 | 834.38
2016-12-14 22:00 | 38872 | 13208.7592 | 135524.3401 | 59.79 | 699.696
2016-12-14 23:00 | 35831 | 13175.0704 | 135598.1592 | 59.79 | 644.958
2016-12-15 | 34224 | 13099.7136 | 129580.8892 | 59.79 | 616.032
2016-12-15 01:00 | 33340 | 13596.866 | 129296.3182 | 59.79 | 600.12
2016-12-15 02:00 | 32972 | 13462.0184 | 129296.3182 | 59.79 | 593.496
2016-12-15 03:00 | 33060 | 13593.3198 | 130804.6682 | 59.79 | 595.08
2016-12-15 04:00 | 33998 | 14051.5069 | 131665.9502 | 59.79 | 611.964
2016-12-15 05:00 | 36607 | 14406.669 | 132541.3412 | 59.79 | 658.926
2016-12-15 06:00 | 40844 | 14658.363 | 130804.6682 | 59.79 | 735.192
2016-12-15 07:00 | 41877 | 15063.7547 | 130030.3382 | 59.79 | 753.786
2016-12-15 08:00 | 40678 | 15287.9626 | 130078.3382 | 59.79 | 732.204
2016-12-15 09:00 | 40376 | 15455.4273 | 130078.3382 | 59.79 | 726.768
2016-12-15 10:00 | 40081 | 15539.8425 | 130696.3382 | 59.79 | 721.458
2016-12-15 11:00 | 39839 | 14862.0325 | 130696.3382 | 59.79 | 717.102
2016-12-15 12:00 | 39644 | 13838.4891 | 131470.6682 | 59.79 | 713.592
2016-12-15 13:00 | 39782 | 12810.7568 | 132531.1882 | 59.79 | 716.076
2016-12-15 14:00 | 39917 | 12834.4696 | 132061.3132 | 59.79 | 718.506
2016-12-15 15:00 | 39829 | 12651.1286 | 132061.3132 | 59.79 | 716.922
2016-12-15 16:00 | 39761 | 12668.2909 | 134106.8632 | 59.79 | 715.698
2016-12-15 17:00 | 41226 | 13468.3233 | 134106.8632 | 59.77 | 824.52
2016-12-15 18:00 | 42289 | 14534.232 | 136539.8632 | 59.77 | 845.78
2016-12-15 19:00 | 43351 | 14565.9627 | 136539.8632 | 59.77 | 867.02
2016-12-15 20:00 | 42605 | 14328.4041 | 136539.8632 | 59.77 | 852.1
2016-12-15 21:00 | 41189 | 14307.7925 | 133319.9432 | 59.79 | 741.402
2016-12-15 22:00 | 38301 | 14070.8143 | 133319.9432 | 59.79 | 689.418
2016-12-15 23:00 | 35024 | 13664.504 | 133319.9432 | 59.79 | 630.432
2016-12-16 | 31912 | 12280.5796 | 130998.9287 | 59.79 | 574.416
2016-12-16 01:00 | 30920 | 10647.5664 | 131283.4997 | 59.79 | 556.56
2016-12-16 02:00 | 30382 | 11237.2223 | 131283.4997 | 59.79 | 546.876
2016-12-16 03:00 | 30475 | 11135.6684 | 131283.4997 | 59.79 | 548.55
2016-12-16 04:00 | 31387 | 12458.1222 | 138475.0897 | 59.79 | 564.966
2016-12-16 05:00 | 34022 | 12169.6195 | 141695.0097 | 59.79 | 612.396
2016-12-16 06:00 | 38620 | 11026.5491 | 141621.1906 | 59.77 | 772.4
2016-12-16 07:00 | 40323 | 9788.414 | 149425.2406 | 59.77 | 806.46
2016-12-16 08:00 | 40057 | 8812.0753 | 154372.9206 | 59.77 | 801.14
2016-12-16 09:00 | 40251 | 7392.804 | 168444.453 | 59.78 | 764.769
2016-12-16 10:00 | 40203 | 7107.3115 | 168849.6924 | 59.78 | 763.857
2016-12-16 11:00 | 40013 | 5081.1036 | 183747.0584 | 59.78 | 760.247
2016-12-16 12:00 | 39597 | 4255.4609 | 185997.0584 | 59.78 | 752.343
2016-12-16 13:00 | 39345 | 3152.7259 | 188156.4584 | 59.78 | 747.555
2016-12-16 14:00 | 38863 | 3014.8541 | 188626.3334 | 59.78 | 738.397
2016-12-16 15:00 | 38604 | 3687.7399 | 188626.3334 | 59.78 | 733.476
2016-12-16 16:00 | 38885 | 3925.7145 | 190203.1034 | 59.78 | 738.815
2016-12-16 17:00 | 41014 | 3977.6902 | 194549.6034 | 59.78 | 779.266
2016-12-16 18:00 | 42321 | 5046.0256 | 192110.0034 | 59.78 | 804.099
2016-12-16 19:00 | 43627 | 5411.3131 | 193708.9465 | 59.77 | 872.54
2016-12-16 20:00 | 43547 | 5837.8602 | 193126.0034 | 59.77 | 870.94
2016-12-16 21:00 | 42436 | 7114.1541 | 179816.7874 | 59.78 | 806.284
2016-12-16 22:00 | 40138 | 7290.2513 | 176111.8114 | 59.78 | 762.622
2016-12-16 23:00 | 37484 | 6328.6162 | 176111.8114 | 59.77 | 749.68
2016-12-17 | 37305 | 5577.275 | 174610.1614 | 59.77 | 746.1
2016-12-17 01:00 | 36549 | 6272.0422 | 174610.1614 | 59.77 | 730.98
2016-12-17 02:00 | 36261 | 6139.0847 | 174610.1614 | 59.77 | 725.22
2016-12-17 03:00 | 36554 | 5362.3634 | 174610.1614 | 59.77 | 731.08
2016-12-17 04:00 | 37704 | 4724.676 | 176931.176 | 59.78 | 716.376
2016-12-17 05:00 | 40566 | 4015.0653 | 192816.412 | 59.78 | 770.754
2016-12-17 06:00 | 45256 | 3115.1925 | 225844.4004 | 59.77 | 905.12
2016-12-17 07:00 | 46608 | 3567.8798 | 227443.3435 | 59.78 | 885.552
2016-12-17 08:00 | 45737 | 4533.9869 | 225844.4004 | 59.77 | 914.74
2016-12-17 09:00 | 45340 | 5418.8622 | 226993.2924 | 59.77 | 906.8
2016-12-17 10:00 | 44790 | 5215.7635 | 226993.2924 | 59.77 | 895.8
2016-12-17 11:00 | 43993 | 3539.7476 | 226993.2924 | 59.77 | 879.86
2016-12-17 12:00 | 43070 | 2685.0818 | 226993.2924 | 59.77 | 861.4
2016-12-17 13:00 | 42361 | 1660.1358 | 224112.8964 | 59.77 | 847.22
2016-12-17 14:00 | 41820 | 1666.6763 | 223521.8884 | 59.77 | 836.4
2016-12-17 15:00 | 41917 | 1643.5992 | 223521.8884 | 59.77 | 838.34
2016-12-17 16:00 | 42672 | 1736.5328 | 223521.8884 | 59.77 | 853.44
2016-12-17 17:00 | 45387 | 2179.0301 | 224537.8884 | 59.78 | 862.353
2016-12-17 18:00 | 46270 | 2944.5059 | 225961.4884 | 59.78 | 879.13
2016-12-17 19:00 | 47153 | 3071.6212 | 227560.4315 | 59.78 | 895.907
2016-12-17 20:00 | 46723 | 3268.6874 | 226385.4884 | 59.78 | 887.737
2016-12-17 21:00 | 45788 | 3370.4954 | 218089.1384 | 59.77 | 915.76
2016-12-17 22:00 | 44021 | 2964.8825 | 213600.8484 | 59.77 | 880.42
2016-12-17 23:00 | 41885 | 3023.9814 | 213600.8484 | 59.77 | 837.7
2016-12-18 | 42090 | 3602.7508 | 210500.3384 | 59.77 | 841.8
2016-12-18 01:00 | 42174 | 3555.0013 | 210500.3384 | 59.77 | 843.48
2016-12-18 02:00 | 41832 | 3701.5492 | 210500.3384 | 59.77 | 836.64
2016-12-18 03:00 | 42055 | 4020.7171 | 210500.3384 | 59.77 | 841.1
2016-12-18 04:00 | 42837 | 4166.4379 | 210500.3384 | 59.77 | 856.74
2016-12-18 05:00 | 44449 | 4483.5404 | 210500.3384 | 59.77 | 888.98
2016-12-18 06:00 | 46933 | 4256.1707 | 224974.9784 | 59.78 | 891.727
2016-12-18 07:00 | 48979 | 4768.5895 | 236178.2499 | 59.78 | 930.601
2016-12-18 08:00 | 49778 | 5662.9209 | 234377.6184 | 59.78 | 945.782
2016-12-18 09:00 | 49022 | 6085.1992 | 233205.0219 | 59.78 | 931.418
2016-12-18 10:00 | 47178 | 4428.6729 | 233205.0219 | 59.78 | 896.382
2016-12-18 11:00 | 45079 | 4656.2736 | 228618.0884 | 59.77 | 901.58
2016-12-18 12:00 | 43098 | 4321.1101 | 228618.0884 | 59.77 | 861.96
2016-12-18 13:00 | 41455 | 3133.6848 | 231498.4844 | 59.77 | 829.1
2016-12-18 14:00 | 40272 | 2333.1939 | 232089.4924 | 59.77 | 805.44
2016-12-18 15:00 | 39706 | 1736.651 | 232089.4924 | 59.77 | 794.12
2016-12-18 16:00 | 40083 | 1470.1494 | 232089.4924 | 59.77 | 801.66
2016-12-18 17:00 | 43068 | 1475.4898 | 232089.4924 | 59.77 | 861.36
2016-12-18 18:00 | 45083 | 2552.7417 | 233105.4924 | 59.78 | 856.577
2016-12-18 19:00 | 47097 | 5755.8877 | 229313.543 | 59.77 | 941.94
2016-12-18 20:00 | 47378 | 9109.3213 | 211849.567 | 59.77 | 947.56
2016-12-18 21:00 | 47071 | 9662.3505 | 205662.909 | 59.78 | 894.349
2016-12-18 22:00 | 45911 | 9193.2784 | 205662.909 | 59.78 | 872.309
2016-12-18 23:00 | 44230 | 9088.8887 | 195066.7606 | 59.78 | 840.37
2016-12-19 | 43414 | 9311.8522 | 197418.9206 | 59.78 | 824.866
2016-12-19 01:00 | 42455 | 9265.2795 | 197130.9206 | 59.78 | 806.645
2016-12-19 02:00 | 42149 | 9546.8037 | 197130.9206 | 59.78 | 800.831
2016-12-19 03:00 | 42172 | 9593.353 | 197130.9206 | 59.78 | 801.268
2016-12-19 04:00 | 42576 | 9327.654 | 197130.9206 | 59.78 | 808.944
2016-12-19 05:00 | 43662 | 9126.9169 | 198003.031 | 59.78 | 829.578
2016-12-19 06:00 | 45297 | 8768.1965 | 201269.031 | 59.78 | 860.643
2016-12-19 07:00 | 46635 | 9129.8582 | 207987.2849 | 59.77 | 932.7
2016-12-19 08:00 | 47392 | 9431.7554 | 207694.5129 | 59.77 | 947.84
2016-12-19 09:00 | 46536 | 9687.5019 | 197588.1129 | 59.78 | 884.184
2016-12-19 10:00 | 44707 | 7913.4689 | 197588.1129 | 59.78 | 849.433
2016-12-19 11:00 | 42957 | 5435.0566 | 200262.6464 | 59.77 | 859.14
2016-12-19 12:00 | 41638 | 4846.8724 | 198743.6464 | 59.78 | 791.122
2016-12-19 13:00 | 40566 | 5045.5319 | 195387.2464 | 59.78 | 770.754
2016-12-19 14:00 | 39679 | 5029.5199 | 193483.2464 | 59.78 | 753.901
2016-12-19 15:00 | 39310 | 5370.0018 | 193483.2464 | 59.78 | 746.89
2016-12-19 16:00 | 39700 | 5860.8031 | 193483.2464 | 59.78 | 754.3
2016-12-19 17:00 | 42418 | 6334.5409 | 193483.2464 | 59.78 | 805.942
2016-12-19 18:00 | 44265 | 7628.7668 | 193483.2464 | 59.78 | 841.035
2016-12-19 19:00 | 46112 | 9112.7524 | 195937.6464 | 59.78 | 876.128
2016-12-19 20:00 | 45904 | 10148.3141 | 187097.266 | 59.78 | 872.176
2016-12-19 21:00 | 44854 | 11077.4889 | 173177.138 | 59.78 | 852.226
2016-12-19 22:00 | 42815 | 10398.9831 | 164715.668 | 59.77 | 856.3
2016-12-19 23:00 | 40108 | 10993.2829 | 145887.9236 | 59.77 | 802.16
2016-12-20 | 36348 | 11656.7925 | 141889.0536 | 59.79 | 654.264
2016-12-20 01:00 | 35328 | 11840.501 | 141313.7536 | 59.79 | 635.904
2016-12-20 02:00 | 34843 | 11879.5784 | 137729.4836 | 59.79 | 627.174
2016-12-20 03:00 | 34808 | 11910.9061 | 137729.4836 | 59.79 | 626.544
2016-12-20 04:00 | 35502 | 11914.6961 | 137729.4836 | 59.79 | 639.036
2016-12-20 05:00 | 37640 | 11602.6948 | 144842.4436 | 59.79 | 677.52
2016-12-20 06:00 | 40651 | 11109.4847 | 144842.4436 | 59.77 | 813.02
2016-12-20 07:00 | 41990 | 11490.4425 | 144842.4436 | 59.77 | 839.8
2016-12-20 08:00 | 42325 | 11705.7831 | 145858.4436 | 59.77 | 846.5
2016-12-20 09:00 | 42645 | 13051.2609 | 144842.4436 | 59.77 | 852.9
2016-12-20 10:00 | 42670 | 12145.8999 | 144842.4436 | 59.77 | 853.4
2016-12-20 11:00 | 42518 | 11996.4239 | 144842.4436 | 59.77 | 850.36
2016-12-20 12:00 | 42340 | 11890.5978 | 146361.4436 | 59.77 | 846.8
2016-12-20 13:00 | 42385 | 11894.9199 | 146361.4436 | 59.77 | 847.7
2016-12-20 14:00 | 42378 | 11699.2929 | 148265.4436 | 59.77 | 847.56
2016-12-20 15:00 | 42289 | 11163.643 | 148265.4436 | 59.77 | 845.78
2016-12-20 16:00 | 42160 | 11596.2073 | 148265.4436 | 59.77 | 843.2
2016-12-20 17:00 | 43589 | 11073.3437 | 154282.7136 | 59.78 | 828.191
2016-12-20 18:00 | 44670 | 10881.0482 | 159144.3302 | 59.78 | 848.73
2016-12-20 19:00 | 45751 | 12229.68 | 158906.0336 | 59.78 | 869.269
2016-12-20 20:00 | 44781 | 13081.7439 | 157890.0336 | 59.77 | 895.62
2016-12-20 21:00 | 43420 | 13812.8555 | 149722.4336 | 59.77 | 868.4
2016-12-20 22:00 | 40932 | 13753.9183 | 145912.6336 | 59.79 | 736.776
2016-12-20 23:00 | 37837 | 12271.8195 | 145361.9461 | 59.79 | 681.066
2016-12-21 | 34772 | 11567.8579 | 140295.7061 | 59.79 | 625.896
2016-12-21 01:00 | 33427 | 10795.7732 | 141159.0061 | 59.79 | 601.686
2016-12-21 02:00 | 32719 | 9455.6539 | 141159.0061 | 59.79 | 588.942
2016-12-21 03:00 | 32332 | 9239.2502 | 141159.0061 | 59.79 | 581.976
2016-12-21 04:00 | 32854 | 9214.3549 | 141159.0061 | 59.79 | 591.372
2016-12-21 05:00 | 34523 | 8957.5772 | 143159.7561 | 59.79 | 621.414
2016-12-21 06:00 | 37329 | 8714.8587 | 143159.7561 | 59.77 | 746.58
2016-12-21 07:00 | 38963 | 9615.2112 | 143159.7561 | 59.77 | 779.26
2016-12-21 08:00 | 39840 | 10445.1723 | 143159.7561 | 59.77 | 796.8
2016-12-21 09:00 | 40975 | 11169.1855 | 143159.7561 | 59.77 | 819.5
2016-12-21 10:00 | 41829 | 10097.5119 | 150189.4761 | 59.77 | 836.58
2016-12-21 11:00 | 42289 | 8235.1371 | 165337.0925 | 59.78 | 803.491
2016-12-21 12:00 | 42699 | 6810.5694 | 173829.8705 | 59.78 | 811.281
2016-12-21 13:00 | 43419 | 5948.5484 | 185528.0105 | 59.78 | 824.961
2016-12-21 14:00 | 43857 | 5861.1619 | 191963.9065 | 59.77 | 877.14
2016-12-21 15:00 | 44093 | 5192.4701 | 198560.4065 | 59.77 | 881.86
2016-12-21 16:00 | 43830 | 4528.4341 | 198560.4065 | 59.77 | 876.6
2016-12-21 17:00 | 44503 | 4169.8475 | 202932.8065 | 59.77 | 890.06
2016-12-21 18:00 | 45062 | 4876.903 | 202372.8065 | 59.77 | 901.24
2016-12-21 19:00 | 45621 | 5211.1013 | 202932.8065 | 59.77 | 912.42
2016-12-21 20:00 | 44474 | 5639.3011 | 194837.1965 | 59.77 | 889.48
2016-12-21 21:00 | 42990 | 5275.8706 | 190358.7965 | 59.77 | 859.8
2016-12-21 22:00 | 40345 | 4803.453 | 175461.4305 | 59.78 | 766.555
2016-12-21 23:00 | 37282 | 3992.4172 | 164395.13 | 59.78 | 708.358
2016-12-22 | 33013 | 3273.18 | 150572.8736 | 59.77 | 660.26
2016-12-22 01:00 | 31783 | 3235.0115 | 150572.8736 | 59.77 | 635.66
2016-12-22 02:00 | 31199 | 3003.7799 | 150572.8736 | 59.77 | 623.98
2016-12-22 03:00 | 31069 | 4173.6987 | 150446.3936 | 59.79 | 559.242
2016-12-22 04:00 | 31657 | 6018.6996 | 150446.3936 | 59.79 | 569.826
2016-12-22 05:00 | 33460 | 5655.9328 | 150446.3936 | 59.77 | 669.2
2016-12-22 06:00 | 36566 | 5709.1701 | 146761.2736 | 59.77 | 731.32
2016-12-22 07:00 | 38484 | 5456.9572 | 157977.21 | 59.78 | 731.196
2016-12-22 08:00 | 39386 | 5315.5364 | 167501.418 | 59.78 | 748.334
2016-12-22 09:00 | 40274 | 5425.8783 | 171486.2222 | 59.78 | 765.206
2016-12-22 10:00 | 40740 | 4923.4668 | 174835.3122 | 59.78 | 774.06
2016-12-22 11:00 | 40929 | 4244.2887 | 181188.0832 | 59.78 | 777.651
2016-12-22 12:00 | 40667 | 3559.5087 | 184660.3732 | 59.78 | 772.673
2016-12-22 13:00 | 40494 | 3690.1194 | 184660.3732 | 59.78 | 769.386
2016-12-22 14:00 | 40299 | 4031.036 | 184660.3732 | 59.78 | 765.681
2016-12-22 15:00 | 40216 | 4279.1127 | 184660.3732 | 59.78 | 764.104
2016-12-22 16:00 | 40380 | 4547.8437 | 184660.3732 | 59.78 | 767.22
2016-12-22 17:00 | 42123 | 4093.9166 | 191256.8732 | 59.77 | 842.46
2016-12-22 18:00 | 42787 | 4657.4588 | 191256.8732 | 59.77 | 855.74
2016-12-22 19:00 | 43450 | 6025.3343 | 187900.4732 | 59.78 | 825.55
2016-12-22 20:00 | 42766 | 7287.0235 | 177992.2872 | 59.78 | 812.554
2016-12-22 21:00 | 41693 | 7233.053 | 172858.5908 | 59.78 | 792.167
2016-12-22 22:00 | 39532 | 5776.2723 | 167792.3508 | 59.78 | 751.108
2016-12-22 23:00 | 37062 | 4879.0198 | 167792.3508 | 59.77 | 741.24
2016-12-23 | 35459 | 3830.4697 | 167792.3508 | 59.77 | 709.18
2016-12-23 01:00 | 34175 | 3136.7945 | 167792.3508 | 59.77 | 683.5
2016-12-23 02:00 | 33431 | 2618.3684 | 167792.3508 | 59.77 | 668.62
2016-12-23 03:00 | 33190 | 2331.1472 | 167918.8308 | 59.77 | 663.8
2016-12-23 04:00 | 33745 | 1848.9156 | 167918.8308 | 59.77 | 674.9
2016-12-23 05:00 | 35334 | 1689.0432 | 172632.8508 | 59.78 | 671.346
2016-12-23 06:00 | 37622 | 1645.4626 | 179940.2908 | 59.78 | 714.818
2016-12-23 07:00 | 39112 | 1800.272 | 190140.2272 | 59.78 | 743.128
2016-12-23 08:00 | 40086 | 2066.8921 | 195280.5252 | 59.77 | 801.72
2016-12-23 09:00 | 41194 | 1837.2166 | 200660.771 | 59.77 | 823.88
2016-12-23 10:00 | 41616 | 2659.3635 | 199644.771 | 59.77 | 832.32
2016-12-23 11:00 | 41444 | 4259.063 | 189524.076 | 59.78 | 787.436
2016-12-23 12:00 | 40775 | 5959.6335 | 186174.986 | 59.78 | 774.725
2016-12-23 13:00 | 40276 | 6822.5909 | 182702.696 | 59.78 | 765.244
2016-12-23 14:00 | 39799 | 7621.0161 | 182702.696 | 59.77 | 795.98
2016-12-23 15:00 | 39464 | 7899.1511 | 180315.196 | 59.77 | 789.28
2016-12-23 16:00 | 39574 | 6387.6942 | 180315.196 | 59.78 | 751.906
2016-12-23 17:00 | 41625 | 6684.3088 | 180315.196 | 59.78 | 790.875
2016-12-23 18:00 | 42234 | 7005.3003 | 180315.196 | 59.78 | 802.446
2016-12-23 19:00 | 42842 | 7440.3637 | 180315.196 | 59.78 | 813.998
2016-12-23 20:00 | 42218 | 7672.7765 | 180315.196 | 59.78 | 802.142
2016-12-23 21:00 | 41157 | 5778.2904 | 180315.196 | 59.78 | 781.983
2016-12-23 22:00 | 39395 | 5072.484 | 173841.856 | 59.78 | 748.505
2016-12-23 23:00 | 37068 | 4501.3043 | 170642.63 | 59.78 | 704.292
2016-12-24 | 36551 | 3944.2281 | 170642.63 | 59.78 | 694.469
2016-12-24 01:00 | 35188 | 3461.073 | 168730.23 | 59.77 | 703.76
2016-12-24 02:00 | 34366 | 3328.6193 | 166841.28 | 59.77 | 687.32
2016-12-24 03:00 | 34044 | 3794.4964 | 166841.28 | 59.77 | 680.88
2016-12-24 04:00 | 34345 | 4666.9047 | 166841.28 | 59.77 | 686.9
2016-12-24 05:00 | 35314 | 5040.8775 | 166841.28 | 59.77 | 706.28
2016-12-24 06:00 | 36940 | 4558.9275 | 166841.28 | 59.77 | 738.8
2016-12-24 07:00 | 38153 | 4586.0958 | 173797.69 | 59.78 | 724.907
2016-12-24 08:00 | 39600 | 5234.8381 | 178292.514 | 59.78 | 752.4
2016-12-24 09:00 | 41361 | 5758.3903 | 182545.184 | 59.78 | 785.859
2016-12-24 10:00 | 42372 | 6664.3136 | 181529.184 | 59.78 | 805.068
2016-12-24 11:00 | 42832 | 7768.8323 | 181529.184 | 59.78 | 813.808
2016-12-24 12:00 | 42849 | 9509.0767 | 181529.184 | 59.78 | 814.131
2016-12-24 13:00 | 42782 | 9886.7405 | 181529.184 | 59.78 | 812.858
2016-12-24 14:00 | 42736 | 10424.9382 | 180837.584 | 59.77 | 854.72
2016-12-24 15:00 | 42628 | 10154.9686 | 183225.084 | 59.77 | 852.56
2016-12-24 16:00 | 42863 | 10458.5834 | 183225.084 | 59.77 | 857.26
2016-12-24 17:00 | 44425 | 10210.5534 | 183225.084 | 59.78 | 844.075
2016-12-24 18:00 | 44309 | 9130.7198 | 188831.484 | 59.78 | 841.871
2016-12-24 19:00 | 44194 | 7001.8408 | 188831.484 | 59.78 | 839.686
2016-12-24 20:00 | 43436 | 5113.1908 | 193353.984 | 59.77 | 868.72
2016-12-24 21:00 | 42626 | 4870.5226 | 193177.984 | 59.77 | 852.52
2016-12-24 22:00 | 41604 | 5137.2601 | 185529.4632 | 59.78 | 790.476
2016-12-24 23:00 | 40349 | 4870.2125 | 181922.1432 | 59.78 | 766.631
2016-12-25 | 39717 | 5706.4436 | 173460.6732 | 59.78 | 754.623
2016-12-25 01:00 | 39046 | 7504.6283 | 173460.6732 | 59.77 | 780.92
2016-12-25 02:00 | 38741 | 8122.2979 | 175349.6232 | 59.77 | 774.82
2016-12-25 03:00 | 38750 | 7950.8853 | 175349.6232 | 59.77 | 775
2016-12-25 04:00 | 39221 | 8223.0965 | 174486.3232 | 59.77 | 784.42
2016-12-25 05:00 | 40296 | 8278.1829 | 174486.3232 | 59.77 | 805.92
2016-12-25 06:00 | 41886 | 8520.2256 | 174486.3232 | 59.78 | 795.834
2016-12-25 07:00 | 43641 | 7909.3659 | 174486.3232 | 59.78 | 829.179
2016-12-25 08:00 | 45366 | 7337.6132 | 187163.0192 | 59.77 | 907.32
2016-12-25 09:00 | 46612 | 8910.197 | 186707.0192 | 59.77 | 932.24
2016-12-25 10:00 | 46985 | 10662.6588 | 186147.0192 | 59.78 | 892.715
2016-12-25 11:00 | 46672 | 8916.3797 | 186147.0192 | 59.77 | 933.44
2016-12-25 12:00 | 45485 | 8444.6883 | 186147.0192 | 59.78 | 864.215
2016-12-25 13:00 | 43812 | 9052.5427 | 186147.0192 | 59.78 | 832.428
2016-12-25 14:00 | 42345 | 7996.5023 | 186838.6192 | 59.78 | 804.555
2016-12-25 15:00 | 41461 | 7496.7708 | 186838.6192 | 59.78 | 787.759
2016-12-25 16:00 | 41663 | 7095.8645 | 186838.6192 | 59.78 | 791.597
2016-12-25 17:00 | 44248 | 5916.6098 | 192358.3392 | 59.77 | 884.96
2016-12-25 18:00 | 46276 | 4882.245 | 212410.3692 | 59.77 | 925.52
2016-12-25 19:00 | 48304 | 4479.6204 | 225256.5176 | 59.78 | 917.776
2016-12-25 20:00 | 48778 | 4121.3622 | 232691.3376 | 59.78 | 926.782
2016-12-25 21:00 | 48790 | 4612.8426 | 232691.3376 | 59.78 | 927.01
2016-12-25 22:00 | 48185 | 4922.3922 | 231464.3624 | 59.78 | 915.515
2016-12-25 23:00 | 46859 | 3883.8786 | 231464.3624 | 59.78 | 890.321
2016-12-26 | 47197 | 3644.1938 | 229828.6838 | 59.78 | 896.743
2016-12-26 01:00 | 47598 | 3997.1301 | 229828.6838 | 59.78 | 904.362
2016-12-26 02:00 | 47443 | 3881.2066 | 229828.6838 | 59.78 | 901.417
2016-12-26 03:00 | 47913 | 3802.4478 | 233834.2318 | 59.78 | 910.347
2016-12-26 04:00 | 48756 | 4174.8721 | 244301.394 | 59.78 | 926.364
2016-12-26 05:00 | 50036 | 4242.0583 | 252457.424 | 59.78 | 950.684
2016-12-26 06:00 | 51942 | 4348.6562 | 259727.912 | 59.76 | 1090.782
2016-12-26 07:00 | 53302 | 4227.2128 | 269914.117 | 59.76 | 1119.342
2016-12-26 08:00 | 53663 | 4119.057 | 270930.117 | 59.76 | 1126.923
2016-12-26 09:00 | 52847 | 3854.9403 | 266778.207 | 59.76 | 1109.787
2016-12-26 10:00 | 51018 | 3148.2465 | 265440.6576 | 59.76 | 1071.378
2016-12-26 11:00 | 48719 | 2306.5984 | 254469.9907 | 59.78 | 925.661
2016-12-26 12:00 | 46601 | 2522.0219 | 244866.1285 | 59.78 | 885.419
2016-12-26 13:00 | 44581 | 3045.9946 | 234316.8685 | 59.77 | 891.62
2016-12-26 14:00 | 43018 | 3630.2779 | 234316.8685 | 59.77 | 860.36
2016-12-26 15:00 | 42177 | 4588.2574 | 234129.6685 | 59.77 | 843.54
2016-12-26 16:00 | 42569 | 5306.4223 | 234129.6685 | 59.78 | 808.811
2016-12-26 17:00 | 46126 | 5154.4162 | 234129.6685 | 59.77 | 922.52
2016-12-26 18:00 | 49368 | 6690.3388 | 234129.6685 | 59.78 | 937.992
2016-12-26 19:00 | 52609 | 8976.3544 | 232797.3185 | 59.78 | 999.571
2016-12-26 20:00 | 53452 | 11145.362 | 226917.3585 | 59.77 | 1069.04
2016-12-26 21:00 | 53577 | 11952.9278 | 221817.1135 | 59.77 | 1071.54
2016-12-26 22:00 | 52228 | 11262.0272 | 219236.2255 | 59.77 | 1044.56
2016-12-26 23:00 | 50449 | 10940.0114 | 209249.8755 | 59.77 | 1008.98
2016-12-27 | 45263 | 10626.9279 | 210191.1035 | 59.78 | 859.997
2016-12-27 01:00 | 44842 | 10212.8791 | 210191.1035 | 59.78 | 851.998
2016-12-27 02:00 | 44883 | 10382.306 | 210191.1035 | 59.78 | 852.777
2016-12-27 03:00 | 45338 | 10443.4402 | 210191.1035 | 59.78 | 861.422
2016-12-27 04:00 | 46534 | 11129.8719 | 210191.1035 | 59.78 | 884.146
2016-12-27 05:00 | 49043 | 11322.4069 | 212584.3335 | 59.77 | 980.86
2016-12-27 06:00 | 51892 | 10807.5919 | 214549.9255 | 59.77 | 1037.84
2016-12-27 07:00 | 53409 | 10872.7334 | 216148.8686 | 59.78 | 1014.771
2016-12-27 08:00 | 53054 | 11127.3771 | 215285.9255 | 59.77 | 1061.08
2016-12-27 09:00 | 51723 | 10866.8672 | 210522.1239 | 59.77 | 1034.46
2016-12-27 10:00 | 50081 | 10261.6328 | 210522.1239 | 59.77 | 1001.62
2016-12-27 11:00 | 48063 | 9132.2233 | 213654.5228 | 59.77 | 961.26
2016-12-27 12:00 | 45970 | 8461.5389 | 213654.5228 | 59.77 | 919.4
2016-12-27 13:00 | 44353 | 6209.9993 | 211333.5082 | 59.77 | 887.06
2016-12-27 14:00 | 42932 | 5315.9277 | 211333.5082 | 59.77 | 858.64
2016-12-27 15:00 | 42398 | 5061.7189 | 211216.6282 | 59.78 | 805.562
2016-12-27 16:00 | 43056 | 4174.7589 | 211216.6282 | 59.77 | 861.12
2016-12-27 17:00 | 45921 | 4325.0756 | 216104.5382 | 59.77 | 918.42
2016-12-27 18:00 | 47124 | 5238.8408 | 215551.4813 | 59.77 | 942.48
2016-12-27 19:00 | 48328 | 7529.6653 | 210137.1778 | 59.77 | 966.56
2016-12-27 20:00 | 47531 | 9365.6863 | 191187.7078 | 59.77 | 950.62
2016-12-27 21:00 | 46238 | 9314.6986 | 185369.8118 | 59.78 | 878.522
2016-12-27 22:00 | 43718 | 8917.0161 | 180349.3238 | 59.78 | 830.642
2016-12-27 23:00 | 40997 | 7822.8213 | 180349.3238 | 59.78 | 778.943
2016-12-28 | 39929 | 7284.3913 | 176742.0038 | 59.78 | 758.651
2016-12-28 01:00 | 38668 | 6464.2894 | 176742.0038 | 59.77 | 773.36
2016-12-28 02:00 | 37972 | 5856.976 | 176742.0038 | 59.77 | 759.44
2016-12-28 03:00 | 37780 | 5353.1638 | 176742.0038 | 59.77 | 755.6
2016-12-28 04:00 | 38360 | 4499.7127 | 176742.0038 | 59.78 | 728.84
2016-12-28 05:00 | 40229 | 3915.7868 | 185704.8038 | 59.78 | 764.351
2016-12-28 06:00 | 42733 | 3615.4086 | 200161.7778 | 59.77 | 854.66
2016-12-28 07:00 | 44223 | 4170.5292 | 208015.4882 | 59.77 | 884.46
2016-12-28 08:00 | 44968 | 4626.8416 | 210107.6762 | 59.77 | 899.36
2016-12-28 09:00 | 45714 | 4793.8234 | 217193.5398 | 59.77 | 914.28
2016-12-28 10:00 | 46187 | 4857.741 | 217193.5398 | 59.77 | 923.74
2016-12-28 11:00 | 46229 | 4484.3991 | 217193.5398 | 59.77 | 924.58
2016-12-28 12:00 | 45526 | 5070.826 | 217193.5398 | 59.77 | 910.52
2016-12-28 13:00 | 44975 | 5475.5776 | 219514.5544 | 59.77 | 899.5
2016-12-28 14:00 | 44302 | 5489.072 | 219514.5544 | 59.77 | 886.04
2016-12-28 15:00 | 44012 | 4827.8648 | 219631.4344 | 59.77 | 880.24
2016-12-28 16:00 | 44326 | 4469.2526 | 219631.4344 | 59.77 | 886.52
2016-12-28 17:00 | 46442 | 4639.8905 | 219631.4344 | 59.77 | 928.84
2016-12-28 18:00 | 46918 | 5443.6853 | 218878.4844 | 59.77 | 938.36
2016-12-28 19:00 | 47394 | 5979.5757 | 218878.4844 | 59.77 | 947.88
2016-12-28 20:00 | 46322 | 6602.8213 | 206032.336 | 59.77 | 926.44
2016-12-28 21:00 | 44430 | 6297.5234 | 193795.666 | 59.77 | 888.6
2016-12-28 22:00 | 41696 | 6482.4698 | 174924.68 | 59.78 | 792.224
2016-12-28 23:00 | 38934 | 6533.3447 | 159764.55 | 59.77 | 778.68
2016-12-29 | 35274 | 6224.1971 | 144616.9336 | 59.77 | 705.48
2016-12-29 01:00 | 33933 | 7255.4832 | 142704.5336 | 59.79 | 610.794
2016-12-29 02:00 | 33224 | 8291.2528 | 142704.5336 | 59.79 | 598.032
2016-12-29 03:00 | 32928 | 8952.8036 | 142704.5336 | 59.79 | 592.704
2016-12-29 04:00 | 33234 | 9038.2281 | 142704.5336 | 59.79 | 598.212
2016-12-29 05:00 | 34732 | 9777.7734 | 142704.5336 | 59.79 | 625.176
2016-12-29 06:00 | 36982 | 9308.4037 | 142704.5336 | 59.77 | 739.64
2016-12-29 07:00 | 38444 | 9827.6905 | 142704.5336 | 59.77 | 768.88
2016-12-29 08:00 | 38983 | 10300.7237 | 142704.5336 | 59.77 | 779.66
2016-12-29 09:00 | 39868 | 10776.9728 | 142704.5336 | 59.77 | 797.36
2016-12-29 10:00 | 40404 | 11056.8782 | 142704.5336 | 59.77 | 808.08
2016-12-29 11:00 | 40597 | 10939.3084 | 142704.5336 | 59.77 | 811.94
2016-12-29 12:00 | 40370 | 11719.2379 | 139120.2636 | 59.77 | 807.4
2016-12-29 13:00 | 40023 | 12234.3757 | 139120.2636 | 59.77 | 800.46
2016-12-29 14:00 | 39811 | 12437.5763 | 139120.2636 | 59.79 | 716.598
2016-12-29 15:00 | 39575 | 12634.4259 | 139120.2636 | 59.79 | 712.35
2016-12-29 16:00 | 39605 | 12092.2239 | 139120.2636 | 59.77 | 792.1
2016-12-29 17:00 | 40751 | 11710.8416 | 139120.2636 | 59.77 | 815.02
2016-12-29 18:00 | 41451 | 12139.7246 | 139432.4436 | 59.77 | 829.02
2016-12-29 19:00 | 42151 | 13135.3117 | 138283.5516 | 59.77 | 843.02
2016-12-29 20:00 | 41285 | 13770.237 | 135063.6316 | 59.77 | 825.7
2016-12-29 21:00 | 39862 | 14626.4309 | 128033.9116 | 59.79 | 717.516
2016-12-29 22:00 | 37815 | 14483.6026 | 128107.7307 | 59.79 | 680.67
2016-12-29 23:00 | 35432 | 14512.9123 | 130958.6347 | 59.79 | 637.776
2016-12-30 | 33408 | 13823.6282 | 127474.9187 | 59.79 | 601.344
2016-12-30 01:00 | 32214 | 13310.0198 | 127474.9187 | 59.79 | 579.852
2016-12-30 02:00 | 31548 | 12661.3889 | 127474.9187 | 59.79 | 567.864
2016-12-30 03:00 | 31320 | 11928.4974 | 127535.9147 | 59.79 | 563.76
2016-12-30 04:00 | 31724 | 11017.2058 | 131798.4787 | 59.79 | 571.032
2016-12-30 05:00 | 33173 | 11108.863 | 132848.9479 | 59.79 | 597.114
2016-12-30 06:00 | 35363 | 11189.6629 | 130937.1967 | 59.79 | 636.534
2016-12-30 07:00 | 36679 | 12273.2317 | 130621.4407 | 59.79 | 660.222
2016-12-30 08:00 | 37388 | 13064.3441 | 130621.4407 | 59.79 | 672.984
2016-12-30 09:00 | 38299 | 14564.3361 | 130538.3157 | 59.79 | 689.382
2016-12-30 10:00 | 39020 | 14088.6743 | 128083.9157 | 59.79 | 702.36
2016-12-30 11:00 | 39240 | 12824.3004 | 135113.6357 | 59.79 | 706.32
2016-12-30 12:00 | 39156 | 12653.16 | 135113.6357 | 59.79 | 704.808
2016-12-30 13:00 | 39097 | 12319.1379 | 135113.6357 | 59.79 | 703.746
2016-12-30 14:00 | 38873 | 12239.0239 | 135113.6357 | 59.79 | 699.714
2016-12-30 15:00 | 38622 | 11923.0622 | 135113.6357 | 59.79 | 695.196
2016-12-30 16:00 | 38478 | 11873.1912 | 135113.6357 | 59.79 | 692.604
2016-12-30 17:00 | 39752 | 11355.4208 | 138333.5557 | 59.77 | 795.04
2016-12-30 18:00 | 40629 | 12415.2555 | 139910.3257 | 59.77 | 812.58
2016-12-30 19:00 | 41507 | 13643.8283 | 141059.2177 | 59.77 | 830.14
2016-12-30 20:00 | 40770 | 13557.417 | 137249.4177 | 59.79 | 733.86
2016-12-30 21:00 | 39566 | 14126.7139 | 134029.4977 | 59.79 | 712.188
2016-12-30 22:00 | 37827 | 14850.7045 | 134029.4977 | 59.79 | 680.886
2016-12-30 23:00 | 35548 | 12475.2791 | 134029.4977 | 59.79 | 639.864

## Current_2016_NSRS
NSRS Requirement in Plexos
2016-01-01 |  | 2016-02-01 |  | 2016-03-01 |  | 2016-04-01 |  | 2016-05-01 |  | 2016-06-01 |  | 2016-07-01 |  | 2016-08-01 |  | 2016-09-01 |  | 2016-10-01 |  | 2016-11-01 |  | 2016-12-01
IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement | IE | NSRS Requirement
1 | 1864 | 1 | 2000 | 1 | 1903 | 1 | 2000 | 1 | 2000 | 1 | 2000 | 1 | 1278 | 1 | 1571 | 1 | 1719 | 1 | 1903 | 1 | 2000 | 1 | 2000
2 | 1864 | 2 | 2000 | 2 | 1903 | 2 | 2000 | 2 | 2000 | 2 | 2000 | 2 | 1278 | 2 | 1571 | 2 | 1719 | 2 | 1903 | 2 | 2000 | 2 | 2000
3 | 1687 | 3 | 2000 | 3 | 2000 | 3 | 2000 | 3 | 2000 | 3 | 2000 | 3 | 1889 | 3 | 1967 | 3 | 1994 | 3 | 2000 | 3 | 2000 | 3 | 2000
4 | 1687 | 4 | 2000 | 4 | 2000 | 4 | 2000 | 4 | 2000 | 4 | 2000 | 4 | 1889 | 4 | 1967 | 4 | 1994 | 4 | 2000 | 4 | 2000 | 4 | 2000
5 | 1687 | 5 | 2000 | 5 | 2000 | 5 | 2000 | 5 | 2000 | 5 | 2000 | 5 | 1889 | 5 | 1967 | 5 | 1994 | 5 | 2000 | 5 | 2000 | 5 | 2000
6 | 1687 | 6 | 2000 | 6 | 2000 | 6 | 2000 | 6 | 2000 | 6 | 2000 | 6 | 1889 | 6 | 1967 | 6 | 1994 | 6 | 2000 | 6 | 2000 | 6 | 2000
7 | 1938 | 7 | 2000 | 7 | 2000 | 7 | 2000 | 7 | 2000 | 7 | 2000 | 7 | 1665 | 7 | 1988 | 7 | 1713 | 7 | 2000 | 7 | 2000 | 7 | 2000
8 | 1938 | 8 | 2000 | 8 | 2000 | 8 | 2000 | 8 | 2000 | 8 | 2000 | 8 | 1665 | 8 | 1988 | 8 | 1713 | 8 | 2000 | 8 | 2000 | 8 | 2000
9 | 1938 | 9 | 2000 | 9 | 2000 | 9 | 2000 | 9 | 2000 | 9 | 2000 | 9 | 1665 | 9 | 1988 | 9 | 1713 | 9 | 2000 | 9 | 2000 | 9 | 2000
10 | 1938 | 10 | 2000 | 10 | 2000 | 10 | 2000 | 10 | 2000 | 10 | 2000 | 10 | 1665 | 10 | 1988 | 10 | 1713 | 10 | 2000 | 10 | 2000 | 10 | 2000
11 | 1962 | 11 | 2000 | 11 | 2000 | 11 | 2000 | 11 | 1928 | 11 | 2000 | 11 | 1644 | 11 | 1908 | 11 | 1652 | 11 | 2000 | 11 | 2000 | 11 | 2000
12 | 1962 | 12 | 2000 | 12 | 2000 | 12 | 2000 | 12 | 1928 | 12 | 2000 | 12 | 1644 | 12 | 1908 | 12 | 1652 | 12 | 2000 | 12 | 2000 | 12 | 2000
13 | 1962 | 13 | 2000 | 13 | 2000 | 13 | 2000 | 13 | 1928 | 13 | 2000 | 13 | 1644 | 13 | 1908 | 13 | 1652 | 13 | 2000 | 13 | 2000 | 13 | 2000
14 | 1962 | 14 | 2000 | 14 | 2000 | 14 | 2000 | 14 | 1928 | 14 | 2000 | 14 | 1644 | 14 | 1908 | 14 | 1652 | 14 | 2000 | 14 | 2000 | 14 | 2000
15 | 2000 | 15 | 2000 | 15 | 2000 | 15 | 1884 | 15 | 2000 | 15 | 2000 | 15 | 2000 | 15 | 2000 | 15 | 2000 | 15 | 2000 | 15 | 1985 | 15 | 2000
16 | 2000 | 16 | 2000 | 16 | 2000 | 16 | 1884 | 16 | 2000 | 16 | 2000 | 16 | 2000 | 16 | 2000 | 16 | 2000 | 16 | 2000 | 16 | 1985 | 16 | 2000
17 | 2000 | 17 | 2000 | 17 | 2000 | 17 | 1884 | 17 | 2000 | 17 | 2000 | 17 | 2000 | 17 | 2000 | 17 | 2000 | 17 | 2000 | 17 | 1985 | 17 | 2000
18 | 2000 | 18 | 2000 | 18 | 2000 | 18 | 1884 | 18 | 2000 | 18 | 2000 | 18 | 2000 | 18 | 2000 | 18 | 2000 | 18 | 2000 | 18 | 1985 | 18 | 2000
19 | 1940 | 19 | 2000 | 19 | 1707 | 19 | 1998 | 19 | 1925 | 19 | 2000 | 19 | 2000 | 19 | 2000 | 19 | 1848 | 19 | 1619 | 19 | 2000 | 19 | 2000
20 | 1940 | 20 | 2000 | 20 | 1707 | 20 | 1998 | 20 | 1925 | 20 | 2000 | 20 | 2000 | 20 | 2000 | 20 | 1848 | 20 | 1619 | 20 | 2000 | 20 | 2000
21 | 1940 | 21 | 2000 | 21 | 1707 | 21 | 1998 | 21 | 1925 | 21 | 2000 | 21 | 2000 | 21 | 2000 | 21 | 1848 | 21 | 1619 | 21 | 2000 | 21 | 2000
22 | 1940 | 22 | 2000 | 22 | 1707 | 22 | 1998 | 22 | 1925 | 22 | 2000 | 22 | 2000 | 22 | 2000 | 22 | 1848 | 22 | 1619 | 22 | 2000 | 22 | 2000
23 | 1864 | 23 | 2000 | 23 | 1903 | 23 | 2000 | 23 | 2000 | 23 | 2000 | 23 | 1278 | 23 | 1571 | 23 | 1719 | 23 | 1903 | 23 | 2000 | 23 | 2000
24 | 1864 | 24 | 2000 | 24 | 1903 | 24 | 2000 | 24 | 2000 | 24 | 2000 | 24 | 1278 | 24 | 1571 | 24 | 1719 | 24 | 1903 | 24 | 2000 | 24 | 2000
Total | 45564 | Total | 48000 | Total | 46440 | Total | 47528 | Total | 47412 | Total | 48000 | Total | 41904 | Total | 45736 | Total | 43704 | Total | 46088 | Total | 47940 | Total | 48000

## FAS_2016_SRS
SRS Requirement in Plexos
| Net Load Forecast Error, 95th percentile, MW | CRS, MW | Reg-up, MW | Min PFR, based on BAL-003 IFRO, MW | Max FFR, MW | SRS Req., MW
2016-01-01 | 2231 | 818.08 | 351 | 1240 | 1430.7692 | 0
2016-01-01 01:00 | 2231 | 819.82 | 351 | 1240 | 1430.7692 | 0
2016-01-01 02:00 | 2257 | 821.38 | 369 | 1240 | 1430.7692 | 0
2016-01-01 03:00 | 2257 | 825.96 | 453 | 1240 | 1430.7692 | 0
2016-01-01 04:00 | 2257 | 841.1 | 645 | 1240 | 1430.7692 | 0
2016-01-01 05:00 | 2257 | 867.6 | 847 | 1240 | 1430.7692 | 0
2016-01-01 06:00 | 2385 | 894.92 | 586 | 1240 | 1430.7692 | 0
2016-01-01 07:00 | 2385 | 905.86 | 510 | 1240 | 1430.7692 | 0
2016-01-01 08:00 | 2385 | 907.32 | 351 | 1240 | 1430.7692 | 0
2016-01-01 09:00 | 2385 | 900.52 | 387 | 1240 | 1430.7692 | 0
2016-01-01 10:00 | 2194 | 881.28 | 488 | 1240 | 1430.7692 | 0
2016-01-01 11:00 | 2194 | 851.26 | 391 | 1240 | 1430.7692 | 0
2016-01-01 12:00 | 2194 | 816.8 | 376 | 1240 | 1430.7692 | 0
2016-01-01 13:00 | 2194 | 781.66 | 351 | 1240 | 1430.7692 | 0
2016-01-01 14:00 | 3049 | 752.44 | 351 | 1240 | 1430.7692 | 0
2016-01-01 15:00 | 3049 | 733.72 | 512 | 1240 | 1430.7692 | 0
2016-01-01 16:00 | 3049 | 741.16 | 633 | 1240 | 1430.7692 | 0
2016-01-01 17:00 | 3049 | 788.64 | 619 | 1240 | 1430.7692 | 0
2016-01-01 18:00 | 2327 | 832.12 | 561 | 1240 | 1430.7692 | 0
2016-01-01 19:00 | 2327 | 831.839 | 351 | 1240 | 1440 | 0
2016-01-01 20:00 | 2327 | 842.27 | 351 | 1240 | 1440 | 0
2016-01-01 21:00 | 2327 | 843.885 | 351 | 1240 | 1440 | 0
2016-01-01 22:00 | 2231 | 831.231 | 351 | 1240 | 1440 | 0
2016-01-01 23:00 | 2231 | 812.155 | 471 | 1240 | 1440 | 0
2016-01-02 | 2231 | 811.737 | 351 | 1240 | 1440 | 0
2016-01-02 01:00 | 2231 | 811.3 | 351 | 1240 | 1440 | 0
2016-01-02 02:00 | 2257 | 811.794 | 369 | 1240 | 1440 | 0
2016-01-02 03:00 | 2257 | 820.325 | 453 | 1240 | 1440 | 0
2016-01-02 04:00 | 2257 | 836.171 | 645 | 1240 | 1440 | 0
2016-01-02 05:00 | 2257 | 867.388 | 847 | 1240 | 1440 | 0
2016-01-02 06:00 | 2385 | 900.049 | 586 | 1240 | 1440 | 0
2016-01-02 07:00 | 2385 | 926.858 | 510 | 1240 | 1440 | 0
2016-01-02 08:00 | 2385 | 937.403 | 351 | 1240 | 1440 | 0
2016-01-02 09:00 | 2385 | 921.272 | 387 | 1240 | 1440 | 0
2016-01-02 10:00 | 2194 | 886.179 | 488 | 1240 | 1440 | 0
2016-01-02 11:00 | 2194 | 843.296 | 391 | 1240 | 1440 | 0
2016-01-02 12:00 | 2194 | 800.603 | 376 | 1240 | 1440 | 0
2016-01-02 13:00 | 2194 | 804.52 | 351 | 1240 | 1430.7692 | 0
2016-01-02 14:00 | 3049 | 778.8 | 351 | 1240 | 1430.7692 | 0
2016-01-02 15:00 | 3049 | 764.58 | 512 | 1240 | 1430.7692 | 0
2016-01-02 16:00 | 3049 | 782.5 | 633 | 1240 | 1430.7692 | 0
2016-01-02 17:00 | 3049 | 838.26 | 619 | 1240 | 1430.7692 | 0
2016-01-02 18:00 | 2327 | 877.98 | 561 | 1240 | 1430.7692 | 0
2016-01-02 19:00 | 2327 | 917.72 | 351 | 1240 | 1430.7692 | 0
2016-01-02 20:00 | 2327 | 924.18 | 351 | 1240 | 1430.7692 | 0
2016-01-02 21:00 | 2327 | 914.92 | 351 | 1240 | 1430.7692 | 0
2016-01-02 22:00 | 2231 | 886.9 | 351 | 1240 | 1430.7692 | 0
2016-01-02 23:00 | 2231 | 855.96 | 471 | 1240 | 1430.7692 | 0
2016-01-03 | 2231 | 854.68 | 351 | 1240 | 1430.7692 | 0
2016-01-03 01:00 | 2231 | 853.4 | 351 | 1240 | 1430.7692 | 0
2016-01-03 02:00 | 2257 | 845.22 | 369 | 1240 | 1430.7692 | 0
2016-01-03 03:00 | 2257 | 842.4 | 453 | 1240 | 1430.7692 | 0
2016-01-03 04:00 | 2257 | 849.52 | 645 | 1240 | 1430.7692 | 0
2016-01-03 05:00 | 2257 | 871.84 | 847 | 1240 | 1430.7692 | 0
2016-01-03 06:00 | 2385 | 897.2 | 586 | 1240 | 1430.7692 | 0
2016-01-03 07:00 | 2385 | 876.204 | 510 | 1240 | 1440 | 0
2016-01-03 08:00 | 2385 | 900.391 | 351 | 1240 | 1440 | 0
2016-01-03 09:00 | 2385 | 919.22 | 387 | 1240 | 1440 | 0
2016-01-03 10:00 | 2194 | 922.222 | 488 | 1240 | 1440 | 0
2016-01-03 11:00 | 2194 | 912.703 | 391 | 1240 | 1440 | 0
2016-01-03 12:00 | 2194 | 900.581 | 376 | 1240 | 1440 | 0
2016-01-03 13:00 | 2194 | 882.588 | 351 | 1240 | 1440 | 0
2016-01-03 14:00 | 3049 | 870.162 | 351 | 1240 | 1440 | 0
2016-01-03 15:00 | 3049 | 866.932 | 512 | 1240 | 1440 | 0
2016-01-03 16:00 | 3049 | 934.1 | 633 | 1240 | 1238.9381 | 0
2016-01-03 17:00 | 3049 | 981.76 | 619 | 1240 | 1238.9381 | 0
2016-01-03 18:00 | 2327 | 1012.36 | 561 | 1240 | 1238.9381 | 0
2016-01-03 19:00 | 2327 | 1042.96 | 351 | 1240 | 1238.9381 | 0
2016-01-03 20:00 | 2327 | 1035.96 | 351 | 1240 | 1238.9381 | 0
2016-01-03 21:00 | 2327 | 1011.86 | 351 | 1240 | 1238.9381 | 0
2016-01-03 22:00 | 2231 | 968.22 | 351 | 1240 | 1238.9381 | 0
2016-01-03 23:00 | 2231 | 922.68 | 471 | 1240 | 1238.9381 | 0
2016-01-04 | 2231 | 776.796 | 351 | 1240 | 1440 | 0
2016-01-04 01:00 | 2231 | 768.588 | 351 | 1240 | 1440 | 0
2016-01-04 02:00 | 2257 | 769.671 | 369 | 1240 | 1440 | 0
2016-01-04 03:00 | 2257 | 781.147 | 453 | 1240 | 1440 | 0
2016-01-04 04:00 | 2257 | 812.402 | 645 | 1240 | 1440 | 0
2016-01-04 05:00 | 2257 | 878.693 | 847 | 1240 | 1440 | 0
2016-01-04 06:00 | 2385 | 1022.18 | 586 | 1240 | 1238.9381 | 0
2016-01-04 07:00 | 2385 | 1012.073 | 510 | 1240 | 1296.2963 | 0
2016-01-04 08:00 | 2385 | 1002.858 | 351 | 1240 | 1296.2963 | 0
2016-01-04 09:00 | 2385 | 997.595 | 387 | 1240 | 1296.2963 | 0
2016-01-04 10:00 | 2194 | 987.829 | 488 | 1240 | 1296.2963 | 0
2016-01-04 11:00 | 2194 | 961.248 | 391 | 1240 | 1296.2963 | 0
2016-01-04 12:00 | 2194 | 931.247 | 376 | 1240 | 1296.2963 | 0
2016-01-04 13:00 | 2194 | 901.094 | 351 | 1240 | 1296.2963 | 0
2016-01-04 14:00 | 3049 | 878.579 | 351 | 1240 | 1296.2963 | 0
2016-01-04 15:00 | 3049 | 864.082 | 512 | 1240 | 1296.2963 | 0
2016-01-04 16:00 | 3049 | 877.173 | 633 | 1240 | 1296.2963 | 0
2016-01-04 17:00 | 3049 | 934.781 | 619 | 1240 | 1296.2963 | 0
2016-01-04 18:00 | 2327 | 982.813 | 561 | 1240 | 1296.2963 | 0
2016-01-04 19:00 | 2327 | 1030.826 | 351 | 1240 | 1296.2963 | 0
2016-01-04 20:00 | 2327 | 1033.182 | 351 | 1240 | 1296.2963 | 0
2016-01-04 21:00 | 2327 | 1065.42 | 351 | 1240 | 1238.9381 | 0
2016-01-04 22:00 | 2231 | 965.409 | 351 | 1240 | 1440 | 0
2016-01-04 23:00 | 2231 | 923.514 | 471 | 1240 | 1440 | 0
2016-01-05 | 2231 | 875.121 | 351 | 1240 | 1440 | 0
2016-01-05 01:00 | 2231 | 866.191 | 351 | 1240 | 1440 | 0
2016-01-05 02:00 | 2257 | 875.919 | 369 | 1240 | 1440 | 0
2016-01-05 03:00 | 2257 | 889.884 | 453 | 1240 | 1440 | 0
2016-01-05 04:00 | 2257 | 916.674 | 645 | 1240 | 1440 | 0
2016-01-05 05:00 | 2257 | 980.305 | 847 | 1240 | 1440 | 0
2016-01-05 06:00 | 2385 | 1133.06 | 586 | 1240 | 1238.9381 | 0
2016-01-05 07:00 | 2385 | 1159.7 | 510 | 1240 | 1238.9381 | 0
2016-01-05 08:00 | 2385 | 1116.06 | 351 | 1240 | 1238.9381 | 0
2016-01-05 09:00 | 2385 | 1021.687 | 387 | 1240 | 1440 | 0
2016-01-05 10:00 | 2194 | 982.604 | 488 | 1240 | 1440 | 0
2016-01-05 11:00 | 2194 | 940.386 | 391 | 1240 | 1440 | 0
2016-01-05 12:00 | 2194 | 897.104 | 376 | 1240 | 1440 | 0
2016-01-05 13:00 | 2194 | 860.852 | 351 | 1240 | 1440 | 0
2016-01-05 14:00 | 3049 | 832.485 | 351 | 1240 | 1440 | 0
2016-01-05 15:00 | 3049 | 826.766 | 512 | 1240 | 1440 | 0
2016-01-05 16:00 | 3049 | 827.545 | 633 | 1240 | 1440 | 0
2016-01-05 17:00 | 3049 | 884.488 | 619 | 1240 | 1440 | 0
2016-01-05 18:00 | 2327 | 936.548 | 561 | 1240 | 1440 | 0
2016-01-05 19:00 | 2327 | 988.589 | 351 | 1240 | 1440 | 0
2016-01-05 20:00 | 2327 | 994.327 | 351 | 1240 | 1440 | 0
2016-01-05 21:00 | 2327 | 1020.56 | 351 | 1240 | 1430.7692 | 0
2016-01-05 22:00 | 2231 | 973.66 | 351 | 1240 | 1430.7692 | 0
2016-01-05 23:00 | 2231 | 921.44 | 471 | 1240 | 1430.7692 | 0
2016-01-06 | 2231 | 784.188 | 351 | 1240 | 1521.4286 | 0
2016-01-06 01:00 | 2231 | 774.144 | 351 | 1240 | 1521.4286 | 0
2016-01-06 02:00 | 2257 | 772.398 | 369 | 1240 | 1521.4286 | 0
2016-01-06 03:00 | 2257 | 774.486 | 453 | 1240 | 1521.4286 | 0
2016-01-06 04:00 | 2257 | 790.542 | 645 | 1240 | 1521.4286 | 0
2016-01-06 05:00 | 2257 | 834.552 | 847 | 1240 | 1521.4286 | 0
2016-01-06 06:00 | 2385 | 1009.64 | 586 | 1240 | 1430.7692 | 0
2016-01-06 07:00 | 2385 | 1031.18 | 510 | 1240 | 1430.7692 | 0
2016-01-06 08:00 | 2385 | 950.798 | 351 | 1240 | 1440 | 0
2016-01-06 09:00 | 2385 | 934.078 | 387 | 1240 | 1440 | 0
2016-01-06 10:00 | 2194 | 919.334 | 488 | 1240 | 1440 | 0
2016-01-06 11:00 | 2194 | 902.31 | 391 | 1240 | 1440 | 0
2016-01-06 12:00 | 2194 | 883.101 | 376 | 1240 | 1440 | 0
2016-01-06 13:00 | 2194 | 865.811 | 351 | 1240 | 1440 | 0
2016-01-06 14:00 | 3049 | 847.552 | 351 | 1240 | 1440 | 0
2016-01-06 15:00 | 3049 | 841.016 | 512 | 1240 | 1440 | 0
2016-01-06 16:00 | 3049 | 849.794 | 633 | 1240 | 1440 | 0
2016-01-06 17:00 | 3049 | 881.125 | 619 | 1240 | 1440 | 0
2016-01-06 18:00 | 2327 | 891.024 | 561 | 1240 | 1440 | 0
2016-01-06 19:00 | 2327 | 948.34 | 351 | 1240 | 1430.7692 | 0
2016-01-06 20:00 | 2327 | 930.58 | 351 | 1240 | 1430.7692 | 0
2016-01-06 21:00 | 2327 | 808.668 | 351 | 1240 | 1521.4286 | 0
2016-01-06 22:00 | 2231 | 754.416 | 351 | 1240 | 1673.3333 | 0
2016-01-06 23:00 | 2231 | 701.442 | 471 | 1240 | 1730 | 0
2016-01-07 | 2231 | 631.242 | 351 | 1240 | 1730 | 0
2016-01-07 01:00 | 2231 | 627.732 | 351 | 1240 | 1730 | 0
2016-01-07 02:00 | 2257 | 634.014 | 369 | 1240 | 1730 | 0
2016-01-07 03:00 | 2257 | 648.954 | 453 | 1240 | 1730 | 0
2016-01-07 04:00 | 2257 | 677.538 | 645 | 1240 | 1730 | 0
2016-01-07 05:00 | 2257 | 736.272 | 847 | 1240 | 1673.3333 | 0
2016-01-07 06:00 | 2385 | 823.212 | 586 | 1240 | 1521.4286 | 0
2016-01-07 07:00 | 2385 | 961.26 | 510 | 1240 | 1430.7692 | 0
2016-01-07 08:00 | 2385 | 969.2 | 351 | 1240 | 1430.7692 | 0
2016-01-07 09:00 | 2385 | 987.34 | 387 | 1240 | 1430.7692 | 0
2016-01-07 10:00 | 2194 | 996.52 | 488 | 1240 | 1430.7692 | 0
2016-01-07 11:00 | 2194 | 989.8 | 391 | 1240 | 1430.7692 | 0
2016-01-07 12:00 | 2194 | 976.48 | 376 | 1240 | 1430.7692 | 0
2016-01-07 13:00 | 2194 | 960.96 | 351 | 1240 | 1430.7692 | 0
2016-01-07 14:00 | 3049 | 945.94 | 351 | 1240 | 1430.7692 | 0
2016-01-07 15:00 | 3049 | 940.22 | 512 | 1240 | 1430.7692 | 0
2016-01-07 16:00 | 3049 | 961.88 | 633 | 1240 | 1430.7692 | 0
2016-01-07 17:00 | 3049 | 974.244 | 619 | 1240 | 1440 | 0
2016-01-07 18:00 | 2327 | 1012.244 | 561 | 1240 | 1440 | 0
2016-01-07 19:00 | 2327 | 1105.52 | 351 | 1240 | 1238.9381 | 0
2016-01-07 20:00 | 2327 | 1099.56 | 351 | 1240 | 1238.9381 | 0
2016-01-07 21:00 | 2327 | 1081.8 | 351 | 1240 | 1238.9381 | 0
2016-01-07 22:00 | 2231 | 1041.1 | 351 | 1240 | 1238.9381 | 0
2016-01-07 23:00 | 2231 | 1007.48 | 471 | 1240 | 1238.9381 | 0
2016-01-08 | 2231 | 908.76 | 351 | 1240 | 1238.9381 | 0
2016-01-08 01:00 | 2231 | 901.4 | 351 | 1240 | 1238.9381 | 0
2016-01-08 02:00 | 2257 | 905.26 | 369 | 1240 | 1238.9381 | 0
2016-01-08 03:00 | 2257 | 917.68 | 453 | 1240 | 1238.9381 | 0
2016-01-08 04:00 | 2257 | 939.6 | 645 | 1240 | 1238.9381 | 0
2016-01-08 05:00 | 2257 | 987.88 | 847 | 1240 | 1238.9381 | 0
2016-01-08 06:00 | 2385 | 1060.38 | 586 | 1240 | 1238.9381 | 0
2016-01-08 07:00 | 2385 | 1087.38 | 510 | 1240 | 1238.9381 | 0
2016-01-08 08:00 | 2385 | 1017.621 | 351 | 1240 | 1296.2963 | 0
2016-01-08 09:00 | 2385 | 1010.268 | 387 | 1240 | 1296.2963 | 0
2016-01-08 10:00 | 2194 | 995.201 | 488 | 1240 | 1296.2963 | 0
2016-01-08 11:00 | 2194 | 1021.7 | 391 | 1240 | 1238.9381 | 0
2016-01-08 12:00 | 2194 | 994.68 | 376 | 1240 | 1238.9381 | 0
2016-01-08 13:00 | 2194 | 966.7 | 351 | 1240 | 1238.9381 | 0
2016-01-08 14:00 | 3049 | 943.3 | 351 | 1240 | 1238.9381 | 0
2016-01-08 15:00 | 3049 | 930.72 | 512 | 1240 | 1238.9381 | 0
2016-01-08 16:00 | 3049 | 939.6 | 633 | 1240 | 1238.9381 | 0
2016-01-08 17:00 | 3049 | 979.22 | 619 | 1240 | 1238.9381 | 0
2016-01-08 18:00 | 2327 | 1004.8 | 561 | 1240 | 1238.9381 | 0
2016-01-08 19:00 | 2327 | 1030.38 | 351 | 1240 | 1238.9381 | 0
2016-01-08 20:00 | 2327 | 1027.5 | 351 | 1240 | 1238.9381 | 0
2016-01-08 21:00 | 2327 | 1009.56 | 351 | 1240 | 1238.9381 | 0
2016-01-08 22:00 | 2231 | 983.94 | 351 | 1240 | 1238.9381 | 0
2016-01-08 23:00 | 2231 | 960.48 | 471 | 1240 | 1238.9381 | 0
2016-01-09 | 2231 | 960.48 | 351 | 1240 | 1238.9381 | 0
2016-01-09 01:00 | 2231 | 994.62 | 351 | 1240 | 1238.9381 | 0
2016-01-09 02:00 | 2257 | 1059.88 | 369 | 1240 | 1238.9381 | 0
2016-01-09 03:00 | 2257 | 1068.88 | 453 | 1240 | 1238.9381 | 0
2016-01-09 04:00 | 2257 | 1086.6 | 645 | 1240 | 1238.9381 | 0
2016-01-09 05:00 | 2257 | 1109.66 | 847 | 1240 | 1238.9381 | 0
2016-01-09 06:00 | 2385 | 1148.52 | 586 | 1240 | 1238.9381 | 0
2016-01-09 07:00 | 2385 | 1166.68 | 510 | 1240 | 1238.9381 | 0
2016-01-09 08:00 | 2385 | 1156.98 | 351 | 1240 | 1238.9381 | 0
2016-01-09 09:00 | 2385 | 1122.64 | 387 | 1240 | 1238.9381 | 0
2016-01-09 10:00 | 2194 | 1074.8 | 488 | 1240 | 1238.9381 | 0
2016-01-09 11:00 | 2194 | 1013.02 | 391 | 1240 | 1238.9381 | 0
2016-01-09 12:00 | 2194 | 960.84 | 376 | 1240 | 1238.9381 | 0
2016-01-09 13:00 | 2194 | 910.02 | 351 | 1240 | 1238.9381 | 0
2016-01-09 14:00 | 3049 | 872.58 | 351 | 1240 | 1238.9381 | 0
2016-01-09 15:00 | 3049 | 850.3 | 512 | 1240 | 1238.9381 | 0
2016-01-09 16:00 | 3049 | 853.28 | 633 | 1240 | 1238.9381 | 0
2016-01-09 17:00 | 3049 | 908.96 | 619 | 1240 | 1238.9381 | 0
2016-01-09 18:00 | 2327 | 961.68 | 561 | 1240 | 1238.9381 | 0
2016-01-09 19:00 | 2327 | 1014.42 | 351 | 1240 | 1238.9381 | 0
2016-01-09 20:00 | 2327 | 1024.78 | 351 | 1240 | 1238.9381 | 0
2016-01-09 21:00 | 2327 | 1025.6 | 351 | 1240 | 1238.9381 | 0
2016-01-09 22:00 | 2231 | 1006.3 | 351 | 1240 | 1238.9381 | 0
2016-01-09 23:00 | 2231 | 989.86 | 471 | 1240 | 1238.9381 | 0
2016-01-10 | 2231 | 994.62 | 351 | 1240 | 1238.9381 | 0
2016-01-10 01:00 | 2231 | 1004.62 | 351 | 1240 | 1238.9381 | 0
2016-01-10 02:00 | 2257 | 1017.9 | 369 | 1240 | 1238.9381 | 0
2016-01-10 03:00 | 2257 | 1024.74 | 453 | 1240 | 1238.9381 | 0
2016-01-10 04:00 | 2257 | 1040.78 | 645 | 1240 | 1238.9381 | 0
2016-01-10 05:00 | 2257 | 1065.68 | 847 | 1240 | 1238.9381 | 0
2016-01-10 06:00 | 2385 | 1102.74 | 586 | 1240 | 1238.9381 | 0
2016-01-10 07:00 | 2385 | 1128.84 | 510 | 1240 | 1238.9381 | 0
2016-01-10 08:00 | 2385 | 1126.48 | 351 | 1240 | 1238.9381 | 0
2016-01-10 09:00 | 2385 | 1027.349 | 387 | 1240 | 1440 | 0
2016-01-10 10:00 | 2194 | 974.928 | 488 | 1240 | 1440 | 0
2016-01-10 11:00 | 2194 | 918.137 | 391 | 1240 | 1440 | 0
2016-01-10 12:00 | 2194 | 870.846 | 376 | 1240 | 1440 | 0
2016-01-10 13:00 | 2194 | 827.317 | 351 | 1240 | 1440 | 0
2016-01-10 14:00 | 3049 | 793.307 | 351 | 1240 | 1440 | 0
2016-01-10 15:00 | 3049 | 773.3 | 512 | 1240 | 1440 | 0
2016-01-10 16:00 | 3049 | 783.655 | 633 | 1240 | 1440 | 0
2016-01-10 17:00 | 3049 | 837.957 | 619 | 1240 | 1440 | 0
2016-01-10 18:00 | 2327 | 897.408 | 561 | 1240 | 1440 | 0
2016-01-10 19:00 | 2327 | 956.878 | 351 | 1240 | 1440 | 0
2016-01-10 20:00 | 2327 | 969.684 | 351 | 1240 | 1440 | 0
2016-01-10 21:00 | 2327 | 960.887 | 351 | 1240 | 1440 | 0
2016-01-10 22:00 | 2231 | 924.179 | 351 | 1240 | 1440 | 0
2016-01-10 23:00 | 2231 | 887.851 | 471 | 1240 | 1440 | 0
2016-01-11 | 2231 | 862.809 | 351 | 1240 | 1440 | 0
2016-01-11 01:00 | 2231 | 859.294 | 351 | 1240 | 1440 | 0
2016-01-11 02:00 | 2257 | 866.609 | 369 | 1240 | 1440 | 0
2016-01-11 03:00 | 2257 | 881.106 | 453 | 1240 | 1440 | 0
2016-01-11 04:00 | 2257 | 907.877 | 645 | 1240 | 1440 | 0
2016-01-11 05:00 | 2257 | 962.673 | 847 | 1240 | 1440 | 0
2016-01-11 06:00 | 2385 | 1106.3 | 586 | 1240 | 1238.9381 | 0
2016-01-11 07:00 | 2385 | 1132.14 | 510 | 1240 | 1238.9381 | 0
2016-01-11 08:00 | 2385 | 1081.82 | 351 | 1240 | 1238.9381 | 0
2016-01-11 09:00 | 2385 | 1023.54 | 387 | 1240 | 1238.9381 | 0
2016-01-11 10:00 | 2194 | 971 | 488 | 1240 | 1238.9381 | 0
2016-01-11 11:00 | 2194 | 918.14 | 391 | 1240 | 1238.9381 | 0
2016-01-11 12:00 | 2194 | 829.445 | 376 | 1240 | 1440 | 0
2016-01-11 13:00 | 2194 | 795.701 | 351 | 1240 | 1440 | 0
2016-01-11 14:00 | 3049 | 769.956 | 351 | 1240 | 1440 | 0
2016-01-11 15:00 | 3049 | 754.87 | 512 | 1240 | 1440 | 0
2016-01-11 16:00 | 3049 | 796.52 | 633 | 1240 | 1440 | 0
2016-01-11 17:00 | 3049 | 842.06 | 619 | 1240 | 1440 | 0
2016-01-11 18:00 | 2327 | 880.78 | 561 | 1240 | 1440 | 0
2016-01-11 19:00 | 2327 | 873.525 | 351 | 1240 | 1238.9381 | 0
2016-01-11 20:00 | 2327 | 872.974 | 351 | 1240 | 1238.9381 | 0
2016-01-11 21:00 | 2327 | 855.855 | 351 | 1240 | 1238.9381 | 0
2016-01-11 22:00 | 2231 | 852.26 | 351 | 1240 | 1238.9381 | 0
2016-01-11 23:00 | 2231 | 807.88 | 471 | 1240 | 1238.9381 | 0
2016-01-12 | 2231 | 814.62 | 351 | 1240 | 1238.9381 | 0
2016-01-12 01:00 | 2231 | 829.64 | 351 | 1240 | 1238.9381 | 0
2016-01-12 02:00 | 2257 | 833.68 | 369 | 1240 | 1238.9381 | 0
2016-01-12 03:00 | 2257 | 845.84 | 453 | 1240 | 1238.9381 | 0
2016-01-12 04:00 | 2257 | 874.2 | 645 | 1240 | 1238.9381 | 0
2016-01-12 05:00 | 2257 | 890.853 | 847 | 1240 | 1238.9381 | 0
2016-01-12 06:00 | 2385 | 1090.551 | 586 | 1240 | 1296.2963 | 0
2016-01-12 07:00 | 2385 | 1120.917 | 510 | 1240 | 1296.2963 | 0
2016-01-12 08:00 | 2385 | 1073.73 | 351 | 1240 | 1296.2963 | 0
2016-01-12 09:00 | 2385 | 922.146 | 387 | 1240 | 1238.9381 | 0
2016-01-12 10:00 | 2194 | 881.771 | 488 | 1240 | 1238.9381 | 0
2016-01-12 11:00 | 2194 | 844.208 | 391 | 1240 | 1440 | 0
2016-01-12 12:00 | 2194 | 855.68 | 376 | 1240 | 1440 | 0
2016-01-12 13:00 | 2194 | 826.74 | 351 | 1240 | 1440 | 0
2016-01-12 14:00 | 3049 | 804.9 | 351 | 1240 | 1440 | 0
2016-01-12 15:00 | 3049 | 752.818 | 512 | 1240 | 1440 | 0
2016-01-12 16:00 | 3049 | 764.978 | 633 | 1240 | 1440 | 0
2016-01-12 17:00 | 3049 | 842.82 | 619 | 1240 | 1440 | 0
2016-01-12 18:00 | 2327 | 877.98 | 561 | 1240 | 1430.7692 | 0
2016-01-12 19:00 | 2327 | 913.14 | 351 | 1240 | 1430.7692 | 0
2016-01-12 20:00 | 2327 | 914.96 | 351 | 1240 | 1430.7692 | 0
2016-01-12 21:00 | 2327 | 896.3 | 351 | 1240 | 1430.7692 | 0
2016-01-12 22:00 | 2231 | 812.573 | 351 | 1240 | 1521.4286 | 0
2016-01-12 23:00 | 2231 | 811.3 | 471 | 1240 | 1521.4286 | 0
2016-01-13 | 2231 | 776.34 | 351 | 1240 | 1521.4286 | 0
2016-01-13 01:00 | 2231 | 769.14 | 351 | 1240 | 1521.4286 | 0
2016-01-13 02:00 | 2257 | 770.58 | 369 | 1240 | 1521.4286 | 0
2016-01-13 03:00 | 2257 | 779.54 | 453 | 1240 | 1521.4286 | 0
2016-01-13 04:00 | 2257 | 804.92 | 645 | 1240 | 1521.4286 | 0
2016-01-13 05:00 | 2257 | 822.548 | 847 | 1240 | 1521.4286 | 0
2016-01-13 06:00 | 2385 | 959.5 | 586 | 1240 | 1430.7692 | 0
2016-01-13 07:00 | 2385 | 984.7 | 510 | 1240 | 1430.7692 | 0
2016-01-13 08:00 | 2385 | 902.5 | 351 | 1240 | 1430.7692 | 0
2016-01-13 09:00 | 2385 | 877.002 | 387 | 1240 | 1521.4286 | 0
2016-01-13 10:00 | 2194 | 852.416 | 488 | 1240 | 1521.4286 | 0
2016-01-13 11:00 | 2194 | 823.232 | 391 | 1240 | 1521.4286 | 0
2016-01-13 12:00 | 2194 | 843.42 | 376 | 1240 | 1521.4286 | 0
2016-01-13 13:00 | 2194 | 829.66 | 351 | 1240 | 1673.3333 | 0
2016-01-13 14:00 | 3049 | 815.8 | 351 | 1240 | 1673.3333 | 0
2016-01-13 15:00 | 3049 | 812.32 | 512 | 1240 | 1673.3333 | 0
2016-01-13 16:00 | 3049 | 830.88 | 633 | 1240 | 1673.3333 | 0
2016-01-13 17:00 | 3049 | 824.068 | 619 | 1240 | 1673.3333 | 0
2016-01-13 18:00 | 2327 | 839.439 | 561 | 1240 | 1673.3333 | 0
2016-01-13 19:00 | 2327 | 854.791 | 351 | 1240 | 1673.3333 | 0
2016-01-13 20:00 | 2327 | 887.16 | 351 | 1240 | 1673.3333 | 0
2016-01-13 21:00 | 2327 | 857.46 | 351 | 1240 | 1673.3333 | 0
2016-01-13 22:00 | 2231 | 802.9 | 351 | 1240 | 1673.3333 | 0
2016-01-13 23:00 | 2231 | 672.408 | 471 | 1240 | 1673.3333 | 0
2016-01-14 | 2231 | 640.026 | 351 | 1240 | 1673.3333 | 0
2016-01-14 01:00 | 2231 | 626.346 | 351 | 1240 | 1673.3333 | 0
2016-01-14 02:00 | 2257 | 621.45 | 369 | 1240 | 1673.3333 | 0
2016-01-14 03:00 | 2257 | 625.428 | 453 | 1240 | 1673.3333 | 0
2016-01-14 04:00 | 2257 | 710.8 | 645 | 1240 | 1673.3333 | 0
2016-01-14 05:00 | 2257 | 765.84 | 847 | 1240 | 1673.3333 | 0
2016-01-14 06:00 | 2385 | 807.671 | 586 | 1240 | 1521.4286 | 0
2016-01-14 07:00 | 2385 | 830.566 | 510 | 1240 | 1521.4286 | 0
2016-01-14 08:00 | 2385 | 810.597 | 351 | 1240 | 1521.4286 | 0
2016-01-14 09:00 | 2385 | 808.868 | 387 | 1240 | 1521.4286 | 0
2016-01-14 10:00 | 2194 | 806.664 | 488 | 1240 | 1521.4286 | 0
2016-01-14 11:00 | 2194 | 797.544 | 391 | 1240 | 1521.4286 | 0
2016-01-14 12:00 | 2194 | 787.151 | 376 | 1240 | 1521.4286 | 0
2016-01-14 13:00 | 2194 | 781.869 | 351 | 1240 | 1521.4286 | 0
2016-01-14 14:00 | 3049 | 775.561 | 351 | 1240 | 1521.4286 | 0
2016-01-14 15:00 | 3049 | 772.483 | 512 | 1240 | 1521.4286 | 0
2016-01-14 16:00 | 3049 | 781.85 | 633 | 1240 | 1521.4286 | 0
2016-01-14 17:00 | 3049 | 806.512 | 619 | 1240 | 1521.4286 | 0
2016-01-14 18:00 | 2327 | 862.4 | 561 | 1240 | 1521.4286 | 0
2016-01-14 19:00 | 2327 | 875.86 | 351 | 1240 | 1430.7692 | 0
2016-01-14 20:00 | 2327 | 859.64 | 351 | 1240 | 1430.7692 | 0
2016-01-14 21:00 | 2327 | 782.439 | 351 | 1240 | 1521.4286 | 0
2016-01-14 22:00 | 2231 | 732.678 | 351 | 1240 | 1521.4286 | 0
2016-01-14 23:00 | 2231 | 719.2 | 471 | 1240 | 1521.4286 | 0
2016-01-15 | 2231 | 692.88 | 351 | 1240 | 1521.4286 | 0
2016-01-15 01:00 | 2231 | 675.66 | 351 | 1240 | 1521.4286 | 0
2016-01-15 02:00 | 2257 | 668.44 | 369 | 1240 | 1521.4286 | 0
2016-01-15 03:00 | 2257 | 669.5 | 453 | 1240 | 1521.4286 | 0
2016-01-15 04:00 | 2257 | 687.22 | 645 | 1240 | 1521.4286 | 0
2016-01-15 05:00 | 2257 | 701.708 | 847 | 1240 | 1521.4286 | 0
2016-01-15 06:00 | 2385 | 819.26 | 586 | 1240 | 1430.7692 | 0
2016-01-15 07:00 | 2385 | 856.14 | 510 | 1240 | 1430.7692 | 0
2016-01-15 08:00 | 2385 | 848.78 | 351 | 1240 | 1430.7692 | 0
2016-01-15 09:00 | 2385 | 856.6 | 387 | 1240 | 1430.7692 | 0
2016-01-15 10:00 | 2194 | 862.84 | 488 | 1240 | 1430.7692 | 0
2016-01-15 11:00 | 2194 | 858.78 | 391 | 1240 | 1430.7692 | 0
2016-01-15 12:00 | 2194 | 850.14 | 376 | 1240 | 1430.7692 | 0
2016-01-15 13:00 | 2194 | 848 | 351 | 1240 | 1430.7692 | 0
2016-01-15 14:00 | 3049 | 844.02 | 351 | 1240 | 1430.7692 | 0
2016-01-15 15:00 | 3049 | 845.28 | 512 | 1240 | 1430.7692 | 0
2016-01-15 16:00 | 3049 | 858.2 | 633 | 1240 | 1430.7692 | 0
2016-01-15 17:00 | 3049 | 887.38 | 619 | 1240 | 1430.7692 | 0
2016-01-15 18:00 | 2327 | 892.88 | 561 | 1240 | 1430.7692 | 0
2016-01-15 19:00 | 2327 | 898.4 | 351 | 1240 | 1430.7692 | 0
2016-01-15 20:00 | 2327 | 884.64 | 351 | 1240 | 1430.7692 | 0
2016-01-15 21:00 | 2327 | 861.08 | 351 | 1240 | 1430.7692 | 0
2016-01-15 22:00 | 2231 | 782.99 | 351 | 1240 | 1521.4286 | 0
2016-01-15 23:00 | 2231 | 743.527 | 471 | 1240 | 1521.4286 | 0
2016-01-16 | 2231 | 745.389 | 351 | 1240 | 1521.4286 | 0
2016-01-16 01:00 | 2231 | 751.678 | 351 | 1240 | 1521.4286 | 0
2016-01-16 02:00 | 2257 | 745.864 | 369 | 1240 | 1521.4286 | 0
2016-01-16 03:00 | 2257 | 745.731 | 453 | 1240 | 1521.4286 | 0
2016-01-16 04:00 | 2257 | 750.424 | 645 | 1240 | 1521.4286 | 0
2016-01-16 05:00 | 2257 | 771.799 | 847 | 1240 | 1521.4286 | 0
2016-01-16 06:00 | 2385 | 845.78 | 586 | 1240 | 1521.4286 | 0
2016-01-16 07:00 | 2385 | 881.74 | 510 | 1240 | 1430.7692 | 0
2016-01-16 08:00 | 2385 | 910.32 | 351 | 1240 | 1430.7692 | 0
2016-01-16 09:00 | 2385 | 935.16 | 387 | 1240 | 1440 | 0
2016-01-16 10:00 | 2194 | 896.914 | 488 | 1240 | 1440 | 0
2016-01-16 11:00 | 2194 | 882.379 | 391 | 1240 | 1440 | 0
2016-01-16 12:00 | 2194 | 891.1 | 376 | 1240 | 1440 | 0
2016-01-16 13:00 | 2194 | 860.94 | 351 | 1240 | 1440 | 0
2016-01-16 14:00 | 3049 | 837.38 | 351 | 1240 | 1440 | 0
2016-01-16 15:00 | 3049 | 823.54 | 512 | 1240 | 1440 | 0
2016-01-16 16:00 | 3049 | 821.86 | 633 | 1240 | 1440 | 0
2016-01-16 17:00 | 3049 | 850.92 | 619 | 1240 | 1440 | 0
2016-01-16 18:00 | 2327 | 836.646 | 561 | 1240 | 1440 | 0
2016-01-16 19:00 | 2327 | 864.918 | 351 | 1240 | 1440 | 0
2016-01-16 20:00 | 2327 | 859.636 | 351 | 1240 | 1440 | 0
2016-01-16 21:00 | 2327 | 845.215 | 351 | 1240 | 1440 | 0
2016-01-16 22:00 | 2231 | 859.46 | 351 | 1240 | 1440 | 0
2016-01-16 23:00 | 2231 | 827.78 | 471 | 1240 | 1430.7692 | 0
2016-01-17 | 2231 | 827.3 | 351 | 1240 | 1430.7692 | 0
2016-01-17 01:00 | 2231 | 776.245 | 351 | 1240 | 1430.7692 | 0
2016-01-17 02:00 | 2257 | 772.027 | 369 | 1240 | 1430.7692 | 0
2016-01-17 03:00 | 2257 | 773.585 | 453 | 1240 | 1430.7692 | 0
2016-01-17 04:00 | 2257 | 783.598 | 645 | 1240 | 1430.7692 | 0
2016-01-17 05:00 | 2257 | 804.935 | 847 | 1240 | 1430.7692 | 0
2016-01-17 06:00 | 2385 | 838.698 | 586 | 1240 | 1430.7692 | 0
2016-01-17 07:00 | 2385 | 912.4 | 510 | 1240 | 1430.7692 | 0
2016-01-17 08:00 | 2385 | 934.46 | 351 | 1240 | 1430.7692 | 0
2016-01-17 09:00 | 2385 | 923.08 | 387 | 1240 | 1430.7692 | 0
2016-01-17 10:00 | 2194 | 889.26 | 488 | 1240 | 1430.7692 | 0
2016-01-17 11:00 | 2194 | 854.74 | 391 | 1240 | 1430.7692 | 0
2016-01-17 12:00 | 2194 | 823.56 | 376 | 1240 | 1430.7692 | 0
2016-01-17 13:00 | 2194 | 798.58 | 351 | 1240 | 1521.4286 | 0
2016-01-17 14:00 | 3049 | 739.119 | 351 | 1240 | 1521.4286 | 0
2016-01-17 15:00 | 3049 | 729.733 | 512 | 1240 | 1521.4286 | 0
2016-01-17 16:00 | 3049 | 742.026 | 633 | 1240 | 1521.4286 | 0
2016-01-17 17:00 | 3049 | 768.968 | 619 | 1240 | 1521.4286 | 0
2016-01-17 18:00 | 2327 | 802.37 | 561 | 1240 | 1521.4286 | 0
2016-01-17 19:00 | 2327 | 835.791 | 351 | 1240 | 1521.4286 | 0
2016-01-17 20:00 | 2327 | 829.863 | 351 | 1240 | 1521.4286 | 0
2016-01-17 21:00 | 2327 | 859.18 | 351 | 1240 | 1673.3333 | 0
2016-01-17 22:00 | 2231 | 829.82 | 351 | 1240 | 1730 | 0
2016-01-17 23:00 | 2231 | 713.376 | 471 | 1240 | 1730 | 0
2016-01-18 | 2231 | 655.956 | 351 | 1240 | 1730 | 0
2016-01-18 01:00 | 2231 | 647.01 | 351 | 1240 | 1730 | 0
2016-01-18 02:00 | 2257 | 647.1 | 369 | 1240 | 1730 | 0
2016-01-18 03:00 | 2257 | 653.094 | 453 | 1240 | 1730 | 0
2016-01-18 04:00 | 2257 | 673.038 | 645 | 1240 | 1730 | 0
2016-01-18 05:00 | 2257 | 795.08 | 847 | 1240 | 1730 | 0
2016-01-18 06:00 | 2385 | 861.98 | 586 | 1240 | 1673.3333 | 0
2016-01-18 07:00 | 2385 | 849.509 | 510 | 1240 | 1521.4286 | 0
2016-01-18 08:00 | 2385 | 847.647 | 351 | 1240 | 1521.4286 | 0
2016-01-18 09:00 | 2385 | 845.044 | 387 | 1240 | 1521.4286 | 0
2016-01-18 10:00 | 2194 | 838.109 | 488 | 1240 | 1521.4286 | 0
2016-01-18 11:00 | 2194 | 822.928 | 391 | 1240 | 1430.7692 | 0
2016-01-18 12:00 | 2194 | 802.978 | 376 | 1240 | 1430.7692 | 0
2016-01-18 13:00 | 2194 | 786.391 | 351 | 1240 | 1521.4286 | 0
2016-01-18 14:00 | 3049 | 773.813 | 351 | 1240 | 1521.4286 | 0
2016-01-18 15:00 | 3049 | 763.496 | 512 | 1240 | 1521.4286 | 0
2016-01-18 16:00 | 3049 | 766.441 | 633 | 1240 | 1521.4286 | 0
2016-01-18 17:00 | 3049 | 783.313 | 619 | 1240 | 1430.7692 | 0
2016-01-18 18:00 | 2327 | 806.645 | 561 | 1240 | 1521.4286 | 0
2016-01-18 19:00 | 2327 | 829.996 | 351 | 1240 | 1521.4286 | 0
2016-01-18 20:00 | 2327 | 813.903 | 351 | 1240 | 1521.4286 | 0
2016-01-18 21:00 | 2327 | 781.869 | 351 | 1240 | 1521.4286 | 0
2016-01-18 22:00 | 2231 | 771.18 | 351 | 1240 | 1673.3333 | 0
2016-01-18 23:00 | 2231 | 641.07 | 471 | 1240 | 1730 | 0
2016-01-19 | 2231 | 601.272 | 351 | 1240 | 1730 | 0
2016-01-19 01:00 | 2231 | 584.28 | 351 | 1240 | 1730 | 0
2016-01-19 02:00 | 2257 | 579.492 | 369 | 1240 | 1730 | 0
2016-01-19 03:00 | 2257 | 581.256 | 453 | 1240 | 1730 | 0
2016-01-19 04:00 | 2257 | 594.414 | 645 | 1240 | 1730 | 0
2016-01-19 05:00 | 2257 | 644.544 | 847 | 1240 | 1730 | 0
2016-01-19 06:00 | 2385 | 809.66 | 586 | 1240 | 1673.3333 | 0
2016-01-19 07:00 | 2385 | 795.169 | 510 | 1240 | 1521.4286 | 0
2016-01-19 08:00 | 2385 | 814.54 | 351 | 1240 | 1521.4286 | 0
2016-01-19 09:00 | 2385 | 813.04 | 387 | 1240 | 1521.4286 | 0
2016-01-19 10:00 | 2194 | 776.036 | 488 | 1240 | 1521.4286 | 0
2016-01-19 11:00 | 2194 | 775.295 | 391 | 1240 | 1521.4286 | 0
2016-01-19 12:00 | 2194 | 772.692 | 376 | 1240 | 1521.4286 | 0
2016-01-19 13:00 | 2194 | 770.526 | 351 | 1240 | 1521.4286 | 0
2016-01-19 14:00 | 3049 | 764.522 | 351 | 1240 | 1521.4286 | 0
2016-01-19 15:00 | 3049 | 801.16 | 512 | 1240 | 1673.3333 | 0
2016-01-19 16:00 | 3049 | 801.46 | 633 | 1240 | 1673.3333 | 0
2016-01-19 17:00 | 3049 | 815.84 | 619 | 1240 | 1673.3333 | 0
2016-01-19 18:00 | 2327 | 838.96 | 561 | 1240 | 1673.3333 | 0
2016-01-19 19:00 | 2327 | 818.976 | 351 | 1240 | 1673.3333 | 0
2016-01-19 20:00 | 2327 | 847.64 | 351 | 1240 | 1673.3333 | 0
2016-01-19 21:00 | 2327 | 812.58 | 351 | 1240 | 1730 | 0
2016-01-19 22:00 | 2231 | 682.56 | 351 | 1240 | 1730 | 0
2016-01-19 23:00 | 2231 | 629.532 | 471 | 1240 | 1730 | 0
2016-01-20 | 2231 | 574.794 | 351 | 1240 | 1730 | 0
2016-01-20 01:00 | 2231 | 556.362 | 351 | 1240 | 1730 | 0
2016-01-20 02:00 | 2257 | 547.308 | 369 | 1240 | 1730 | 0
2016-01-20 03:00 | 2257 | 545.184 | 453 | 1240 | 1730 | 0
2016-01-20 04:00 | 2257 | 555.912 | 645 | 1240 | 1730 | 0
2016-01-20 05:00 | 2257 | 669 | 847 | 1240 | 1730 | 0
2016-01-20 06:00 | 2385 | 718.371 | 586 | 1240 | 1521.4286 | 0
2016-01-20 07:00 | 2385 | 749.987 | 510 | 1240 | 1521.4286 | 0
2016-01-20 08:00 | 2385 | 742.748 | 351 | 1240 | 1521.4286 | 0
2016-01-20 09:00 | 2385 | 786.48 | 387 | 1240 | 1521.4286 | 0
2016-01-20 10:00 | 2194 | 755.44 | 488 | 1240 | 1521.4286 | 0
2016-01-20 11:00 | 2194 | 758.024 | 391 | 1240 | 1521.4286 | 0
2016-01-20 12:00 | 2194 | 760.228 | 376 | 1240 | 1521.4286 | 0
2016-01-20 13:00 | 2194 | 757.872 | 351 | 1240 | 1521.4286 | 0
2016-01-20 14:00 | 3049 | 793.62 | 351 | 1240 | 1673.3333 | 0
2016-01-20 15:00 | 3049 | 791.06 | 512 | 1240 | 1673.3333 | 0
2016-01-20 16:00 | 3049 | 796.98 | 633 | 1240 | 1673.3333 | 0
2016-01-20 17:00 | 3049 | 804.92 | 619 | 1240 | 1673.3333 | 0
2016-01-20 18:00 | 2327 | 821.94 | 561 | 1240 | 1673.3333 | 0
2016-01-20 19:00 | 2327 | 838.96 | 351 | 1240 | 1730 | 0
2016-01-20 20:00 | 2327 | 823.26 | 351 | 1240 | 1730 | 0
2016-01-20 21:00 | 2327 | 712.476 | 351 | 1240 | 1730 | 0
2016-01-20 22:00 | 2231 | 663.624 | 351 | 1240 | 1730 | 0
2016-01-20 23:00 | 2231 | 612.9 | 471 | 1240 | 1730 | 0
2016-01-21 | 2231 | 557.892 | 351 | 1240 | 1730 | 0
2016-01-21 01:00 | 2231 | 543.492 | 351 | 1240 | 1730 | 0
2016-01-21 02:00 | 2257 | 537.498 | 369 | 1240 | 1730 | 0
2016-01-21 03:00 | 2257 | 539.874 | 453 | 1240 | 1730 | 0
2016-01-21 04:00 | 2257 | 554.328 | 645 | 1240 | 1730 | 0
2016-01-21 05:00 | 2257 | 598.698 | 847 | 1240 | 1730 | 0
2016-01-21 06:00 | 2385 | 681.984 | 586 | 1240 | 1730 | 0
2016-01-21 07:00 | 2385 | 791.46 | 510 | 1240 | 1673.3333 | 0
2016-01-21 08:00 | 2385 | 773.52 | 351 | 1240 | 1673.3333 | 0
2016-01-21 09:00 | 2385 | 769.1 | 387 | 1240 | 1673.3333 | 0
2016-01-21 10:00 | 2194 | 728.308 | 488 | 1240 | 1673.3333 | 0
2016-01-21 11:00 | 2194 | 724.717 | 391 | 1240 | 1521.4286 | 0
2016-01-21 12:00 | 2194 | 718.77 | 376 | 1240 | 1521.4286 | 0
2016-01-21 13:00 | 2194 | 718.637 | 351 | 1240 | 1521.4286 | 0
2016-01-21 14:00 | 3049 | 715.863 | 351 | 1240 | 1521.4286 | 0
2016-01-21 15:00 | 3049 | 712.861 | 512 | 1240 | 1521.4286 | 0
2016-01-21 16:00 | 3049 | 709.935 | 633 | 1240 | 1521.4286 | 0
2016-01-21 17:00 | 3049 | 712.196 | 619 | 1240 | 1521.4286 | 0
2016-01-21 18:00 | 2327 | 732.526 | 561 | 1240 | 1521.4286 | 0
2016-01-21 19:00 | 2327 | 752.837 | 351 | 1240 | 1521.4286 | 0
2016-01-21 20:00 | 2327 | 742.444 | 351 | 1240 | 1673.3333 | 0
2016-01-21 21:00 | 2327 | 753.78 | 351 | 1240 | 1673.3333 | 0
2016-01-21 22:00 | 2231 | 639.414 | 351 | 1240 | 1730 | 0
2016-01-21 23:00 | 2231 | 594.846 | 471 | 1240 | 1730 | 0
2016-01-22 | 2231 | 576.054 | 351 | 1240 | 1730 | 0
2016-01-22 01:00 | 2231 | 562.32 | 351 | 1240 | 1730 | 0
2016-01-22 02:00 | 2257 | 560.268 | 369 | 1240 | 1730 | 0
2016-01-22 03:00 | 2257 | 564.192 | 453 | 1240 | 1730 | 0
2016-01-22 04:00 | 2257 | 580.248 | 645 | 1240 | 1730 | 0
2016-01-22 05:00 | 2257 | 628.722 | 847 | 1240 | 1730 | 0
2016-01-22 06:00 | 2385 | 790.54 | 586 | 1240 | 1673.3333 | 0
2016-01-22 07:00 | 2385 | 821.8 | 510 | 1240 | 1673.3333 | 0
2016-01-22 08:00 | 2385 | 797.88 | 351 | 1240 | 1730 | 0
2016-01-22 09:00 | 2385 | 706.194 | 387 | 1240 | 1730 | 0
2016-01-22 10:00 | 2194 | 699.21 | 488 | 1240 | 1730 | 0
2016-01-22 11:00 | 2194 | 690.354 | 391 | 1240 | 1730 | 0
2016-01-22 12:00 | 2194 | 687.96 | 376 | 1240 | 1730 | 0
2016-01-22 13:00 | 2194 | 684.54 | 351 | 1240 | 1730 | 0
2016-01-22 14:00 | 3049 | 680.886 | 351 | 1240 | 1730 | 0
2016-01-22 15:00 | 3049 | 679.32 | 512 | 1240 | 1730 | 0
2016-01-22 16:00 | 3049 | 679.626 | 633 | 1240 | 1730 | 0
2016-01-22 17:00 | 3049 | 679.698 | 619 | 1240 | 1730 | 0
2016-01-22 18:00 | 2327 | 688.914 | 561 | 1240 | 1730 | 0
2016-01-22 19:00 | 2327 | 698.13 | 351 | 1240 | 1730 | 0
2016-01-22 20:00 | 2327 | 684.324 | 351 | 1240 | 1730 | 0
2016-01-22 21:00 | 2327 | 662.49 | 351 | 1240 | 1800 | 0
2016-01-22 22:00 | 2231 | 631.71 | 351 | 1240 | 1800 | 0
2016-01-22 23:00 | 2231 | 594.306 | 471 | 1240 | 1800 | 0
2016-01-23 | 2231 | 594.558 | 351 | 1240 | 1800 | 0
2016-01-23 01:00 | 2231 | 596.358 | 351 | 1240 | 1800 | 0
2016-01-23 02:00 | 2257 | 597.816 | 369 | 1240 | 1800 | 0
2016-01-23 03:00 | 2257 | 590.724 | 453 | 1240 | 1730 | 0
2016-01-23 04:00 | 2257 | 591.426 | 645 | 1240 | 1730 | 0
2016-01-23 05:00 | 2257 | 606.564 | 847 | 1240 | 1730 | 0
2016-01-23 06:00 | 2385 | 636.084 | 586 | 1240 | 1730 | 0
2016-01-23 07:00 | 2385 | 740.04 | 510 | 1240 | 1673.3333 | 0
2016-01-23 08:00 | 2385 | 735.623 | 351 | 1240 | 1673.3333 | 0
2016-01-23 09:00 | 2385 | 771.153 | 387 | 1240 | 1673.3333 | 0
2016-01-23 10:00 | 2194 | 838.02 | 488 | 1240 | 1673.3333 | 0
2016-01-23 11:00 | 2194 | 846.36 | 391 | 1240 | 1673.3333 | 0
2016-01-23 12:00 | 2194 | 840.36 | 376 | 1240 | 1673.3333 | 0
2016-01-23 13:00 | 2194 | 835.08 | 351 | 1240 | 1673.3333 | 0
2016-01-23 14:00 | 3049 | 835.5 | 351 | 1240 | 1673.3333 | 0
2016-01-23 15:00 | 3049 | 747.378 | 512 | 1240 | 1673.3333 | 0
2016-01-23 16:00 | 3049 | 748.296 | 633 | 1240 | 1673.3333 | 0
2016-01-23 17:00 | 3049 | 758.07 | 619 | 1240 | 1673.3333 | 0
2016-01-23 18:00 | 2327 | 863.06 | 561 | 1240 | 1673.3333 | 0
2016-01-23 19:00 | 2327 | 883.82 | 351 | 1240 | 1673.3333 | 0
2016-01-23 20:00 | 2327 | 868.24 | 351 | 1240 | 1673.3333 | 0
2016-01-23 21:00 | 2327 | 845.5 | 351 | 1240 | 1673.3333 | 0
2016-01-23 22:00 | 2231 | 730.926 | 351 | 1240 | 1730 | 0
2016-01-23 23:00 | 2231 | 698.778 | 471 | 1240 | 1730 | 0
2016-01-24 | 2231 | 663.894 | 351 | 1240 | 1730 | 0
2016-01-24 01:00 | 2231 | 645.984 | 351 | 1240 | 1730 | 0
2016-01-24 02:00 | 2257 | 638.73 | 369 | 1240 | 1730 | 0
2016-01-24 03:00 | 2257 | 635.22 | 453 | 1240 | 1730 | 0
2016-01-24 04:00 | 2257 | 640.656 | 645 | 1240 | 1730 | 0
2016-01-24 05:00 | 2257 | 656.208 | 847 | 1240 | 1730 | 0
2016-01-24 06:00 | 2385 | 685.242 | 586 | 1240 | 1730 | 0
2016-01-24 07:00 | 2385 | 791.3 | 510 | 1240 | 1730 | 0
2016-01-24 08:00 | 2385 | 820.32 | 351 | 1240 | 1730 | 0
2016-01-24 09:00 | 2385 | 834.48 | 387 | 1240 | 1673.3333 | 0
2016-01-24 10:00 | 2194 | 830.14 | 488 | 1240 | 1673.3333 | 0
2016-01-24 11:00 | 2194 | 818.2 | 391 | 1240 | 1673.3333 | 0
2016-01-24 12:00 | 2194 | 808.1 | 376 | 1240 | 1730 | 0
2016-01-24 13:00 | 2194 | 797.36 | 351 | 1240 | 1673.3333 | 0
2016-01-24 14:00 | 3049 | 787.76 | 351 | 1240 | 1673.3333 | 0
2016-01-24 15:00 | 3049 | 781.72 | 512 | 1240 | 1673.3333 | 0
2016-01-24 16:00 | 3049 | 792.64 | 633 | 1240 | 1673.3333 | 0
2016-01-24 17:00 | 3049 | 817.74 | 619 | 1240 | 1673.3333 | 0
2016-01-24 18:00 | 2327 | 863.14 | 561 | 1240 | 1673.3333 | 0
2016-01-24 19:00 | 2327 | 863.132 | 351 | 1240 | 1521.4286 | 0
2016-01-24 20:00 | 2327 | 856.216 | 351 | 1240 | 1521.4286 | 0
2016-01-24 21:00 | 2327 | 885.04 | 351 | 1240 | 1521.4286 | 0
2016-01-24 22:00 | 2231 | 803.529 | 351 | 1240 | 1521.4286 | 0
2016-01-24 23:00 | 2231 | 756.257 | 471 | 1240 | 1521.4286 | 0
2016-01-25 | 2231 | 716.86 | 351 | 1240 | 1521.4286 | 0
2016-01-25 01:00 | 2231 | 637.956 | 351 | 1240 | 1521.4286 | 0
2016-01-25 02:00 | 2257 | 639.612 | 369 | 1240 | 1521.4286 | 0
2016-01-25 03:00 | 2257 | 722.92 | 453 | 1240 | 1521.4286 | 0
2016-01-25 04:00 | 2257 | 754.28 | 645 | 1240 | 1521.4286 | 0
2016-01-25 05:00 | 2257 | 786.809 | 847 | 1240 | 1430.7692 | 0
2016-01-25 06:00 | 2385 | 947.62 | 586 | 1240 | 1440 | 0
2016-01-25 07:00 | 2385 | 939.132 | 510 | 1240 | 1440 | 0
2016-01-25 08:00 | 2385 | 902.082 | 351 | 1240 | 1440 | 0
2016-01-25 09:00 | 2385 | 910.52 | 387 | 1240 | 1440 | 0
2016-01-25 10:00 | 2194 | 879.56 | 488 | 1240 | 1440 | 0
2016-01-25 11:00 | 2194 | 852.1 | 391 | 1240 | 1440 | 0
2016-01-25 12:00 | 2194 | 829.5 | 376 | 1240 | 1440 | 0
2016-01-25 13:00 | 2194 | 814.04 | 351 | 1240 | 1440 | 0
2016-01-25 14:00 | 3049 | 799.16 | 351 | 1240 | 1440 | 0
2016-01-25 15:00 | 3049 | 788.72 | 512 | 1240 | 1440 | 0
2016-01-25 16:00 | 3049 | 795.48 | 633 | 1240 | 1440 | 0
2016-01-25 17:00 | 3049 | 819.14 | 619 | 1240 | 1440 | 0
2016-01-25 18:00 | 2327 | 856.3 | 561 | 1240 | 1440 | 0
2016-01-25 19:00 | 2327 | 848.787 | 351 | 1240 | 1440 | 0
2016-01-25 20:00 | 2327 | 841.643 | 351 | 1240 | 1440 | 0
2016-01-25 21:00 | 2327 | 858.04 | 351 | 1240 | 1440 | 0
2016-01-25 22:00 | 2231 | 806.3 | 351 | 1240 | 1430.7692 | 0
2016-01-25 23:00 | 2231 | 719.017 | 471 | 1240 | 1430.7692 | 0
2016-01-26 | 2231 | 698.193 | 351 | 1240 | 1430.7692 | 0
2016-01-26 01:00 | 2231 | 689.016 | 351 | 1240 | 1430.7692 | 0
2016-01-26 02:00 | 2257 | 691.315 | 369 | 1240 | 1430.7692 | 0
2016-01-26 03:00 | 2257 | 703.532 | 453 | 1240 | 1430.7692 | 0
2016-01-26 04:00 | 2257 | 731.291 | 645 | 1240 | 1430.7692 | 0
2016-01-26 05:00 | 2257 | 800.527 | 847 | 1240 | 1430.7692 | 0
2016-01-26 06:00 | 2385 | 955.06 | 586 | 1240 | 1440 | 0
2016-01-26 07:00 | 2385 | 938.277 | 510 | 1240 | 1440 | 0
2016-01-26 08:00 | 2385 | 942.44 | 351 | 1240 | 1440 | 0
2016-01-26 09:00 | 2385 | 899.58 | 387 | 1240 | 1430.7692 | 0
2016-01-26 10:00 | 2194 | 868.76 | 488 | 1240 | 1430.7692 | 0
2016-01-26 11:00 | 2194 | 842.7 | 391 | 1240 | 1430.7692 | 0
2016-01-26 12:00 | 2194 | 780.026 | 376 | 1240 | 1430.7692 | 0
2016-01-26 13:00 | 2194 | 767.182 | 351 | 1240 | 1430.7692 | 0
2016-01-26 14:00 | 3049 | 754.338 | 351 | 1240 | 1521.4286 | 0
2016-01-26 15:00 | 3049 | 788.08 | 512 | 1240 | 1521.4286 | 0
2016-01-26 16:00 | 3049 | 793.72 | 633 | 1240 | 1521.4286 | 0
2016-01-26 17:00 | 3049 | 772.198 | 619 | 1240 | 1521.4286 | 0
2016-01-26 18:00 | 2327 | 805.847 | 561 | 1240 | 1521.4286 | 0
2016-01-26 19:00 | 2327 | 839.496 | 351 | 1240 | 1521.4286 | 0
2016-01-26 20:00 | 2327 | 879.32 | 351 | 1240 | 1673.3333 | 0
2016-01-26 21:00 | 2327 | 851.92 | 351 | 1240 | 1673.3333 | 0
2016-01-26 22:00 | 2231 | 718.794 | 351 | 1240 | 1730 | 0
2016-01-26 23:00 | 2231 | 671.292 | 471 | 1240 | 1730 | 0
2016-01-27 | 2231 | 634.23 | 351 | 1240 | 1730 | 0
2016-01-27 01:00 | 2231 | 621.594 | 351 | 1240 | 1730 | 0
2016-01-27 02:00 | 2257 | 616.68 | 369 | 1240 | 1730 | 0
2016-01-27 03:00 | 2257 | 619.308 | 453 | 1240 | 1730 | 0
2016-01-27 04:00 | 2257 | 632.772 | 645 | 1240 | 1730 | 0
2016-01-27 05:00 | 2257 | 757.24 | 847 | 1240 | 1730 | 0
2016-01-27 06:00 | 2385 | 806.132 | 586 | 1240 | 1673.3333 | 0
2016-01-27 07:00 | 2385 | 832.846 | 510 | 1240 | 1521.4286 | 0
2016-01-27 08:00 | 2385 | 810.502 | 351 | 1240 | 1521.4286 | 0
2016-01-27 09:00 | 2385 | 846.66 | 387 | 1240 | 1521.4286 | 0
2016-01-27 10:00 | 2194 | 844.14 | 488 | 1240 | 1673.3333 | 0
2016-01-27 11:00 | 2194 | 831 | 391 | 1240 | 1673.3333 | 0
2016-01-27 12:00 | 2194 | 817.26 | 376 | 1240 | 1673.3333 | 0
2016-01-27 13:00 | 2194 | 806.52 | 351 | 1240 | 1673.3333 | 0
2016-01-27 14:00 | 3049 | 752.229 | 351 | 1240 | 1521.4286 | 0
2016-01-27 15:00 | 3049 | 744.154 | 512 | 1240 | 1521.4286 | 0
2016-01-27 16:00 | 3049 | 751.317 | 633 | 1240 | 1521.4286 | 0
2016-01-27 17:00 | 3049 | 775.238 | 619 | 1240 | 1521.4286 | 0
2016-01-27 18:00 | 2327 | 790.78 | 561 | 1240 | 1521.4286 | 0
2016-01-27 19:00 | 2327 | 806.303 | 351 | 1240 | 1521.4286 | 0
2016-01-27 20:00 | 2327 | 832.64 | 351 | 1240 | 1673.3333 | 0
2016-01-27 21:00 | 2327 | 802.44 | 351 | 1240 | 1673.3333 | 0
2016-01-27 22:00 | 2231 | 749.14 | 351 | 1240 | 1673.3333 | 0
2016-01-27 23:00 | 2231 | 622.386 | 471 | 1240 | 1730 | 0
2016-01-28 | 2231 | 566.532 | 351 | 1240 | 1730 | 0
2016-01-28 01:00 | 2231 | 550.512 | 351 | 1240 | 1730 | 0
2016-01-28 02:00 | 2257 | 542.934 | 369 | 1240 | 1730 | 0
2016-01-28 03:00 | 2257 | 545.832 | 453 | 1240 | 1730 | 0
2016-01-28 04:00 | 2257 | 561.69 | 645 | 1240 | 1730 | 0
2016-01-28 05:00 | 2257 | 608.868 | 847 | 1240 | 1730 | 0
2016-01-28 06:00 | 2385 | 761.26 | 586 | 1240 | 1730 | 0
2016-01-28 07:00 | 2385 | 799.12 | 510 | 1240 | 1730 | 0
2016-01-28 08:00 | 2385 | 709.74 | 351 | 1240 | 1730 | 0
2016-01-28 09:00 | 2385 | 715.032 | 387 | 1240 | 1730 | 0
2016-01-28 10:00 | 2194 | 721.584 | 488 | 1240 | 1730 | 0
2016-01-28 11:00 | 2194 | 721.35 | 391 | 1240 | 1730 | 0
2016-01-28 12:00 | 2194 | 720.756 | 376 | 1240 | 1800 | 0
2016-01-28 13:00 | 2194 | 721.746 | 351 | 1240 | 1800 | 0
2016-01-28 14:00 | 3049 | 716.904 | 351 | 1240 | 1800 | 0
2016-01-28 15:00 | 3049 | 719.01 | 512 | 1240 | 1800 | 0
2016-01-28 16:00 | 3049 | 729.846 | 633 | 1240 | 1730 | 0
2016-01-28 17:00 | 3049 | 834.48 | 619 | 1240 | 1730 | 0
2016-01-28 18:00 | 2327 | 764.37 | 561 | 1240 | 1730 | 0
2016-01-28 19:00 | 2327 | 864.12 | 351 | 1240 | 1730 | 0
2016-01-28 20:00 | 2327 | 851.04 | 351 | 1240 | 1730 | 0
2016-01-28 21:00 | 2327 | 820.28 | 351 | 1240 | 1730 | 0
2016-01-28 22:00 | 2231 | 695.052 | 351 | 1240 | 1730 | 0
2016-01-28 23:00 | 2231 | 649.314 | 471 | 1240 | 1730 | 0
2016-01-29 | 2231 | 604.818 | 351 | 1240 | 1730 | 0
2016-01-29 01:00 | 2231 | 591.156 | 351 | 1240 | 1730 | 0
2016-01-29 02:00 | 2257 | 586.278 | 369 | 1240 | 1730 | 0
2016-01-29 03:00 | 2257 | 591.048 | 453 | 1240 | 1730 | 0
2016-01-29 04:00 | 2257 | 609.336 | 645 | 1240 | 1730 | 0
2016-01-29 05:00 | 2257 | 737.56 | 847 | 1240 | 1730 | 0
2016-01-29 06:00 | 2385 | 789.45 | 586 | 1240 | 1521.4286 | 0
2016-01-29 07:00 | 2385 | 881.32 | 510 | 1240 | 1430.7692 | 0
2016-01-29 08:00 | 2385 | 879.18 | 351 | 1240 | 1430.7692 | 0
2016-01-29 09:00 | 2385 | 847.761 | 387 | 1240 | 1430.7692 | 0
2016-01-29 10:00 | 2194 | 855.969 | 488 | 1240 | 1430.7692 | 0
2016-01-29 11:00 | 2194 | 853.917 | 391 | 1240 | 1430.7692 | 0
2016-01-29 12:00 | 2194 | 845.614 | 376 | 1240 | 1430.7692 | 0
2016-01-29 13:00 | 2194 | 845.424 | 351 | 1240 | 1430.7692 | 0
2016-01-29 14:00 | 3049 | 847.761 | 351 | 1240 | 1521.4286 | 0
2016-01-29 15:00 | 3049 | 854.354 | 512 | 1240 | 1521.4286 | 0
2016-01-29 16:00 | 3049 | 868.813 | 633 | 1240 | 1521.4286 | 0
2016-01-29 17:00 | 3049 | 945.92 | 619 | 1240 | 1430.7692 | 0
2016-01-29 18:00 | 2327 | 972.22 | 561 | 1240 | 1430.7692 | 0
2016-01-29 19:00 | 2327 | 998.54 | 351 | 1240 | 1440 | 0
2016-01-29 20:00 | 2327 | 942.02 | 351 | 1240 | 1440 | 0
2016-01-29 21:00 | 2327 | 924.236 | 351 | 1240 | 1440 | 0
2016-01-29 22:00 | 2231 | 893.551 | 351 | 1240 | 1440 | 0
2016-01-29 23:00 | 2231 | 904.5 | 471 | 1240 | 1440 | 0
2016-01-30 | 2231 | 902.14 | 351 | 1240 | 1440 | 0
2016-01-30 01:00 | 2231 | 890.46 | 351 | 1240 | 1440 | 0
2016-01-30 02:00 | 2257 | 887.78 | 369 | 1240 | 1440 | 0
2016-01-30 03:00 | 2257 | 894.52 | 453 | 1240 | 1440 | 0
2016-01-30 04:00 | 2257 | 907.48 | 645 | 1240 | 1440 | 0
2016-01-30 05:00 | 2257 | 934.94 | 847 | 1240 | 1440 | 0
2016-01-30 06:00 | 2385 | 923.571 | 586 | 1240 | 1440 | 0
2016-01-30 07:00 | 2385 | 956.213 | 510 | 1240 | 1238.9381 | 0
2016-01-30 08:00 | 2385 | 984.561 | 351 | 1240 | 1238.9381 | 0
2016-01-30 09:00 | 2385 | 1107.498 | 387 | 1240 | 1238.9381 | 0
2016-01-30 10:00 | 2194 | 1097.523 | 488 | 1240 | 1238.9381 | 0
2016-01-30 11:00 | 2194 | 1068.879 | 391 | 1240 | 1238.9381 | 0
2016-01-30 12:00 | 2194 | 934.515 | 376 | 1240 | 1238.9381 | 0
2016-01-30 13:00 | 2194 | 899.764 | 351 | 1240 | 1238.9381 | 0
2016-01-30 14:00 | 3049 | 874.19 | 351 | 1240 | 1238.9381 | 0
2016-01-30 15:00 | 3049 | 868.49 | 512 | 1240 | 1238.9381 | 0
2016-01-30 16:00 | 3049 | 876.052 | 633 | 1240 | 1238.9381 | 0
2016-01-30 17:00 | 3049 | 898.187 | 619 | 1240 | 1238.9381 | 0
2016-01-30 18:00 | 2327 | 1025.304 | 561 | 1240 | 1238.9381 | 0
2016-01-30 19:00 | 2327 | 1057.875 | 351 | 1240 | 1238.9381 | 0
2016-01-30 20:00 | 2327 | 953.895 | 351 | 1240 | 1238.9381 | 0
2016-01-30 21:00 | 2327 | 940.348 | 351 | 1240 | 1238.9381 | 0
2016-01-30 22:00 | 2231 | 908.257 | 351 | 1240 | 1440 | 0
2016-01-30 23:00 | 2231 | 926.14 | 471 | 1240 | 1440 | 0
2016-01-31 | 2231 | 925.62 | 351 | 1240 | 1440 | 0
2016-01-31 01:00 | 2231 | 925.08 | 351 | 1240 | 1440 | 0
2016-01-31 02:00 | 2257 | 915.96 | 369 | 1240 | 1440 | 0
2016-01-31 03:00 | 2257 | 914.34 | 453 | 1240 | 1440 | 0
2016-01-31 04:00 | 2257 | 921.36 | 645 | 1240 | 1440 | 0
2016-01-31 05:00 | 2257 | 940 | 847 | 1240 | 1440 | 0
2016-01-31 06:00 | 2385 | 921.196 | 586 | 1240 | 1440 | 0
2016-01-31 07:00 | 2385 | 948.442 | 510 | 1240 | 1440 | 0
2016-01-31 08:00 | 2385 | 977.531 | 351 | 1240 | 1238.9381 | 0
2016-01-31 09:00 | 2385 | 994.27 | 387 | 1240 | 1238.9381 | 0
2016-01-31 10:00 | 2194 | 1096.641 | 488 | 1240 | 1238.9381 | 0
2016-01-31 11:00 | 2194 | 1074.171 | 391 | 1240 | 1238.9381 | 0
2016-01-31 12:00 | 2194 | 952.603 | 376 | 1240 | 1238.9381 | 0
2016-01-31 13:00 | 2194 | 931.076 | 351 | 1240 | 1238.9381 | 0
2016-01-31 14:00 | 3049 | 909.663 | 351 | 1240 | 1440 | 0
2016-01-31 15:00 | 3049 | 942.78 | 512 | 1240 | 1440 | 0
2016-01-31 16:00 | 3049 | 943.66 | 633 | 1240 | 1440 | 0
2016-01-31 17:00 | 3049 | 921.234 | 619 | 1240 | 1440 | 0
2016-01-31 18:00 | 2327 | 964.307 | 561 | 1240 | 1440 | 0
2016-01-31 19:00 | 2327 | 1007.399 | 351 | 1240 | 1440 | 0
2016-01-31 20:00 | 2327 | 1007.741 | 351 | 1240 | 1440 | 0
2016-01-31 21:00 | 2327 | 984.257 | 351 | 1240 | 1440 | 0
2016-01-31 22:00 | 2231 | 987.28 | 351 | 1240 | 1430.7692 | 0
2016-01-31 23:00 | 2231 | 933.38 | 471 | 1240 | 1430.7692 | 0
2016-02-01 | 2818 | 829.008 | 374 | 1240 | 1430.7692 | 0
2016-02-01 01:00 | 2818 | 816.221 | 337 | 1240 | 1430.7692 | 0
2016-02-01 02:00 | 2512 | 813.618 | 339 | 1240 | 1430.7692 | 0
2016-02-01 03:00 | 2512 | 859.84 | 399 | 1240 | 1430.7692 | 0
2016-02-01 04:00 | 2512 | 880.84 | 620 | 1240 | 1430.7692 | 0
2016-02-01 05:00 | 2512 | 940.32 | 769 | 1240 | 1440 | 0
2016-02-01 06:00 | 3020 | 981.806 | 578 | 1240 | 1238.9381 | 0
2016-02-01 07:00 | 3020 | 1113.399 | 408 | 1240 | 1238.9381 | 0
2016-02-01 08:00 | 3020 | 980.552 | 378 | 1240 | 1238.9381 | 0
2016-02-01 09:00 | 3020 | 966.378 | 404 | 1240 | 1238.9381 | 0
2016-02-01 10:00 | 2484 | 950.342 | 364 | 1240 | 1238.9381 | 0
2016-02-01 11:00 | 2484 | 927.466 | 337 | 1240 | 1238.9381 | 0
2016-02-01 12:00 | 2484 | 902.31 | 350 | 1240 | 1238.9381 | 0
2016-02-01 13:00 | 2484 | 880.479 | 339 | 1240 | 1238.9381 | 0
2016-02-01 14:00 | 2568 | 859.864 | 337 | 1240 | 1238.9381 | 0
2016-02-01 15:00 | 2568 | 851.58 | 354 | 1240 | 1238.9381 | 0
2016-02-01 16:00 | 2568 | 861.992 | 437 | 1240 | 1238.9381 | 0
2016-02-01 17:00 | 2568 | 891.347 | 574 | 1240 | 1238.9381 | 0
2016-02-01 18:00 | 3274 | 910.974 | 690 | 1240 | 1238.9381 | 0
2016-02-01 19:00 | 3274 | 1028.559 | 381 | 1240 | 1238.9381 | 0
2016-02-01 20:00 | 3274 | 912.627 | 337 | 1240 | 1238.9381 | 0
2016-02-01 21:00 | 3274 | 878.313 | 337 | 1240 | 1440 | 0
2016-02-01 22:00 | 2818 | 861.6 | 337 | 1240 | 1440 | 0
2016-02-01 23:00 | 2818 | 761.596 | 457 | 1240 | 1440 | 0
2016-02-02 | 2818 | 759.164 | 374 | 1240 | 1440 | 0
2016-02-02 01:00 | 2818 | 742.406 | 337 | 1240 | 1440 | 0
2016-02-02 02:00 | 2512 | 738.15 | 339 | 1240 | 1440 | 0
2016-02-02 03:00 | 2512 | 741.703 | 399 | 1240 | 1430.7692 | 0
2016-02-02 04:00 | 2512 | 801.36 | 620 | 1240 | 1430.7692 | 0
2016-02-02 05:00 | 2512 | 860.48 | 769 | 1240 | 1440 | 0
2016-02-02 06:00 | 3020 | 908.048 | 578 | 1240 | 1238.9381 | 0
2016-02-02 07:00 | 3020 | 934.895 | 408 | 1240 | 1238.9381 | 0
2016-02-02 08:00 | 3020 | 910.233 | 378 | 1240 | 1238.9381 | 0
2016-02-02 09:00 | 3020 | 902.899 | 404 | 1240 | 1238.9381 | 0
2016-02-02 10:00 | 2484 | 894.425 | 364 | 1240 | 1238.9381 | 0
2016-02-02 11:00 | 2484 | 874.684 | 337 | 1240 | 1238.9381 | 0
2016-02-02 12:00 | 2484 | 853.822 | 350 | 1240 | 1238.9381 | 0
2016-02-02 13:00 | 2484 | 834.936 | 339 | 1240 | 1440 | 0
2016-02-02 14:00 | 2568 | 859.76 | 337 | 1240 | 1440 | 0
2016-02-02 15:00 | 2568 | 848.96 | 354 | 1240 | 1440 | 0
2016-02-02 16:00 | 2568 | 856.56 | 437 | 1240 | 1440 | 0
2016-02-02 17:00 | 2568 | 887.74 | 574 | 1240 | 1440 | 0
2016-02-02 18:00 | 3274 | 924.42 | 690 | 1240 | 1440 | 0
2016-02-02 19:00 | 3274 | 913.026 | 381 | 1240 | 1440 | 0
2016-02-02 20:00 | 3274 | 906.357 | 337 | 1240 | 1440 | 0
2016-02-02 21:00 | 3274 | 925.72 | 337 | 1240 | 1440 | 0
2016-02-02 22:00 | 2818 | 875.6 | 337 | 1240 | 1430.7692 | 0
2016-02-02 23:00 | 2818 | 778.582 | 457 | 1240 | 1430.7692 | 0
2016-02-03 | 2818 | 740.12 | 374 | 1240 | 1430.7692 | 0
2016-02-03 01:00 | 2818 | 728.66 | 337 | 1240 | 1430.7692 | 0
2016-02-03 02:00 | 2512 | 726.08 | 339 | 1240 | 1430.7692 | 0
2016-02-03 03:00 | 2512 | 729.1 | 399 | 1240 | 1430.7692 | 0
2016-02-03 04:00 | 2512 | 751.88 | 620 | 1240 | 1430.7692 | 0
2016-02-03 05:00 | 2512 | 770.488 | 769 | 1240 | 1430.7692 | 0
2016-02-03 06:00 | 3020 | 902.46 | 578 | 1240 | 1430.7692 | 0
2016-02-03 07:00 | 3020 | 932.36 | 408 | 1240 | 1430.7692 | 0
2016-02-03 08:00 | 3020 | 912.3 | 378 | 1240 | 1430.7692 | 0
2016-02-03 09:00 | 3020 | 864.937 | 404 | 1240 | 1430.7692 | 0
2016-02-03 10:00 | 2484 | 861.574 | 364 | 1240 | 1521.4286 | 0
2016-02-03 11:00 | 2484 | 853.252 | 337 | 1240 | 1521.4286 | 0
2016-02-03 12:00 | 2484 | 844.208 | 350 | 1240 | 1521.4286 | 0
2016-02-03 13:00 | 2484 | 884.22 | 339 | 1240 | 1521.4286 | 0
2016-02-03 14:00 | 2568 | 881.24 | 337 | 1240 | 1673.3333 | 0
2016-02-03 15:00 | 2568 | 886 | 354 | 1240 | 1673.3333 | 0
2016-02-03 16:00 | 2568 | 898.72 | 437 | 1240 | 1673.3333 | 0
2016-02-03 17:00 | 2568 | 928.86 | 574 | 1240 | 1673.3333 | 0
2016-02-03 18:00 | 3274 | 941.66 | 690 | 1240 | 1673.3333 | 0
2016-02-03 19:00 | 3274 | 906.756 | 381 | 1240 | 1521.4286 | 0
2016-02-03 20:00 | 3274 | 891.252 | 337 | 1240 | 1521.4286 | 0
2016-02-03 21:00 | 3274 | 857.166 | 337 | 1240 | 1521.4286 | 0
2016-02-03 22:00 | 2818 | 802.56 | 337 | 1240 | 1521.4286 | 0
2016-02-03 23:00 | 2818 | 789.96 | 457 | 1240 | 1521.4286 | 0
2016-02-04 | 2818 | 729.64 | 374 | 1240 | 1673.3333 | 0
2016-02-04 01:00 | 2818 | 713 | 337 | 1240 | 1673.3333 | 0
2016-02-04 02:00 | 2512 | 705.08 | 339 | 1240 | 1673.3333 | 0
2016-02-04 03:00 | 2512 | 706.62 | 399 | 1240 | 1673.3333 | 0
2016-02-04 04:00 | 2512 | 684.285 | 620 | 1240 | 1521.4286 | 0
2016-02-04 05:00 | 2512 | 728.631 | 769 | 1240 | 1521.4286 | 0
2016-02-04 06:00 | 3020 | 848.68 | 578 | 1240 | 1430.7692 | 0
2016-02-04 07:00 | 3020 | 880.9 | 408 | 1240 | 1440 | 0
2016-02-04 08:00 | 3020 | 866.62 | 378 | 1240 | 1440 | 0
2016-02-04 09:00 | 3020 | 866.24 | 404 | 1240 | 1440 | 0
2016-02-04 10:00 | 2484 | 870.4 | 364 | 1240 | 1440 | 0
2016-02-04 11:00 | 2484 | 868.28 | 337 | 1240 | 1440 | 0
2016-02-04 12:00 | 2484 | 860.46 | 350 | 1240 | 1440 | 0
2016-02-04 13:00 | 2484 | 854.32 | 339 | 1240 | 1440 | 0
2016-02-04 14:00 | 2568 | 844.56 | 337 | 1240 | 1440 | 0
2016-02-04 15:00 | 2568 | 840.76 | 354 | 1240 | 1440 | 0
2016-02-04 16:00 | 2568 | 849.32 | 437 | 1240 | 1440 | 0
2016-02-04 17:00 | 2568 | 869.34 | 574 | 1240 | 1440 | 0
2016-02-04 18:00 | 3274 | 884.22 | 690 | 1240 | 1440 | 0
2016-02-04 19:00 | 3274 | 854.145 | 381 | 1240 | 1440 | 0
2016-02-04 20:00 | 3274 | 838.793 | 337 | 1240 | 1440 | 0
2016-02-04 21:00 | 3274 | 849.48 | 337 | 1240 | 1430.7692 | 0
2016-02-04 22:00 | 2818 | 796.46 | 337 | 1240 | 1430.7692 | 0
2016-02-04 23:00 | 2818 | 705.432 | 457 | 1240 | 1521.4286 | 0
2016-02-05 | 2818 | 692.379 | 374 | 1240 | 1521.4286 | 0
2016-02-05 01:00 | 2818 | 710.06 | 337 | 1240 | 1521.4286 | 0
2016-02-05 02:00 | 2512 | 705 | 339 | 1240 | 1521.4286 | 0
2016-02-05 03:00 | 2512 | 709.82 | 399 | 1240 | 1521.4286 | 0
2016-02-05 04:00 | 2512 | 729.12 | 620 | 1240 | 1521.4286 | 0
2016-02-05 05:00 | 2512 | 784.1 | 769 | 1240 | 1521.4286 | 0
2016-02-05 06:00 | 3020 | 828.134 | 578 | 1240 | 1521.4286 | 0
2016-02-05 07:00 | 3020 | 898.8 | 408 | 1240 | 1521.4286 | 0
2016-02-05 08:00 | 3020 | 834.765 | 378 | 1240 | 1521.4286 | 0
2016-02-05 09:00 | 3020 | 824.733 | 404 | 1240 | 1521.4286 | 0
2016-02-05 10:00 | 2484 | 810.274 | 364 | 1240 | 1521.4286 | 0
2016-02-05 11:00 | 2484 | 786.657 | 337 | 1240 | 1430.7692 | 0
2016-02-05 12:00 | 2484 | 761.767 | 350 | 1240 | 1430.7692 | 0
2016-02-05 13:00 | 2484 | 744.42 | 339 | 1240 | 1430.7692 | 0
2016-02-05 14:00 | 2568 | 726.636 | 337 | 1240 | 1430.7692 | 0
2016-02-05 15:00 | 2568 | 714.704 | 354 | 1240 | 1430.7692 | 0
2016-02-05 16:00 | 2568 | 710.049 | 437 | 1240 | 1430.7692 | 0
2016-02-05 17:00 | 2568 | 719.511 | 574 | 1240 | 1430.7692 | 0
2016-02-05 18:00 | 3274 | 745.845 | 690 | 1240 | 1430.7692 | 0
2016-02-05 19:00 | 3274 | 812.84 | 381 | 1240 | 1430.7692 | 0
2016-02-05 20:00 | 3274 | 805.76 | 337 | 1240 | 1430.7692 | 0
2016-02-05 21:00 | 3274 | 793.86 | 337 | 1240 | 1430.7692 | 0
2016-02-05 22:00 | 2818 | 731.424 | 337 | 1240 | 1430.7692 | 0
2016-02-05 23:00 | 2818 | 702.658 | 457 | 1240 | 1430.7692 | 0
2016-02-06 | 2818 | 707.389 | 374 | 1240 | 1430.7692 | 0
2016-02-06 01:00 | 2818 | 722.589 | 337 | 1240 | 1430.7692 | 0
2016-02-06 02:00 | 2512 | 735.224 | 339 | 1240 | 1430.7692 | 0
2016-02-06 03:00 | 2512 | 740.487 | 399 | 1240 | 1430.7692 | 0
2016-02-06 04:00 | 2512 | 758.347 | 620 | 1240 | 1430.7692 | 0
2016-02-06 05:00 | 2512 | 790.704 | 769 | 1240 | 1430.7692 | 0
2016-02-06 06:00 | 3020 | 878.3 | 578 | 1240 | 1440 | 0
2016-02-06 07:00 | 3020 | 867.616 | 408 | 1240 | 1440 | 0
2016-02-06 08:00 | 3020 | 884.469 | 378 | 1240 | 1238.9381 | 0
2016-02-06 09:00 | 3020 | 880.878 | 404 | 1240 | 1238.9381 | 0
2016-02-06 10:00 | 2484 | 866.115 | 364 | 1240 | 1238.9381 | 0
2016-02-06 11:00 | 2484 | 840.351 | 337 | 1240 | 1440 | 0
2016-02-06 12:00 | 2484 | 856.24 | 350 | 1240 | 1440 | 0
2016-02-06 13:00 | 2484 | 826.5 | 339 | 1240 | 1440 | 0
2016-02-06 14:00 | 2568 | 803.14 | 337 | 1240 | 1440 | 0
2016-02-06 15:00 | 2568 | 792.02 | 354 | 1240 | 1440 | 0
2016-02-06 16:00 | 2568 | 793.6 | 437 | 1240 | 1440 | 0
2016-02-06 17:00 | 2568 | 814.34 | 574 | 1240 | 1440 | 0
2016-02-06 18:00 | 3274 | 852.58 | 690 | 1240 | 1440 | 0
2016-02-06 19:00 | 3274 | 890.82 | 381 | 1240 | 1440 | 0
2016-02-06 20:00 | 3274 | 886.18 | 337 | 1240 | 1430.7692 | 0
2016-02-06 21:00 | 3274 | 828.115 | 337 | 1240 | 1521.4286 | 0
2016-02-06 22:00 | 2818 | 803.947 | 337 | 1240 | 1521.4286 | 0
2016-02-06 23:00 | 2818 | 774.421 | 457 | 1240 | 1521.4286 | 0
2016-02-07 | 2818 | 758.955 | 374 | 1240 | 1521.4286 | 0
2016-02-07 01:00 | 2818 | 745.275 | 337 | 1240 | 1521.4286 | 0
2016-02-07 02:00 | 2512 | 737.523 | 339 | 1240 | 1521.4286 | 0
2016-02-07 03:00 | 2512 | 737.162 | 399 | 1240 | 1521.4286 | 0
2016-02-07 04:00 | 2512 | 742.102 | 620 | 1240 | 1521.4286 | 0
2016-02-07 05:00 | 2512 | 759.126 | 769 | 1240 | 1521.4286 | 0
2016-02-07 06:00 | 3020 | 787.531 | 578 | 1240 | 1430.7692 | 0
2016-02-07 07:00 | 3020 | 859.04 | 408 | 1240 | 1430.7692 | 0
2016-02-07 08:00 | 3020 | 893.5 | 378 | 1240 | 1430.7692 | 0
2016-02-07 09:00 | 3020 | 919.72 | 404 | 1240 | 1430.7692 | 0
2016-02-07 10:00 | 2484 | 924.78 | 364 | 1240 | 1430.7692 | 0
2016-02-07 11:00 | 2484 | 918.74 | 337 | 1240 | 1430.7692 | 0
2016-02-07 12:00 | 2484 | 866.951 | 350 | 1240 | 1430.7692 | 0
2016-02-07 13:00 | 2484 | 860.89 | 339 | 1240 | 1430.7692 | 0
2016-02-07 14:00 | 2568 | 855.95 | 337 | 1240 | 1521.4286 | 0
2016-02-07 15:00 | 2568 | 852.682 | 354 | 1240 | 1521.4286 | 0
2016-02-07 16:00 | 2568 | 857.147 | 437 | 1240 | 1521.4286 | 0
2016-02-07 17:00 | 2568 | 875.14 | 574 | 1240 | 1521.4286 | 0
2016-02-07 18:00 | 3274 | 885.381 | 690 | 1240 | 1521.4286 | 0
2016-02-07 19:00 | 3274 | 895.622 | 381 | 1240 | 1521.4286 | 0
2016-02-07 20:00 | 3274 | 880.194 | 337 | 1240 | 1521.4286 | 0
2016-02-07 21:00 | 3274 | 875.273 | 337 | 1240 | 1521.4286 | 0
2016-02-07 22:00 | 2818 | 828.989 | 337 | 1240 | 1521.4286 | 0
2016-02-07 23:00 | 2818 | 810 | 457 | 1240 | 1673.3333 | 0
2016-02-08 | 2818 | 733.02 | 374 | 1240 | 1673.3333 | 0
2016-02-08 01:00 | 2818 | 712.92 | 337 | 1240 | 1673.3333 | 0
2016-02-08 02:00 | 2512 | 705.7 | 339 | 1240 | 1673.3333 | 0
2016-02-08 03:00 | 2512 | 707.08 | 399 | 1240 | 1673.3333 | 0
2016-02-08 04:00 | 2512 | 726.22 | 620 | 1240 | 1673.3333 | 0
2016-02-08 05:00 | 2512 | 782.86 | 769 | 1240 | 1521.4286 | 0
2016-02-08 06:00 | 3020 | 829.103 | 578 | 1240 | 1521.4286 | 0
2016-02-08 07:00 | 3020 | 905.76 | 408 | 1240 | 1430.7692 | 0
2016-02-08 08:00 | 3020 | 849.148 | 378 | 1240 | 1430.7692 | 0
2016-02-08 09:00 | 3020 | 851.523 | 404 | 1240 | 1430.7692 | 0
2016-02-08 10:00 | 2484 | 857.451 | 364 | 1240 | 1430.7692 | 0
2016-02-08 11:00 | 2484 | 855.646 | 337 | 1240 | 1430.7692 | 0
2016-02-08 12:00 | 2484 | 850.098 | 350 | 1240 | 1430.7692 | 0
2016-02-08 13:00 | 2484 | 846.469 | 339 | 1240 | 1430.7692 | 0
2016-02-08 14:00 | 2568 | 839.382 | 337 | 1240 | 1430.7692 | 0
2016-02-08 15:00 | 2568 | 839.439 | 354 | 1240 | 1430.7692 | 0
2016-02-08 16:00 | 2568 | 850.535 | 437 | 1240 | 1430.7692 | 0
2016-02-08 17:00 | 2568 | 876.546 | 574 | 1240 | 1430.7692 | 0
2016-02-08 18:00 | 3274 | 902.025 | 690 | 1240 | 1430.7692 | 0
2016-02-08 19:00 | 3274 | 976.32 | 381 | 1240 | 1430.7692 | 0
2016-02-08 20:00 | 3274 | 968.02 | 337 | 1240 | 1430.7692 | 0
2016-02-08 21:00 | 3274 | 943.82 | 337 | 1240 | 1430.7692 | 0
2016-02-08 22:00 | 2818 | 893.22 | 337 | 1240 | 1430.7692 | 0
2016-02-08 23:00 | 2818 | 802.009 | 457 | 1240 | 1430.7692 | 0
2016-02-09 | 2818 | 776.5 | 374 | 1240 | 1430.7692 | 0
2016-02-09 01:00 | 2818 | 771.22 | 337 | 1240 | 1430.7692 | 0
2016-02-09 02:00 | 2512 | 778.06 | 339 | 1240 | 1430.7692 | 0
2016-02-09 03:00 | 2512 | 791.82 | 399 | 1240 | 1430.7692 | 0
2016-02-09 04:00 | 2512 | 784.149 | 620 | 1240 | 1430.7692 | 0
2016-02-09 05:00 | 2512 | 899.06 | 769 | 1240 | 1430.7692 | 0
2016-02-09 06:00 | 3020 | 958.246 | 578 | 1240 | 1238.9381 | 0
2016-02-09 07:00 | 3020 | 1093.071 | 408 | 1240 | 1238.9381 | 0
2016-02-09 08:00 | 3020 | 957.505 | 378 | 1240 | 1238.9381 | 0
2016-02-09 09:00 | 3020 | 934.287 | 404 | 1240 | 1238.9381 | 0
2016-02-09 10:00 | 2484 | 912.874 | 364 | 1240 | 1238.9381 | 0
2016-02-09 11:00 | 2484 | 889.58 | 337 | 1240 | 1238.9381 | 0
2016-02-09 12:00 | 2484 | 862.315 | 350 | 1240 | 1238.9381 | 0
2016-02-09 13:00 | 2484 | 835.791 | 339 | 1240 | 1238.9381 | 0
2016-02-09 14:00 | 2568 | 852.38 | 337 | 1240 | 1238.9381 | 0
2016-02-09 15:00 | 2568 | 835.48 | 354 | 1240 | 1238.9381 | 0
2016-02-09 16:00 | 2568 | 848.24 | 437 | 1240 | 1238.9381 | 0
2016-02-09 17:00 | 2568 | 836.893 | 574 | 1240 | 1238.9381 | 0
2016-02-09 18:00 | 3274 | 889.77 | 690 | 1240 | 1238.9381 | 0
2016-02-09 19:00 | 3274 | 942.628 | 381 | 1240 | 1238.9381 | 0
2016-02-09 20:00 | 3274 | 950.646 | 337 | 1240 | 1238.9381 | 0
2016-02-09 21:00 | 3274 | 935.104 | 337 | 1240 | 1440 | 0
2016-02-09 22:00 | 2818 | 932.54 | 337 | 1240 | 1440 | 0
2016-02-09 23:00 | 2818 | 884.7 | 457 | 1240 | 1430.7692 | 0
2016-02-10 | 2818 | 803.054 | 374 | 1240 | 1430.7692 | 0
2016-02-10 01:00 | 2818 | 791.692 | 337 | 1240 | 1430.7692 | 0
2016-02-10 02:00 | 2512 | 789.602 | 339 | 1240 | 1430.7692 | 0
2016-02-10 03:00 | 2512 | 796.119 | 399 | 1240 | 1430.7692 | 0
2016-02-10 04:00 | 2512 | 819.527 | 620 | 1240 | 1430.7692 | 0
2016-02-10 05:00 | 2512 | 924.94 | 769 | 1240 | 1430.7692 | 0
2016-02-10 06:00 | 3020 | 968.506 | 578 | 1240 | 1440 | 0
2016-02-10 07:00 | 3020 | 988.741 | 408 | 1240 | 1440 | 0
2016-02-10 08:00 | 3020 | 956.327 | 378 | 1240 | 1440 | 0
2016-02-10 09:00 | 3020 | 986.2 | 404 | 1240 | 1440 | 0
2016-02-10 10:00 | 2484 | 970.6 | 364 | 1240 | 1430.7692 | 0
2016-02-10 11:00 | 2484 | 954.76 | 337 | 1240 | 1430.7692 | 0
2016-02-10 12:00 | 2484 | 938.42 | 350 | 1240 | 1430.7692 | 0
2016-02-10 13:00 | 2484 | 927.18 | 339 | 1240 | 1430.7692 | 0
2016-02-10 14:00 | 2568 | 915.9 | 337 | 1240 | 1430.7692 | 0
2016-02-10 15:00 | 2568 | 917.92 | 354 | 1240 | 1440 | 0
2016-02-10 16:00 | 2568 | 938.68 | 437 | 1240 | 1440 | 0
2016-02-10 17:00 | 2568 | 974.28 | 574 | 1240 | 1440 | 0
2016-02-10 18:00 | 3274 | 997.94 | 690 | 1240 | 1440 | 0
2016-02-10 19:00 | 3274 | 1021.6 | 381 | 1240 | 1440 | 0
2016-02-10 20:00 | 3274 | 1006.08 | 337 | 1240 | 1430.7692 | 0
2016-02-10 21:00 | 3274 | 975.44 | 337 | 1240 | 1430.7692 | 0
2016-02-10 22:00 | 2818 | 907.92 | 337 | 1240 | 1430.7692 | 0
2016-02-10 23:00 | 2818 | 813.162 | 457 | 1240 | 1430.7692 | 0
2016-02-11 | 2818 | 779.7 | 374 | 1240 | 1430.7692 | 0
2016-02-11 01:00 | 2818 | 734.882 | 337 | 1240 | 1430.7692 | 0
2016-02-11 02:00 | 2512 | 725.458 | 339 | 1240 | 1430.7692 | 0
2016-02-11 03:00 | 2512 | 731.481 | 399 | 1240 | 1430.7692 | 0
2016-02-11 04:00 | 2512 | 754.775 | 620 | 1240 | 1430.7692 | 0
2016-02-11 05:00 | 2512 | 850.32 | 769 | 1240 | 1430.7692 | 0
2016-02-11 06:00 | 3020 | 890.093 | 578 | 1240 | 1440 | 0
2016-02-11 07:00 | 3020 | 918.46 | 408 | 1240 | 1238.9381 | 0
2016-02-11 08:00 | 3020 | 902.272 | 378 | 1240 | 1440 | 0
2016-02-11 09:00 | 3020 | 901.759 | 404 | 1240 | 1440 | 0
2016-02-11 10:00 | 2484 | 901.113 | 364 | 1240 | 1440 | 0
2016-02-11 11:00 | 2484 | 901.265 | 337 | 1240 | 1440 | 0
2016-02-11 12:00 | 2484 | 897.389 | 350 | 1240 | 1440 | 0
2016-02-11 13:00 | 2484 | 893.323 | 339 | 1240 | 1238.9381 | 0
2016-02-11 14:00 | 2568 | 886.882 | 337 | 1240 | 1238.9381 | 0
2016-02-11 15:00 | 2568 | 885.514 | 354 | 1240 | 1238.9381 | 0
2016-02-11 16:00 | 2568 | 898.51 | 437 | 1240 | 1238.9381 | 0
2016-02-11 17:00 | 2568 | 921.557 | 574 | 1240 | 1238.9381 | 0
2016-02-11 18:00 | 3274 | 936.548 | 690 | 1240 | 1238.9381 | 0
2016-02-11 19:00 | 3274 | 1051.722 | 381 | 1240 | 1238.9381 | 0
2016-02-11 20:00 | 3274 | 931.589 | 337 | 1240 | 1238.9381 | 0
2016-02-11 21:00 | 3274 | 898.358 | 337 | 1240 | 1238.9381 | 0
2016-02-11 22:00 | 2818 | 848.027 | 337 | 1240 | 1440 | 0
2016-02-11 23:00 | 2818 | 846.32 | 457 | 1240 | 1440 | 0
2016-02-12 | 2818 | 828.62 | 374 | 1240 | 1440 | 0
2016-02-12 01:00 | 2818 | 811.88 | 337 | 1240 | 1440 | 0
2016-02-12 02:00 | 2512 | 808.42 | 339 | 1240 | 1440 | 0
2016-02-12 03:00 | 2512 | 810.52 | 399 | 1240 | 1440 | 0
2016-02-12 04:00 | 2512 | 832.16 | 620 | 1240 | 1440 | 0
2016-02-12 05:00 | 2512 | 879.02 | 769 | 1240 | 1440 | 0
2016-02-12 06:00 | 3020 | 901.588 | 578 | 1240 | 1440 | 0
2016-02-12 07:00 | 3020 | 923.324 | 408 | 1240 | 1440 | 0
2016-02-12 08:00 | 3020 | 915.078 | 378 | 1240 | 1440 | 0
2016-02-12 09:00 | 3020 | 910.537 | 404 | 1240 | 1440 | 0
2016-02-12 10:00 | 2484 | 897.256 | 364 | 1240 | 1440 | 0
2016-02-12 11:00 | 2484 | 881.258 | 337 | 1240 | 1440 | 0
2016-02-12 12:00 | 2484 | 863.246 | 350 | 1240 | 1440 | 0
2016-02-12 13:00 | 2484 | 848.407 | 339 | 1240 | 1440 | 0
2016-02-12 14:00 | 2568 | 831.839 | 337 | 1240 | 1440 | 0
2016-02-12 15:00 | 2568 | 864.48 | 354 | 1240 | 1440 | 0
2016-02-12 16:00 | 2568 | 863.26 | 437 | 1240 | 1440 | 0
2016-02-12 17:00 | 2568 | 836.304 | 574 | 1240 | 1440 | 0
2016-02-12 18:00 | 3274 | 861.346 | 690 | 1240 | 1440 | 0
2016-02-12 19:00 | 3274 | 886.369 | 381 | 1240 | 1440 | 0
2016-02-12 20:00 | 3274 | 880.175 | 337 | 1240 | 1440 | 0
2016-02-12 21:00 | 3274 | 911.32 | 337 | 1240 | 1430.7692 | 0
2016-02-12 22:00 | 2818 | 878.36 | 337 | 1240 | 1521.4286 | 0
2016-02-12 23:00 | 2818 | 827.089 | 457 | 1240 | 1521.4286 | 0
2016-02-13 | 2818 | 830.889 | 374 | 1240 | 1521.4286 | 0
2016-02-13 01:00 | 2818 | 840.389 | 337 | 1240 | 1521.4286 | 0
2016-02-13 02:00 | 2512 | 855.988 | 339 | 1240 | 1521.4286 | 0
2016-02-13 03:00 | 2512 | 859.446 | 399 | 1240 | 1521.4286 | 0
2016-02-13 04:00 | 2512 | 872.043 | 620 | 1240 | 1521.4286 | 0
2016-02-13 05:00 | 2512 | 898.567 | 769 | 1240 | 1430.7692 | 0
2016-02-13 06:00 | 3020 | 981.94 | 578 | 1240 | 1430.7692 | 0
2016-02-13 07:00 | 3020 | 1012.62 | 408 | 1240 | 1430.7692 | 0
2016-02-13 08:00 | 3020 | 1032.48 | 378 | 1240 | 1440 | 0
2016-02-13 09:00 | 3020 | 982.205 | 404 | 1240 | 1440 | 0
2016-02-13 10:00 | 2484 | 962.977 | 364 | 1240 | 1440 | 0
2016-02-13 11:00 | 2484 | 923.001 | 337 | 1240 | 1440 | 0
2016-02-13 12:00 | 2484 | 923.98 | 350 | 1240 | 1440 | 0
2016-02-13 13:00 | 2484 | 876.82 | 339 | 1240 | 1440 | 0
2016-02-13 14:00 | 2568 | 836.22 | 337 | 1240 | 1440 | 0
2016-02-13 15:00 | 2568 | 767.182 | 354 | 1240 | 1440 | 0
2016-02-13 16:00 | 2568 | 760.38 | 437 | 1240 | 1440 | 0
2016-02-13 17:00 | 2568 | 780.007 | 574 | 1240 | 1440 | 0
2016-02-13 18:00 | 3274 | 866.42 | 690 | 1240 | 1440 | 0
2016-02-13 19:00 | 3274 | 911.76 | 381 | 1240 | 1440 | 0
2016-02-13 20:00 | 3274 | 867.578 | 337 | 1240 | 1440 | 0
2016-02-13 21:00 | 3274 | 857.584 | 337 | 1240 | 1440 | 0
2016-02-13 22:00 | 2818 | 879.88 | 337 | 1240 | 1440 | 0
2016-02-13 23:00 | 2818 | 850.78 | 457 | 1240 | 1430.7692 | 0
2016-02-14 | 2818 | 846.62 | 374 | 1240 | 1430.7692 | 0
2016-02-14 01:00 | 2818 | 846.36 | 337 | 1240 | 1430.7692 | 0
2016-02-14 02:00 | 2512 | 842.18 | 339 | 1240 | 1430.7692 | 0
2016-02-14 03:00 | 2512 | 802.18 | 399 | 1240 | 1430.7692 | 0
2016-02-14 04:00 | 2512 | 813.219 | 620 | 1240 | 1430.7692 | 0
2016-02-14 05:00 | 2512 | 834.176 | 769 | 1240 | 1430.7692 | 0
2016-02-14 06:00 | 3020 | 910.76 | 578 | 1240 | 1430.7692 | 0
2016-02-14 07:00 | 3020 | 933.04 | 408 | 1240 | 1430.7692 | 0
2016-02-14 08:00 | 3020 | 945.62 | 378 | 1240 | 1430.7692 | 0
2016-02-14 09:00 | 3020 | 933.74 | 404 | 1240 | 1430.7692 | 0
2016-02-14 10:00 | 2484 | 913.08 | 364 | 1240 | 1430.7692 | 0
2016-02-14 11:00 | 2484 | 846.773 | 337 | 1240 | 1521.4286 | 0
2016-02-14 12:00 | 2484 | 837.178 | 350 | 1240 | 1521.4286 | 0
2016-02-14 13:00 | 2484 | 874.68 | 339 | 1240 | 1521.4286 | 0
2016-02-14 14:00 | 2568 | 868.94 | 337 | 1240 | 1521.4286 | 0
2016-02-14 15:00 | 2568 | 873.56 | 354 | 1240 | 1521.4286 | 0
2016-02-14 16:00 | 2568 | 890.42 | 437 | 1240 | 1521.4286 | 0
2016-02-14 17:00 | 2568 | 873.487 | 574 | 1240 | 1521.4286 | 0
2016-02-14 18:00 | 3274 | 908.96 | 690 | 1240 | 1521.4286 | 0
2016-02-14 19:00 | 3274 | 994.14 | 381 | 1240 | 1430.7692 | 0
2016-02-14 20:00 | 3274 | 947.188 | 337 | 1240 | 1440 | 0
2016-02-14 21:00 | 3274 | 937.479 | 337 | 1240 | 1440 | 0
2016-02-14 22:00 | 2818 | 907.972 | 337 | 1240 | 1440 | 0
2016-02-14 23:00 | 2818 | 922.6 | 457 | 1240 | 1440 | 0
2016-02-15 | 2818 | 780.862 | 374 | 1240 | 1440 | 0
2016-02-15 01:00 | 2818 | 781.242 | 337 | 1240 | 1440 | 0
2016-02-15 02:00 | 2512 | 788.709 | 339 | 1240 | 1440 | 0
2016-02-15 03:00 | 2512 | 801.553 | 399 | 1240 | 1440 | 0
2016-02-15 04:00 | 2512 | 830.034 | 620 | 1240 | 1440 | 0
2016-02-15 05:00 | 2512 | 932.76 | 769 | 1240 | 1440 | 0
2016-02-15 06:00 | 3020 | 967.309 | 578 | 1240 | 1440 | 0
2016-02-15 07:00 | 3020 | 998.165 | 408 | 1240 | 1440 | 0
2016-02-15 08:00 | 3020 | 976.828 | 378 | 1240 | 1440 | 0
2016-02-15 09:00 | 3020 | 1008.38 | 404 | 1240 | 1430.7692 | 0
2016-02-15 10:00 | 2484 | 986.16 | 364 | 1240 | 1440 | 0
2016-02-15 11:00 | 2484 | 955.24 | 337 | 1240 | 1430.7692 | 0
2016-02-15 12:00 | 2484 | 921.4 | 350 | 1240 | 1430.7692 | 0
2016-02-15 13:00 | 2484 | 846.089 | 339 | 1240 | 1430.7692 | 0
2016-02-15 14:00 | 2568 | 817.969 | 337 | 1240 | 1430.7692 | 0
2016-02-15 15:00 | 2568 | 799.273 | 354 | 1240 | 1430.7692 | 0
2016-02-15 16:00 | 2568 | 847 | 437 | 1240 | 1430.7692 | 0
2016-02-15 17:00 | 2568 | 867.8 | 574 | 1240 | 1430.7692 | 0
2016-02-15 18:00 | 3274 | 872.651 | 690 | 1240 | 1440 | 0
2016-02-15 19:00 | 3274 | 920.873 | 381 | 1240 | 1238.9381 | 0
2016-02-15 20:00 | 3274 | 925.965 | 337 | 1240 | 1238.9381 | 0
2016-02-15 21:00 | 3274 | 914.527 | 337 | 1240 | 1238.9381 | 0
2016-02-15 22:00 | 2818 | 876.185 | 337 | 1240 | 1238.9381 | 0
2016-02-15 23:00 | 2818 | 835.145 | 457 | 1240 | 1238.9381 | 0
2016-02-16 | 2818 | 829.73 | 374 | 1240 | 1238.9381 | 0
2016-02-16 01:00 | 2818 | 869.34 | 337 | 1240 | 1238.9381 | 0
2016-02-16 02:00 | 2512 | 834.632 | 339 | 1240 | 1238.9381 | 0
2016-02-16 03:00 | 2512 | 848.521 | 399 | 1240 | 1238.9381 | 0
2016-02-16 04:00 | 2512 | 877.819 | 620 | 1240 | 1238.9381 | 0
2016-02-16 05:00 | 2512 | 1041.726 | 769 | 1240 | 1238.9381 | 0
2016-02-16 06:00 | 3020 | 1198.89 | 578 | 1240 | 1296.2963 | 0
2016-02-16 07:00 | 3020 | 1213.762 | 408 | 1240 | 1296.2963 | 0
2016-02-16 08:00 | 3020 | 1093.911 | 378 | 1240 | 1296.2963 | 0
2016-02-16 09:00 | 3020 | 1032.528 | 404 | 1240 | 1238.9381 | 0
2016-02-16 10:00 | 2484 | 890.055 | 364 | 1240 | 1238.9381 | 0
2016-02-16 11:00 | 2484 | 849.471 | 337 | 1240 | 1238.9381 | 0
2016-02-16 12:00 | 2484 | 859.44 | 350 | 1240 | 1440 | 0
2016-02-16 13:00 | 2484 | 833.44 | 339 | 1240 | 1440 | 0
2016-02-16 14:00 | 2568 | 809.46 | 337 | 1240 | 1440 | 0
2016-02-16 15:00 | 2568 | 795.86 | 354 | 1240 | 1440 | 0
2016-02-16 16:00 | 2568 | 798.4 | 437 | 1240 | 1440 | 0
2016-02-16 17:00 | 2568 | 823.28 | 574 | 1240 | 1440 | 0
2016-02-16 18:00 | 3274 | 836.589 | 690 | 1240 | 1440 | 0
2016-02-16 19:00 | 3274 | 891.062 | 381 | 1240 | 1238.9381 | 0
2016-02-16 20:00 | 3274 | 900.372 | 337 | 1240 | 1238.9381 | 0
2016-02-16 21:00 | 3274 | 889.371 | 337 | 1240 | 1238.9381 | 0
2016-02-16 22:00 | 2818 | 850.003 | 337 | 1240 | 1238.9381 | 0
2016-02-16 23:00 | 2818 | 855.14 | 457 | 1240 | 1440 | 0
2016-02-17 | 2818 | 837.02 | 374 | 1240 | 1440 | 0
2016-02-17 01:00 | 2818 | 833.4 | 337 | 1240 | 1440 | 0
2016-02-17 02:00 | 2512 | 842 | 339 | 1240 | 1440 | 0
2016-02-17 03:00 | 2512 | 857.8 | 399 | 1240 | 1440 | 0
2016-02-17 04:00 | 2512 | 847.172 | 620 | 1240 | 1238.9381 | 0
2016-02-17 05:00 | 2512 | 915.496 | 769 | 1240 | 1296.2963 | 0
2016-02-17 06:00 | 3020 | 1125.726 | 578 | 1240 | 1296.2963 | 0
2016-02-17 07:00 | 3020 | 1140.069 | 408 | 1240 | 1296.2963 | 0
2016-02-17 08:00 | 3020 | 965.808 | 378 | 1240 | 1238.9381 | 0
2016-02-17 09:00 | 3020 | 909.834 | 404 | 1240 | 1238.9381 | 0
2016-02-17 10:00 | 2484 | 908.96 | 364 | 1240 | 1440 | 0
2016-02-17 11:00 | 2484 | 865.94 | 337 | 1240 | 1440 | 0
2016-02-17 12:00 | 2484 | 829.18 | 350 | 1240 | 1440 | 0
2016-02-17 13:00 | 2484 | 764.446 | 339 | 1240 | 1430.7692 | 0
2016-02-17 14:00 | 2568 | 742.425 | 337 | 1240 | 1430.7692 | 0
2016-02-17 15:00 | 2568 | 731.937 | 354 | 1240 | 1430.7692 | 0
2016-02-17 16:00 | 2568 | 737.124 | 437 | 1240 | 1430.7692 | 0
2016-02-17 17:00 | 2568 | 759.81 | 574 | 1240 | 1430.7692 | 0
2016-02-17 18:00 | 3274 | 844.04 | 690 | 1240 | 1430.7692 | 0
2016-02-17 19:00 | 3274 | 888.28 | 381 | 1240 | 1430.7692 | 0
2016-02-17 20:00 | 3274 | 855.209 | 337 | 1240 | 1430.7692 | 0
2016-02-17 21:00 | 3274 | 849.11 | 337 | 1240 | 1521.4286 | 0
2016-02-17 22:00 | 2818 | 853.22 | 337 | 1240 | 1521.4286 | 0
2016-02-17 23:00 | 2818 | 809.72 | 457 | 1240 | 1521.4286 | 0
2016-02-18 | 2818 | 673.758 | 374 | 1240 | 1521.4286 | 0
2016-02-18 01:00 | 2818 | 669.744 | 337 | 1240 | 1521.4286 | 0
2016-02-18 02:00 | 2512 | 674.622 | 339 | 1240 | 1521.4286 | 0
2016-02-18 03:00 | 2512 | 686.538 | 399 | 1240 | 1521.4286 | 0
2016-02-18 04:00 | 2512 | 790.72 | 620 | 1240 | 1521.4286 | 0
2016-02-18 05:00 | 2512 | 861.94 | 769 | 1240 | 1521.4286 | 0
2016-02-18 06:00 | 3020 | 909.34 | 578 | 1240 | 1430.7692 | 0
2016-02-18 07:00 | 3020 | 972.1 | 408 | 1240 | 1430.7692 | 0
2016-02-18 08:00 | 3020 | 870.181 | 378 | 1240 | 1521.4286 | 0
2016-02-18 09:00 | 3020 | 864.32 | 404 | 1240 | 1673.3333 | 0
2016-02-18 10:00 | 2484 | 833.9 | 364 | 1240 | 1673.3333 | 0
2016-02-18 11:00 | 2484 | 721.998 | 337 | 1240 | 1730 | 0
2016-02-18 12:00 | 2484 | 694.098 | 350 | 1240 | 1730 | 0
2016-02-18 13:00 | 2484 | 674.082 | 339 | 1240 | 1730 | 0
2016-02-18 14:00 | 2568 | 659.196 | 337 | 1240 | 1730 | 0
2016-02-18 15:00 | 2568 | 651.78 | 354 | 1240 | 1730 | 0
2016-02-18 16:00 | 2568 | 653.508 | 437 | 1240 | 1730 | 0
2016-02-18 17:00 | 2568 | 667.566 | 574 | 1240 | 1730 | 0
2016-02-18 18:00 | 3274 | 704.52 | 690 | 1240 | 1730 | 0
2016-02-18 19:00 | 3274 | 823.86 | 381 | 1240 | 1730 | 0
2016-02-18 20:00 | 3274 | 824.78 | 337 | 1240 | 1730 | 0
2016-02-18 21:00 | 3274 | 724.086 | 337 | 1240 | 1730 | 0
2016-02-18 22:00 | 2818 | 687.078 | 337 | 1240 | 1730 | 0
2016-02-18 23:00 | 2818 | 646.002 | 457 | 1240 | 1730 | 0
2016-02-19 | 2818 | 628.902 | 374 | 1240 | 1730 | 0
2016-02-19 01:00 | 2818 | 620.082 | 337 | 1240 | 1730 | 0
2016-02-19 02:00 | 2512 | 614.916 | 339 | 1240 | 1730 | 0
2016-02-19 03:00 | 2512 | 617.274 | 399 | 1240 | 1730 | 0
2016-02-19 04:00 | 2512 | 633.744 | 620 | 1240 | 1730 | 0
2016-02-19 05:00 | 2512 | 753.46 | 769 | 1240 | 1730 | 0
2016-02-19 06:00 | 3020 | 794.238 | 578 | 1240 | 1521.4286 | 0
2016-02-19 07:00 | 3020 | 815.176 | 408 | 1240 | 1521.4286 | 0
2016-02-19 08:00 | 3020 | 794.751 | 378 | 1240 | 1521.4286 | 0
2016-02-19 09:00 | 3020 | 785.194 | 404 | 1240 | 1521.4286 | 0
2016-02-19 10:00 | 2484 | 777.024 | 364 | 1240 | 1521.4286 | 0
2016-02-19 11:00 | 2484 | 761.387 | 337 | 1240 | 1521.4286 | 0
2016-02-19 12:00 | 2484 | 744.002 | 350 | 1240 | 1521.4286 | 0
2016-02-19 13:00 | 2484 | 730.759 | 339 | 1240 | 1521.4286 | 0
2016-02-19 14:00 | 2568 | 714.666 | 337 | 1240 | 1521.4286 | 0
2016-02-19 15:00 | 2568 | 707.066 | 354 | 1240 | 1521.4286 | 0
2016-02-19 16:00 | 2568 | 708.643 | 437 | 1240 | 1521.4286 | 0
2016-02-19 17:00 | 2568 | 719.321 | 574 | 1240 | 1521.4286 | 0
2016-02-19 18:00 | 3274 | 735.205 | 690 | 1240 | 1521.4286 | 0
2016-02-19 19:00 | 3274 | 751.089 | 381 | 1240 | 1521.4286 | 0
2016-02-19 20:00 | 3274 | 740.487 | 337 | 1240 | 1521.4286 | 0
2016-02-19 21:00 | 3274 | 720.328 | 337 | 1240 | 1521.4286 | 0
2016-02-19 22:00 | 2818 | 723.78 | 337 | 1240 | 1673.3333 | 0
2016-02-19 23:00 | 2818 | 616.86 | 457 | 1240 | 1673.3333 | 0
2016-02-20 | 2818 | 613.188 | 374 | 1240 | 1673.3333 | 0
2016-02-20 01:00 | 2818 | 607.788 | 337 | 1240 | 1673.3333 | 0
2016-02-20 02:00 | 2512 | 597.996 | 339 | 1240 | 1673.3333 | 0
2016-02-20 03:00 | 2512 | 599.616 | 399 | 1240 | 1673.3333 | 0
2016-02-20 04:00 | 2512 | 603.234 | 620 | 1240 | 1673.3333 | 0
2016-02-20 05:00 | 2512 | 623.07 | 769 | 1240 | 1673.3333 | 0
2016-02-20 06:00 | 3020 | 717.34 | 578 | 1240 | 1673.3333 | 0
2016-02-20 07:00 | 3020 | 744.5 | 408 | 1240 | 1673.3333 | 0
2016-02-20 08:00 | 3020 | 770.18 | 378 | 1240 | 1673.3333 | 0
2016-02-20 09:00 | 3020 | 784.06 | 404 | 1240 | 1673.3333 | 0
2016-02-20 10:00 | 2484 | 783.4 | 364 | 1240 | 1673.3333 | 0
2016-02-20 11:00 | 2484 | 769.68 | 337 | 1240 | 1673.3333 | 0
2016-02-20 12:00 | 2484 | 752.84 | 350 | 1240 | 1673.3333 | 0
2016-02-20 13:00 | 2484 | 733.2 | 339 | 1240 | 1673.3333 | 0
2016-02-20 14:00 | 2568 | 650.844 | 337 | 1240 | 1730 | 0
2016-02-20 15:00 | 2568 | 646.758 | 354 | 1240 | 1730 | 0
2016-02-20 16:00 | 2568 | 648.468 | 437 | 1240 | 1730 | 0
2016-02-20 17:00 | 2568 | 664.668 | 574 | 1240 | 1730 | 0
2016-02-20 18:00 | 3274 | 683.64 | 690 | 1240 | 1730 | 0
2016-02-20 19:00 | 3274 | 780.68 | 381 | 1240 | 1730 | 0
2016-02-20 20:00 | 3274 | 768.94 | 337 | 1240 | 1730 | 0
2016-02-20 21:00 | 3274 | 671.958 | 337 | 1240 | 1730 | 0
2016-02-20 22:00 | 2818 | 645.282 | 337 | 1240 | 1730 | 0
2016-02-20 23:00 | 2818 | 612.144 | 457 | 1240 | 1730 | 0
2016-02-21 | 2818 | 612.558 | 374 | 1240 | 1730 | 0
2016-02-21 01:00 | 2818 | 681.02 | 337 | 1240 | 1730 | 0
2016-02-21 02:00 | 2512 | 681.54 | 339 | 1240 | 1730 | 0
2016-02-21 03:00 | 2512 | 678.62 | 399 | 1240 | 1730 | 0
2016-02-21 04:00 | 2512 | 609.318 | 620 | 1240 | 1730 | 0
2016-02-21 05:00 | 2512 | 621.684 | 769 | 1240 | 1730 | 0
2016-02-21 06:00 | 3020 | 714.34 | 578 | 1240 | 1730 | 0
2016-02-21 07:00 | 3020 | 733.14 | 408 | 1240 | 1673.3333 | 0
2016-02-21 08:00 | 3020 | 766 | 378 | 1240 | 1673.3333 | 0
2016-02-21 09:00 | 3020 | 757.701 | 404 | 1240 | 1521.4286 | 0
2016-02-21 10:00 | 2484 | 770.849 | 364 | 1240 | 1521.4286 | 0
2016-02-21 11:00 | 2484 | 772.255 | 337 | 1240 | 1521.4286 | 0
2016-02-21 12:00 | 2484 | 766.517 | 350 | 1240 | 1521.4286 | 0
2016-02-21 13:00 | 2484 | 796.3 | 339 | 1240 | 1521.4286 | 0
2016-02-21 14:00 | 2568 | 790.68 | 337 | 1240 | 1521.4286 | 0
2016-02-21 15:00 | 2568 | 787.24 | 354 | 1240 | 1521.4286 | 0
2016-02-21 16:00 | 2568 | 793.88 | 437 | 1240 | 1521.4286 | 0
2016-02-21 17:00 | 2568 | 774.915 | 574 | 1240 | 1521.4286 | 0
2016-02-21 18:00 | 3274 | 856.86 | 690 | 1240 | 1430.7692 | 0
2016-02-21 19:00 | 3274 | 898 | 381 | 1240 | 1430.7692 | 0
2016-02-21 20:00 | 3274 | 895.34 | 337 | 1240 | 1430.7692 | 0
2016-02-21 21:00 | 3274 | 876.44 | 337 | 1240 | 1430.7692 | 0
2016-02-21 22:00 | 2818 | 832.82 | 337 | 1240 | 1430.7692 | 0
2016-02-21 23:00 | 2818 | 743.09 | 457 | 1240 | 1430.7692 | 0
2016-02-22 | 2818 | 676.16 | 374 | 1240 | 1430.7692 | 0
2016-02-22 01:00 | 2818 | 665.9 | 337 | 1240 | 1430.7692 | 0
2016-02-22 02:00 | 2512 | 669.34 | 339 | 1240 | 1430.7692 | 0
2016-02-22 03:00 | 2512 | 683.44 | 399 | 1240 | 1430.7692 | 0
2016-02-22 04:00 | 2512 | 676.818 | 620 | 1240 | 1430.7692 | 0
2016-02-22 05:00 | 2512 | 743.014 | 769 | 1240 | 1430.7692 | 0
2016-02-22 06:00 | 3020 | 889.28 | 578 | 1240 | 1440 | 0
2016-02-22 07:00 | 3020 | 882.398 | 408 | 1240 | 1440 | 0
2016-02-22 08:00 | 3020 | 874.266 | 378 | 1240 | 1440 | 0
2016-02-22 09:00 | 3020 | 874.931 | 404 | 1240 | 1440 | 0
2016-02-22 10:00 | 2484 | 877.135 | 364 | 1240 | 1440 | 0
2016-02-22 11:00 | 2484 | 867.559 | 337 | 1240 | 1440 | 0
2016-02-22 12:00 | 2484 | 853.537 | 350 | 1240 | 1440 | 0
2016-02-22 13:00 | 2484 | 840.579 | 339 | 1240 | 1440 | 0
2016-02-22 14:00 | 2568 | 871.08 | 337 | 1240 | 1440 | 0
2016-02-22 15:00 | 2568 | 864.3 | 354 | 1240 | 1440 | 0
2016-02-22 16:00 | 2568 | 868.72 | 437 | 1240 | 1440 | 0
2016-02-22 17:00 | 2568 | 893.94 | 574 | 1240 | 1440 | 0
2016-02-22 18:00 | 3274 | 933.32 | 690 | 1240 | 1440 | 0
2016-02-22 19:00 | 3274 | 972.72 | 381 | 1240 | 1430.7692 | 0
2016-02-22 20:00 | 3274 | 965.74 | 337 | 1240 | 1430.7692 | 0
2016-02-22 21:00 | 3274 | 891.879 | 337 | 1240 | 1430.7692 | 0
2016-02-22 22:00 | 2818 | 840.427 | 337 | 1240 | 1430.7692 | 0
2016-02-22 23:00 | 2818 | 793.326 | 457 | 1240 | 1430.7692 | 0
2016-02-23 | 2818 | 729.524 | 374 | 1240 | 1521.4286 | 0
2016-02-23 01:00 | 2818 | 722.722 | 337 | 1240 | 1521.4286 | 0
2016-02-23 02:00 | 2512 | 763.58 | 339 | 1240 | 1521.4286 | 0
2016-02-23 03:00 | 2512 | 773.08 | 399 | 1240 | 1521.4286 | 0
2016-02-23 04:00 | 2512 | 757.473 | 620 | 1240 | 1521.4286 | 0
2016-02-23 05:00 | 2512 | 815.385 | 769 | 1240 | 1430.7692 | 0
2016-02-23 06:00 | 3020 | 955.94 | 578 | 1240 | 1440 | 0
2016-02-23 07:00 | 3020 | 938.961 | 408 | 1240 | 1440 | 0
2016-02-23 08:00 | 3020 | 976.74 | 378 | 1240 | 1440 | 0
2016-02-23 09:00 | 3020 | 931.969 | 404 | 1240 | 1440 | 0
2016-02-23 10:00 | 2484 | 939.797 | 364 | 1240 | 1440 | 0
2016-02-23 11:00 | 2484 | 938.885 | 337 | 1240 | 1440 | 0
2016-02-23 12:00 | 2484 | 979.14 | 350 | 1240 | 1440 | 0
2016-02-23 13:00 | 2484 | 975 | 339 | 1240 | 1440 | 0
2016-02-23 14:00 | 2568 | 971.34 | 337 | 1240 | 1440 | 0
2016-02-23 15:00 | 2568 | 969.88 | 354 | 1240 | 1440 | 0
2016-02-23 16:00 | 2568 | 986.76 | 437 | 1240 | 1440 | 0
2016-02-23 17:00 | 2568 | 961.438 | 574 | 1240 | 1440 | 0
2016-02-23 18:00 | 3274 | 987.107 | 690 | 1240 | 1440 | 0
2016-02-23 19:00 | 3274 | 1012.757 | 381 | 1240 | 1238.9381 | 0
2016-02-23 20:00 | 3274 | 1000.407 | 337 | 1240 | 1238.9381 | 0
2016-02-23 21:00 | 3274 | 967.803 | 337 | 1240 | 1238.9381 | 0
2016-02-23 22:00 | 2818 | 910.955 | 337 | 1240 | 1238.9381 | 0
2016-02-23 23:00 | 2818 | 908.06 | 457 | 1240 | 1238.9381 | 0
2016-02-24 | 2818 | 888.14 | 374 | 1240 | 1238.9381 | 0
2016-02-24 01:00 | 2818 | 879.08 | 337 | 1240 | 1238.9381 | 0
2016-02-24 02:00 | 2512 | 883.44 | 339 | 1240 | 1238.9381 | 0
2016-02-24 03:00 | 2512 | 890.4 | 399 | 1240 | 1238.9381 | 0
2016-02-24 04:00 | 2512 | 917.76 | 620 | 1240 | 1238.9381 | 0
2016-02-24 05:00 | 2512 | 932.767 | 769 | 1240 | 1238.9381 | 0
2016-02-24 06:00 | 3020 | 1134.672 | 578 | 1240 | 1296.2963 | 0
2016-02-24 07:00 | 3020 | 1149.225 | 408 | 1240 | 1296.2963 | 0
2016-02-24 08:00 | 3020 | 1091.559 | 378 | 1240 | 1238.9381 | 0
2016-02-24 09:00 | 3020 | 940.538 | 404 | 1240 | 1238.9381 | 0
2016-02-24 10:00 | 2484 | 899.118 | 364 | 1240 | 1440 | 0
2016-02-24 11:00 | 2484 | 902.7 | 337 | 1240 | 1430.7692 | 0
2016-02-24 12:00 | 2484 | 864.5 | 350 | 1240 | 1430.7692 | 0
2016-02-24 13:00 | 2484 | 794.352 | 339 | 1240 | 1430.7692 | 0
2016-02-24 14:00 | 2568 | 769.69 | 337 | 1240 | 1430.7692 | 0
2016-02-24 15:00 | 2568 | 752.4 | 354 | 1240 | 1430.7692 | 0
2016-02-24 16:00 | 2568 | 748.657 | 437 | 1240 | 1430.7692 | 0
2016-02-24 17:00 | 2568 | 765.529 | 574 | 1240 | 1430.7692 | 0
2016-02-24 18:00 | 3274 | 819.299 | 690 | 1240 | 1430.7692 | 0
2016-02-24 19:00 | 3274 | 919 | 381 | 1240 | 1430.7692 | 0
2016-02-24 20:00 | 3274 | 926.78 | 337 | 1240 | 1430.7692 | 0
2016-02-24 21:00 | 3274 | 873.012 | 337 | 1240 | 1521.4286 | 0
2016-02-24 22:00 | 2818 | 880.58 | 337 | 1240 | 1673.3333 | 0
2016-02-24 23:00 | 2818 | 840.62 | 457 | 1240 | 1673.3333 | 0
2016-02-25 | 2818 | 786.9 | 374 | 1240 | 1673.3333 | 0
2016-02-25 01:00 | 2818 | 782.3 | 337 | 1240 | 1673.3333 | 0
2016-02-25 02:00 | 2512 | 707.328 | 339 | 1240 | 1673.3333 | 0
2016-02-25 03:00 | 2512 | 797.16 | 399 | 1240 | 1673.3333 | 0
2016-02-25 04:00 | 2512 | 824.78 | 620 | 1240 | 1673.3333 | 0
2016-02-25 05:00 | 2512 | 888.66 | 769 | 1240 | 1521.4286 | 0
2016-02-25 06:00 | 3020 | 929.556 | 578 | 1240 | 1521.4286 | 0
2016-02-25 07:00 | 3020 | 935.883 | 408 | 1240 | 1521.4286 | 0
2016-02-25 08:00 | 3020 | 882.512 | 378 | 1240 | 1521.4286 | 0
2016-02-25 09:00 | 3020 | 884.84 | 404 | 1240 | 1673.3333 | 0
2016-02-25 10:00 | 2484 | 850.12 | 364 | 1240 | 1673.3333 | 0
2016-02-25 11:00 | 2484 | 813.56 | 337 | 1240 | 1673.3333 | 0
2016-02-25 12:00 | 2484 | 701.964 | 350 | 1240 | 1673.3333 | 0
2016-02-25 13:00 | 2484 | 757.5 | 339 | 1240 | 1673.3333 | 0
2016-02-25 14:00 | 2568 | 665.676 | 337 | 1240 | 1673.3333 | 0
2016-02-25 15:00 | 2568 | 659.268 | 354 | 1240 | 1673.3333 | 0
2016-02-25 16:00 | 2568 | 670.5 | 437 | 1240 | 1673.3333 | 0
2016-02-25 17:00 | 2568 | 687.348 | 574 | 1240 | 1673.3333 | 0
2016-02-25 18:00 | 3274 | 789.72 | 690 | 1240 | 1673.3333 | 0
2016-02-25 19:00 | 3274 | 815.74 | 381 | 1240 | 1673.3333 | 0
2016-02-25 20:00 | 3274 | 816.08 | 337 | 1240 | 1673.3333 | 0
2016-02-25 21:00 | 3274 | 792.06 | 337 | 1240 | 1673.3333 | 0
2016-02-25 22:00 | 2818 | 746.3 | 337 | 1240 | 1673.3333 | 0
2016-02-25 23:00 | 2818 | 632.592 | 457 | 1240 | 1673.3333 | 0
2016-02-26 | 2818 | 631.584 | 374 | 1240 | 1673.3333 | 0
2016-02-26 01:00 | 2818 | 619.002 | 337 | 1240 | 1673.3333 | 0
2016-02-26 02:00 | 2512 | 617.544 | 339 | 1240 | 1673.3333 | 0
2016-02-26 03:00 | 2512 | 621.162 | 399 | 1240 | 1673.3333 | 0
2016-02-26 04:00 | 2512 | 711.72 | 620 | 1240 | 1673.3333 | 0
2016-02-26 05:00 | 2512 | 766.36 | 769 | 1240 | 1673.3333 | 0
2016-02-26 06:00 | 3020 | 810.16 | 578 | 1240 | 1521.4286 | 0
2016-02-26 07:00 | 3020 | 829.654 | 408 | 1240 | 1521.4286 | 0
2016-02-26 08:00 | 3020 | 807.272 | 378 | 1240 | 1521.4286 | 0
2016-02-26 09:00 | 3020 | 838.62 | 404 | 1240 | 1673.3333 | 0
2016-02-26 10:00 | 2484 | 838.02 | 364 | 1240 | 1673.3333 | 0
2016-02-26 11:00 | 2484 | 832.6 | 337 | 1240 | 1673.3333 | 0
2016-02-26 12:00 | 2484 | 827.7 | 350 | 1240 | 1673.3333 | 0
2016-02-26 13:00 | 2484 | 743.814 | 339 | 1240 | 1673.3333 | 0
2016-02-26 14:00 | 2568 | 741.348 | 337 | 1240 | 1673.3333 | 0
2016-02-26 15:00 | 2568 | 740.538 | 354 | 1240 | 1673.3333 | 0
2016-02-26 16:00 | 2568 | 747.018 | 437 | 1240 | 1673.3333 | 0
2016-02-26 17:00 | 2568 | 843.9 | 574 | 1240 | 1673.3333 | 0
2016-02-26 18:00 | 3274 | 867.04 | 690 | 1240 | 1673.3333 | 0
2016-02-26 19:00 | 3274 | 845.671 | 381 | 1240 | 1521.4286 | 0
2016-02-26 20:00 | 3274 | 879.22 | 337 | 1240 | 1430.7692 | 0
2016-02-26 21:00 | 3274 | 859.86 | 337 | 1240 | 1430.7692 | 0
2016-02-26 22:00 | 2818 | 830.3 | 337 | 1240 | 1430.7692 | 0
2016-02-26 23:00 | 2818 | 755.307 | 457 | 1240 | 1430.7692 | 0
2016-02-27 | 2818 | 764.864 | 374 | 1240 | 1430.7692 | 0
2016-02-27 01:00 | 2818 | 770.944 | 337 | 1240 | 1430.7692 | 0
2016-02-27 02:00 | 2512 | 827.58 | 339 | 1240 | 1430.7692 | 0
2016-02-27 03:00 | 2512 | 833.76 | 399 | 1240 | 1430.7692 | 0
2016-02-27 04:00 | 2512 | 848.62 | 620 | 1240 | 1430.7692 | 0
2016-02-27 05:00 | 2512 | 881.48 | 769 | 1240 | 1440 | 0
2016-02-27 06:00 | 3020 | 881.98 | 578 | 1240 | 1440 | 0
2016-02-27 07:00 | 3020 | 908.39 | 408 | 1240 | 1440 | 0
2016-02-27 08:00 | 3020 | 901.284 | 378 | 1240 | 1440 | 0
2016-02-27 09:00 | 3020 | 917.34 | 404 | 1240 | 1440 | 0
2016-02-27 10:00 | 2484 | 875.42 | 364 | 1240 | 1440 | 0
2016-02-27 11:00 | 2484 | 834.84 | 337 | 1240 | 1430.7692 | 0
2016-02-27 12:00 | 2484 | 798.18 | 350 | 1240 | 1430.7692 | 0
2016-02-27 13:00 | 2484 | 728.232 | 339 | 1240 | 1521.4286 | 0
2016-02-27 14:00 | 2568 | 707.085 | 337 | 1240 | 1521.4286 | 0
2016-02-27 15:00 | 2568 | 693.918 | 354 | 1240 | 1521.4286 | 0
2016-02-27 16:00 | 2568 | 690.688 | 437 | 1240 | 1521.4286 | 0
2016-02-27 17:00 | 2568 | 703.855 | 574 | 1240 | 1521.4286 | 0
2016-02-27 18:00 | 3274 | 742.102 | 690 | 1240 | 1521.4286 | 0
2016-02-27 19:00 | 3274 | 780.349 | 381 | 1240 | 1521.4286 | 0
2016-02-27 20:00 | 3274 | 823.16 | 337 | 1240 | 1673.3333 | 0
2016-02-27 21:00 | 3274 | 818.62 | 337 | 1240 | 1673.3333 | 0
2016-02-27 22:00 | 2818 | 799.04 | 337 | 1240 | 1673.3333 | 0
2016-02-27 23:00 | 2818 | 771.22 | 457 | 1240 | 1673.3333 | 0
2016-02-28 | 2818 | 774.62 | 374 | 1240 | 1673.3333 | 0
2016-02-28 01:00 | 2818 | 781.06 | 337 | 1240 | 1673.3333 | 0
2016-02-28 02:00 | 2512 | 780.84 | 339 | 1240 | 1673.3333 | 0
2016-02-28 03:00 | 2512 | 787 | 399 | 1240 | 1673.3333 | 0
2016-02-28 04:00 | 2512 | 803.92 | 620 | 1240 | 1673.3333 | 0
2016-02-28 05:00 | 2512 | 833.54 | 769 | 1240 | 1673.3333 | 0
2016-02-28 06:00 | 3020 | 864.44 | 578 | 1240 | 1673.3333 | 0
2016-02-28 07:00 | 3020 | 840.826 | 408 | 1240 | 1673.3333 | 0
2016-02-28 08:00 | 3020 | 847.457 | 378 | 1240 | 1673.3333 | 0
2016-02-28 09:00 | 3020 | 871.3 | 404 | 1240 | 1673.3333 | 0
2016-02-28 10:00 | 2484 | 844.1 | 364 | 1240 | 1730 | 0
2016-02-28 11:00 | 2484 | 739.728 | 337 | 1240 | 1730 | 0
2016-02-28 12:00 | 2484 | 721.278 | 350 | 1240 | 1730 | 0
2016-02-28 13:00 | 2484 | 705.87 | 339 | 1240 | 1730 | 0
2016-02-28 14:00 | 2568 | 695.034 | 337 | 1240 | 1730 | 0
2016-02-28 15:00 | 2568 | 694.044 | 354 | 1240 | 1730 | 0
2016-02-28 16:00 | 2568 | 698.202 | 437 | 1240 | 1730 | 0
2016-02-28 17:00 | 2568 | 722.862 | 574 | 1240 | 1730 | 0
2016-02-28 18:00 | 3274 | 843.86 | 690 | 1240 | 1673.3333 | 0
2016-02-28 19:00 | 3274 | 884.54 | 381 | 1240 | 1673.3333 | 0
2016-02-28 20:00 | 3274 | 877.28 | 337 | 1240 | 1673.3333 | 0
2016-02-28 21:00 | 3274 | 852.98 | 337 | 1240 | 1673.3333 | 0
2016-02-28 22:00 | 2818 | 806.74 | 337 | 1240 | 1673.3333 | 0
2016-02-28 23:00 | 2818 | 756.14 | 457 | 1240 | 1673.3333 | 0
2016-02-29 | 2818 | 694.728 | 374 | 1240 | 1673.3333 | 0
2016-02-29 01:00 | 2818 | 781.06 | 337 | 1240 | 1673.3333 | 0
2016-02-29 02:00 | 2512 | 780.84 | 339 | 1240 | 1673.3333 | 0
2016-02-29 03:00 | 2512 | 787 | 399 | 1240 | 1673.3333 | 0
2016-02-29 04:00 | 2512 | 803.92 | 620 | 1240 | 1673.3333 | 0
2016-02-29 05:00 | 2512 | 833.54 | 769 | 1240 | 1673.3333 | 0
2016-02-29 06:00 | 3020 | 864.44 | 578 | 1240 | 1673.3333 | 0
2016-02-29 07:00 | 3020 | 840.826 | 408 | 1240 | 1673.3333 | 0
2016-02-29 08:00 | 3020 | 847.457 | 378 | 1240 | 1673.3333 | 0
2016-02-29 09:00 | 3020 | 871.3 | 404 | 1240 | 1673.3333 | 0
2016-02-29 10:00 | 2484 | 844.1 | 364 | 1240 | 1730 | 0
2016-02-29 11:00 | 2484 | 739.728 | 337 | 1240 | 1730 | 0
2016-02-29 12:00 | 2484 | 721.278 | 350 | 1240 | 1730 | 0
2016-02-29 13:00 | 2484 | 705.87 | 339 | 1240 | 1730 | 0
2016-02-29 14:00 | 2568 | 695.034 | 337 | 1240 | 1730 | 0
2016-02-29 15:00 | 2568 | 694.044 | 354 | 1240 | 1730 | 0
2016-02-29 16:00 | 2568 | 698.202 | 437 | 1240 | 1730 | 0
2016-02-29 17:00 | 2568 | 722.862 | 574 | 1240 | 1730 | 0
2016-02-29 18:00 | 3274 | 843.86 | 690 | 1240 | 1730 | 0
2016-02-29 19:00 | 3274 | 884.54 | 381 | 1240 | 1673.3333 | 0
2016-02-29 20:00 | 3274 | 877.28 | 337 | 1240 | 1673.3333 | 0
2016-02-29 21:00 | 3274 | 852.98 | 337 | 1240 | 1673.3333 | 0
2016-02-29 22:00 | 2818 | 806.74 | 337 | 1240 | 1673.3333 | 0
2016-02-29 23:00 | 2818 | 756.14 | 457 | 1240 | 1673.3333 | 0
2016-03-01 | 2301 | 599.922 | 455 | 1240 | 1730 | 0
2016-03-01 01:00 | 2301 | 587.628 | 307 | 1240 | 1730 | 0
2016-03-01 02:00 | 2712 | 585.918 | 307 | 1240 | 1730 | 0
2016-03-01 03:00 | 2712 | 592.02 | 351 | 1240 | 1673.3333 | 0
2016-03-01 04:00 | 2712 | 681.34 | 563 | 1240 | 1673.3333 | 0
2016-03-01 05:00 | 2712 | 746 | 763 | 1240 | 1521.4286 | 0
2016-03-01 06:00 | 2797 | 851.84 | 505 | 1240 | 1430.7692 | 0
2016-03-01 07:00 | 2797 | 886.04 | 372 | 1240 | 1430.7692 | 0
2016-03-01 08:00 | 2797 | 830.927 | 470 | 1240 | 1430.7692 | 0
2016-03-01 09:00 | 2797 | 834.347 | 452 | 1240 | 1430.7692 | 0
2016-03-01 10:00 | 2716 | 838.128 | 433 | 1240 | 1521.4286 | 0
2016-03-01 11:00 | 2716 | 877.44 | 383 | 1240 | 1521.4286 | 0
2016-03-01 12:00 | 2716 | 873.32 | 347 | 1240 | 1521.4286 | 0
2016-03-01 13:00 | 2716 | 872.08 | 413 | 1240 | 1521.4286 | 0
2016-03-01 14:00 | 2048 | 868.62 | 326 | 1240 | 1521.4286 | 0
2016-03-01 15:00 | 2048 | 873.96 | 366 | 1240 | 1521.4286 | 0
2016-03-01 16:00 | 2048 | 891.06 | 396 | 1240 | 1521.4286 | 0
2016-03-01 17:00 | 2048 | 916.8 | 598 | 1240 | 1521.4286 | 0
2016-03-01 18:00 | 1993 | 896.971 | 723 | 1240 | 1521.4286 | 0
2016-03-01 19:00 | 1993 | 923.001 | 518 | 1240 | 1430.7692 | 0
2016-03-01 20:00 | 1993 | 958.72 | 322 | 1240 | 1430.7692 | 0
2016-03-01 21:00 | 1993 | 927.88 | 307 | 1240 | 1430.7692 | 0
2016-03-01 22:00 | 2301 | 872.84 | 307 | 1240 | 1430.7692 | 0
2016-03-01 23:00 | 2301 | 777.328 | 511 | 1240 | 1430.7692 | 0
2016-03-02 | 2301 | 736.516 | 455 | 1240 | 1430.7692 | 0
2016-03-02 01:00 | 2301 | 726.104 | 307 | 1240 | 1430.7692 | 0
2016-03-02 02:00 | 2712 | 728.384 | 307 | 1240 | 1430.7692 | 0
2016-03-02 03:00 | 2712 | 738.72 | 351 | 1240 | 1430.7692 | 0
2016-03-02 04:00 | 2712 | 768.664 | 563 | 1240 | 1430.7692 | 0
2016-03-02 05:00 | 2712 | 878.1 | 763 | 1240 | 1430.7692 | 0
2016-03-02 06:00 | 2797 | 933.185 | 505 | 1240 | 1440 | 0
2016-03-02 07:00 | 2797 | 943.654 | 372 | 1240 | 1440 | 0
2016-03-02 08:00 | 2797 | 897.161 | 470 | 1240 | 1440 | 0
2016-03-02 09:00 | 2797 | 867.426 | 452 | 1240 | 1440 | 0
2016-03-02 10:00 | 2716 | 885.72 | 433 | 1240 | 1440 | 0
2016-03-02 11:00 | 2716 | 855.22 | 383 | 1240 | 1440 | 0
2016-03-02 12:00 | 2716 | 828.06 | 347 | 1240 | 1440 | 0
2016-03-02 13:00 | 2716 | 807.04 | 413 | 1240 | 1440 | 0
2016-03-02 14:00 | 2048 | 749.436 | 326 | 1240 | 1440 | 0
2016-03-02 15:00 | 2048 | 741.475 | 366 | 1240 | 1440 | 0
2016-03-02 16:00 | 2048 | 740.886 | 396 | 1240 | 1440 | 0
2016-03-02 17:00 | 2048 | 794 | 598 | 1240 | 1440 | 0
2016-03-02 18:00 | 1993 | 838.96 | 723 | 1240 | 1440 | 0
2016-03-02 19:00 | 1993 | 839.724 | 518 | 1240 | 1440 | 0
2016-03-02 20:00 | 1993 | 843.22 | 322 | 1240 | 1440 | 0
2016-03-02 21:00 | 1993 | 868.18 | 307 | 1240 | 1440 | 0
2016-03-02 22:00 | 2301 | 823.72 | 307 | 1240 | 1430.7692 | 0
2016-03-02 23:00 | 2301 | 740.658 | 511 | 1240 | 1430.7692 | 0
2016-03-03 | 2301 | 726.76 | 455 | 1240 | 1430.7692 | 0
2016-03-03 01:00 | 2301 | 722.94 | 307 | 1240 | 1430.7692 | 0
2016-03-03 02:00 | 2712 | 727.66 | 307 | 1240 | 1430.7692 | 0
2016-03-03 03:00 | 2712 | 739.04 | 351 | 1240 | 1430.7692 | 0
2016-03-03 04:00 | 2712 | 731.044 | 563 | 1240 | 1430.7692 | 0
2016-03-03 05:00 | 2712 | 796.556 | 763 | 1240 | 1430.7692 | 0
2016-03-03 06:00 | 2797 | 934.24 | 505 | 1240 | 1430.7692 | 0
2016-03-03 07:00 | 2797 | 938.9 | 372 | 1240 | 1430.7692 | 0
2016-03-03 08:00 | 2797 | 880.78 | 470 | 1240 | 1430.7692 | 0
2016-03-03 09:00 | 2797 | 832.42 | 452 | 1240 | 1430.7692 | 0
2016-03-03 10:00 | 2716 | 756.466 | 433 | 1240 | 1430.7692 | 0
2016-03-03 11:00 | 2716 | 731.386 | 383 | 1240 | 1521.4286 | 0
2016-03-03 12:00 | 2716 | 709.327 | 347 | 1240 | 1521.4286 | 0
2016-03-03 13:00 | 2716 | 695.628 | 413 | 1240 | 1521.4286 | 0
2016-03-03 14:00 | 2048 | 684.152 | 326 | 1240 | 1521.4286 | 0
2016-03-03 15:00 | 2048 | 679.307 | 366 | 1240 | 1521.4286 | 0
2016-03-03 16:00 | 2048 | 677.16 | 396 | 1240 | 1521.4286 | 0
2016-03-03 17:00 | 2048 | 683.468 | 598 | 1240 | 1521.4286 | 0
2016-03-03 18:00 | 1993 | 718.618 | 723 | 1240 | 1521.4286 | 0
2016-03-03 19:00 | 1993 | 753.787 | 518 | 1240 | 1673.3333 | 0
2016-03-03 20:00 | 1993 | 793.28 | 322 | 1240 | 1673.3333 | 0
2016-03-03 21:00 | 1993 | 774.96 | 307 | 1240 | 1730 | 0
2016-03-03 22:00 | 2301 | 656.352 | 307 | 1240 | 1730 | 0
2016-03-03 23:00 | 2301 | 617.058 | 511 | 1240 | 1730 | 0
2016-03-04 | 2301 | 599.112 | 455 | 1240 | 1730 | 0
2016-03-04 01:00 | 2301 | 592.542 | 307 | 1240 | 1730 | 0
2016-03-04 02:00 | 2712 | 595.944 | 307 | 1240 | 1730 | 0
2016-03-04 03:00 | 2712 | 606.87 | 351 | 1240 | 1730 | 0
2016-03-04 04:00 | 2712 | 629.928 | 563 | 1240 | 1673.3333 | 0
2016-03-04 05:00 | 2712 | 755.84 | 763 | 1240 | 1673.3333 | 0
2016-03-04 06:00 | 2797 | 809.78 | 505 | 1240 | 1673.3333 | 0
2016-03-04 07:00 | 2797 | 817.323 | 372 | 1240 | 1673.3333 | 0
2016-03-04 08:00 | 2797 | 816.62 | 470 | 1240 | 1673.3333 | 0
2016-03-04 09:00 | 2797 | 790.28 | 452 | 1240 | 1673.3333 | 0
2016-03-04 10:00 | 2716 | 691.434 | 433 | 1240 | 1730 | 0
2016-03-04 11:00 | 2716 | 675.504 | 383 | 1240 | 1730 | 0
2016-03-04 12:00 | 2716 | 662.796 | 347 | 1240 | 1730 | 0
2016-03-04 13:00 | 2716 | 657.234 | 413 | 1240 | 1730 | 0
2016-03-04 14:00 | 2048 | 649.134 | 326 | 1240 | 1800 | 0
2016-03-04 15:00 | 2048 | 643.896 | 366 | 1240 | 1800 | 0
2016-03-04 16:00 | 2048 | 638.28 | 396 | 1240 | 1800 | 0
2016-03-04 17:00 | 2048 | 644.31 | 598 | 1240 | 1800 | 0
2016-03-04 18:00 | 1993 | 672.48 | 723 | 1240 | 1800 | 0
2016-03-04 19:00 | 1993 | 700.65 | 518 | 1240 | 1800 | 0
2016-03-04 20:00 | 1993 | 697.914 | 322 | 1240 | 1800 | 0
2016-03-04 21:00 | 1993 | 677.268 | 307 | 1240 | 1800 | 0
2016-03-04 22:00 | 2301 | 637.362 | 307 | 1240 | 1800 | 0
2016-03-04 23:00 | 2301 | 593.352 | 511 | 1240 | 1800 | 0
2016-03-05 | 2301 | 589.158 | 455 | 1240 | 1800 | 0
2016-03-05 01:00 | 2301 | 585.504 | 307 | 1240 | 1800 | 0
2016-03-05 02:00 | 2712 | 584.01 | 307 | 1240 | 1800 | 0
2016-03-05 03:00 | 2712 | 588.906 | 351 | 1240 | 1800 | 0
2016-03-05 04:00 | 2712 | 609.786 | 563 | 1240 | 1730 | 0
2016-03-05 05:00 | 2712 | 657.846 | 763 | 1240 | 1730 | 0
2016-03-05 06:00 | 2797 | 828.84 | 505 | 1240 | 1673.3333 | 0
2016-03-05 07:00 | 2797 | 844.42 | 372 | 1240 | 1673.3333 | 0
2016-03-05 08:00 | 2797 | 820 | 470 | 1240 | 1673.3333 | 0
2016-03-05 09:00 | 2797 | 810.94 | 452 | 1240 | 1673.3333 | 0
2016-03-05 10:00 | 2716 | 801.5 | 433 | 1240 | 1673.3333 | 0
2016-03-05 11:00 | 2716 | 707.634 | 383 | 1240 | 1673.3333 | 0
2016-03-05 12:00 | 2716 | 695.538 | 347 | 1240 | 1673.3333 | 0
2016-03-05 13:00 | 2716 | 766.4 | 413 | 1240 | 1673.3333 | 0
2016-03-05 14:00 | 2048 | 758.1 | 326 | 1240 | 1673.3333 | 0
2016-03-05 15:00 | 2048 | 751.16 | 366 | 1240 | 1673.3333 | 0
2016-03-05 16:00 | 2048 | 749.16 | 396 | 1240 | 1673.3333 | 0
2016-03-05 17:00 | 2048 | 751.44 | 598 | 1240 | 1673.3333 | 0
2016-03-05 18:00 | 1993 | 773.14 | 723 | 1240 | 1673.3333 | 0
2016-03-05 19:00 | 1993 | 794.82 | 518 | 1240 | 1673.3333 | 0
2016-03-05 20:00 | 1993 | 786.8 | 322 | 1240 | 1673.3333 | 0
2016-03-05 21:00 | 1993 | 688.662 | 307 | 1240 | 1730 | 0
2016-03-05 22:00 | 2301 | 657.774 | 307 | 1240 | 1730 | 0
2016-03-05 23:00 | 2301 | 622.566 | 511 | 1240 | 1730 | 0
2016-03-06 | 2301 | 622.746 | 455 | 1240 | 1730 | 0
2016-03-06 01:00 | 2301 | 622.872 | 307 | 1240 | 1730 | 0
2016-03-06 02:00 | 2712 | 615.438 | 307 | 1240 | 1730 | 0
2016-03-06 03:00 | 2712 | 619.524 | 351 | 1240 | 1730 | 0
2016-03-06 04:00 | 2712 | 621.144 | 563 | 1240 | 1730 | 0
2016-03-06 05:00 | 2712 | 631.116 | 763 | 1240 | 1673.3333 | 0
2016-03-06 06:00 | 2797 | 728.88 | 505 | 1240 | 1673.3333 | 0
2016-03-06 07:00 | 2797 | 753.26 | 372 | 1240 | 1673.3333 | 0
2016-03-06 08:00 | 2797 | 778.9 | 470 | 1240 | 1673.3333 | 0
2016-03-06 09:00 | 2797 | 789.86 | 452 | 1240 | 1673.3333 | 0
2016-03-06 10:00 | 2716 | 785.6 | 433 | 1240 | 1673.3333 | 0
2016-03-06 11:00 | 2716 | 775.4 | 383 | 1240 | 1673.3333 | 0
2016-03-06 12:00 | 2716 | 761 | 347 | 1240 | 1673.3333 | 0
2016-03-06 13:00 | 2716 | 746.98 | 413 | 1240 | 1673.3333 | 0
2016-03-06 14:00 | 2048 | 737.52 | 326 | 1240 | 1673.3333 | 0
2016-03-06 15:00 | 2048 | 730.6 | 366 | 1240 | 1673.3333 | 0
2016-03-06 16:00 | 2048 | 730.5 | 396 | 1240 | 1673.3333 | 0
2016-03-06 17:00 | 2048 | 739.8 | 598 | 1240 | 1673.3333 | 0
2016-03-06 18:00 | 1993 | 768.02 | 723 | 1240 | 1673.3333 | 0
2016-03-06 19:00 | 1993 | 796.24 | 518 | 1240 | 1673.3333 | 0
2016-03-06 20:00 | 1993 | 787.42 | 322 | 1240 | 1673.3333 | 0
2016-03-06 21:00 | 1993 | 769.94 | 307 | 1240 | 1730 | 0
2016-03-06 22:00 | 2301 | 663.894 | 307 | 1240 | 1730 | 0
2016-03-06 23:00 | 2301 | 631.71 | 511 | 1240 | 1730 | 0
2016-03-07 | 2301 | 623.376 | 455 | 1240 | 1730 | 0
2016-03-07 01:00 | 2301 | 605.106 | 307 | 1240 | 1730 | 0
2016-03-07 02:00 | 2712 | 596.502 | 307 | 1240 | 1730 | 0
2016-03-07 03:00 | 2712 | 593.1 | 351 | 1240 | 1730 | 0
2016-03-07 04:00 | 2712 | 594.648 | 563 | 1240 | 1730 | 0
2016-03-07 05:00 | 2712 | 603.324 | 763 | 1240 | 1730 | 0
2016-03-07 06:00 | 2797 | 624.114 | 505 | 1240 | 1730 | 0
2016-03-07 07:00 | 2797 | 716.92 | 372 | 1240 | 1730 | 0
2016-03-07 08:00 | 2797 | 754.68 | 470 | 1240 | 1673.3333 | 0
2016-03-07 09:00 | 2797 | 783.1 | 452 | 1240 | 1673.3333 | 0
2016-03-07 10:00 | 2716 | 794.94 | 433 | 1240 | 1673.3333 | 0
2016-03-07 11:00 | 2716 | 799.14 | 383 | 1240 | 1673.3333 | 0
2016-03-07 12:00 | 2716 | 799.18 | 347 | 1240 | 1673.3333 | 0
2016-03-07 13:00 | 2716 | 795.44 | 413 | 1240 | 1673.3333 | 0
2016-03-07 14:00 | 2048 | 789.86 | 326 | 1240 | 1673.3333 | 0
2016-03-07 15:00 | 2048 | 788.8 | 366 | 1240 | 1673.3333 | 0
2016-03-07 16:00 | 2048 | 798.08 | 396 | 1240 | 1673.3333 | 0
2016-03-07 17:00 | 2048 | 820.9 | 598 | 1240 | 1673.3333 | 0
2016-03-07 18:00 | 1993 | 850 | 723 | 1240 | 1673.3333 | 0
2016-03-07 19:00 | 1993 | 835.126 | 518 | 1240 | 1673.3333 | 0
2016-03-07 20:00 | 1993 | 824.011 | 322 | 1240 | 1673.3333 | 0
2016-03-07 21:00 | 1993 | 796.556 | 307 | 1240 | 1673.3333 | 0
2016-03-07 22:00 | 2301 | 790.72 | 307 | 1240 | 1673.3333 | 0
2016-03-07 23:00 | 2301 | 740.28 | 511 | 1240 | 1730 | 0
2016-03-08 | 2301 | 572.166 | 455 | 1240 | 1730 | 0
2016-03-08 01:00 | 2301 | 557.172 | 307 | 1240 | 1730 | 0
2016-03-08 02:00 | 2712 | 550.134 | 307 | 1240 | 1730 | 0
2016-03-08 03:00 | 2712 | 552.852 | 351 | 1240 | 1730 | 0
2016-03-08 04:00 | 2712 | 575.352 | 563 | 1240 | 1730 | 0
2016-03-08 05:00 | 2712 | 605.106 | 763 | 1240 | 1730 | 0
2016-03-08 06:00 | 2797 | 758.48 | 505 | 1240 | 1730 | 0
2016-03-08 07:00 | 2797 | 788.84 | 372 | 1240 | 1730 | 0
2016-03-08 08:00 | 2797 | 706.068 | 470 | 1240 | 1730 | 0
2016-03-08 09:00 | 2797 | 711.126 | 452 | 1240 | 1730 | 0
2016-03-08 10:00 | 2716 | 719.316 | 433 | 1240 | 1730 | 0
2016-03-08 11:00 | 2716 | 720.81 | 383 | 1240 | 1730 | 0
2016-03-08 12:00 | 2716 | 718.182 | 347 | 1240 | 1730 | 0
2016-03-08 13:00 | 2716 | 716.004 | 413 | 1240 | 1730 | 0
2016-03-08 14:00 | 2048 | 712.854 | 326 | 1240 | 1730 | 0
2016-03-08 15:00 | 2048 | 709.704 | 366 | 1240 | 1730 | 0
2016-03-08 16:00 | 2048 | 715.392 | 396 | 1240 | 1730 | 0
2016-03-08 17:00 | 2048 | 721.386 | 598 | 1240 | 1730 | 0
2016-03-08 18:00 | 1993 | 734.922 | 723 | 1240 | 1730 | 0
2016-03-08 19:00 | 1993 | 748.458 | 518 | 1240 | 1730 | 0
2016-03-08 20:00 | 1993 | 738.576 | 322 | 1240 | 1730 | 0
2016-03-08 21:00 | 1993 | 708.948 | 307 | 1240 | 1730 | 0
2016-03-08 22:00 | 2301 | 656.19 | 307 | 1240 | 1730 | 0
2016-03-08 23:00 | 2301 | 607.41 | 511 | 1240 | 1730 | 0
2016-03-09 | 2301 | 585.954 | 455 | 1240 | 1730 | 0
2016-03-09 01:00 | 2301 | 568.548 | 307 | 1240 | 1730 | 0
2016-03-09 02:00 | 2712 | 560.466 | 307 | 1240 | 1730 | 0
2016-03-09 03:00 | 2712 | 561.618 | 351 | 1240 | 1730 | 0
2016-03-09 04:00 | 2712 | 575.316 | 563 | 1240 | 1730 | 0
2016-03-09 05:00 | 2712 | 615.294 | 763 | 1240 | 1730 | 0
2016-03-09 06:00 | 2797 | 694.908 | 505 | 1240 | 1730 | 0
2016-03-09 07:00 | 2797 | 789.1 | 372 | 1240 | 1673.3333 | 0
2016-03-09 08:00 | 2797 | 775.38 | 470 | 1240 | 1673.3333 | 0
2016-03-09 09:00 | 2797 | 777.82 | 452 | 1240 | 1673.3333 | 0
2016-03-09 10:00 | 2716 | 785.1 | 433 | 1240 | 1673.3333 | 0
2016-03-09 11:00 | 2716 | 787.2 | 383 | 1240 | 1673.3333 | 0
2016-03-09 12:00 | 2716 | 787.44 | 347 | 1240 | 1673.3333 | 0
2016-03-09 13:00 | 2716 | 793.28 | 413 | 1240 | 1673.3333 | 0
2016-03-09 14:00 | 2048 | 797.22 | 326 | 1240 | 1673.3333 | 0
2016-03-09 15:00 | 2048 | 801.76 | 366 | 1240 | 1673.3333 | 0
2016-03-09 16:00 | 2048 | 800.24 | 396 | 1240 | 1673.3333 | 0
2016-03-09 17:00 | 2048 | 796.74 | 598 | 1240 | 1673.3333 | 0
2016-03-09 18:00 | 1993 | 815.98 | 723 | 1240 | 1521.4286 | 0
2016-03-09 19:00 | 1993 | 793.478 | 518 | 1240 | 1521.4286 | 0
2016-03-09 20:00 | 1993 | 780.634 | 322 | 1240 | 1521.4286 | 0
2016-03-09 21:00 | 1993 | 747.232 | 307 | 1240 | 1521.4286 | 0
2016-03-09 22:00 | 2301 | 730.84 | 307 | 1240 | 1730 | 0
2016-03-09 23:00 | 2301 | 603.216 | 511 | 1240 | 1730 | 0
2016-03-10 | 2301 | 539.712 | 455 | 1240 | 1730 | 0
2016-03-10 01:00 | 2301 | 523.386 | 307 | 1240 | 1730 | 0
2016-03-10 02:00 | 2712 | 517.482 | 307 | 1240 | 1800 | 0
2016-03-10 03:00 | 2712 | 516.456 | 351 | 1240 | 1800 | 0
2016-03-10 04:00 | 2712 | 528.39 | 563 | 1240 | 1800 | 0
2016-03-10 05:00 | 2712 | 565.704 | 763 | 1240 | 1800 | 0
2016-03-10 06:00 | 2797 | 638.172 | 505 | 1240 | 1730 | 0
2016-03-10 07:00 | 2797 | 658.296 | 372 | 1240 | 1730 | 0
2016-03-10 08:00 | 2797 | 657.774 | 470 | 1240 | 1730 | 0
2016-03-10 09:00 | 2797 | 662.976 | 452 | 1240 | 1800 | 0
2016-03-10 10:00 | 2716 | 672.336 | 433 | 1240 | 1800 | 0
2016-03-10 11:00 | 2716 | 675.828 | 383 | 1240 | 1730 | 0
2016-03-10 12:00 | 2716 | 677.988 | 347 | 1240 | 1730 | 0
2016-03-10 13:00 | 2716 | 681.3 | 413 | 1240 | 1730 | 0
2016-03-10 14:00 | 2048 | 683.208 | 326 | 1240 | 1730 | 0
2016-03-10 15:00 | 2048 | 680.724 | 366 | 1240 | 1730 | 0
2016-03-10 16:00 | 2048 | 680.58 | 396 | 1240 | 1730 | 0
2016-03-10 17:00 | 2048 | 674.118 | 598 | 1240 | 1730 | 0
2016-03-10 18:00 | 1993 | 689.958 | 723 | 1240 | 1730 | 0
2016-03-10 19:00 | 1993 | 784.22 | 518 | 1240 | 1730 | 0
2016-03-10 20:00 | 1993 | 732.925 | 322 | 1240 | 1521.4286 | 0
2016-03-10 21:00 | 1993 | 703.76 | 307 | 1240 | 1521.4286 | 0
2016-03-10 22:00 | 2301 | 689.06 | 307 | 1240 | 1673.3333 | 0
2016-03-10 23:00 | 2301 | 637.16 | 511 | 1240 | 1673.3333 | 0
2016-03-11 | 2301 | 544.392 | 455 | 1240 | 1673.3333 | 0
2016-03-11 01:00 | 2301 | 530.19 | 307 | 1240 | 1673.3333 | 0
2016-03-11 02:00 | 2712 | 524.79 | 307 | 1240 | 1673.3333 | 0
2016-03-11 03:00 | 2712 | 526.914 | 351 | 1240 | 1673.3333 | 0
2016-03-11 04:00 | 2712 | 542.376 | 563 | 1240 | 1673.3333 | 0
2016-03-11 05:00 | 2712 | 587.16 | 763 | 1240 | 1673.3333 | 0
2016-03-11 06:00 | 2797 | 739.84 | 505 | 1240 | 1673.3333 | 0
2016-03-11 07:00 | 2797 | 760.68 | 372 | 1240 | 1673.3333 | 0
2016-03-11 08:00 | 2797 | 747.4 | 470 | 1240 | 1673.3333 | 0
2016-03-11 09:00 | 2797 | 742.72 | 452 | 1240 | 1673.3333 | 0
2016-03-11 10:00 | 2716 | 708.624 | 433 | 1240 | 1673.3333 | 0
2016-03-11 11:00 | 2716 | 749.9 | 383 | 1240 | 1673.3333 | 0
2016-03-11 12:00 | 2716 | 750.94 | 347 | 1240 | 1673.3333 | 0
2016-03-11 13:00 | 2716 | 758.52 | 413 | 1240 | 1673.3333 | 0
2016-03-11 14:00 | 2048 | 761.34 | 326 | 1240 | 1673.3333 | 0
2016-03-11 15:00 | 2048 | 758.26 | 366 | 1240 | 1673.3333 | 0
2016-03-11 16:00 | 2048 | 682.65 | 396 | 1240 | 1673.3333 | 0
2016-03-11 17:00 | 2048 | 680.562 | 598 | 1240 | 1673.3333 | 0
2016-03-11 18:00 | 1993 | 694.962 | 723 | 1240 | 1673.3333 | 0
2016-03-11 19:00 | 1993 | 788.18 | 518 | 1240 | 1673.3333 | 0
2016-03-11 20:00 | 1993 | 780.16 | 322 | 1240 | 1673.3333 | 0
2016-03-11 21:00 | 1993 | 712.139 | 307 | 1240 | 1673.3333 | 0
2016-03-11 22:00 | 2301 | 702.22 | 307 | 1240 | 1673.3333 | 0
2016-03-11 23:00 | 2301 | 586.782 | 511 | 1240 | 1673.3333 | 0
2016-03-12 | 2301 | 592.758 | 455 | 1240 | 1730 | 0
2016-03-12 01:00 | 2301 | 595.35 | 307 | 1240 | 1730 | 0
2016-03-12 02:00 | 2712 | 591.102 | 307 | 1240 | 1730 | 0
2016-03-12 03:00 | 2712 | 594.684 | 351 | 1240 | 1730 | 0
2016-03-12 04:00 | 2712 | 612.702 | 563 | 1240 | 1730 | 0
2016-03-12 05:00 | 2712 | 663.264 | 763 | 1240 | 1730 | 0
2016-03-12 06:00 | 2797 | 828.54 | 505 | 1240 | 1673.3333 | 0
2016-03-12 07:00 | 2797 | 805.296 | 372 | 1240 | 1673.3333 | 0
2016-03-12 08:00 | 2797 | 789.488 | 470 | 1240 | 1521.4286 | 0
2016-03-12 09:00 | 2797 | 780.615 | 452 | 1240 | 1521.4286 | 0
2016-03-12 10:00 | 2716 | 774.231 | 433 | 1240 | 1521.4286 | 0
2016-03-12 11:00 | 2716 | 773.3 | 383 | 1240 | 1521.4286 | 0
2016-03-12 12:00 | 2716 | 762.926 | 347 | 1240 | 1521.4286 | 0
2016-03-12 13:00 | 2716 | 762.508 | 413 | 1240 | 1521.4286 | 0
2016-03-12 14:00 | 2048 | 796.2 | 326 | 1240 | 1673.3333 | 0
2016-03-12 15:00 | 2048 | 793.1 | 366 | 1240 | 1673.3333 | 0
2016-03-12 16:00 | 2048 | 788.5 | 396 | 1240 | 1673.3333 | 0
2016-03-12 17:00 | 2048 | 788.5 | 598 | 1240 | 1673.3333 | 0
2016-03-12 18:00 | 1993 | 804.18 | 723 | 1240 | 1673.3333 | 0
2016-03-12 19:00 | 1993 | 819.88 | 518 | 1240 | 1673.3333 | 0
2016-03-12 20:00 | 1993 | 767.6 | 322 | 1240 | 1673.3333 | 0
2016-03-12 21:00 | 1993 | 744.819 | 307 | 1240 | 1673.3333 | 0
2016-03-12 22:00 | 2301 | 712.329 | 307 | 1240 | 1673.3333 | 0
2016-03-12 23:00 | 2301 | 710.66 | 511 | 1240 | 1673.3333 | 0
2016-03-13 | 2301 | 708.92 | 455 | 1240 | 1673.3333 | 0
2016-03-13 01:00 | 2301 | 672.334 | 307 | 1240 | 1521.4286 | 0
2016-03-13 02:00 | 2712 | 698.78 | 307 | 1240 | 1521.4286 | 0
2016-03-13 03:00 | 2712 | 697.24 | 351 | 1240 | 1673.3333 | 0
2016-03-13 04:00 | 2712 | 708.52 | 563 | 1240 | 1673.3333 | 0
2016-03-13 05:00 | 2712 | 700.416 | 763 | 1240 | 1521.4286 | 0
2016-03-13 06:00 | 2797 | 737.01 | 505 | 1240 | 1521.4286 | 0
2016-03-13 07:00 | 2797 | 800.88 | 372 | 1240 | 1430.7692 | 0
2016-03-13 08:00 | 2797 | 819.54 | 470 | 1240 | 1430.7692 | 0
2016-03-13 09:00 | 2797 | 824.08 | 452 | 1240 | 1430.7692 | 0
2016-03-13 10:00 | 2716 | 820.02 | 433 | 1240 | 1430.7692 | 0
2016-03-13 11:00 | 2716 | 810.78 | 383 | 1240 | 1430.7692 | 0
2016-03-13 12:00 | 2716 | 798.28 | 347 | 1240 | 1430.7692 | 0
2016-03-13 13:00 | 2716 | 747.308 | 413 | 1240 | 1430.7692 | 0
2016-03-13 14:00 | 2048 | 740.886 | 326 | 1240 | 1430.7692 | 0
2016-03-13 15:00 | 2048 | 739.499 | 366 | 1240 | 1430.7692 | 0
2016-03-13 16:00 | 2048 | 779.12 | 396 | 1240 | 1430.7692 | 0
2016-03-13 17:00 | 2048 | 780.4 | 598 | 1240 | 1430.7692 | 0
2016-03-13 18:00 | 1993 | 806.06 | 723 | 1240 | 1430.7692 | 0
2016-03-13 19:00 | 1993 | 831.7 | 518 | 1240 | 1430.7692 | 0
2016-03-13 20:00 | 1993 | 777.993 | 322 | 1240 | 1521.4286 | 0
2016-03-13 21:00 | 1993 | 796.78 | 307 | 1240 | 1673.3333 | 0
2016-03-13 22:00 | 2301 | 685.998 | 307 | 1240 | 1673.3333 | 0
2016-03-13 23:00 | 2301 | 653.4 | 511 | 1240 | 1673.3333 | 0
2016-03-14 | 2301 | 657.558 | 455 | 1240 | 1673.3333 | 0
2016-03-14 01:00 | 2301 | 665.424 | 307 | 1240 | 1673.3333 | 0
2016-03-14 02:00 | 2712 | 731.24 | 307 | 1240 | 1673.3333 | 0
2016-03-14 03:00 | 2712 | 724.6 | 351 | 1240 | 1673.3333 | 0
2016-03-14 04:00 | 2712 | 727.76 | 563 | 1240 | 1673.3333 | 0
2016-03-14 05:00 | 2712 | 740.2 | 763 | 1240 | 1673.3333 | 0
2016-03-14 06:00 | 2797 | 765.42 | 505 | 1240 | 1673.3333 | 0
2016-03-14 07:00 | 2797 | 756.675 | 372 | 1240 | 1521.4286 | 0
2016-03-14 08:00 | 2797 | 776.017 | 470 | 1240 | 1521.4286 | 0
2016-03-14 09:00 | 2797 | 789.165 | 452 | 1240 | 1521.4286 | 0
2016-03-14 10:00 | 2716 | 787.075 | 433 | 1240 | 1521.4286 | 0
2016-03-14 11:00 | 2716 | 786.524 | 383 | 1240 | 1521.4286 | 0
2016-03-14 12:00 | 2716 | 790.096 | 347 | 1240 | 1521.4286 | 0
2016-03-14 13:00 | 2716 | 788.519 | 413 | 1240 | 1521.4286 | 0
2016-03-14 14:00 | 2048 | 787.151 | 326 | 1240 | 1521.4286 | 0
2016-03-14 15:00 | 2048 | 790.628 | 366 | 1240 | 1521.4286 | 0
2016-03-14 16:00 | 2048 | 797.43 | 396 | 1240 | 1521.4286 | 0
2016-03-14 17:00 | 2048 | 846.88 | 598 | 1240 | 1673.3333 | 0
2016-03-14 18:00 | 1993 | 860.94 | 723 | 1240 | 1673.3333 | 0
2016-03-14 19:00 | 1993 | 875.02 | 518 | 1240 | 1673.3333 | 0
2016-03-14 20:00 | 1993 | 915.74 | 322 | 1240 | 1673.3333 | 0
2016-03-14 21:00 | 1993 | 895.46 | 307 | 1240 | 1673.3333 | 0
2016-03-14 22:00 | 2301 | 853.16 | 307 | 1240 | 1673.3333 | 0
2016-03-14 23:00 | 2301 | 794.48 | 511 | 1240 | 1673.3333 | 0
2016-03-15 | 2301 | 598.158 | 455 | 1240 | 1673.3333 | 0
2016-03-15 01:00 | 2301 | 575.406 | 307 | 1240 | 1673.3333 | 0
2016-03-15 02:00 | 2712 | 564.408 | 307 | 1240 | 1673.3333 | 0
2016-03-15 03:00 | 2712 | 563.166 | 351 | 1240 | 1673.3333 | 0
2016-03-15 04:00 | 2712 | 576.45 | 563 | 1240 | 1673.3333 | 0
2016-03-15 05:00 | 2712 | 679.08 | 763 | 1240 | 1673.3333 | 0
2016-03-15 06:00 | 2797 | 740.22 | 505 | 1240 | 1673.3333 | 0
2016-03-15 07:00 | 2797 | 787.76 | 372 | 1240 | 1673.3333 | 0
2016-03-15 08:00 | 2797 | 804.1 | 470 | 1240 | 1673.3333 | 0
2016-03-15 09:00 | 2797 | 823.08 | 452 | 1240 | 1673.3333 | 0
2016-03-15 10:00 | 2716 | 837.42 | 433 | 1240 | 1673.3333 | 0
2016-03-15 11:00 | 2716 | 838.46 | 383 | 1240 | 1673.3333 | 0
2016-03-15 12:00 | 2716 | 843.38 | 347 | 1240 | 1673.3333 | 0
2016-03-15 13:00 | 2716 | 841.7 | 413 | 1240 | 1673.3333 | 0
2016-03-15 14:00 | 2048 | 839.28 | 326 | 1240 | 1673.3333 | 0
2016-03-15 15:00 | 2048 | 834.58 | 366 | 1240 | 1673.3333 | 0
2016-03-15 16:00 | 2048 | 832.48 | 396 | 1240 | 1673.3333 | 0
2016-03-15 17:00 | 2048 | 830.5 | 598 | 1240 | 1673.3333 | 0
2016-03-15 18:00 | 1993 | 749.412 | 723 | 1240 | 1673.3333 | 0
2016-03-15 19:00 | 1993 | 834.86 | 518 | 1240 | 1673.3333 | 0
2016-03-15 20:00 | 1993 | 859.92 | 322 | 1240 | 1673.3333 | 0
2016-03-15 21:00 | 1993 | 837.74 | 307 | 1240 | 1673.3333 | 0
2016-03-15 22:00 | 2301 | 785.34 | 307 | 1240 | 1673.3333 | 0
2016-03-15 23:00 | 2301 | 728.04 | 511 | 1240 | 1673.3333 | 0
2016-03-16 | 2301 | 687.76 | 455 | 1240 | 1673.3333 | 0
2016-03-16 01:00 | 2301 | 596.016 | 307 | 1240 | 1673.3333 | 0
2016-03-16 02:00 | 2712 | 583.884 | 307 | 1240 | 1673.3333 | 0
2016-03-16 03:00 | 2712 | 581.346 | 351 | 1240 | 1673.3333 | 0
2016-03-16 04:00 | 2712 | 589.932 | 563 | 1240 | 1673.3333 | 0
2016-03-16 05:00 | 2712 | 696 | 763 | 1240 | 1673.3333 | 0
2016-03-16 06:00 | 2797 | 721.639 | 505 | 1240 | 1521.4286 | 0
2016-03-16 07:00 | 2797 | 763.059 | 372 | 1240 | 1521.4286 | 0
2016-03-16 08:00 | 2797 | 775.96 | 470 | 1240 | 1521.4286 | 0
2016-03-16 09:00 | 2797 | 793.003 | 452 | 1240 | 1521.4286 | 0
2016-03-16 10:00 | 2716 | 807.329 | 433 | 1240 | 1521.4286 | 0
2016-03-16 11:00 | 2716 | 855.86 | 383 | 1240 | 1430.7692 | 0
2016-03-16 12:00 | 2716 | 850.64 | 347 | 1240 | 1430.7692 | 0
2016-03-16 13:00 | 2716 | 841.7 | 413 | 1240 | 1430.7692 | 0
2016-03-16 14:00 | 2048 | 830.62 | 326 | 1240 | 1430.7692 | 0
2016-03-16 15:00 | 2048 | 779.969 | 366 | 1240 | 1430.7692 | 0
2016-03-16 16:00 | 2048 | 772.977 | 396 | 1240 | 1430.7692 | 0
2016-03-16 17:00 | 2048 | 771.248 | 598 | 1240 | 1430.7692 | 0
2016-03-16 18:00 | 1993 | 823.04 | 723 | 1240 | 1440 | 0
2016-03-16 19:00 | 1993 | 834.26 | 518 | 1240 | 1440 | 0
2016-03-16 20:00 | 1993 | 860.34 | 322 | 1240 | 1440 | 0
2016-03-16 21:00 | 1993 | 843.36 | 307 | 1240 | 1440 | 0
2016-03-16 22:00 | 2301 | 802.66 | 307 | 1240 | 1430.7692 | 0
2016-03-16 23:00 | 2301 | 710.6 | 511 | 1240 | 1430.7692 | 0
2016-03-17 | 2301 | 636.348 | 455 | 1240 | 1430.7692 | 0
2016-03-17 01:00 | 2301 | 652.16 | 307 | 1240 | 1430.7692 | 0
2016-03-17 02:00 | 2712 | 644.48 | 307 | 1240 | 1521.4286 | 0
2016-03-17 03:00 | 2712 | 645.64 | 351 | 1240 | 1521.4286 | 0
2016-03-17 04:00 | 2712 | 662.04 | 563 | 1240 | 1521.4286 | 0
2016-03-17 05:00 | 2712 | 705.92 | 763 | 1240 | 1521.4286 | 0
2016-03-17 06:00 | 2797 | 735.889 | 505 | 1240 | 1521.4286 | 0
2016-03-17 07:00 | 2797 | 776.511 | 372 | 1240 | 1521.4286 | 0
2016-03-17 08:00 | 2797 | 772.141 | 470 | 1240 | 1521.4286 | 0
2016-03-17 09:00 | 2797 | 763.363 | 452 | 1240 | 1430.7692 | 0
2016-03-17 10:00 | 2716 | 755.136 | 433 | 1240 | 1430.7692 | 0
2016-03-17 11:00 | 2716 | 743.185 | 383 | 1240 | 1430.7692 | 0
2016-03-17 12:00 | 2716 | 730.246 | 347 | 1240 | 1430.7692 | 0
2016-03-17 13:00 | 2716 | 722.304 | 413 | 1240 | 1521.4286 | 0
2016-03-17 14:00 | 2048 | 713.089 | 326 | 1240 | 1521.4286 | 0
2016-03-17 15:00 | 2048 | 708.7 | 366 | 1240 | 1521.4286 | 0
2016-03-17 16:00 | 2048 | 708.795 | 396 | 1240 | 1521.4286 | 0
2016-03-17 17:00 | 2048 | 706.097 | 598 | 1240 | 1521.4286 | 0
2016-03-17 18:00 | 1993 | 708.814 | 723 | 1240 | 1521.4286 | 0
2016-03-17 19:00 | 1993 | 748.98 | 518 | 1240 | 1521.4286 | 0
2016-03-17 20:00 | 1993 | 741.931 | 322 | 1240 | 1521.4286 | 0
2016-03-17 21:00 | 1993 | 766.42 | 307 | 1240 | 1673.3333 | 0
2016-03-17 22:00 | 2301 | 728.84 | 307 | 1240 | 1673.3333 | 0
2016-03-17 23:00 | 2301 | 680.06 | 511 | 1240 | 1673.3333 | 0
2016-03-18 | 2301 | 665.92 | 455 | 1240 | 1673.3333 | 0
2016-03-18 01:00 | 2301 | 581.94 | 307 | 1240 | 1673.3333 | 0
2016-03-18 02:00 | 2712 | 575.964 | 307 | 1240 | 1673.3333 | 0
2016-03-18 03:00 | 2712 | 643.42 | 351 | 1240 | 1673.3333 | 0
2016-03-18 04:00 | 2712 | 659.96 | 563 | 1240 | 1673.3333 | 0
2016-03-18 05:00 | 2712 | 706.84 | 763 | 1240 | 1673.3333 | 0
2016-03-18 06:00 | 2797 | 740.392 | 505 | 1240 | 1521.4286 | 0
2016-03-18 07:00 | 2797 | 827.64 | 372 | 1240 | 1430.7692 | 0
2016-03-18 08:00 | 2797 | 785.802 | 470 | 1240 | 1430.7692 | 0
2016-03-18 09:00 | 2797 | 820.26 | 452 | 1240 | 1430.7692 | 0
2016-03-18 10:00 | 2716 | 814.36 | 433 | 1240 | 1430.7692 | 0
2016-03-18 11:00 | 2716 | 763.876 | 383 | 1240 | 1521.4286 | 0
2016-03-18 12:00 | 2716 | 750.88 | 347 | 1240 | 1521.4286 | 0
2016-03-18 13:00 | 2716 | 747.764 | 413 | 1240 | 1521.4286 | 0
2016-03-18 14:00 | 2048 | 744.629 | 326 | 1240 | 1521.4286 | 0
2016-03-18 15:00 | 2048 | 740.753 | 366 | 1240 | 1521.4286 | 0
2016-03-18 16:00 | 2048 | 737.675 | 396 | 1240 | 1521.4286 | 0
2016-03-18 17:00 | 2048 | 730.094 | 598 | 1240 | 1521.4286 | 0
2016-03-18 18:00 | 1993 | 770.48 | 723 | 1240 | 1673.3333 | 0
2016-03-18 19:00 | 1993 | 772.42 | 518 | 1240 | 1730 | 0
2016-03-18 20:00 | 1993 | 808.42 | 322 | 1240 | 1730 | 0
2016-03-18 21:00 | 1993 | 713.88 | 307 | 1240 | 1730 | 0
2016-03-18 22:00 | 2301 | 676.458 | 307 | 1240 | 1730 | 0
2016-03-18 23:00 | 2301 | 631.854 | 511 | 1240 | 1730 | 0
2016-03-19 | 2301 | 629.406 | 455 | 1240 | 1730 | 0
2016-03-19 01:00 | 2301 | 611.01 | 307 | 1240 | 1730 | 0
2016-03-19 02:00 | 2712 | 602.874 | 307 | 1240 | 1730 | 0
2016-03-19 03:00 | 2712 | 602.748 | 351 | 1240 | 1730 | 0
2016-03-19 04:00 | 2712 | 612.594 | 563 | 1240 | 1730 | 0
2016-03-19 05:00 | 2712 | 652.086 | 763 | 1240 | 1730 | 0
2016-03-19 06:00 | 2797 | 715.482 | 505 | 1240 | 1730 | 0
2016-03-19 07:00 | 2797 | 831.42 | 372 | 1240 | 1730 | 0
2016-03-19 08:00 | 2797 | 835.64 | 470 | 1240 | 1730 | 0
2016-03-19 09:00 | 2797 | 754.938 | 452 | 1240 | 1730 | 0
2016-03-19 10:00 | 2716 | 840.62 | 433 | 1240 | 1730 | 0
2016-03-19 11:00 | 2716 | 834.4 | 383 | 1240 | 1730 | 0
2016-03-19 12:00 | 2716 | 823.88 | 347 | 1240 | 1730 | 0
2016-03-19 13:00 | 2716 | 818.62 | 413 | 1240 | 1673.3333 | 0
2016-03-19 14:00 | 2048 | 811.1 | 326 | 1240 | 1673.3333 | 0
2016-03-19 15:00 | 2048 | 809.58 | 366 | 1240 | 1673.3333 | 0
2016-03-19 16:00 | 2048 | 802.94 | 396 | 1240 | 1673.3333 | 0
2016-03-19 17:00 | 2048 | 792.74 | 598 | 1240 | 1673.3333 | 0
2016-03-19 18:00 | 1993 | 714.168 | 723 | 1240 | 1730 | 0
2016-03-19 19:00 | 1993 | 714.852 | 518 | 1240 | 1730 | 0
2016-03-19 20:00 | 1993 | 742.626 | 322 | 1240 | 1730 | 0
2016-03-19 21:00 | 1993 | 727.218 | 307 | 1240 | 1730 | 0
2016-03-19 22:00 | 2301 | 696.996 | 307 | 1240 | 1730 | 0
2016-03-19 23:00 | 2301 | 657.072 | 511 | 1240 | 1730 | 0
2016-03-20 | 2301 | 625.662 | 455 | 1240 | 1730 | 0
2016-03-20 01:00 | 2301 | 601.218 | 307 | 1240 | 1730 | 0
2016-03-20 02:00 | 2712 | 587.25 | 307 | 1240 | 1730 | 0
2016-03-20 03:00 | 2712 | 580.572 | 351 | 1240 | 1730 | 0
2016-03-20 04:00 | 2712 | 581.76 | 563 | 1240 | 1730 | 0
2016-03-20 05:00 | 2712 | 600.174 | 763 | 1240 | 1730 | 0
2016-03-20 06:00 | 2797 | 632.718 | 505 | 1240 | 1730 | 0
2016-03-20 07:00 | 2797 | 677.088 | 372 | 1240 | 1730 | 0
2016-03-20 08:00 | 2797 | 712.584 | 470 | 1240 | 1730 | 0
2016-03-20 09:00 | 2797 | 757.656 | 452 | 1240 | 1730 | 0
2016-03-20 10:00 | 2716 | 886.78 | 433 | 1240 | 1673.3333 | 0
2016-03-20 11:00 | 2716 | 912.66 | 383 | 1240 | 1673.3333 | 0
2016-03-20 12:00 | 2716 | 923.28 | 347 | 1240 | 1673.3333 | 0
2016-03-20 13:00 | 2716 | 919.64 | 413 | 1240 | 1673.3333 | 0
2016-03-20 14:00 | 2048 | 915.08 | 326 | 1240 | 1673.3333 | 0
2016-03-20 15:00 | 2048 | 915.92 | 366 | 1240 | 1673.3333 | 0
2016-03-20 16:00 | 2048 | 928.62 | 396 | 1240 | 1673.3333 | 0
2016-03-20 17:00 | 2048 | 945 | 598 | 1240 | 1673.3333 | 0
2016-03-20 18:00 | 1993 | 924.274 | 723 | 1240 | 1430.7692 | 0
2016-03-20 19:00 | 1993 | 950.798 | 518 | 1240 | 1430.7692 | 0
2016-03-20 20:00 | 1993 | 1038.18 | 322 | 1240 | 1440 | 0
2016-03-20 21:00 | 1993 | 979.203 | 307 | 1240 | 1440 | 0
2016-03-20 22:00 | 2301 | 952.318 | 307 | 1240 | 1440 | 0
2016-03-20 23:00 | 2301 | 966.26 | 511 | 1240 | 1440 | 0
2016-03-21 | 2301 | 817.741 | 455 | 1240 | 1440 | 0
2016-03-21 01:00 | 2301 | 844.18 | 307 | 1240 | 1440 | 0
2016-03-21 02:00 | 2712 | 835.48 | 307 | 1240 | 1430.7692 | 0
2016-03-21 03:00 | 2712 | 833.76 | 351 | 1240 | 1430.7692 | 0
2016-03-21 04:00 | 2712 | 838.36 | 563 | 1240 | 1430.7692 | 0
2016-03-21 05:00 | 2712 | 853.98 | 763 | 1240 | 1430.7692 | 0
2016-03-21 06:00 | 2797 | 841.529 | 505 | 1240 | 1430.7692 | 0
2016-03-21 07:00 | 2797 | 873.012 | 372 | 1240 | 1430.7692 | 0
2016-03-21 08:00 | 2797 | 888.649 | 470 | 1240 | 1430.7692 | 0
2016-03-21 09:00 | 2797 | 936.58 | 452 | 1240 | 1430.7692 | 0
2016-03-21 10:00 | 2716 | 879.776 | 433 | 1240 | 1430.7692 | 0
2016-03-21 11:00 | 2716 | 864.063 | 383 | 1240 | 1521.4286 | 0
2016-03-21 12:00 | 2716 | 889.9 | 347 | 1240 | 1521.4286 | 0
2016-03-21 13:00 | 2716 | 865.16 | 413 | 1240 | 1521.4286 | 0
2016-03-21 14:00 | 2048 | 839.58 | 326 | 1240 | 1521.4286 | 0
2016-03-21 15:00 | 2048 | 818 | 366 | 1240 | 1521.4286 | 0
2016-03-21 16:00 | 2048 | 726.354 | 396 | 1240 | 1521.4286 | 0
2016-03-21 17:00 | 2048 | 806.88 | 598 | 1240 | 1521.4286 | 0
2016-03-21 18:00 | 1993 | 823.92 | 723 | 1240 | 1521.4286 | 0
2016-03-21 19:00 | 1993 | 798.931 | 518 | 1240 | 1430.7692 | 0
2016-03-21 20:00 | 1993 | 877.28 | 322 | 1240 | 1440 | 0
2016-03-21 21:00 | 1993 | 860.46 | 307 | 1240 | 1440 | 0
2016-03-21 22:00 | 2301 | 816.68 | 307 | 1240 | 1430.7692 | 0
2016-03-21 23:00 | 2301 | 722.988 | 511 | 1240 | 1430.7692 | 0
2016-03-22 | 2301 | 722.342 | 455 | 1240 | 1440 | 0
2016-03-22 01:00 | 2301 | 708.966 | 307 | 1240 | 1440 | 0
2016-03-22 02:00 | 2712 | 708.111 | 307 | 1240 | 1440 | 0
2016-03-22 03:00 | 2712 | 719.112 | 351 | 1240 | 1440 | 0
2016-03-22 04:00 | 2712 | 747.574 | 563 | 1240 | 1440 | 0
2016-03-22 05:00 | 2712 | 812.326 | 763 | 1240 | 1440 | 0
2016-03-22 06:00 | 2797 | 970.32 | 505 | 1240 | 1440 | 0
2016-03-22 07:00 | 2797 | 967.328 | 372 | 1240 | 1440 | 0
2016-03-22 08:00 | 2797 | 980.68 | 470 | 1240 | 1440 | 0
2016-03-22 09:00 | 2797 | 936.08 | 452 | 1240 | 1440 | 0
2016-03-22 10:00 | 2716 | 899.62 | 433 | 1240 | 1430.7692 | 0
2016-03-22 11:00 | 2716 | 820.097 | 383 | 1240 | 1430.7692 | 0
2016-03-22 12:00 | 2716 | 794.466 | 347 | 1240 | 1521.4286 | 0
2016-03-22 13:00 | 2716 | 777.575 | 413 | 1240 | 1521.4286 | 0
2016-03-22 14:00 | 2048 | 763.534 | 326 | 1240 | 1521.4286 | 0
2016-03-22 15:00 | 2048 | 757.853 | 366 | 1240 | 1521.4286 | 0
2016-03-22 16:00 | 2048 | 758.556 | 396 | 1240 | 1521.4286 | 0
2016-03-22 17:00 | 2048 | 754.851 | 598 | 1240 | 1521.4286 | 0
2016-03-22 18:00 | 1993 | 762.166 | 723 | 1240 | 1521.4286 | 0
2016-03-22 19:00 | 1993 | 809.96 | 518 | 1240 | 1673.3333 | 0
2016-03-22 20:00 | 1993 | 850.92 | 322 | 1240 | 1673.3333 | 0
2016-03-22 21:00 | 1993 | 832.48 | 307 | 1240 | 1673.3333 | 0
2016-03-22 22:00 | 2301 | 701.946 | 307 | 1240 | 1730 | 0
2016-03-22 23:00 | 2301 | 651.402 | 511 | 1240 | 1730 | 0
2016-03-23 | 2301 | 613.242 | 455 | 1240 | 1730 | 0
2016-03-23 01:00 | 2301 | 599.85 | 307 | 1240 | 1730 | 0
2016-03-23 02:00 | 2712 | 594.522 | 307 | 1240 | 1730 | 0
2016-03-23 03:00 | 2712 | 600.786 | 351 | 1240 | 1730 | 0
2016-03-23 04:00 | 2712 | 620.1 | 563 | 1240 | 1730 | 0
2016-03-23 05:00 | 2712 | 675.288 | 763 | 1240 | 1730 | 0
2016-03-23 06:00 | 2797 | 858.74 | 505 | 1240 | 1673.3333 | 0
2016-03-23 07:00 | 2797 | 905.48 | 372 | 1240 | 1673.3333 | 0
2016-03-23 08:00 | 2797 | 874.48 | 470 | 1240 | 1673.3333 | 0
2016-03-23 09:00 | 2797 | 848.8 | 452 | 1240 | 1673.3333 | 0
2016-03-23 10:00 | 2716 | 830.16 | 433 | 1240 | 1673.3333 | 0
2016-03-23 11:00 | 2716 | 819.16 | 383 | 1240 | 1673.3333 | 0
2016-03-23 12:00 | 2716 | 810.36 | 347 | 1240 | 1673.3333 | 0
2016-03-23 13:00 | 2716 | 808.38 | 413 | 1240 | 1673.3333 | 0
2016-03-23 14:00 | 2048 | 802.12 | 326 | 1240 | 1673.3333 | 0
2016-03-23 15:00 | 2048 | 802.44 | 366 | 1240 | 1673.3333 | 0
2016-03-23 16:00 | 2048 | 806.44 | 396 | 1240 | 1673.3333 | 0
2016-03-23 17:00 | 2048 | 802.4 | 598 | 1240 | 1673.3333 | 0
2016-03-23 18:00 | 1993 | 804.88 | 723 | 1240 | 1673.3333 | 0
2016-03-23 19:00 | 1993 | 807.36 | 518 | 1240 | 1673.3333 | 0
2016-03-23 20:00 | 1993 | 846.86 | 322 | 1240 | 1673.3333 | 0
2016-03-23 21:00 | 1993 | 826.36 | 307 | 1240 | 1730 | 0
2016-03-23 22:00 | 2301 | 692.73 | 307 | 1240 | 1730 | 0
2016-03-23 23:00 | 2301 | 632.088 | 511 | 1240 | 1730 | 0
2016-03-24 | 2301 | 540.486 | 455 | 1240 | 1730 | 0
2016-03-24 01:00 | 2301 | 521.604 | 307 | 1240 | 1730 | 0
2016-03-24 02:00 | 2712 | 511.434 | 307 | 1240 | 1730 | 0
2016-03-24 03:00 | 2712 | 507.978 | 351 | 1240 | 1730 | 0
2016-03-24 04:00 | 2712 | 516.222 | 563 | 1240 | 1730 | 0
2016-03-24 05:00 | 2712 | 550.098 | 763 | 1240 | 1730 | 0
2016-03-24 06:00 | 2797 | 621.468 | 505 | 1240 | 1730 | 0
2016-03-24 07:00 | 2797 | 732.94 | 372 | 1240 | 1673.3333 | 0
2016-03-24 08:00 | 2797 | 721.28 | 470 | 1240 | 1673.3333 | 0
2016-03-24 09:00 | 2797 | 725.64 | 452 | 1240 | 1673.3333 | 0
2016-03-24 10:00 | 2716 | 734.9 | 433 | 1240 | 1673.3333 | 0
2016-03-24 11:00 | 2716 | 739.2 | 383 | 1240 | 1673.3333 | 0
2016-03-24 12:00 | 2716 | 737.94 | 347 | 1240 | 1673.3333 | 0
2016-03-24 13:00 | 2716 | 738.38 | 413 | 1240 | 1673.3333 | 0
2016-03-24 14:00 | 2048 | 664.236 | 326 | 1240 | 1730 | 0
2016-03-24 15:00 | 2048 | 665.946 | 366 | 1240 | 1730 | 0
2016-03-24 16:00 | 2048 | 668.97 | 396 | 1240 | 1730 | 0
2016-03-24 17:00 | 2048 | 670.446 | 598 | 1240 | 1730 | 0
2016-03-24 18:00 | 1993 | 678.078 | 723 | 1240 | 1730 | 0
2016-03-24 19:00 | 1993 | 685.71 | 518 | 1240 | 1730 | 0
2016-03-24 20:00 | 1993 | 774.48 | 322 | 1240 | 1730 | 0
2016-03-24 21:00 | 1993 | 677.79 | 307 | 1240 | 1730 | 0
2016-03-24 22:00 | 2301 | 631.422 | 307 | 1240 | 1730 | 0
2016-03-24 23:00 | 2301 | 582.894 | 511 | 1240 | 1730 | 0
2016-03-25 | 2301 | 550.026 | 455 | 1240 | 1730 | 0
2016-03-25 01:00 | 2301 | 531.612 | 307 | 1240 | 1730 | 0
2016-03-25 02:00 | 2712 | 523.08 | 307 | 1240 | 1730 | 0
2016-03-25 03:00 | 2712 | 522.522 | 351 | 1240 | 1730 | 0
2016-03-25 04:00 | 2712 | 534.312 | 563 | 1240 | 1730 | 0
2016-03-25 05:00 | 2712 | 573.714 | 763 | 1240 | 1730 | 0
2016-03-25 06:00 | 2797 | 656.1 | 505 | 1240 | 1730 | 0
2016-03-25 07:00 | 2797 | 771.62 | 372 | 1240 | 1730 | 0
2016-03-25 08:00 | 2797 | 761.26 | 470 | 1240 | 1730 | 0
2016-03-25 09:00 | 2797 | 762 | 452 | 1240 | 1730 | 0
2016-03-25 10:00 | 2716 | 766.72 | 433 | 1240 | 1730 | 0
2016-03-25 11:00 | 2716 | 765.88 | 383 | 1240 | 1730 | 0
2016-03-25 12:00 | 2716 | 758.56 | 347 | 1240 | 1673.3333 | 0
2016-03-25 13:00 | 2716 | 752.7 | 413 | 1240 | 1673.3333 | 0
2016-03-25 14:00 | 2048 | 744.22 | 326 | 1240 | 1673.3333 | 0
2016-03-25 15:00 | 2048 | 699.162 | 366 | 1240 | 1521.4286 | 0
2016-03-25 16:00 | 2048 | 696.939 | 396 | 1240 | 1521.4286 | 0
2016-03-25 17:00 | 2048 | 689.833 | 598 | 1240 | 1521.4286 | 0
2016-03-25 18:00 | 1993 | 692.759 | 723 | 1240 | 1521.4286 | 0
2016-03-25 19:00 | 1993 | 695.685 | 518 | 1240 | 1521.4286 | 0
2016-03-25 20:00 | 1993 | 735.68 | 322 | 1240 | 1521.4286 | 0
2016-03-25 21:00 | 1993 | 721.126 | 307 | 1240 | 1521.4286 | 0
2016-03-25 22:00 | 2301 | 714.34 | 307 | 1240 | 1521.4286 | 0
2016-03-25 23:00 | 2301 | 665.36 | 511 | 1240 | 1673.3333 | 0
2016-03-26 | 2301 | 597.888 | 455 | 1240 | 1673.3333 | 0
2016-03-26 01:00 | 2301 | 596.772 | 307 | 1240 | 1673.3333 | 0
2016-03-26 02:00 | 2712 | 592.452 | 307 | 1240 | 1673.3333 | 0
2016-03-26 03:00 | 2712 | 595.674 | 351 | 1240 | 1673.3333 | 0
2016-03-26 04:00 | 2712 | 613.782 | 563 | 1240 | 1673.3333 | 0
2016-03-26 05:00 | 2712 | 664.344 | 763 | 1240 | 1673.3333 | 0
2016-03-26 06:00 | 2797 | 842.86 | 505 | 1240 | 1673.3333 | 0
2016-03-26 07:00 | 2797 | 843.847 | 372 | 1240 | 1673.3333 | 0
2016-03-26 08:00 | 2797 | 857.56 | 470 | 1240 | 1673.3333 | 0
2016-03-26 09:00 | 2797 | 838.18 | 452 | 1240 | 1673.3333 | 0
2016-03-26 10:00 | 2716 | 825.64 | 433 | 1240 | 1673.3333 | 0
2016-03-26 11:00 | 2716 | 813.34 | 383 | 1240 | 1730 | 0
2016-03-26 12:00 | 2716 | 720.396 | 347 | 1240 | 1730 | 0
2016-03-26 13:00 | 2716 | 722.556 | 413 | 1240 | 1730 | 0
2016-03-26 14:00 | 2048 | 722.394 | 326 | 1240 | 1730 | 0
2016-03-26 15:00 | 2048 | 721.566 | 366 | 1240 | 1730 | 0
2016-03-26 16:00 | 2048 | 717.588 | 396 | 1240 | 1730 | 0
2016-03-26 17:00 | 2048 | 709.974 | 598 | 1240 | 1730 | 0
2016-03-26 18:00 | 1993 | 700.974 | 723 | 1240 | 1730 | 0
2016-03-26 19:00 | 1993 | 691.992 | 518 | 1240 | 1730 | 0
2016-03-26 20:00 | 1993 | 722.232 | 322 | 1240 | 1730 | 0
2016-03-26 21:00 | 1993 | 708.534 | 307 | 1240 | 1730 | 0
2016-03-26 22:00 | 2301 | 677.376 | 307 | 1240 | 1730 | 0
2016-03-26 23:00 | 2301 | 636.57 | 511 | 1240 | 1730 | 0
2016-03-27 | 2301 | 634.158 | 455 | 1240 | 1730 | 0
2016-03-27 01:00 | 2301 | 615.6 | 307 | 1240 | 1730 | 0
2016-03-27 02:00 | 2712 | 601.614 | 307 | 1240 | 1730 | 0
2016-03-27 03:00 | 2712 | 592.92 | 351 | 1240 | 1730 | 0
2016-03-27 04:00 | 2712 | 597.348 | 563 | 1240 | 1730 | 0
2016-03-27 05:00 | 2712 | 615.078 | 763 | 1240 | 1730 | 0
2016-03-27 06:00 | 2797 | 651.474 | 505 | 1240 | 1730 | 0
2016-03-27 07:00 | 2797 | 684.054 | 372 | 1240 | 1730 | 0
2016-03-27 08:00 | 2797 | 780.32 | 470 | 1240 | 1730 | 0
2016-03-27 09:00 | 2797 | 803.56 | 452 | 1240 | 1730 | 0
2016-03-27 10:00 | 2716 | 813.96 | 433 | 1240 | 1730 | 0
2016-03-27 11:00 | 2716 | 815.98 | 383 | 1240 | 1730 | 0
2016-03-27 12:00 | 2716 | 814.82 | 347 | 1240 | 1730 | 0
2016-03-27 13:00 | 2716 | 812.3 | 413 | 1240 | 1730 | 0
2016-03-27 14:00 | 2048 | 729.396 | 326 | 1240 | 1730 | 0
2016-03-27 15:00 | 2048 | 730.926 | 366 | 1240 | 1730 | 0
2016-03-27 16:00 | 2048 | 735.876 | 396 | 1240 | 1730 | 0
2016-03-27 17:00 | 2048 | 736.074 | 598 | 1240 | 1730 | 0
2016-03-27 18:00 | 1993 | 817.02 | 723 | 1240 | 1730 | 0
2016-03-27 19:00 | 1993 | 816.18 | 518 | 1240 | 1730 | 0
2016-03-27 20:00 | 1993 | 847.06 | 322 | 1240 | 1673.3333 | 0
2016-03-27 21:00 | 1993 | 783.256 | 307 | 1240 | 1673.3333 | 0
2016-03-27 22:00 | 2301 | 748.581 | 307 | 1240 | 1673.3333 | 0
2016-03-27 23:00 | 2301 | 742.82 | 511 | 1240 | 1673.3333 | 0
2016-03-28 | 2301 | 710.98 | 455 | 1240 | 1673.3333 | 0
2016-03-28 01:00 | 2301 | 614.628 | 307 | 1240 | 1673.3333 | 0
2016-03-28 02:00 | 2712 | 602.424 | 307 | 1240 | 1673.3333 | 0
2016-03-28 03:00 | 2712 | 594.936 | 351 | 1240 | 1673.3333 | 0
2016-03-28 04:00 | 2712 | 597.636 | 563 | 1240 | 1673.3333 | 0
2016-03-28 05:00 | 2712 | 608.796 | 763 | 1240 | 1673.3333 | 0
2016-03-28 06:00 | 2797 | 633.69 | 505 | 1240 | 1673.3333 | 0
2016-03-28 07:00 | 2797 | 728.12 | 372 | 1240 | 1673.3333 | 0
2016-03-28 08:00 | 2797 | 758.92 | 470 | 1240 | 1673.3333 | 0
2016-03-28 09:00 | 2797 | 781.18 | 452 | 1240 | 1673.3333 | 0
2016-03-28 10:00 | 2716 | 789.36 | 433 | 1240 | 1673.3333 | 0
2016-03-28 11:00 | 2716 | 792.06 | 383 | 1240 | 1673.3333 | 0
2016-03-28 12:00 | 2716 | 791.18 | 347 | 1240 | 1673.3333 | 0
2016-03-28 13:00 | 2716 | 785.16 | 413 | 1240 | 1673.3333 | 0
2016-03-28 14:00 | 2048 | 781.02 | 326 | 1240 | 1673.3333 | 0
2016-03-28 15:00 | 2048 | 699.192 | 366 | 1240 | 1673.3333 | 0
2016-03-28 16:00 | 2048 | 779.26 | 396 | 1240 | 1673.3333 | 0
2016-03-28 17:00 | 2048 | 783.9 | 598 | 1240 | 1673.3333 | 0
2016-03-28 18:00 | 1993 | 797.94 | 723 | 1240 | 1521.4286 | 0
2016-03-28 19:00 | 1993 | 771.362 | 518 | 1240 | 1430.7692 | 0
2016-03-28 20:00 | 1993 | 860.12 | 322 | 1240 | 1440 | 0
2016-03-28 21:00 | 1993 | 847.68 | 307 | 1240 | 1440 | 0
2016-03-28 22:00 | 2301 | 799.14 | 307 | 1240 | 1430.7692 | 0
2016-03-28 23:00 | 2301 | 701.689 | 511 | 1240 | 1430.7692 | 0
2016-03-29 | 2301 | 652 | 455 | 1240 | 1430.7692 | 0
2016-03-29 01:00 | 2301 | 632.72 | 307 | 1240 | 1430.7692 | 0
2016-03-29 02:00 | 2712 | 566.532 | 307 | 1240 | 1521.4286 | 0
2016-03-29 03:00 | 2712 | 572.184 | 351 | 1240 | 1521.4286 | 0
2016-03-29 04:00 | 2712 | 592.992 | 563 | 1240 | 1521.4286 | 0
2016-03-29 05:00 | 2712 | 719.36 | 763 | 1240 | 1521.4286 | 0
2016-03-29 06:00 | 2797 | 786.03 | 505 | 1240 | 1521.4286 | 0
2016-03-29 07:00 | 2797 | 830.167 | 372 | 1240 | 1521.4286 | 0
2016-03-29 08:00 | 2797 | 807.215 | 470 | 1240 | 1521.4286 | 0
2016-03-29 09:00 | 2797 | 788.766 | 452 | 1240 | 1430.7692 | 0
2016-03-29 10:00 | 2716 | 779.266 | 433 | 1240 | 1430.7692 | 0
2016-03-29 11:00 | 2716 | 772.559 | 383 | 1240 | 1430.7692 | 0
2016-03-29 12:00 | 2716 | 769.804 | 347 | 1240 | 1430.7692 | 0
2016-03-29 13:00 | 2716 | 769.804 | 413 | 1240 | 1430.7692 | 0
2016-03-29 14:00 | 2048 | 769.994 | 326 | 1240 | 1430.7692 | 0
2016-03-29 15:00 | 2048 | 775.884 | 366 | 1240 | 1430.7692 | 0
2016-03-29 16:00 | 2048 | 781.527 | 396 | 1240 | 1430.7692 | 0
2016-03-29 17:00 | 2048 | 776.853 | 598 | 1240 | 1430.7692 | 0
2016-03-29 18:00 | 1993 | 774.459 | 723 | 1240 | 1430.7692 | 0
2016-03-29 19:00 | 1993 | 772.065 | 518 | 1240 | 1521.4286 | 0
2016-03-29 20:00 | 1993 | 810.426 | 322 | 1240 | 1521.4286 | 0
2016-03-29 21:00 | 1993 | 829.58 | 307 | 1240 | 1673.3333 | 0
2016-03-29 22:00 | 2301 | 691.632 | 307 | 1240 | 1730 | 0
2016-03-29 23:00 | 2301 | 630.036 | 511 | 1240 | 1730 | 0
2016-03-30 | 2301 | 605.592 | 455 | 1240 | 1730 | 0
2016-03-30 01:00 | 2301 | 585.936 | 307 | 1240 | 1730 | 0
2016-03-30 02:00 | 2712 | 576.09 | 307 | 1240 | 1730 | 0
2016-03-30 03:00 | 2712 | 576.342 | 351 | 1240 | 1730 | 0
2016-03-30 04:00 | 2712 | 588.996 | 563 | 1240 | 1730 | 0
2016-03-30 05:00 | 2712 | 635.166 | 763 | 1240 | 1730 | 0
2016-03-30 06:00 | 2797 | 728.028 | 505 | 1240 | 1730 | 0
2016-03-30 07:00 | 2797 | 850.76 | 372 | 1240 | 1673.3333 | 0
2016-03-30 08:00 | 2797 | 832.38 | 470 | 1240 | 1673.3333 | 0
2016-03-30 09:00 | 2797 | 835.52 | 452 | 1240 | 1521.4286 | 0
2016-03-30 10:00 | 2716 | 836.92 | 433 | 1240 | 1521.4286 | 0
2016-03-30 11:00 | 2716 | 836.36 | 383 | 1240 | 1521.4286 | 0
2016-03-30 12:00 | 2716 | 840.5 | 347 | 1240 | 1521.4286 | 0
2016-03-30 13:00 | 2716 | 848.98 | 413 | 1240 | 1521.4286 | 0
2016-03-30 14:00 | 2048 | 857.54 | 326 | 1240 | 1521.4286 | 0
2016-03-30 15:00 | 2048 | 861.42 | 366 | 1240 | 1673.3333 | 0
2016-03-30 16:00 | 2048 | 867.24 | 396 | 1240 | 1673.3333 | 0
2016-03-30 17:00 | 2048 | 865.28 | 598 | 1240 | 1673.3333 | 0
2016-03-30 18:00 | 1993 | 859.6 | 723 | 1240 | 1673.3333 | 0
2016-03-30 19:00 | 1993 | 768.546 | 518 | 1240 | 1673.3333 | 0
2016-03-30 20:00 | 1993 | 892.44 | 322 | 1240 | 1673.3333 | 0
2016-03-30 21:00 | 1993 | 867.18 | 307 | 1240 | 1673.3333 | 0
2016-03-30 22:00 | 2301 | 722.178 | 307 | 1240 | 1730 | 0
2016-03-30 23:00 | 2301 | 653.31 | 511 | 1240 | 1800 | 0
2016-03-31 | 2301 | 570.618 | 455 | 1240 | 1800 | 0
2016-03-31 01:00 | 2301 | 549.612 | 307 | 1240 | 1800 | 0
2016-03-31 02:00 | 2712 | 538.056 | 307 | 1240 | 1800 | 0
2016-03-31 03:00 | 2712 | 534.564 | 351 | 1240 | 1800 | 0
2016-03-31 04:00 | 2712 | 542.682 | 563 | 1240 | 1730 | 0
2016-03-31 05:00 | 2712 | 579.888 | 763 | 1240 | 1730 | 0
2016-03-31 06:00 | 2797 | 657.504 | 505 | 1240 | 1730 | 0
2016-03-31 07:00 | 2797 | 688.824 | 372 | 1240 | 1730 | 0
2016-03-31 08:00 | 2797 | 679.896 | 470 | 1240 | 1730 | 0
2016-03-31 09:00 | 2797 | 688.374 | 452 | 1240 | 1730 | 0
2016-03-31 10:00 | 2716 | 782.74 | 433 | 1240 | 1673.3333 | 0
2016-03-31 11:00 | 2716 | 795.76 | 383 | 1240 | 1673.3333 | 0
2016-03-31 12:00 | 2716 | 808.42 | 347 | 1240 | 1521.4286 | 0
2016-03-31 13:00 | 2716 | 784.776 | 413 | 1240 | 1521.4286 | 0
2016-03-31 14:00 | 2048 | 800.508 | 326 | 1240 | 1521.4286 | 0
2016-03-31 15:00 | 2048 | 858.46 | 366 | 1240 | 1521.4286 | 0
2016-03-31 16:00 | 2048 | 869.84 | 396 | 1240 | 1521.4286 | 0
2016-03-31 17:00 | 2048 | 869.98 | 598 | 1240 | 1673.3333 | 0
2016-03-31 18:00 | 1993 | 859.86 | 723 | 1240 | 1673.3333 | 0
2016-03-31 19:00 | 1993 | 764.766 | 518 | 1240 | 1673.3333 | 0
2016-03-31 20:00 | 1993 | 881.84 | 322 | 1240 | 1673.3333 | 0
2016-03-31 21:00 | 1993 | 772.56 | 307 | 1240 | 1673.3333 | 0
2016-03-31 22:00 | 2301 | 716.958 | 307 | 1240 | 1730 | 0
2016-03-31 23:00 | 2301 | 653.04 | 511 | 1240 | 1730 | 0
2016-04-01 | 3006 | 581.256 | 497 | 1240 | 1800 | 0
2016-04-01 01:00 | 3006 | 554.868 | 297 | 1240 | 1800 | 0
2016-04-01 02:00 | 2430 | 540.414 | 320 | 1240 | 1800 | 0
2016-04-01 03:00 | 2430 | 533.304 | 348 | 1240 | 1800 | 0
2016-04-01 04:00 | 2430 | 537.696 | 366 | 1240 | 1800 | 0
2016-04-01 05:00 | 2430 | 568.854 | 569 | 1240 | 1800 | 0
2016-04-01 06:00 | 3265 | 636.372 | 809 | 1240 | 1800 | 0
2016-04-01 07:00 | 3265 | 664.128 | 532 | 1240 | 1800 | 0
2016-04-01 08:00 | 3265 | 663.12 | 432 | 1240 | 1800 | 0
2016-04-01 09:00 | 3265 | 678.24 | 470 | 1240 | 1800 | 0
2016-04-01 10:00 | 2890 | 694.17 | 432 | 1240 | 1800 | 0
2016-04-01 11:00 | 2890 | 707.544 | 472 | 1240 | 1800 | 0
2016-04-01 12:00 | 2890 | 716.22 | 456 | 1240 | 1800 | 0
2016-04-01 13:00 | 2890 | 729.648 | 439 | 1240 | 1800 | 0
2016-04-01 14:00 | 2303 | 740.97 | 450 | 1240 | 1800 | 0
2016-04-01 15:00 | 2303 | 747.216 | 435 | 1240 | 1800 | 0
2016-04-01 16:00 | 2303 | 749.25 | 386 | 1240 | 1800 | 0
2016-04-01 17:00 | 2303 | 740.196 | 329 | 1240 | 1800 | 0
2016-04-01 18:00 | 2498 | 730.332 | 426 | 1240 | 1800 | 0
2016-04-01 19:00 | 2498 | 720.468 | 539 | 1240 | 1800 | 0
2016-04-01 20:00 | 2498 | 741.024 | 549 | 1240 | 1800 | 0
2016-04-01 21:00 | 2498 | 722.43 | 307 | 1240 | 1800 | 0
2016-04-01 22:00 | 3006 | 680.616 | 297 | 1240 | 1800 | 0
2016-04-01 23:00 | 3006 | 629.622 | 297 | 1240 | 1800 | 0
2016-04-02 | 3006 | 627.984 | 497 | 1240 | 1800 | 0
2016-04-02 01:00 | 3006 | 600.066 | 297 | 1240 | 1800 | 0
2016-04-02 02:00 | 2430 | 585.27 | 320 | 1240 | 1800 | 0
2016-04-02 03:00 | 2430 | 578.25 | 348 | 1240 | 1800 | 0
2016-04-02 04:00 | 2430 | 580.95 | 366 | 1240 | 1800 | 0
2016-04-02 05:00 | 2430 | 602.172 | 569 | 1240 | 1730 | 0
2016-04-02 06:00 | 3265 | 645.3 | 809 | 1240 | 1730 | 0
2016-04-02 07:00 | 3265 | 675.45 | 532 | 1240 | 1730 | 0
2016-04-02 08:00 | 3265 | 767.88 | 432 | 1240 | 1673.3333 | 0
2016-04-02 09:00 | 3265 | 797.34 | 470 | 1240 | 1673.3333 | 0
2016-04-02 10:00 | 2890 | 822.08 | 432 | 1240 | 1673.3333 | 0
2016-04-02 11:00 | 2890 | 839.76 | 472 | 1240 | 1673.3333 | 0
2016-04-02 12:00 | 2890 | 842.74 | 456 | 1240 | 1673.3333 | 0
2016-04-02 13:00 | 2890 | 844.96 | 439 | 1240 | 1673.3333 | 0
2016-04-02 14:00 | 2303 | 847.26 | 450 | 1240 | 1673.3333 | 0
2016-04-02 15:00 | 2303 | 850.34 | 435 | 1240 | 1673.3333 | 0
2016-04-02 16:00 | 2303 | 855 | 386 | 1240 | 1673.3333 | 0
2016-04-02 17:00 | 2303 | 854.48 | 329 | 1240 | 1673.3333 | 0
2016-04-02 18:00 | 2498 | 840.66 | 426 | 1240 | 1673.3333 | 0
2016-04-02 19:00 | 2498 | 826.84 | 539 | 1240 | 1673.3333 | 0
2016-04-02 20:00 | 2498 | 843.12 | 549 | 1240 | 1673.3333 | 0
2016-04-02 21:00 | 2498 | 822.58 | 307 | 1240 | 1673.3333 | 0
2016-04-02 22:00 | 3006 | 780.08 | 297 | 1240 | 1673.3333 | 0
2016-04-02 23:00 | 3006 | 728.72 | 297 | 1240 | 1673.3333 | 0
2016-04-03 | 3006 | 707.7 | 497 | 1240 | 1673.3333 | 0
2016-04-03 01:00 | 3006 | 675.16 | 297 | 1240 | 1673.3333 | 0
2016-04-03 02:00 | 2430 | 587.106 | 320 | 1240 | 1673.3333 | 0
2016-04-03 03:00 | 2430 | 577.368 | 348 | 1240 | 1673.3333 | 0
2016-04-03 04:00 | 2430 | 639.02 | 366 | 1240 | 1673.3333 | 0
2016-04-03 05:00 | 2430 | 648.36 | 569 | 1240 | 1521.4286 | 0
2016-04-03 06:00 | 3265 | 674.22 | 809 | 1240 | 1521.4286 | 0
2016-04-03 07:00 | 3265 | 661.048 | 532 | 1240 | 1521.4286 | 0
2016-04-03 08:00 | 3265 | 698.402 | 432 | 1240 | 1521.4286 | 0
2016-04-03 09:00 | 3265 | 733.742 | 470 | 1240 | 1430.7692 | 0
2016-04-03 10:00 | 2890 | 757.188 | 432 | 1240 | 1430.7692 | 0
2016-04-03 11:00 | 2890 | 771.571 | 472 | 1240 | 1430.7692 | 0
2016-04-03 12:00 | 2890 | 826.02 | 456 | 1240 | 1430.7692 | 0
2016-04-03 13:00 | 2890 | 832.5 | 439 | 1240 | 1521.4286 | 0
2016-04-03 14:00 | 2303 | 844.38 | 450 | 1240 | 1521.4286 | 0
2016-04-03 15:00 | 2303 | 858.06 | 435 | 1240 | 1521.4286 | 0
2016-04-03 16:00 | 2303 | 826.994 | 386 | 1240 | 1521.4286 | 0
2016-04-03 17:00 | 2303 | 831.269 | 329 | 1240 | 1521.4286 | 0
2016-04-03 18:00 | 2498 | 821.351 | 426 | 1240 | 1521.4286 | 0
2016-04-03 19:00 | 2498 | 854.12 | 539 | 1240 | 1521.4286 | 0
2016-04-03 20:00 | 2498 | 879.04 | 549 | 1240 | 1521.4286 | 0
2016-04-03 21:00 | 2498 | 861.36 | 307 | 1240 | 1521.4286 | 0
2016-04-03 22:00 | 3006 | 821.88 | 297 | 1240 | 1673.3333 | 0
2016-04-03 23:00 | 3006 | 692.55 | 297 | 1240 | 1673.3333 | 0
2016-04-04 | 3006 | 677.826 | 497 | 1240 | 1730 | 0
2016-04-04 01:00 | 3006 | 644.544 | 297 | 1240 | 1730 | 0
2016-04-04 02:00 | 2430 | 622.296 | 320 | 1240 | 1730 | 0
2016-04-04 03:00 | 2430 | 610.236 | 348 | 1240 | 1730 | 0
2016-04-04 04:00 | 2430 | 606.096 | 366 | 1240 | 1730 | 0
2016-04-04 05:00 | 2430 | 611.226 | 569 | 1240 | 1730 | 0
2016-04-04 06:00 | 3265 | 628.704 | 809 | 1240 | 1730 | 0
2016-04-04 07:00 | 3265 | 648.162 | 532 | 1240 | 1730 | 0
2016-04-04 08:00 | 3265 | 679.698 | 432 | 1240 | 1673.3333 | 0
2016-04-04 09:00 | 3265 | 794.3 | 470 | 1240 | 1673.3333 | 0
2016-04-04 10:00 | 2890 | 816.28 | 432 | 1240 | 1673.3333 | 0
2016-04-04 11:00 | 2890 | 827.7 | 472 | 1240 | 1673.3333 | 0
2016-04-04 12:00 | 2890 | 838.9 | 456 | 1240 | 1673.3333 | 0
2016-04-04 13:00 | 2890 | 849 | 439 | 1240 | 1673.3333 | 0
2016-04-04 14:00 | 2303 | 860.1 | 450 | 1240 | 1521.4286 | 0
2016-04-04 15:00 | 2303 | 827.298 | 435 | 1240 | 1521.4286 | 0
2016-04-04 16:00 | 2303 | 836.095 | 386 | 1240 | 1521.4286 | 0
2016-04-04 17:00 | 2303 | 842.061 | 329 | 1240 | 1521.4286 | 0
2016-04-04 18:00 | 2498 | 846.887 | 426 | 1240 | 1430.7692 | 0
2016-04-04 19:00 | 2498 | 851.713 | 539 | 1240 | 1430.7692 | 0
2016-04-04 20:00 | 2498 | 895.983 | 549 | 1240 | 1430.7692 | 0
2016-04-04 21:00 | 2498 | 889.58 | 307 | 1240 | 1430.7692 | 0
2016-04-04 22:00 | 3006 | 886.26 | 297 | 1240 | 1521.4286 | 0
2016-04-04 23:00 | 3006 | 812.38 | 297 | 1240 | 1673.3333 | 0
2016-04-05 | 3006 | 612.972 | 497 | 1240 | 1730 | 0
2016-04-05 01:00 | 3006 | 586.152 | 297 | 1240 | 1730 | 0
2016-04-05 02:00 | 2430 | 570.762 | 320 | 1240 | 1730 | 0
2016-04-05 03:00 | 2430 | 563.202 | 348 | 1240 | 1730 | 0
2016-04-05 04:00 | 2430 | 572.886 | 366 | 1240 | 1730 | 0
2016-04-05 05:00 | 2430 | 607.482 | 569 | 1240 | 1730 | 0
2016-04-05 06:00 | 3265 | 678.87 | 809 | 1240 | 1673.3333 | 0
2016-04-05 07:00 | 3265 | 793.72 | 532 | 1240 | 1673.3333 | 0
2016-04-05 08:00 | 3265 | 795.62 | 432 | 1240 | 1673.3333 | 0
2016-04-05 09:00 | 3265 | 817.56 | 470 | 1240 | 1673.3333 | 0
2016-04-05 10:00 | 2890 | 842.62 | 432 | 1240 | 1673.3333 | 0
2016-04-05 11:00 | 2890 | 858.58 | 472 | 1240 | 1673.3333 | 0
2016-04-05 12:00 | 2890 | 872.6 | 456 | 1240 | 1673.3333 | 0
2016-04-05 13:00 | 2890 | 891.56 | 439 | 1240 | 1521.4286 | 0
2016-04-05 14:00 | 2303 | 908.98 | 450 | 1240 | 1521.4286 | 0
2016-04-05 15:00 | 2303 | 926.72 | 435 | 1240 | 1521.4286 | 0
2016-04-05 16:00 | 2303 | 941.68 | 386 | 1240 | 1521.4286 | 0
2016-04-05 17:00 | 2303 | 943.34 | 329 | 1240 | 1521.4286 | 0
2016-04-05 18:00 | 2498 | 927.2 | 426 | 1240 | 1521.4286 | 0
2016-04-05 19:00 | 2498 | 911.04 | 539 | 1240 | 1521.4286 | 0
2016-04-05 20:00 | 2498 | 936.78 | 549 | 1240 | 1521.4286 | 0
2016-04-05 21:00 | 2498 | 909.04 | 307 | 1240 | 1673.3333 | 0
2016-04-05 22:00 | 3006 | 756.288 | 297 | 1240 | 1730 | 0
2016-04-05 23:00 | 3006 | 685.386 | 297 | 1240 | 1800 | 0
2016-04-06 | 3006 | 625.572 | 497 | 1240 | 1800 | 0
2016-04-06 01:00 | 3006 | 596.448 | 297 | 1240 | 1800 | 0
2016-04-06 02:00 | 2430 | 578.628 | 320 | 1240 | 1800 | 0
2016-04-06 03:00 | 2430 | 569.448 | 348 | 1240 | 1800 | 0
2016-04-06 04:00 | 2430 | 574.578 | 366 | 1240 | 1800 | 0
2016-04-06 05:00 | 2430 | 608.31 | 569 | 1240 | 1730 | 0
2016-04-06 06:00 | 3265 | 682.218 | 809 | 1240 | 1730 | 0
2016-04-06 07:00 | 3265 | 712.296 | 532 | 1240 | 1730 | 0
2016-04-06 08:00 | 3265 | 710.424 | 432 | 1240 | 1730 | 0
2016-04-06 09:00 | 3265 | 726.408 | 470 | 1240 | 1730 | 0
2016-04-06 10:00 | 2890 | 743.634 | 432 | 1240 | 1730 | 0
2016-04-06 11:00 | 2890 | 762.48 | 472 | 1240 | 1673.3333 | 0
2016-04-06 12:00 | 2890 | 869.9 | 456 | 1240 | 1673.3333 | 0
2016-04-06 13:00 | 2890 | 892.26 | 439 | 1240 | 1673.3333 | 0
2016-04-06 14:00 | 2303 | 911.4 | 450 | 1240 | 1521.4286 | 0
2016-04-06 15:00 | 2303 | 925.6 | 435 | 1240 | 1521.4286 | 0
2016-04-06 16:00 | 2303 | 935.66 | 386 | 1240 | 1521.4286 | 0
2016-04-06 17:00 | 2303 | 928.98 | 329 | 1240 | 1521.4286 | 0
2016-04-06 18:00 | 2498 | 911.16 | 426 | 1240 | 1521.4286 | 0
2016-04-06 19:00 | 2498 | 893.34 | 539 | 1240 | 1521.4286 | 0
2016-04-06 20:00 | 2498 | 872.347 | 549 | 1240 | 1521.4286 | 0
2016-04-06 21:00 | 2498 | 891.84 | 307 | 1240 | 1521.4286 | 0
2016-04-06 22:00 | 3006 | 827.16 | 297 | 1240 | 1521.4286 | 0
2016-04-06 23:00 | 3006 | 674.694 | 297 | 1240 | 1673.3333 | 0
2016-04-07 | 3006 | 587.736 | 497 | 1240 | 1730 | 0
2016-04-07 01:00 | 3006 | 561.204 | 297 | 1240 | 1730 | 0
2016-04-07 02:00 | 2430 | 547.488 | 320 | 1240 | 1730 | 0
2016-04-07 03:00 | 2430 | 541.458 | 348 | 1240 | 1730 | 0
2016-04-07 04:00 | 2430 | 545.04 | 366 | 1240 | 1730 | 0
2016-04-07 05:00 | 2430 | 576.162 | 569 | 1240 | 1730 | 0
2016-04-07 06:00 | 3265 | 643.446 | 809 | 1240 | 1730 | 0
2016-04-07 07:00 | 3265 | 665.784 | 532 | 1240 | 1730 | 0
2016-04-07 08:00 | 3265 | 737.02 | 432 | 1240 | 1673.3333 | 0
2016-04-07 09:00 | 3265 | 750.38 | 470 | 1240 | 1673.3333 | 0
2016-04-07 10:00 | 2890 | 691.884 | 432 | 1240 | 1673.3333 | 0
2016-04-07 11:00 | 2890 | 778.22 | 472 | 1240 | 1673.3333 | 0
2016-04-07 12:00 | 2890 | 787.46 | 456 | 1240 | 1673.3333 | 0
2016-04-07 13:00 | 2890 | 714.51 | 439 | 1240 | 1673.3333 | 0
2016-04-07 14:00 | 2303 | 717.93 | 450 | 1240 | 1673.3333 | 0
2016-04-07 15:00 | 2303 | 721.17 | 435 | 1240 | 1673.3333 | 0
2016-04-07 16:00 | 2303 | 722.844 | 386 | 1240 | 1673.3333 | 0
2016-04-07 17:00 | 2303 | 717.66 | 329 | 1240 | 1673.3333 | 0
2016-04-07 18:00 | 2498 | 708.462 | 426 | 1240 | 1673.3333 | 0
2016-04-07 19:00 | 2498 | 699.264 | 539 | 1240 | 1673.3333 | 0
2016-04-07 20:00 | 2498 | 789.96 | 549 | 1240 | 1673.3333 | 0
2016-04-07 21:00 | 2498 | 764.78 | 307 | 1240 | 1673.3333 | 0
2016-04-07 22:00 | 3006 | 709.52 | 297 | 1240 | 1673.3333 | 0
2016-04-07 23:00 | 3006 | 645.94 | 297 | 1240 | 1673.3333 | 0
2016-04-08 | 3006 | 637.54 | 497 | 1240 | 1673.3333 | 0
2016-04-08 01:00 | 3006 | 549.684 | 297 | 1240 | 1673.3333 | 0
2016-04-08 02:00 | 2430 | 536.598 | 320 | 1240 | 1673.3333 | 0
2016-04-08 03:00 | 2430 | 533.268 | 348 | 1240 | 1673.3333 | 0
2016-04-08 04:00 | 2430 | 542.448 | 366 | 1240 | 1673.3333 | 0
2016-04-08 05:00 | 2430 | 644.88 | 569 | 1240 | 1673.3333 | 0
2016-04-08 06:00 | 3265 | 696.958 | 809 | 1240 | 1521.4286 | 0
2016-04-08 07:00 | 3265 | 727.719 | 532 | 1240 | 1430.7692 | 0
2016-04-08 08:00 | 3265 | 719.207 | 432 | 1240 | 1430.7692 | 0
2016-04-08 09:00 | 3265 | 722.57 | 470 | 1240 | 1430.7692 | 0
2016-04-08 10:00 | 2890 | 727.282 | 432 | 1240 | 1430.7692 | 0
2016-04-08 11:00 | 2890 | 727.871 | 472 | 1240 | 1430.7692 | 0
2016-04-08 12:00 | 2890 | 724.774 | 456 | 1240 | 1430.7692 | 0
2016-04-08 13:00 | 2890 | 728.726 | 439 | 1240 | 1430.7692 | 0
2016-04-08 14:00 | 2303 | 727.7 | 450 | 1240 | 1430.7692 | 0
2016-04-08 15:00 | 2303 | 728.099 | 435 | 1240 | 1430.7692 | 0
2016-04-08 16:00 | 2303 | 729.771 | 386 | 1240 | 1430.7692 | 0
2016-04-08 17:00 | 2303 | 727.016 | 329 | 1240 | 1430.7692 | 0
2016-04-08 18:00 | 2498 | 722.38 | 426 | 1240 | 1430.7692 | 0
2016-04-08 19:00 | 2498 | 717.744 | 539 | 1240 | 1430.7692 | 0
2016-04-08 20:00 | 2498 | 753.312 | 549 | 1240 | 1430.7692 | 0
2016-04-08 21:00 | 2498 | 736.535 | 307 | 1240 | 1521.4286 | 0
2016-04-08 22:00 | 3006 | 652.572 | 297 | 1240 | 1730 | 0
2016-04-08 23:00 | 3006 | 599.04 | 297 | 1240 | 1730 | 0
2016-04-09 | 3006 | 598.158 | 497 | 1240 | 1730 | 0
2016-04-09 01:00 | 3006 | 596.358 | 297 | 1240 | 1730 | 0
2016-04-09 02:00 | 2430 | 595.062 | 320 | 1240 | 1730 | 0
2016-04-09 03:00 | 2430 | 594.882 | 348 | 1240 | 1730 | 0
2016-04-09 04:00 | 2430 | 607.482 | 366 | 1240 | 1730 | 0
2016-04-09 05:00 | 2430 | 653.652 | 569 | 1240 | 1730 | 0
2016-04-09 06:00 | 3265 | 826.4 | 809 | 1240 | 1673.3333 | 0
2016-04-09 07:00 | 3265 | 862.48 | 532 | 1240 | 1521.4286 | 0
2016-04-09 08:00 | 3265 | 808.393 | 432 | 1240 | 1521.4286 | 0
2016-04-09 09:00 | 3265 | 808.374 | 470 | 1240 | 1430.7692 | 0
2016-04-09 10:00 | 2890 | 810.236 | 432 | 1240 | 1430.7692 | 0
2016-04-09 11:00 | 2890 | 807.348 | 472 | 1240 | 1430.7692 | 0
2016-04-09 12:00 | 2890 | 809.096 | 456 | 1240 | 1430.7692 | 0
2016-04-09 13:00 | 2890 | 812.706 | 439 | 1240 | 1430.7692 | 0
2016-04-09 14:00 | 2303 | 813.808 | 450 | 1240 | 1430.7692 | 0
2016-04-09 15:00 | 2303 | 813.694 | 435 | 1240 | 1430.7692 | 0
2016-04-09 16:00 | 2303 | 811.87 | 386 | 1240 | 1430.7692 | 0
2016-04-09 17:00 | 2303 | 842.9 | 329 | 1240 | 1521.4286 | 0
2016-04-09 18:00 | 2498 | 831.82 | 426 | 1240 | 1521.4286 | 0
2016-04-09 19:00 | 2498 | 820.72 | 539 | 1240 | 1673.3333 | 0
2016-04-09 20:00 | 2498 | 851.58 | 549 | 1240 | 1673.3333 | 0
2016-04-09 21:00 | 2498 | 836.44 | 307 | 1240 | 1673.3333 | 0
2016-04-09 22:00 | 3006 | 717.75 | 297 | 1240 | 1730 | 0
2016-04-09 23:00 | 3006 | 669.996 | 297 | 1240 | 1730 | 0
2016-04-10 | 3006 | 659.736 | 497 | 1240 | 1730 | 0
2016-04-10 01:00 | 3006 | 630.324 | 297 | 1240 | 1730 | 0
2016-04-10 02:00 | 2430 | 614.808 | 320 | 1240 | 1730 | 0
2016-04-10 03:00 | 2430 | 604.854 | 348 | 1240 | 1730 | 0
2016-04-10 04:00 | 2430 | 605.376 | 366 | 1240 | 1730 | 0
2016-04-10 05:00 | 2430 | 620.424 | 569 | 1240 | 1730 | 0
2016-04-10 06:00 | 3265 | 651.276 | 809 | 1240 | 1730 | 0
2016-04-10 07:00 | 3265 | 748.88 | 532 | 1240 | 1673.3333 | 0
2016-04-10 08:00 | 3265 | 786.28 | 432 | 1240 | 1673.3333 | 0
2016-04-10 09:00 | 3265 | 818.62 | 470 | 1240 | 1521.4286 | 0
2016-04-10 10:00 | 2890 | 838.3 | 432 | 1240 | 1521.4286 | 0
2016-04-10 11:00 | 2890 | 843.98 | 472 | 1240 | 1521.4286 | 0
2016-04-10 12:00 | 2890 | 804.403 | 456 | 1240 | 1430.7692 | 0
2016-04-10 13:00 | 2890 | 805.277 | 439 | 1240 | 1430.7692 | 0
2016-04-10 14:00 | 2303 | 809.894 | 450 | 1240 | 1430.7692 | 0
2016-04-10 15:00 | 2303 | 815.119 | 435 | 1240 | 1430.7692 | 0
2016-04-10 16:00 | 2303 | 821.484 | 386 | 1240 | 1430.7692 | 0
2016-04-10 17:00 | 2303 | 823.023 | 329 | 1240 | 1430.7692 | 0
2016-04-10 18:00 | 2498 | 818.786 | 426 | 1240 | 1430.7692 | 0
2016-04-10 19:00 | 2498 | 857.42 | 539 | 1240 | 1521.4286 | 0
2016-04-10 20:00 | 2498 | 893.58 | 549 | 1240 | 1521.4286 | 0
2016-04-10 21:00 | 2498 | 878.32 | 307 | 1240 | 1673.3333 | 0
2016-04-10 22:00 | 3006 | 836.38 | 297 | 1240 | 1673.3333 | 0
2016-04-10 23:00 | 3006 | 705.132 | 297 | 1240 | 1730 | 0
2016-04-11 | 3006 | 630.954 | 497 | 1240 | 1730 | 0
2016-04-11 01:00 | 3006 | 603.522 | 297 | 1240 | 1730 | 0
2016-04-11 02:00 | 2430 | 586.836 | 320 | 1240 | 1730 | 0
2016-04-11 03:00 | 2430 | 576.936 | 348 | 1240 | 1730 | 0
2016-04-11 04:00 | 2430 | 573.588 | 366 | 1240 | 1730 | 0
2016-04-11 05:00 | 2430 | 577.26 | 569 | 1240 | 1730 | 0
2016-04-11 06:00 | 3265 | 591.426 | 809 | 1240 | 1730 | 0
2016-04-11 07:00 | 3265 | 669.02 | 532 | 1240 | 1673.3333 | 0
2016-04-11 08:00 | 3265 | 701.32 | 432 | 1240 | 1521.4286 | 0
2016-04-11 09:00 | 3265 | 700.15 | 470 | 1240 | 1521.4286 | 0
2016-04-11 10:00 | 2890 | 725.344 | 432 | 1240 | 1521.4286 | 0
2016-04-11 11:00 | 2890 | 741.247 | 472 | 1240 | 1430.7692 | 0
2016-04-11 12:00 | 2890 | 756.371 | 456 | 1240 | 1430.7692 | 0
2016-04-11 13:00 | 2890 | 766.954 | 439 | 1240 | 1430.7692 | 0
2016-04-11 14:00 | 2303 | 774.288 | 450 | 1240 | 1430.7692 | 0
2016-04-11 15:00 | 2303 | 822.06 | 435 | 1240 | 1430.7692 | 0
2016-04-11 16:00 | 2303 | 832.62 | 386 | 1240 | 1430.7692 | 0
2016-04-11 17:00 | 2303 | 841.3 | 329 | 1240 | 1430.7692 | 0
2016-04-11 18:00 | 2498 | 804.726 | 426 | 1240 | 1430.7692 | 0
2016-04-11 19:00 | 2498 | 810.217 | 539 | 1240 | 1430.7692 | 0
2016-04-11 20:00 | 2498 | 842.612 | 549 | 1240 | 1430.7692 | 0
2016-04-11 21:00 | 2498 | 826.329 | 307 | 1240 | 1430.7692 | 0
2016-04-11 22:00 | 3006 | 813.98 | 297 | 1240 | 1521.4286 | 0
2016-04-11 23:00 | 3006 | 745.2 | 297 | 1240 | 1673.3333 | 0
2016-04-12 | 3006 | 581.814 | 497 | 1240 | 1673.3333 | 0
2016-04-12 01:00 | 3006 | 558.486 | 297 | 1240 | 1673.3333 | 0
2016-04-12 02:00 | 2430 | 546.732 | 320 | 1240 | 1673.3333 | 0
2016-04-12 03:00 | 2430 | 542.232 | 348 | 1240 | 1673.3333 | 0
2016-04-12 04:00 | 2430 | 550.476 | 366 | 1240 | 1673.3333 | 0
2016-04-12 05:00 | 2430 | 587.088 | 569 | 1240 | 1673.3333 | 0
2016-04-12 06:00 | 3265 | 730.68 | 809 | 1240 | 1521.4286 | 0
2016-04-12 07:00 | 3265 | 725.173 | 532 | 1240 | 1521.4286 | 0
2016-04-12 08:00 | 3265 | 728.137 | 432 | 1240 | 1521.4286 | 0
2016-04-12 09:00 | 3265 | 747.004 | 470 | 1240 | 1521.4286 | 0
2016-04-12 10:00 | 2890 | 808.66 | 432 | 1240 | 1521.4286 | 0
2016-04-12 11:00 | 2890 | 829.04 | 472 | 1240 | 1521.4286 | 0
2016-04-12 12:00 | 2890 | 840.94 | 456 | 1240 | 1521.4286 | 0
2016-04-12 13:00 | 2890 | 851.98 | 439 | 1240 | 1521.4286 | 0
2016-04-12 14:00 | 2303 | 861.76 | 450 | 1240 | 1521.4286 | 0
2016-04-12 15:00 | 2303 | 870.16 | 435 | 1240 | 1521.4286 | 0
2016-04-12 16:00 | 2303 | 876.1 | 386 | 1240 | 1521.4286 | 0
2016-04-12 17:00 | 2303 | 869.9 | 329 | 1240 | 1521.4286 | 0
2016-04-12 18:00 | 2498 | 859 | 426 | 1240 | 1521.4286 | 0
2016-04-12 19:00 | 2498 | 848.12 | 539 | 1240 | 1521.4286 | 0
2016-04-12 20:00 | 2498 | 878.56 | 549 | 1240 | 1521.4286 | 0
2016-04-12 21:00 | 2498 | 854.68 | 307 | 1240 | 1521.4286 | 0
2016-04-12 22:00 | 3006 | 710.478 | 297 | 1240 | 1673.3333 | 0
2016-04-12 23:00 | 3006 | 644.904 | 297 | 1240 | 1730 | 0
2016-04-13 | 3006 | 595.512 | 497 | 1240 | 1730 | 0
2016-04-13 01:00 | 3006 | 570.132 | 297 | 1240 | 1730 | 0
2016-04-13 02:00 | 2430 | 555.894 | 320 | 1240 | 1730 | 0
2016-04-13 03:00 | 2430 | 548.424 | 348 | 1240 | 1730 | 0
2016-04-13 04:00 | 2430 | 554.346 | 366 | 1240 | 1730 | 0
2016-04-13 05:00 | 2430 | 588.402 | 569 | 1240 | 1730 | 0
2016-04-13 06:00 | 3265 | 734.92 | 809 | 1240 | 1673.3333 | 0
2016-04-13 07:00 | 3265 | 762.76 | 532 | 1240 | 1673.3333 | 0
2016-04-13 08:00 | 3265 | 690.93 | 432 | 1240 | 1673.3333 | 0
2016-04-13 09:00 | 3265 | 708.984 | 470 | 1240 | 1673.3333 | 0
2016-04-13 10:00 | 2890 | 729.162 | 432 | 1240 | 1673.3333 | 0
2016-04-13 11:00 | 2890 | 750.114 | 472 | 1240 | 1673.3333 | 0
2016-04-13 12:00 | 2890 | 758.322 | 456 | 1240 | 1673.3333 | 0
2016-04-13 13:00 | 2890 | 771.588 | 439 | 1240 | 1673.3333 | 0
2016-04-13 14:00 | 2303 | 865.2 | 450 | 1240 | 1673.3333 | 0
2016-04-13 15:00 | 2303 | 870.86 | 435 | 1240 | 1673.3333 | 0
2016-04-13 16:00 | 2303 | 878.96 | 386 | 1240 | 1673.3333 | 0
2016-04-13 17:00 | 2303 | 878.86 | 329 | 1240 | 1673.3333 | 0
2016-04-13 18:00 | 2498 | 865.52 | 426 | 1240 | 1521.4286 | 0
2016-04-13 19:00 | 2498 | 852.18 | 539 | 1240 | 1521.4286 | 0
2016-04-13 20:00 | 2498 | 836.627 | 549 | 1240 | 1521.4286 | 0
2016-04-13 21:00 | 2498 | 816.582 | 307 | 1240 | 1521.4286 | 0
2016-04-13 22:00 | 3006 | 794.24 | 297 | 1240 | 1521.4286 | 0
2016-04-13 23:00 | 3006 | 650.682 | 297 | 1240 | 1730 | 0
2016-04-14 | 3006 | 571.032 | 497 | 1240 | 1800 | 0
2016-04-14 01:00 | 3006 | 545.76 | 297 | 1240 | 1800 | 0
2016-04-14 02:00 | 2430 | 532.692 | 320 | 1240 | 1800 | 0
2016-04-14 03:00 | 2430 | 526.104 | 348 | 1240 | 1800 | 0
2016-04-14 04:00 | 2430 | 532.458 | 366 | 1240 | 1800 | 0
2016-04-14 05:00 | 2430 | 566.424 | 569 | 1240 | 1800 | 0
2016-04-14 06:00 | 3265 | 634.95 | 809 | 1240 | 1730 | 0
2016-04-14 07:00 | 3265 | 730.16 | 532 | 1240 | 1673.3333 | 0
2016-04-14 08:00 | 3265 | 731.8 | 432 | 1240 | 1673.3333 | 0
2016-04-14 09:00 | 3265 | 747.02 | 470 | 1240 | 1673.3333 | 0
2016-04-14 10:00 | 2890 | 763.12 | 432 | 1240 | 1673.3333 | 0
2016-04-14 11:00 | 2890 | 777.32 | 472 | 1240 | 1673.3333 | 0
2016-04-14 12:00 | 2890 | 790.48 | 456 | 1240 | 1673.3333 | 0
2016-04-14 13:00 | 2890 | 807.06 | 439 | 1240 | 1673.3333 | 0
2016-04-14 14:00 | 2303 | 820.38 | 450 | 1240 | 1673.3333 | 0
2016-04-14 15:00 | 2303 | 829.82 | 435 | 1240 | 1521.4286 | 0
2016-04-14 16:00 | 2303 | 837.74 | 386 | 1240 | 1521.4286 | 0
2016-04-14 17:00 | 2303 | 835.74 | 329 | 1240 | 1521.4286 | 0
2016-04-14 18:00 | 2498 | 823.02 | 426 | 1240 | 1521.4286 | 0
2016-04-14 19:00 | 2498 | 810.3 | 539 | 1240 | 1521.4286 | 0
2016-04-14 20:00 | 2498 | 788.595 | 549 | 1240 | 1521.4286 | 0
2016-04-14 21:00 | 2498 | 769.937 | 307 | 1240 | 1521.4286 | 0
2016-04-14 22:00 | 3006 | 753.42 | 297 | 1240 | 1521.4286 | 0
2016-04-14 23:00 | 3006 | 688.38 | 297 | 1240 | 1521.4286 | 0
2016-04-15 | 3006 | 579.924 | 497 | 1240 | 1521.4286 | 0
2016-04-15 01:00 | 3006 | 555.948 | 297 | 1240 | 1521.4286 | 0
2016-04-15 02:00 | 2430 | 541.368 | 320 | 1240 | 1521.4286 | 0
2016-04-15 03:00 | 2430 | 534.186 | 348 | 1240 | 1521.4286 | 0
2016-04-15 04:00 | 2430 | 540.09 | 366 | 1240 | 1521.4286 | 0
2016-04-15 05:00 | 2430 | 574.128 | 569 | 1240 | 1521.4286 | 0
2016-04-15 06:00 | 3265 | 712.58 | 809 | 1240 | 1521.4286 | 0
2016-04-15 07:00 | 3265 | 705.185 | 532 | 1240 | 1521.4286 | 0
2016-04-15 08:00 | 3265 | 709.175 | 432 | 1240 | 1521.4286 | 0
2016-04-15 09:00 | 3265 | 723.501 | 470 | 1240 | 1521.4286 | 0
2016-04-15 10:00 | 2890 | 741.969 | 432 | 1240 | 1521.4286 | 0
2016-04-15 11:00 | 2890 | 754.585 | 472 | 1240 | 1521.4286 | 0
2016-04-15 12:00 | 2890 | 765.187 | 456 | 1240 | 1521.4286 | 0
2016-04-15 13:00 | 2890 | 818.98 | 439 | 1240 | 1521.4286 | 0
2016-04-15 14:00 | 2303 | 784.491 | 450 | 1240 | 1521.4286 | 0
2016-04-15 15:00 | 2303 | 790.096 | 435 | 1240 | 1521.4286 | 0
2016-04-15 16:00 | 2303 | 792.186 | 386 | 1240 | 1521.4286 | 0
2016-04-15 17:00 | 2303 | 782.458 | 329 | 1240 | 1521.4286 | 0
2016-04-15 18:00 | 2498 | 770.944 | 426 | 1240 | 1521.4286 | 0
2016-04-15 19:00 | 2498 | 759.43 | 539 | 1240 | 1521.4286 | 0
2016-04-15 20:00 | 2498 | 786.448 | 549 | 1240 | 1521.4286 | 0
2016-04-15 21:00 | 2498 | 766.688 | 307 | 1240 | 1521.4286 | 0
2016-04-15 22:00 | 3006 | 753.44 | 297 | 1240 | 1521.4286 | 0
2016-04-15 23:00 | 3006 | 687.26 | 297 | 1240 | 1521.4286 | 0
2016-04-16 | 3006 | 682.58 | 497 | 1240 | 1521.4286 | 0
2016-04-16 01:00 | 3006 | 588.78 | 297 | 1240 | 1521.4286 | 0
2016-04-16 02:00 | 2430 | 637.86 | 320 | 1240 | 1521.4286 | 0
2016-04-16 03:00 | 2430 | 630.34 | 348 | 1240 | 1521.4286 | 0
2016-04-16 04:00 | 2430 | 636.3 | 366 | 1240 | 1521.4286 | 0
2016-04-16 05:00 | 2430 | 675.68 | 569 | 1240 | 1521.4286 | 0
2016-04-16 06:00 | 3265 | 717.079 | 809 | 1240 | 1430.7692 | 0
2016-04-16 07:00 | 3265 | 746.7 | 532 | 1240 | 1430.7692 | 0
2016-04-16 08:00 | 3265 | 753.426 | 432 | 1240 | 1430.7692 | 0
2016-04-16 09:00 | 3265 | 773.452 | 470 | 1240 | 1430.7692 | 0
2016-04-16 10:00 | 2890 | 834.94 | 432 | 1240 | 1440 | 0
2016-04-16 11:00 | 2890 | 845.26 | 472 | 1240 | 1440 | 0
2016-04-16 12:00 | 2890 | 810.426 | 456 | 1240 | 1440 | 0
2016-04-16 13:00 | 2890 | 862.08 | 439 | 1240 | 1440 | 0
2016-04-16 14:00 | 2303 | 873.54 | 450 | 1240 | 1440 | 0
2016-04-16 15:00 | 2303 | 878.74 | 435 | 1240 | 1440 | 0
2016-04-16 16:00 | 2303 | 880.84 | 386 | 1240 | 1440 | 0
2016-04-16 17:00 | 2303 | 869.32 | 329 | 1240 | 1440 | 0
2016-04-16 18:00 | 2498 | 808.032 | 426 | 1240 | 1430.7692 | 0
2016-04-16 19:00 | 2498 | 790.21 | 539 | 1240 | 1430.7692 | 0
2016-04-16 20:00 | 2498 | 853.66 | 549 | 1240 | 1440 | 0
2016-04-16 21:00 | 2498 | 793.801 | 307 | 1240 | 1430.7692 | 0
2016-04-16 22:00 | 3006 | 754.053 | 297 | 1240 | 1430.7692 | 0
2016-04-16 23:00 | 3006 | 703 | 297 | 1240 | 1430.7692 | 0
2016-04-17 | 3006 | 720.78 | 497 | 1240 | 1430.7692 | 0
2016-04-17 01:00 | 3006 | 687.08 | 297 | 1240 | 1430.7692 | 0
2016-04-17 02:00 | 2430 | 663.82 | 320 | 1240 | 1430.7692 | 0
2016-04-17 03:00 | 2430 | 653.34 | 348 | 1240 | 1430.7692 | 0
2016-04-17 04:00 | 2430 | 648.54 | 366 | 1240 | 1430.7692 | 0
2016-04-17 05:00 | 2430 | 658.54 | 569 | 1240 | 1430.7692 | 0
2016-04-17 06:00 | 3265 | 686.32 | 809 | 1240 | 1430.7692 | 0
2016-04-17 07:00 | 3265 | 671.441 | 532 | 1240 | 1430.7692 | 0
2016-04-17 08:00 | 3265 | 707.446 | 432 | 1240 | 1430.7692 | 0
2016-04-17 09:00 | 3265 | 745.161 | 470 | 1240 | 1430.7692 | 0
2016-04-17 10:00 | 2890 | 775.599 | 432 | 1240 | 1430.7692 | 0
2016-04-17 11:00 | 2890 | 794.523 | 472 | 1240 | 1430.7692 | 0
2016-04-17 12:00 | 2890 | 844.84 | 456 | 1240 | 1430.7692 | 0
2016-04-17 13:00 | 2890 | 807.12 | 439 | 1240 | 1430.7692 | 0
2016-04-17 14:00 | 2303 | 851.12 | 450 | 1240 | 1430.7692 | 0
2016-04-17 15:00 | 2303 | 850.82 | 435 | 1240 | 1430.7692 | 0
2016-04-17 16:00 | 2303 | 805.866 | 386 | 1240 | 1430.7692 | 0
2016-04-17 17:00 | 2303 | 798.817 | 329 | 1240 | 1430.7692 | 0
2016-04-17 18:00 | 2498 | 793.801 | 426 | 1240 | 1430.7692 | 0
2016-04-17 19:00 | 2498 | 788.766 | 539 | 1240 | 1430.7692 | 0
2016-04-17 20:00 | 2498 | 802.123 | 549 | 1240 | 1430.7692 | 0
2016-04-17 21:00 | 2498 | 822.94 | 307 | 1240 | 1430.7692 | 0
2016-04-17 22:00 | 3006 | 743.812 | 297 | 1240 | 1430.7692 | 0
2016-04-17 23:00 | 3006 | 697.414 | 297 | 1240 | 1430.7692 | 0
2016-04-18 | 3006 | 679.25 | 497 | 1240 | 1430.7692 | 0
2016-04-18 01:00 | 3006 | 649.211 | 297 | 1240 | 1430.7692 | 0
2016-04-18 02:00 | 2430 | 664 | 320 | 1240 | 1430.7692 | 0
2016-04-18 03:00 | 2430 | 652.42 | 348 | 1240 | 1430.7692 | 0
2016-04-18 04:00 | 2430 | 647.64 | 366 | 1240 | 1430.7692 | 0
2016-04-18 05:00 | 2430 | 653.2 | 569 | 1240 | 1430.7692 | 0
2016-04-18 06:00 | 3265 | 669.32 | 809 | 1240 | 1430.7692 | 0
2016-04-18 07:00 | 3265 | 682.22 | 532 | 1240 | 1430.7692 | 0
2016-04-18 08:00 | 3265 | 682.024 | 432 | 1240 | 1430.7692 | 0
2016-04-18 09:00 | 3265 | 718.96 | 470 | 1240 | 1430.7692 | 0
2016-04-18 10:00 | 2890 | 744.42 | 432 | 1240 | 1430.7692 | 0
2016-04-18 11:00 | 2890 | 757.454 | 472 | 1240 | 1430.7692 | 0
2016-04-18 12:00 | 2890 | 809.72 | 456 | 1240 | 1430.7692 | 0
2016-04-18 13:00 | 2890 | 770.336 | 439 | 1240 | 1430.7692 | 0
2016-04-18 14:00 | 2303 | 770.374 | 450 | 1240 | 1430.7692 | 0
2016-04-18 15:00 | 2303 | 775.181 | 435 | 1240 | 1430.7692 | 0
2016-04-18 16:00 | 2303 | 785.707 | 386 | 1240 | 1430.7692 | 0
2016-04-18 17:00 | 2303 | 838.88 | 329 | 1240 | 1440 | 0
2016-04-18 18:00 | 2498 | 845.96 | 426 | 1240 | 1440 | 0
2016-04-18 19:00 | 2498 | 853.04 | 539 | 1240 | 1440 | 0
2016-04-18 20:00 | 2498 | 880.76 | 549 | 1240 | 1440 | 0
2016-04-18 21:00 | 2498 | 860.26 | 307 | 1240 | 1440 | 0
2016-04-18 22:00 | 3006 | 807.92 | 297 | 1240 | 1430.7692 | 0
2016-04-18 23:00 | 3006 | 703.437 | 297 | 1240 | 1430.7692 | 0
2016-04-19 | 3006 | 641.76 | 497 | 1240 | 1430.7692 | 0
2016-04-19 01:00 | 3006 | 618.06 | 297 | 1240 | 1430.7692 | 0
2016-04-19 02:00 | 2430 | 605.06 | 320 | 1240 | 1430.7692 | 0
2016-04-19 03:00 | 2430 | 601.8 | 348 | 1240 | 1430.7692 | 0
2016-04-19 04:00 | 2430 | 614.22 | 366 | 1240 | 1430.7692 | 0
2016-04-19 05:00 | 2430 | 659.14 | 569 | 1240 | 1430.7692 | 0
2016-04-19 06:00 | 3265 | 707.522 | 809 | 1240 | 1430.7692 | 0
2016-04-19 07:00 | 3265 | 780.64 | 532 | 1240 | 1440 | 0
2016-04-19 08:00 | 3265 | 780.6 | 432 | 1240 | 1440 | 0
2016-04-19 09:00 | 3265 | 791.84 | 470 | 1240 | 1440 | 0
2016-04-19 10:00 | 2890 | 800.96 | 432 | 1240 | 1440 | 0
2016-04-19 11:00 | 2890 | 805.56 | 472 | 1240 | 1440 | 0
2016-04-19 12:00 | 2890 | 807.38 | 456 | 1240 | 1440 | 0
2016-04-19 13:00 | 2890 | 808.5 | 439 | 1240 | 1440 | 0
2016-04-19 14:00 | 2303 | 808.48 | 450 | 1240 | 1440 | 0
2016-04-19 15:00 | 2303 | 808.76 | 435 | 1240 | 1440 | 0
2016-04-19 16:00 | 2303 | 808.68 | 386 | 1240 | 1440 | 0
2016-04-19 17:00 | 2303 | 804.84 | 329 | 1240 | 1430.7692 | 0
2016-04-19 18:00 | 2498 | 807.14 | 426 | 1240 | 1430.7692 | 0
2016-04-19 19:00 | 2498 | 768.949 | 539 | 1240 | 1430.7692 | 0
2016-04-19 20:00 | 2498 | 837.06 | 549 | 1240 | 1430.7692 | 0
2016-04-19 21:00 | 2498 | 770.925 | 307 | 1240 | 1430.7692 | 0
2016-04-19 22:00 | 3006 | 714.818 | 297 | 1240 | 1521.4286 | 0
2016-04-19 23:00 | 3006 | 687.86 | 297 | 1240 | 1521.4286 | 0
2016-04-20 | 3006 | 562.05 | 497 | 1240 | 1673.3333 | 0
2016-04-20 01:00 | 3006 | 541.764 | 297 | 1240 | 1673.3333 | 0
2016-04-20 02:00 | 2430 | 531.342 | 320 | 1240 | 1673.3333 | 0
2016-04-20 03:00 | 2430 | 528.606 | 348 | 1240 | 1673.3333 | 0
2016-04-20 04:00 | 2430 | 537.732 | 366 | 1240 | 1673.3333 | 0
2016-04-20 05:00 | 2430 | 574.992 | 569 | 1240 | 1673.3333 | 0
2016-04-20 06:00 | 3265 | 720.42 | 809 | 1240 | 1521.4286 | 0
2016-04-20 07:00 | 3265 | 707.75 | 532 | 1240 | 1521.4286 | 0
2016-04-20 08:00 | 3265 | 706.192 | 432 | 1240 | 1430.7692 | 0
2016-04-20 09:00 | 3265 | 715.027 | 470 | 1240 | 1430.7692 | 0
2016-04-20 10:00 | 2890 | 727.263 | 432 | 1240 | 1430.7692 | 0
2016-04-20 11:00 | 2890 | 736.383 | 472 | 1240 | 1430.7692 | 0
2016-04-20 12:00 | 2890 | 744.971 | 456 | 1240 | 1430.7692 | 0
2016-04-20 13:00 | 2890 | 756.998 | 439 | 1240 | 1430.7692 | 0
2016-04-20 14:00 | 2303 | 767.258 | 450 | 1240 | 1430.7692 | 0
2016-04-20 15:00 | 2303 | 777.214 | 435 | 1240 | 1430.7692 | 0
2016-04-20 16:00 | 2303 | 827.12 | 386 | 1240 | 1430.7692 | 0
2016-04-20 17:00 | 2303 | 784.567 | 329 | 1240 | 1430.7692 | 0
2016-04-20 18:00 | 2498 | 775.143 | 426 | 1240 | 1430.7692 | 0
2016-04-20 19:00 | 2498 | 765.7 | 539 | 1240 | 1430.7692 | 0
2016-04-20 20:00 | 2498 | 793.516 | 549 | 1240 | 1521.4286 | 0
2016-04-20 21:00 | 2498 | 817.82 | 307 | 1240 | 1521.4286 | 0
2016-04-20 22:00 | 3006 | 682.38 | 297 | 1240 | 1673.3333 | 0
2016-04-20 23:00 | 3006 | 618.966 | 297 | 1240 | 1800 | 0
2016-04-21 | 3006 | 551.862 | 497 | 1240 | 1800 | 0
2016-04-21 01:00 | 3006 | 528.966 | 297 | 1240 | 1800 | 0
2016-04-21 02:00 | 2430 | 515.502 | 320 | 1240 | 1800 | 0
2016-04-21 03:00 | 2430 | 509.706 | 348 | 1240 | 1800 | 0
2016-04-21 04:00 | 2430 | 516.222 | 366 | 1240 | 1800 | 0
2016-04-21 05:00 | 2430 | 550.08 | 569 | 1240 | 1800 | 0
2016-04-21 06:00 | 3265 | 617.994 | 809 | 1240 | 1730 | 0
2016-04-21 07:00 | 3265 | 710.06 | 532 | 1240 | 1673.3333 | 0
2016-04-21 08:00 | 3265 | 716.68 | 432 | 1240 | 1673.3333 | 0
2016-04-21 09:00 | 3265 | 738.16 | 470 | 1240 | 1521.4286 | 0
2016-04-21 10:00 | 2890 | 758.78 | 432 | 1240 | 1521.4286 | 0
2016-04-21 11:00 | 2890 | 773.96 | 472 | 1240 | 1521.4286 | 0
2016-04-21 12:00 | 2890 | 790.3 | 456 | 1240 | 1521.4286 | 0
2016-04-21 13:00 | 2890 | 809.04 | 439 | 1240 | 1521.4286 | 0
2016-04-21 14:00 | 2303 | 822.58 | 450 | 1240 | 1521.4286 | 0
2016-04-21 15:00 | 2303 | 839.26 | 435 | 1240 | 1521.4286 | 0
2016-04-21 16:00 | 2303 | 809.077 | 386 | 1240 | 1521.4286 | 0
2016-04-21 17:00 | 2303 | 807.405 | 329 | 1240 | 1521.4286 | 0
2016-04-21 18:00 | 2498 | 833.86 | 426 | 1240 | 1521.4286 | 0
2016-04-21 19:00 | 2498 | 817.84 | 539 | 1240 | 1521.4286 | 0
2016-04-21 20:00 | 2498 | 840.62 | 549 | 1240 | 1521.4286 | 0
2016-04-21 21:00 | 2498 | 819.56 | 307 | 1240 | 1673.3333 | 0
2016-04-21 22:00 | 3006 | 685.17 | 297 | 1240 | 1730 | 0
2016-04-21 23:00 | 3006 | 621.108 | 297 | 1240 | 1800 | 0
2016-04-22 | 3006 | 573.174 | 497 | 1240 | 1800 | 0
2016-04-22 01:00 | 3006 | 546.03 | 297 | 1240 | 1800 | 0
2016-04-22 02:00 | 2430 | 532.422 | 320 | 1240 | 1800 | 0
2016-04-22 03:00 | 2430 | 525.924 | 348 | 1240 | 1800 | 0
2016-04-22 04:00 | 2430 | 531.81 | 366 | 1240 | 1800 | 0
2016-04-22 05:00 | 2430 | 562.446 | 569 | 1240 | 1800 | 0
2016-04-22 06:00 | 3265 | 627.948 | 809 | 1240 | 1730 | 0
2016-04-22 07:00 | 3265 | 651.942 | 532 | 1240 | 1730 | 0
2016-04-22 08:00 | 3265 | 658.368 | 432 | 1240 | 1730 | 0
2016-04-22 09:00 | 3265 | 674.028 | 470 | 1240 | 1730 | 0
2016-04-22 10:00 | 2890 | 766.52 | 432 | 1240 | 1673.3333 | 0
2016-04-22 11:00 | 2890 | 778.74 | 472 | 1240 | 1673.3333 | 0
2016-04-22 12:00 | 2890 | 786.9 | 456 | 1240 | 1673.3333 | 0
2016-04-22 13:00 | 2890 | 795.82 | 439 | 1240 | 1521.4286 | 0
2016-04-22 14:00 | 2303 | 800.46 | 450 | 1240 | 1521.4286 | 0
2016-04-22 15:00 | 2303 | 798.76 | 435 | 1240 | 1521.4286 | 0
2016-04-22 16:00 | 2303 | 799.32 | 386 | 1240 | 1521.4286 | 0
2016-04-22 17:00 | 2303 | 792.58 | 329 | 1240 | 1521.4286 | 0
2016-04-22 18:00 | 2498 | 790.42 | 426 | 1240 | 1521.4286 | 0
2016-04-22 19:00 | 2498 | 788.26 | 539 | 1240 | 1521.4286 | 0
2016-04-22 20:00 | 2498 | 813.64 | 549 | 1240 | 1521.4286 | 0
2016-04-22 21:00 | 2498 | 800.08 | 307 | 1240 | 1521.4286 | 0
2016-04-22 22:00 | 3006 | 676.098 | 297 | 1240 | 1673.3333 | 0
2016-04-22 23:00 | 3006 | 621.162 | 297 | 1240 | 1730 | 0
2016-04-23 | 3006 | 609.984 | 497 | 1240 | 1730 | 0
2016-04-23 01:00 | 3006 | 584.766 | 297 | 1240 | 1730 | 0
2016-04-23 02:00 | 2430 | 572.922 | 320 | 1240 | 1730 | 0
2016-04-23 03:00 | 2430 | 565.254 | 348 | 1240 | 1730 | 0
2016-04-23 04:00 | 2430 | 573.48 | 366 | 1240 | 1730 | 0
2016-04-23 05:00 | 2430 | 606.618 | 569 | 1240 | 1730 | 0
2016-04-23 06:00 | 3265 | 677.16 | 809 | 1240 | 1730 | 0
2016-04-23 07:00 | 3265 | 788.36 | 532 | 1240 | 1673.3333 | 0
2016-04-23 08:00 | 3265 | 795.98 | 432 | 1240 | 1521.4286 | 0
2016-04-23 09:00 | 3265 | 777.157 | 470 | 1240 | 1521.4286 | 0
2016-04-23 10:00 | 2890 | 841.62 | 432 | 1240 | 1521.4286 | 0
2016-04-23 11:00 | 2890 | 866.46 | 472 | 1240 | 1521.4286 | 0
2016-04-23 12:00 | 2890 | 888.66 | 456 | 1240 | 1521.4286 | 0
2016-04-23 13:00 | 2890 | 869.725 | 439 | 1240 | 1521.4286 | 0
2016-04-23 14:00 | 2303 | 895.185 | 450 | 1240 | 1521.4286 | 0
2016-04-23 15:00 | 2303 | 918.878 | 435 | 1240 | 1521.4286 | 0
2016-04-23 16:00 | 2303 | 935.389 | 386 | 1240 | 1430.7692 | 0
2016-04-23 17:00 | 2303 | 932.368 | 329 | 1240 | 1430.7692 | 0
2016-04-23 18:00 | 2498 | 902.766 | 426 | 1240 | 1521.4286 | 0
2016-04-23 19:00 | 2498 | 919.14 | 539 | 1240 | 1521.4286 | 0
2016-04-23 20:00 | 2498 | 915.6 | 549 | 1240 | 1521.4286 | 0
2016-04-23 21:00 | 2498 | 889.26 | 307 | 1240 | 1521.4286 | 0
2016-04-23 22:00 | 3006 | 838.88 | 297 | 1240 | 1730 | 0
2016-04-23 23:00 | 3006 | 702.144 | 297 | 1240 | 1730 | 0
2016-04-24 | 3006 | 691.362 | 497 | 1240 | 1800 | 0
2016-04-24 01:00 | 3006 | 646.812 | 297 | 1240 | 1800 | 0
2016-04-24 02:00 | 2430 | 616.806 | 320 | 1240 | 1800 | 0
2016-04-24 03:00 | 2430 | 600.588 | 348 | 1240 | 1800 | 0
2016-04-24 04:00 | 2430 | 593.046 | 366 | 1240 | 1800 | 0
2016-04-24 05:00 | 2430 | 597.33 | 569 | 1240 | 1800 | 0
2016-04-24 06:00 | 3265 | 613.962 | 809 | 1240 | 1800 | 0
2016-04-24 07:00 | 3265 | 622.314 | 532 | 1240 | 1800 | 0
2016-04-24 08:00 | 3265 | 660.402 | 432 | 1240 | 1800 | 0
2016-04-24 09:00 | 3265 | 697.644 | 470 | 1240 | 1800 | 0
2016-04-24 10:00 | 2890 | 730.494 | 432 | 1240 | 1730 | 0
2016-04-24 11:00 | 2890 | 744.876 | 472 | 1240 | 1730 | 0
2016-04-24 12:00 | 2890 | 753.606 | 456 | 1240 | 1730 | 0
2016-04-24 13:00 | 2890 | 760.122 | 439 | 1240 | 1673.3333 | 0
2016-04-24 14:00 | 2303 | 857 | 450 | 1240 | 1673.3333 | 0
2016-04-24 15:00 | 2303 | 873.34 | 435 | 1240 | 1673.3333 | 0
2016-04-24 16:00 | 2303 | 888.38 | 386 | 1240 | 1521.4286 | 0
2016-04-24 17:00 | 2303 | 895.7 | 329 | 1240 | 1521.4286 | 0
2016-04-24 18:00 | 2498 | 878.18 | 426 | 1240 | 1430.7692 | 0
2016-04-24 19:00 | 2498 | 817.646 | 539 | 1240 | 1430.7692 | 0
2016-04-24 20:00 | 2498 | 867.84 | 549 | 1240 | 1430.7692 | 0
2016-04-24 21:00 | 2498 | 847.84 | 307 | 1240 | 1430.7692 | 0
2016-04-24 22:00 | 3006 | 759.582 | 297 | 1240 | 1430.7692 | 0
2016-04-24 23:00 | 3006 | 708.149 | 297 | 1240 | 1430.7692 | 0
2016-04-25 | 3006 | 710.52 | 497 | 1240 | 1521.4286 | 0
2016-04-25 01:00 | 3006 | 605.97 | 297 | 1240 | 1521.4286 | 0
2016-04-25 02:00 | 2430 | 584.19 | 320 | 1240 | 1673.3333 | 0
2016-04-25 03:00 | 2430 | 570.744 | 348 | 1240 | 1673.3333 | 0
2016-04-25 04:00 | 2430 | 564.516 | 366 | 1240 | 1673.3333 | 0
2016-04-25 05:00 | 2430 | 567.522 | 569 | 1240 | 1673.3333 | 0
2016-04-25 06:00 | 3265 | 578.106 | 809 | 1240 | 1673.3333 | 0
2016-04-25 07:00 | 3265 | 587.88 | 532 | 1240 | 1673.3333 | 0
2016-04-25 08:00 | 3265 | 695.56 | 432 | 1240 | 1673.3333 | 0
2016-04-25 09:00 | 3265 | 700.416 | 470 | 1240 | 1521.4286 | 0
2016-04-25 10:00 | 2890 | 730.93 | 432 | 1240 | 1521.4286 | 0
2016-04-25 11:00 | 2890 | 753.464 | 472 | 1240 | 1521.4286 | 0
2016-04-25 12:00 | 2890 | 777.67 | 456 | 1240 | 1430.7692 | 0
2016-04-25 13:00 | 2890 | 796.67 | 439 | 1240 | 1430.7692 | 0
2016-04-25 14:00 | 2303 | 815.005 | 450 | 1240 | 1430.7692 | 0
2016-04-25 15:00 | 2303 | 878.98 | 435 | 1240 | 1440 | 0
2016-04-25 16:00 | 2303 | 899.92 | 386 | 1240 | 1440 | 0
2016-04-25 17:00 | 2303 | 916.4 | 329 | 1240 | 1440 | 0
2016-04-25 18:00 | 2498 | 908.96 | 426 | 1240 | 1440 | 0
2016-04-25 19:00 | 2498 | 901.52 | 539 | 1240 | 1440 | 0
2016-04-25 20:00 | 2498 | 872.214 | 549 | 1240 | 1440 | 0
2016-04-25 21:00 | 2498 | 900 | 307 | 1240 | 1440 | 0
2016-04-25 22:00 | 3006 | 791.559 | 297 | 1240 | 1430.7692 | 0
2016-04-25 23:00 | 3006 | 749.66 | 297 | 1240 | 1673.3333 | 0
2016-04-26 | 3006 | 592.434 | 497 | 1240 | 1730 | 0
2016-04-26 01:00 | 3006 | 565.83 | 297 | 1240 | 1730 | 0
2016-04-26 02:00 | 2430 | 550.188 | 320 | 1240 | 1730 | 0
2016-04-26 03:00 | 2430 | 545.346 | 348 | 1240 | 1730 | 0
2016-04-26 04:00 | 2430 | 552.672 | 366 | 1240 | 1730 | 0
2016-04-26 05:00 | 2430 | 589.77 | 569 | 1240 | 1730 | 0
2016-04-26 06:00 | 3265 | 659.916 | 809 | 1240 | 1673.3333 | 0
2016-04-26 07:00 | 3265 | 760.38 | 532 | 1240 | 1673.3333 | 0
2016-04-26 08:00 | 3265 | 773.62 | 432 | 1240 | 1521.4286 | 0
2016-04-26 09:00 | 3265 | 762.394 | 470 | 1240 | 1521.4286 | 0
2016-04-26 10:00 | 2890 | 795.644 | 432 | 1240 | 1521.4286 | 0
2016-04-26 11:00 | 2890 | 824.049 | 472 | 1240 | 1430.7692 | 0
2016-04-26 12:00 | 2890 | 890.5 | 456 | 1240 | 1440 | 0
2016-04-26 13:00 | 2890 | 920.14 | 439 | 1240 | 1440 | 0
2016-04-26 14:00 | 2303 | 945.8 | 450 | 1240 | 1440 | 0
2016-04-26 15:00 | 2303 | 961.32 | 435 | 1240 | 1440 | 0
2016-04-26 16:00 | 2303 | 977.92 | 386 | 1240 | 1440 | 0
2016-04-26 17:00 | 2303 | 970.46 | 329 | 1240 | 1440 | 0
2016-04-26 18:00 | 2498 | 898.833 | 426 | 1240 | 1430.7692 | 0
2016-04-26 19:00 | 2498 | 875.729 | 539 | 1240 | 1430.7692 | 0
2016-04-26 20:00 | 2498 | 886.445 | 549 | 1240 | 1430.7692 | 0
2016-04-26 21:00 | 2498 | 857.166 | 307 | 1240 | 1430.7692 | 0
2016-04-26 22:00 | 3006 | 783.142 | 297 | 1240 | 1521.4286 | 0
2016-04-26 23:00 | 3006 | 742.94 | 297 | 1240 | 1521.4286 | 0
2016-04-27 | 3006 | 690.38 | 497 | 1240 | 1521.4286 | 0
2016-04-27 01:00 | 3006 | 657.9 | 297 | 1240 | 1521.4286 | 0
2016-04-27 02:00 | 2430 | 639.3 | 320 | 1240 | 1521.4286 | 0
2016-04-27 03:00 | 2430 | 630.4 | 348 | 1240 | 1521.4286 | 0
2016-04-27 04:00 | 2430 | 636.7 | 366 | 1240 | 1521.4286 | 0
2016-04-27 05:00 | 2430 | 674.74 | 569 | 1240 | 1521.4286 | 0
2016-04-27 06:00 | 3265 | 717.801 | 809 | 1240 | 1430.7692 | 0
2016-04-27 07:00 | 3265 | 739.423 | 532 | 1240 | 1430.7692 | 0
2016-04-27 08:00 | 3265 | 741.969 | 432 | 1240 | 1430.7692 | 0
2016-04-27 09:00 | 3265 | 798.84 | 470 | 1240 | 1430.7692 | 0
2016-04-27 10:00 | 2890 | 816.66 | 432 | 1240 | 1440 | 0
2016-04-27 11:00 | 2890 | 827.76 | 472 | 1240 | 1440 | 0
2016-04-27 12:00 | 2890 | 835.86 | 456 | 1240 | 1440 | 0
2016-04-27 13:00 | 2890 | 851.18 | 439 | 1240 | 1440 | 0
2016-04-27 14:00 | 2303 | 859.68 | 450 | 1240 | 1440 | 0
2016-04-27 15:00 | 2303 | 867.62 | 435 | 1240 | 1440 | 0
2016-04-27 16:00 | 2303 | 876.54 | 386 | 1240 | 1440 | 0
2016-04-27 17:00 | 2303 | 872.46 | 329 | 1240 | 1440 | 0
2016-04-27 18:00 | 2498 | 859.98 | 426 | 1240 | 1440 | 0
2016-04-27 19:00 | 2498 | 847.48 | 539 | 1240 | 1440 | 0
2016-04-27 20:00 | 2498 | 871.26 | 549 | 1240 | 1440 | 0
2016-04-27 21:00 | 2498 | 807.595 | 307 | 1240 | 1430.7692 | 0
2016-04-27 22:00 | 3006 | 784.74 | 297 | 1240 | 1521.4286 | 0
2016-04-27 23:00 | 3006 | 712.64 | 297 | 1240 | 1673.3333 | 0
2016-04-28 | 3006 | 572.202 | 497 | 1240 | 1730 | 0
2016-04-28 01:00 | 3006 | 549.864 | 297 | 1240 | 1730 | 0
2016-04-28 02:00 | 2430 | 539.478 | 320 | 1240 | 1730 | 0
2016-04-28 03:00 | 2430 | 534.672 | 348 | 1240 | 1730 | 0
2016-04-28 04:00 | 2430 | 542.394 | 366 | 1240 | 1730 | 0
2016-04-28 05:00 | 2430 | 577.224 | 569 | 1240 | 1730 | 0
2016-04-28 06:00 | 3265 | 645.93 | 809 | 1240 | 1730 | 0
2016-04-28 07:00 | 3265 | 665.568 | 532 | 1240 | 1730 | 0
2016-04-28 08:00 | 3265 | 669.978 | 432 | 1240 | 1730 | 0
2016-04-28 09:00 | 3265 | 684.162 | 470 | 1240 | 1673.3333 | 0
2016-04-28 10:00 | 2890 | 704.196 | 432 | 1240 | 1673.3333 | 0
2016-04-28 11:00 | 2890 | 799.48 | 472 | 1240 | 1673.3333 | 0
2016-04-28 12:00 | 2890 | 813.68 | 456 | 1240 | 1673.3333 | 0
2016-04-28 13:00 | 2890 | 834.32 | 439 | 1240 | 1673.3333 | 0
2016-04-28 14:00 | 2303 | 854.06 | 450 | 1240 | 1521.4286 | 0
2016-04-28 15:00 | 2303 | 875.16 | 435 | 1240 | 1521.4286 | 0
2016-04-28 16:00 | 2303 | 893.24 | 386 | 1240 | 1521.4286 | 0
2016-04-28 17:00 | 2303 | 895.6 | 329 | 1240 | 1521.4286 | 0
2016-04-28 18:00 | 2498 | 876.22 | 426 | 1240 | 1673.3333 | 0
2016-04-28 19:00 | 2498 | 856.82 | 539 | 1240 | 1673.3333 | 0
2016-04-28 20:00 | 2498 | 869.66 | 549 | 1240 | 1673.3333 | 0
2016-04-28 21:00 | 2498 | 852.3 | 307 | 1240 | 1673.3333 | 0
2016-04-28 22:00 | 3006 | 709.776 | 297 | 1240 | 1800 | 0
2016-04-28 23:00 | 3006 | 643.896 | 297 | 1240 | 1800 | 0
2016-04-29 | 3006 | 581.472 | 497 | 1240 | 1800 | 0
2016-04-29 01:00 | 3006 | 555.966 | 297 | 1240 | 1800 | 0
2016-04-29 02:00 | 2430 | 541.314 | 320 | 1240 | 1800 | 0
2016-04-29 03:00 | 2430 | 535.464 | 348 | 1240 | 1800 | 0
2016-04-29 04:00 | 2430 | 540.09 | 366 | 1240 | 1800 | 0
2016-04-29 05:00 | 2430 | 572.184 | 569 | 1240 | 1800 | 0
2016-04-29 06:00 | 3265 | 636.948 | 809 | 1240 | 1800 | 0
2016-04-29 07:00 | 3265 | 659.196 | 532 | 1240 | 1800 | 0
2016-04-29 08:00 | 3265 | 670.194 | 432 | 1240 | 1800 | 0
2016-04-29 09:00 | 3265 | 690.588 | 470 | 1240 | 1800 | 0
2016-04-29 10:00 | 2890 | 715.554 | 432 | 1240 | 1800 | 0
2016-04-29 11:00 | 2890 | 739.404 | 472 | 1240 | 1800 | 0
2016-04-29 12:00 | 2890 | 761.346 | 456 | 1240 | 1730 | 0
2016-04-29 13:00 | 2890 | 873.6 | 439 | 1240 | 1730 | 0
2016-04-29 14:00 | 2303 | 898.26 | 450 | 1240 | 1673.3333 | 0
2016-04-29 15:00 | 2303 | 923.02 | 435 | 1240 | 1673.3333 | 0
2016-04-29 16:00 | 2303 | 939.98 | 386 | 1240 | 1673.3333 | 0
2016-04-29 17:00 | 2303 | 936.56 | 329 | 1240 | 1673.3333 | 0
2016-04-29 18:00 | 2498 | 915.66 | 426 | 1240 | 1673.3333 | 0
2016-04-29 19:00 | 2498 | 894.78 | 539 | 1240 | 1673.3333 | 0
2016-04-29 20:00 | 2498 | 910.64 | 549 | 1240 | 1673.3333 | 0
2016-04-29 21:00 | 2498 | 896.06 | 307 | 1240 | 1673.3333 | 0
2016-04-29 22:00 | 3006 | 755.532 | 297 | 1240 | 1730 | 0
2016-04-29 23:00 | 3006 | 689.346 | 297 | 1240 | 1730 | 0
2016-04-30 | 3006 | 680.13 | 497 | 1240 | 1730 | 0
2016-04-30 01:00 | 3006 | 649.98 | 297 | 1240 | 1730 | 0
2016-04-30 02:00 | 2430 | 631.962 | 320 | 1240 | 1730 | 0
2016-04-30 03:00 | 2430 | 624.618 | 348 | 1240 | 1730 | 0
2016-04-30 04:00 | 2430 | 630.036 | 366 | 1240 | 1730 | 0
2016-04-30 05:00 | 2430 | 665.712 | 569 | 1240 | 1730 | 0
2016-04-30 06:00 | 3265 | 821.66 | 809 | 1240 | 1673.3333 | 0
2016-04-30 07:00 | 3265 | 857.58 | 532 | 1240 | 1521.4286 | 0
2016-04-30 08:00 | 3265 | 820.496 | 432 | 1240 | 1521.4286 | 0
2016-04-30 09:00 | 3265 | 842.156 | 470 | 1240 | 1521.4286 | 0
2016-04-30 10:00 | 2890 | 910.96 | 432 | 1240 | 1521.4286 | 0
2016-04-30 11:00 | 2890 | 928.96 | 472 | 1240 | 1521.4286 | 0
2016-04-30 12:00 | 2890 | 893.342 | 456 | 1240 | 1521.4286 | 0
2016-04-30 13:00 | 2890 | 907.744 | 439 | 1240 | 1521.4286 | 0
2016-04-30 14:00 | 2303 | 920.911 | 450 | 1240 | 1430.7692 | 0
2016-04-30 15:00 | 2303 | 931.228 | 435 | 1240 | 1430.7692 | 0
2016-04-30 16:00 | 2303 | 936.244 | 386 | 1240 | 1430.7692 | 0
2016-04-30 17:00 | 2303 | 929.613 | 329 | 1240 | 1430.7692 | 0
2016-04-30 18:00 | 2498 | 907.744 | 426 | 1240 | 1430.7692 | 0
2016-04-30 19:00 | 2498 | 885.875 | 539 | 1240 | 1430.7692 | 0
2016-04-30 20:00 | 2498 | 939.26 | 549 | 1240 | 1440 | 0
2016-04-30 21:00 | 2498 | 920.2 | 307 | 1240 | 1440 | 0
2016-04-30 22:00 | 3006 | 830.357 | 297 | 1240 | 1430.7692 | 0
2016-04-30 23:00 | 3006 | 774.383 | 297 | 1240 | 1430.7692 | 0
2016-05-01 | 2744 | 757.34 | 442 | 1240 | 1430.7692 | 0
2016-05-01 01:00 | 2744 | 756.96 | 534 | 1240 | 1430.7692 | 0
2016-05-01 02:00 | 3084 | 730.38 | 321 | 1240 | 1430.7692 | 0
2016-05-01 03:00 | 3084 | 714.12 | 339 | 1240 | 1430.7692 | 0
2016-05-01 04:00 | 3084 | 706.78 | 366 | 1240 | 1430.7692 | 0
2016-05-01 05:00 | 3084 | 710.5 | 493 | 1240 | 1430.7692 | 0
2016-05-01 06:00 | 2925 | 723.5 | 642 | 1240 | 1430.7692 | 0
2016-05-01 07:00 | 2925 | 698.763 | 490 | 1240 | 1430.7692 | 0
2016-05-01 08:00 | 2925 | 740.506 | 568 | 1240 | 1430.7692 | 0
2016-05-01 09:00 | 2925 | 824.7 | 530 | 1240 | 1440 | 0
2016-05-01 10:00 | 2519 | 864.7 | 592 | 1240 | 1440 | 0
2016-05-01 11:00 | 2519 | 893.96 | 519 | 1240 | 1440 | 0
2016-05-01 12:00 | 2519 | 916.78 | 601 | 1240 | 1440 | 0
2016-05-01 13:00 | 2519 | 935.36 | 617 | 1240 | 1440 | 0
2016-05-01 14:00 | 2685 | 952.68 | 614 | 1240 | 1440 | 0
2016-05-01 15:00 | 2685 | 920.265 | 511 | 1240 | 1440 | 0
2016-05-01 16:00 | 2685 | 979.78 | 500 | 1240 | 1440 | 0
2016-05-01 17:00 | 2685 | 978.66 | 384 | 1240 | 1440 | 0
2016-05-01 18:00 | 2409 | 957.58 | 321 | 1240 | 1440 | 0
2016-05-01 19:00 | 2409 | 936.52 | 570 | 1240 | 1440 | 0
2016-05-01 20:00 | 2409 | 938.34 | 589 | 1240 | 1440 | 0
2016-05-01 21:00 | 2409 | 913.82 | 423 | 1240 | 1440 | 0
2016-05-01 22:00 | 2744 | 862.94 | 321 | 1240 | 1430.7692 | 0
2016-05-01 23:00 | 2744 | 765.32 | 321 | 1240 | 1521.4286 | 0
2016-05-02 | 2744 | 757.02 | 442 | 1240 | 1673.3333 | 0
2016-05-02 01:00 | 2744 | 646.596 | 534 | 1240 | 1673.3333 | 0
2016-05-02 02:00 | 3084 | 622.656 | 321 | 1240 | 1673.3333 | 0
2016-05-02 03:00 | 3084 | 606.582 | 339 | 1240 | 1673.3333 | 0
2016-05-02 04:00 | 3084 | 597.258 | 366 | 1240 | 1673.3333 | 0
2016-05-02 05:00 | 3084 | 594.99 | 493 | 1240 | 1673.3333 | 0
2016-05-02 06:00 | 2925 | 603.396 | 642 | 1240 | 1673.3333 | 0
2016-05-02 07:00 | 2925 | 608.292 | 490 | 1240 | 1673.3333 | 0
2016-05-02 08:00 | 2925 | 720.34 | 568 | 1240 | 1673.3333 | 0
2016-05-02 09:00 | 2925 | 721.544 | 530 | 1240 | 1521.4286 | 0
2016-05-02 10:00 | 2519 | 764.199 | 592 | 1240 | 1521.4286 | 0
2016-05-02 11:00 | 2519 | 830.52 | 519 | 1240 | 1521.4286 | 0
2016-05-02 12:00 | 2519 | 862.18 | 601 | 1240 | 1521.4286 | 0
2016-05-02 13:00 | 2519 | 886.7 | 617 | 1240 | 1521.4286 | 0
2016-05-02 14:00 | 2685 | 918.2 | 614 | 1240 | 1521.4286 | 0
2016-05-02 15:00 | 2685 | 900.011 | 511 | 1240 | 1430.7692 | 0
2016-05-02 16:00 | 2685 | 927.371 | 500 | 1240 | 1430.7692 | 0
2016-05-02 17:00 | 2685 | 941.906 | 384 | 1240 | 1430.7692 | 0
2016-05-02 18:00 | 2409 | 926.402 | 321 | 1240 | 1440 | 0
2016-05-02 19:00 | 2409 | 958.84 | 570 | 1240 | 1440 | 0
2016-05-02 20:00 | 2409 | 900.771 | 589 | 1240 | 1440 | 0
2016-05-02 21:00 | 2409 | 880.042 | 423 | 1240 | 1440 | 0
2016-05-02 22:00 | 2744 | 853.9 | 321 | 1240 | 1440 | 0
2016-05-02 23:00 | 2744 | 768.04 | 321 | 1240 | 1430.7692 | 0
2016-05-03 | 2744 | 592.326 | 442 | 1240 | 1521.4286 | 0
2016-05-03 01:00 | 2744 | 561.996 | 534 | 1240 | 1521.4286 | 0
2016-05-03 02:00 | 3084 | 545.544 | 321 | 1240 | 1673.3333 | 0
2016-05-03 03:00 | 3084 | 541.44 | 339 | 1240 | 1673.3333 | 0
2016-05-03 04:00 | 3084 | 548.748 | 366 | 1240 | 1673.3333 | 0
2016-05-03 05:00 | 3084 | 582.768 | 493 | 1240 | 1673.3333 | 0
2016-05-03 06:00 | 2925 | 719.98 | 642 | 1240 | 1673.3333 | 0
2016-05-03 07:00 | 2925 | 711.512 | 490 | 1240 | 1521.4286 | 0
2016-05-03 08:00 | 2925 | 732.944 | 568 | 1240 | 1521.4286 | 0
2016-05-03 09:00 | 2925 | 766.631 | 530 | 1240 | 1430.7692 | 0
2016-05-03 10:00 | 2519 | 803.738 | 592 | 1240 | 1430.7692 | 0
2016-05-03 11:00 | 2519 | 825.797 | 519 | 1240 | 1430.7692 | 0
2016-05-03 12:00 | 2519 | 902.66 | 601 | 1240 | 1430.7692 | 0
2016-05-03 13:00 | 2519 | 941.12 | 617 | 1240 | 1430.7692 | 0
2016-05-03 14:00 | 2685 | 971.3 | 614 | 1240 | 1440 | 0
2016-05-03 15:00 | 2685 | 988.52 | 511 | 1240 | 1440 | 0
2016-05-03 16:00 | 2685 | 989.14 | 500 | 1240 | 1440 | 0
2016-05-03 17:00 | 2685 | 978.16 | 384 | 1240 | 1440 | 0
2016-05-03 18:00 | 2409 | 952.86 | 321 | 1240 | 1440 | 0
2016-05-03 19:00 | 2409 | 927.54 | 570 | 1240 | 1440 | 0
2016-05-03 20:00 | 2409 | 878.332 | 589 | 1240 | 1440 | 0
2016-05-03 21:00 | 2409 | 895.84 | 423 | 1240 | 1440 | 0
2016-05-03 22:00 | 2744 | 818.64 | 321 | 1240 | 1430.7692 | 0
2016-05-03 23:00 | 2744 | 698.782 | 321 | 1240 | 1521.4286 | 0
2016-05-04 | 2744 | 694.5 | 442 | 1240 | 1673.3333 | 0
2016-05-04 01:00 | 2744 | 592.704 | 534 | 1240 | 1673.3333 | 0
2016-05-04 02:00 | 3084 | 572.238 | 321 | 1240 | 1673.3333 | 0
2016-05-04 03:00 | 3084 | 562.5 | 339 | 1240 | 1673.3333 | 0
2016-05-04 04:00 | 3084 | 566.64 | 366 | 1240 | 1673.3333 | 0
2016-05-04 05:00 | 3084 | 599.58 | 493 | 1240 | 1673.3333 | 0
2016-05-04 06:00 | 2925 | 666.054 | 642 | 1240 | 1673.3333 | 0
2016-05-04 07:00 | 2925 | 766.84 | 490 | 1240 | 1673.3333 | 0
2016-05-04 08:00 | 2925 | 781.08 | 568 | 1240 | 1521.4286 | 0
2016-05-04 09:00 | 2925 | 765.168 | 530 | 1240 | 1521.4286 | 0
2016-05-04 10:00 | 2519 | 797.715 | 592 | 1240 | 1430.7692 | 0
2016-05-04 11:00 | 2519 | 829.977 | 519 | 1240 | 1430.7692 | 0
2016-05-04 12:00 | 2519 | 857.375 | 601 | 1240 | 1430.7692 | 0
2016-05-04 13:00 | 2519 | 891.214 | 617 | 1240 | 1430.7692 | 0
2016-05-04 14:00 | 2685 | 970.94 | 614 | 1240 | 1430.7692 | 0
2016-05-04 15:00 | 2685 | 1007.24 | 511 | 1240 | 1430.7692 | 0
2016-05-04 16:00 | 2685 | 1039.94 | 500 | 1240 | 1440 | 0
2016-05-04 17:00 | 2685 | 1052.62 | 384 | 1240 | 1440 | 0
2016-05-04 18:00 | 2409 | 1028.78 | 321 | 1240 | 1440 | 0
2016-05-04 19:00 | 2409 | 1004.94 | 570 | 1240 | 1430.7692 | 0
2016-05-04 20:00 | 2409 | 995.02 | 589 | 1240 | 1430.7692 | 0
2016-05-04 21:00 | 2409 | 916.731 | 423 | 1240 | 1430.7692 | 0
2016-05-04 22:00 | 2744 | 882.04 | 321 | 1240 | 1521.4286 | 0
2016-05-04 23:00 | 2744 | 712.566 | 321 | 1240 | 1730 | 0
2016-05-05 | 2744 | 601.632 | 442 | 1240 | 1730 | 0
2016-05-05 01:00 | 2744 | 570.204 | 534 | 1240 | 1800 | 0
2016-05-05 02:00 | 3084 | 548.748 | 321 | 1240 | 1800 | 0
2016-05-05 03:00 | 3084 | 538.596 | 339 | 1240 | 1800 | 0
2016-05-05 04:00 | 3084 | 543.042 | 366 | 1240 | 1800 | 0
2016-05-05 05:00 | 3084 | 568.26 | 493 | 1240 | 1730 | 0
2016-05-05 06:00 | 2925 | 625.374 | 642 | 1240 | 1730 | 0
2016-05-05 07:00 | 2925 | 718.74 | 490 | 1240 | 1673.3333 | 0
2016-05-05 08:00 | 2925 | 739.5 | 568 | 1240 | 1521.4286 | 0
2016-05-05 09:00 | 2925 | 772.98 | 530 | 1240 | 1521.4286 | 0
2016-05-05 10:00 | 2519 | 769.253 | 592 | 1240 | 1521.4286 | 0
2016-05-05 11:00 | 2519 | 806.284 | 519 | 1240 | 1430.7692 | 0
2016-05-05 12:00 | 2519 | 883.12 | 601 | 1240 | 1440 | 0
2016-05-05 13:00 | 2519 | 884.032 | 617 | 1240 | 1238.9381 | 0
2016-05-05 14:00 | 2685 | 929.86 | 614 | 1240 | 1296.2963 | 0
2016-05-05 15:00 | 2685 | 1072.155 | 511 | 1240 | 1296.2963 | 0
2016-05-05 16:00 | 2685 | 1102.038 | 500 | 1240 | 1296.2963 | 0
2016-05-05 17:00 | 2685 | 1108.569 | 384 | 1240 | 1296.2963 | 0
2016-05-05 18:00 | 2409 | 1079.568 | 321 | 1240 | 1296.2963 | 0
2016-05-05 19:00 | 2409 | 950.513 | 570 | 1240 | 1238.9381 | 0
2016-05-05 20:00 | 2409 | 977.62 | 589 | 1240 | 1440 | 0
2016-05-05 21:00 | 2409 | 940.78 | 423 | 1240 | 1430.7692 | 0
2016-05-05 22:00 | 2744 | 817.874 | 321 | 1240 | 1521.4286 | 0
2016-05-05 23:00 | 2744 | 769.4 | 321 | 1240 | 1673.3333 | 0
2016-05-06 | 2744 | 620.982 | 442 | 1240 | 1730 | 0
2016-05-06 01:00 | 2744 | 586.188 | 534 | 1240 | 1730 | 0
2016-05-06 02:00 | 3084 | 563.094 | 321 | 1240 | 1730 | 0
2016-05-06 03:00 | 3084 | 551.088 | 339 | 1240 | 1730 | 0
2016-05-06 04:00 | 3084 | 553.662 | 366 | 1240 | 1730 | 0
2016-05-06 05:00 | 3084 | 581.148 | 493 | 1240 | 1730 | 0
2016-05-06 06:00 | 2925 | 637.2 | 642 | 1240 | 1730 | 0
2016-05-06 07:00 | 2925 | 659.394 | 490 | 1240 | 1730 | 0
2016-05-06 08:00 | 2925 | 759.98 | 568 | 1240 | 1673.3333 | 0
2016-05-06 09:00 | 2925 | 795.4 | 530 | 1240 | 1673.3333 | 0
2016-05-06 10:00 | 2519 | 835.98 | 592 | 1240 | 1521.4286 | 0
2016-05-06 11:00 | 2519 | 832.352 | 519 | 1240 | 1521.4286 | 0
2016-05-06 12:00 | 2519 | 862.923 | 601 | 1240 | 1430.7692 | 0
2016-05-06 13:00 | 2519 | 903.26 | 617 | 1240 | 1430.7692 | 0
2016-05-06 14:00 | 2685 | 986.66 | 614 | 1240 | 1430.7692 | 0
2016-05-06 15:00 | 2685 | 1014.88 | 511 | 1240 | 1430.7692 | 0
2016-05-06 16:00 | 2685 | 1041.12 | 500 | 1240 | 1430.7692 | 0
2016-05-06 17:00 | 2685 | 1040.22 | 384 | 1240 | 1430.7692 | 0
2016-05-06 18:00 | 2409 | 956.384 | 321 | 1240 | 1430.7692 | 0
2016-05-06 19:00 | 2409 | 924.559 | 570 | 1240 | 1521.4286 | 0
2016-05-06 20:00 | 2409 | 917.871 | 589 | 1240 | 1521.4286 | 0
2016-05-06 21:00 | 2409 | 894.444 | 423 | 1240 | 1521.4286 | 0
2016-05-06 22:00 | 2744 | 870.12 | 321 | 1240 | 1673.3333 | 0
2016-05-06 23:00 | 2744 | 710.118 | 321 | 1240 | 1673.3333 | 0
2016-05-07 | 2744 | 689.76 | 442 | 1240 | 1730 | 0
2016-05-07 01:00 | 2744 | 654.75 | 534 | 1240 | 1730 | 0
2016-05-07 02:00 | 3084 | 632.682 | 321 | 1240 | 1730 | 0
2016-05-07 03:00 | 3084 | 618.3 | 339 | 1240 | 1730 | 0
2016-05-07 04:00 | 3084 | 619.182 | 366 | 1240 | 1730 | 0
2016-05-07 05:00 | 3084 | 647.316 | 493 | 1240 | 1730 | 0
2016-05-07 06:00 | 2925 | 788.02 | 642 | 1240 | 1673.3333 | 0
2016-05-07 07:00 | 2925 | 813.66 | 490 | 1240 | 1521.4286 | 0
2016-05-07 08:00 | 2925 | 795.568 | 568 | 1240 | 1521.4286 | 0
2016-05-07 09:00 | 2925 | 833.701 | 530 | 1240 | 1521.4286 | 0
2016-05-07 10:00 | 2519 | 877.838 | 592 | 1240 | 1430.7692 | 0
2016-05-07 11:00 | 2519 | 916.161 | 519 | 1240 | 1430.7692 | 0
2016-05-07 12:00 | 2519 | 994.88 | 601 | 1240 | 1440 | 0
2016-05-07 13:00 | 2519 | 1038.38 | 617 | 1240 | 1440 | 0
2016-05-07 14:00 | 2685 | 1017.146 | 614 | 1240 | 1238.9381 | 0
2016-05-07 15:00 | 2685 | 1038.407 | 511 | 1240 | 1238.9381 | 0
2016-05-07 16:00 | 2685 | 1048.192 | 500 | 1240 | 1238.9381 | 0
2016-05-07 17:00 | 2685 | 1035.386 | 384 | 1240 | 1238.9381 | 0
2016-05-07 18:00 | 2409 | 1045.86 | 321 | 1240 | 1440 | 0
2016-05-07 19:00 | 2409 | 1001.86 | 570 | 1240 | 1430.7692 | 0
2016-05-07 20:00 | 2409 | 932.805 | 589 | 1240 | 1430.7692 | 0
2016-05-07 21:00 | 2409 | 906.414 | 423 | 1240 | 1430.7692 | 0
2016-05-07 22:00 | 2744 | 849.186 | 321 | 1240 | 1430.7692 | 0
2016-05-07 23:00 | 2744 | 778.81 | 321 | 1240 | 1521.4286 | 0
2016-05-08 | 2744 | 763.971 | 442 | 1240 | 1521.4286 | 0
2016-05-08 01:00 | 2744 | 746.985 | 534 | 1240 | 1521.4286 | 0
2016-05-08 02:00 | 3084 | 753.9 | 321 | 1240 | 1521.4286 | 0
2016-05-08 03:00 | 3084 | 730.12 | 339 | 1240 | 1521.4286 | 0
2016-05-08 04:00 | 3084 | 718.46 | 366 | 1240 | 1521.4286 | 0
2016-05-08 05:00 | 3084 | 722.2 | 493 | 1240 | 1521.4286 | 0
2016-05-08 06:00 | 2925 | 734.8 | 642 | 1240 | 1521.4286 | 0
2016-05-08 07:00 | 2925 | 748.4 | 490 | 1240 | 1521.4286 | 0
2016-05-08 08:00 | 2925 | 786.28 | 568 | 1240 | 1521.4286 | 0
2016-05-08 09:00 | 2925 | 782.648 | 530 | 1240 | 1521.4286 | 0
2016-05-08 10:00 | 2519 | 812.117 | 592 | 1240 | 1521.4286 | 0
2016-05-08 11:00 | 2519 | 828.856 | 519 | 1240 | 1521.4286 | 0
2016-05-08 12:00 | 2519 | 842.156 | 601 | 1240 | 1430.7692 | 0
2016-05-08 13:00 | 2519 | 848.996 | 617 | 1240 | 1430.7692 | 0
2016-05-08 14:00 | 2685 | 858.173 | 614 | 1240 | 1430.7692 | 0
2016-05-08 15:00 | 2685 | 866.343 | 511 | 1240 | 1430.7692 | 0
2016-05-08 16:00 | 2685 | 917.46 | 500 | 1240 | 1430.7692 | 0
2016-05-08 17:00 | 2685 | 913.82 | 384 | 1240 | 1430.7692 | 0
2016-05-08 18:00 | 2409 | 852.15 | 321 | 1240 | 1430.7692 | 0
2016-05-08 19:00 | 2409 | 836.19 | 570 | 1240 | 1430.7692 | 0
2016-05-08 20:00 | 2409 | 851.162 | 589 | 1240 | 1430.7692 | 0
2016-05-08 21:00 | 2409 | 841.054 | 423 | 1240 | 1430.7692 | 0
2016-05-08 22:00 | 2744 | 801.268 | 321 | 1240 | 1521.4286 | 0
2016-05-08 23:00 | 2744 | 787.22 | 321 | 1240 | 1521.4286 | 0
2016-05-09 | 2744 | 767.32 | 442 | 1240 | 1521.4286 | 0
2016-05-09 01:00 | 2744 | 728.3 | 534 | 1240 | 1521.4286 | 0
2016-05-09 02:00 | 3084 | 704.74 | 321 | 1240 | 1521.4286 | 0
2016-05-09 03:00 | 3084 | 690.52 | 339 | 1240 | 1521.4286 | 0
2016-05-09 04:00 | 3084 | 682.88 | 366 | 1240 | 1521.4286 | 0
2016-05-09 05:00 | 3084 | 686.56 | 493 | 1240 | 1521.4286 | 0
2016-05-09 06:00 | 2925 | 697.1 | 642 | 1240 | 1521.4286 | 0
2016-05-09 07:00 | 2925 | 713 | 490 | 1240 | 1521.4286 | 0
2016-05-09 08:00 | 2925 | 753.74 | 568 | 1240 | 1521.4286 | 0
2016-05-09 09:00 | 2925 | 753.692 | 530 | 1240 | 1521.4286 | 0
2016-05-09 10:00 | 2519 | 778.088 | 592 | 1240 | 1521.4286 | 0
2016-05-09 11:00 | 2519 | 794.903 | 519 | 1240 | 1521.4286 | 0
2016-05-09 12:00 | 2519 | 853.34 | 601 | 1240 | 1521.4286 | 0
2016-05-09 13:00 | 2519 | 822.852 | 617 | 1240 | 1521.4286 | 0
2016-05-09 14:00 | 2685 | 832.808 | 614 | 1240 | 1521.4286 | 0
2016-05-09 15:00 | 2685 | 840.769 | 511 | 1240 | 1521.4286 | 0
2016-05-09 16:00 | 2685 | 847.78 | 500 | 1240 | 1521.4286 | 0
2016-05-09 17:00 | 2685 | 854.354 | 384 | 1240 | 1521.4286 | 0
2016-05-09 18:00 | 2409 | 860.035 | 321 | 1240 | 1521.4286 | 0
2016-05-09 19:00 | 2409 | 911.3 | 570 | 1240 | 1673.3333 | 0
2016-05-09 20:00 | 2409 | 944.72 | 589 | 1240 | 1673.3333 | 0
2016-05-09 21:00 | 2409 | 943.4 | 423 | 1240 | 1673.3333 | 0
2016-05-09 22:00 | 2744 | 898.2 | 321 | 1240 | 1673.3333 | 0
2016-05-09 23:00 | 2744 | 833.74 | 321 | 1240 | 1730 | 0
2016-05-10 | 2744 | 629.91 | 442 | 1240 | 1730 | 0
2016-05-10 01:00 | 2744 | 606.654 | 534 | 1240 | 1730 | 0
2016-05-10 02:00 | 3084 | 594.648 | 321 | 1240 | 1730 | 0
2016-05-10 03:00 | 3084 | 591.444 | 339 | 1240 | 1730 | 0
2016-05-10 04:00 | 3084 | 603.414 | 366 | 1240 | 1730 | 0
2016-05-10 05:00 | 3084 | 636.84 | 493 | 1240 | 1730 | 0
2016-05-10 06:00 | 2925 | 701.316 | 642 | 1240 | 1730 | 0
2016-05-10 07:00 | 2925 | 730.188 | 490 | 1240 | 1730 | 0
2016-05-10 08:00 | 2925 | 833.02 | 568 | 1240 | 1730 | 0
2016-05-10 09:00 | 2925 | 869.74 | 530 | 1240 | 1730 | 0
2016-05-10 10:00 | 2519 | 909.36 | 592 | 1240 | 1730 | 0
2016-05-10 11:00 | 2519 | 944.76 | 519 | 1240 | 1673.3333 | 0
2016-05-10 12:00 | 2519 | 926.345 | 601 | 1240 | 1521.4286 | 0
2016-05-10 13:00 | 2519 | 955.624 | 617 | 1240 | 1521.4286 | 0
2016-05-10 14:00 | 2685 | 980.096 | 614 | 1240 | 1521.4286 | 0
2016-05-10 15:00 | 2685 | 1002.25 | 511 | 1240 | 1430.7692 | 0
2016-05-10 16:00 | 2685 | 1071.94 | 500 | 1240 | 1430.7692 | 0
2016-05-10 17:00 | 2685 | 1070.58 | 384 | 1240 | 1430.7692 | 0
2016-05-10 18:00 | 2409 | 1047.42 | 321 | 1240 | 1430.7692 | 0
2016-05-10 19:00 | 2409 | 973.047 | 570 | 1240 | 1430.7692 | 0
2016-05-10 20:00 | 2409 | 1029.66 | 589 | 1240 | 1430.7692 | 0
2016-05-10 21:00 | 2409 | 1012.2 | 423 | 1240 | 1440 | 0
2016-05-10 22:00 | 2744 | 938.2 | 321 | 1240 | 1430.7692 | 0
2016-05-10 23:00 | 2744 | 807.766 | 321 | 1240 | 1430.7692 | 0
2016-05-11 | 2744 | 772.22 | 442 | 1240 | 1673.3333 | 0
2016-05-11 01:00 | 2744 | 732.38 | 534 | 1240 | 1673.3333 | 0
2016-05-11 02:00 | 3084 | 638.82 | 321 | 1240 | 1673.3333 | 0
2016-05-11 03:00 | 3084 | 628.65 | 339 | 1240 | 1673.3333 | 0
2016-05-11 04:00 | 3084 | 632.484 | 366 | 1240 | 1673.3333 | 0
2016-05-11 05:00 | 3084 | 664.056 | 493 | 1240 | 1673.3333 | 0
2016-05-11 06:00 | 2925 | 807.6 | 642 | 1240 | 1673.3333 | 0
2016-05-11 07:00 | 2925 | 837.72 | 490 | 1240 | 1673.3333 | 0
2016-05-11 08:00 | 2925 | 816.354 | 568 | 1240 | 1521.4286 | 0
2016-05-11 09:00 | 2925 | 852.777 | 530 | 1240 | 1521.4286 | 0
2016-05-11 10:00 | 2519 | 942 | 592 | 1240 | 1430.7692 | 0
2016-05-11 11:00 | 2519 | 980.28 | 519 | 1240 | 1440 | 0
2016-05-11 12:00 | 2519 | 965.808 | 601 | 1240 | 1440 | 0
2016-05-11 13:00 | 2519 | 1008.729 | 617 | 1240 | 1440 | 0
2016-05-11 14:00 | 2685 | 1101.26 | 614 | 1240 | 1440 | 0
2016-05-11 15:00 | 2685 | 1071.809 | 511 | 1240 | 1440 | 0
2016-05-11 16:00 | 2685 | 1087.484 | 500 | 1240 | 1440 | 0
2016-05-11 17:00 | 2685 | 1080.967 | 384 | 1240 | 1440 | 0
2016-05-11 18:00 | 2409 | 1105.46 | 321 | 1240 | 1430.7692 | 0
2016-05-11 19:00 | 2409 | 1073.04 | 570 | 1240 | 1430.7692 | 0
2016-05-11 20:00 | 2409 | 1072.3 | 589 | 1240 | 1430.7692 | 0
2016-05-11 21:00 | 2409 | 1048.82 | 423 | 1240 | 1430.7692 | 0
2016-05-11 22:00 | 2744 | 923.989 | 321 | 1240 | 1521.4286 | 0
2016-05-11 23:00 | 2744 | 877.2 | 321 | 1240 | 1673.3333 | 0
2016-05-12 | 2744 | 695.16 | 442 | 1240 | 1730 | 0
2016-05-12 01:00 | 2744 | 661.302 | 534 | 1240 | 1730 | 0
2016-05-12 02:00 | 3084 | 639.27 | 321 | 1240 | 1730 | 0
2016-05-12 03:00 | 3084 | 626.688 | 339 | 1240 | 1730 | 0
2016-05-12 04:00 | 3084 | 628.452 | 366 | 1240 | 1730 | 0
2016-05-12 05:00 | 3084 | 658.566 | 493 | 1240 | 1730 | 0
2016-05-12 06:00 | 2925 | 798.92 | 642 | 1240 | 1673.3333 | 0
2016-05-12 07:00 | 2925 | 820.76 | 490 | 1240 | 1673.3333 | 0
2016-05-12 08:00 | 2925 | 837.48 | 568 | 1240 | 1673.3333 | 0
2016-05-12 09:00 | 2925 | 834.556 | 530 | 1240 | 1521.4286 | 0
2016-05-12 10:00 | 2519 | 874.361 | 592 | 1240 | 1521.4286 | 0
2016-05-12 11:00 | 2519 | 906.547 | 519 | 1240 | 1521.4286 | 0
2016-05-12 12:00 | 2519 | 930.639 | 601 | 1240 | 1430.7692 | 0
2016-05-12 13:00 | 2519 | 959.804 | 617 | 1240 | 1430.7692 | 0
2016-05-12 14:00 | 2685 | 979.754 | 614 | 1240 | 1430.7692 | 0
2016-05-12 15:00 | 2685 | 995.201 | 511 | 1240 | 1430.7692 | 0
2016-05-12 16:00 | 2685 | 1060.5 | 500 | 1240 | 1430.7692 | 0
2016-05-12 17:00 | 2685 | 1049.32 | 384 | 1240 | 1430.7692 | 0
2016-05-12 18:00 | 2409 | 1024.9 | 321 | 1240 | 1430.7692 | 0
2016-05-12 19:00 | 2409 | 1000.48 | 570 | 1240 | 1430.7692 | 0
2016-05-12 20:00 | 2409 | 1004.62 | 589 | 1240 | 1430.7692 | 0
2016-05-12 21:00 | 2409 | 982.42 | 423 | 1240 | 1430.7692 | 0
2016-05-12 22:00 | 2744 | 865.792 | 321 | 1240 | 1521.4286 | 0
2016-05-12 23:00 | 2744 | 834.44 | 321 | 1240 | 1521.4286 | 0
2016-05-13 | 2744 | 683.802 | 442 | 1240 | 1521.4286 | 0
2016-05-13 01:00 | 2744 | 720.58 | 534 | 1240 | 1521.4286 | 0
2016-05-13 02:00 | 3084 | 626.274 | 321 | 1240 | 1521.4286 | 0
2016-05-13 03:00 | 3084 | 614.538 | 339 | 1240 | 1521.4286 | 0
2016-05-13 04:00 | 3084 | 615.24 | 366 | 1240 | 1521.4286 | 0
2016-05-13 05:00 | 3084 | 714.92 | 493 | 1240 | 1521.4286 | 0
2016-05-13 06:00 | 2925 | 742.463 | 642 | 1240 | 1521.4286 | 0
2016-05-13 07:00 | 2925 | 766.479 | 490 | 1240 | 1521.4286 | 0
2016-05-13 08:00 | 2925 | 779.969 | 568 | 1240 | 1521.4286 | 0
2016-05-13 09:00 | 2925 | 849.2 | 530 | 1240 | 1430.7692 | 0
2016-05-13 10:00 | 2519 | 887.04 | 592 | 1240 | 1430.7692 | 0
2016-05-13 11:00 | 2519 | 914.56 | 519 | 1240 | 1440 | 0
2016-05-13 12:00 | 2519 | 936.22 | 601 | 1240 | 1440 | 0
2016-05-13 13:00 | 2519 | 915.914 | 617 | 1240 | 1440 | 0
2016-05-13 14:00 | 2685 | 931.817 | 614 | 1240 | 1440 | 0
2016-05-13 15:00 | 2685 | 940.994 | 511 | 1240 | 1440 | 0
2016-05-13 16:00 | 2685 | 944.87 | 500 | 1240 | 1440 | 0
2016-05-13 17:00 | 2685 | 930.297 | 384 | 1240 | 1440 | 0
2016-05-13 18:00 | 2409 | 955.16 | 321 | 1240 | 1440 | 0
2016-05-13 19:00 | 2409 | 931.04 | 570 | 1240 | 1430.7692 | 0
2016-05-13 20:00 | 2409 | 890.796 | 589 | 1240 | 1430.7692 | 0
2016-05-13 21:00 | 2409 | 918.18 | 423 | 1240 | 1430.7692 | 0
2016-05-13 22:00 | 2744 | 812.687 | 321 | 1240 | 1521.4286 | 0
2016-05-13 23:00 | 2744 | 780.2 | 321 | 1240 | 1521.4286 | 0
2016-05-14 | 2744 | 772.88 | 442 | 1240 | 1521.4286 | 0
2016-05-14 01:00 | 2744 | 736.42 | 534 | 1240 | 1521.4286 | 0
2016-05-14 02:00 | 3084 | 715.1 | 321 | 1240 | 1521.4286 | 0
2016-05-14 03:00 | 3084 | 702.86 | 339 | 1240 | 1521.4286 | 0
2016-05-14 04:00 | 3084 | 707.64 | 366 | 1240 | 1521.4286 | 0
2016-05-14 05:00 | 3084 | 706.287 | 493 | 1240 | 1521.4286 | 0
2016-05-14 06:00 | 2925 | 771.305 | 642 | 1240 | 1430.7692 | 0
2016-05-14 07:00 | 2925 | 844.02 | 490 | 1240 | 1430.7692 | 0
2016-05-14 08:00 | 2925 | 863.88 | 568 | 1240 | 1430.7692 | 0
2016-05-14 09:00 | 2925 | 893.16 | 530 | 1240 | 1430.7692 | 0
2016-05-14 10:00 | 2519 | 927.18 | 592 | 1240 | 1430.7692 | 0
2016-05-14 11:00 | 2519 | 949.5 | 519 | 1240 | 1430.7692 | 0
2016-05-14 12:00 | 2519 | 961.28 | 601 | 1240 | 1430.7692 | 0
2016-05-14 13:00 | 2519 | 963.38 | 617 | 1240 | 1430.7692 | 0
2016-05-14 14:00 | 2685 | 957.24 | 614 | 1240 | 1430.7692 | 0
2016-05-14 15:00 | 2685 | 941.26 | 511 | 1240 | 1430.7692 | 0
2016-05-14 16:00 | 2685 | 875.121 | 500 | 1240 | 1430.7692 | 0
2016-05-14 17:00 | 2685 | 853.081 | 384 | 1240 | 1521.4286 | 0
2016-05-14 18:00 | 2409 | 828.001 | 321 | 1240 | 1521.4286 | 0
2016-05-14 19:00 | 2409 | 845.18 | 570 | 1240 | 1521.4286 | 0
2016-05-14 20:00 | 2409 | 838.08 | 589 | 1240 | 1521.4286 | 0
2016-05-14 21:00 | 2409 | 820.74 | 423 | 1240 | 1521.4286 | 0
2016-05-14 22:00 | 2744 | 776.14 | 321 | 1240 | 1521.4286 | 0
2016-05-14 23:00 | 2744 | 725.9 | 321 | 1240 | 1521.4286 | 0
2016-05-15 | 2744 | 720.62 | 442 | 1240 | 1521.4286 | 0
2016-05-15 01:00 | 2744 | 714.8 | 534 | 1240 | 1521.4286 | 0
2016-05-15 02:00 | 3084 | 693.38 | 321 | 1240 | 1521.4286 | 0
2016-05-15 03:00 | 3084 | 679.8 | 339 | 1240 | 1521.4286 | 0
2016-05-15 04:00 | 3084 | 675.1 | 366 | 1240 | 1521.4286 | 0
2016-05-15 05:00 | 3084 | 683.38 | 493 | 1240 | 1521.4286 | 0
2016-05-15 06:00 | 2925 | 668.762 | 642 | 1240 | 1521.4286 | 0
2016-05-15 07:00 | 2925 | 688.37 | 490 | 1240 | 1521.4286 | 0
2016-05-15 08:00 | 2925 | 726.503 | 568 | 1240 | 1521.4286 | 0
2016-05-15 09:00 | 2925 | 805.9 | 530 | 1240 | 1430.7692 | 0
2016-05-15 10:00 | 2519 | 844.84 | 592 | 1240 | 1430.7692 | 0
2016-05-15 11:00 | 2519 | 865.32 | 519 | 1240 | 1430.7692 | 0
2016-05-15 12:00 | 2519 | 874.64 | 601 | 1240 | 1430.7692 | 0
2016-05-15 13:00 | 2519 | 882.52 | 617 | 1240 | 1440 | 0
2016-05-15 14:00 | 2685 | 853.765 | 614 | 1240 | 1440 | 0
2016-05-15 15:00 | 2685 | 873.715 | 511 | 1240 | 1440 | 0
2016-05-15 16:00 | 2685 | 920.46 | 500 | 1240 | 1440 | 0
2016-05-15 17:00 | 2685 | 885.875 | 384 | 1240 | 1440 | 0
2016-05-15 18:00 | 2409 | 925.7 | 321 | 1240 | 1440 | 0
2016-05-15 19:00 | 2409 | 918.92 | 570 | 1240 | 1440 | 0
2016-05-15 20:00 | 2409 | 882.93 | 589 | 1240 | 1440 | 0
2016-05-15 21:00 | 2409 | 873.031 | 423 | 1240 | 1440 | 0
2016-05-15 22:00 | 2744 | 875.3 | 321 | 1240 | 1430.7692 | 0
2016-05-15 23:00 | 2744 | 815.78 | 321 | 1240 | 1430.7692 | 0
2016-05-16 | 2744 | 716.813 | 442 | 1240 | 1521.4286 | 0
2016-05-16 01:00 | 2744 | 680.2 | 534 | 1240 | 1521.4286 | 0
2016-05-16 02:00 | 3084 | 687.26 | 321 | 1240 | 1521.4286 | 0
2016-05-16 03:00 | 3084 | 669.34 | 339 | 1240 | 1521.4286 | 0
2016-05-16 04:00 | 3084 | 660.16 | 366 | 1240 | 1521.4286 | 0
2016-05-16 05:00 | 3084 | 662.02 | 493 | 1240 | 1521.4286 | 0
2016-05-16 06:00 | 2925 | 667.5 | 642 | 1240 | 1521.4286 | 0
2016-05-16 07:00 | 2925 | 647.824 | 490 | 1240 | 1521.4286 | 0
2016-05-16 08:00 | 2925 | 697.034 | 568 | 1240 | 1521.4286 | 0
2016-05-16 09:00 | 2925 | 788.02 | 530 | 1240 | 1430.7692 | 0
2016-05-16 10:00 | 2519 | 843.18 | 592 | 1240 | 1430.7692 | 0
2016-05-16 11:00 | 2519 | 853.233 | 519 | 1240 | 1440 | 0
2016-05-16 12:00 | 2519 | 905.92 | 601 | 1240 | 1238.9381 | 0
2016-05-16 13:00 | 2519 | 1055.103 | 617 | 1240 | 1238.9381 | 0
2016-05-16 14:00 | 2685 | 1091.412 | 614 | 1240 | 1296.2963 | 0
2016-05-16 15:00 | 2685 | 1124.109 | 511 | 1240 | 1296.2963 | 0
2016-05-16 16:00 | 2685 | 1204.984 | 500 | 1240 | 1296.2963 | 0
2016-05-16 17:00 | 2685 | 1218.338 | 384 | 1240 | 1296.2963 | 0
2016-05-16 18:00 | 2409 | 1143.66 | 321 | 1240 | 1296.2963 | 0
2016-05-16 19:00 | 2409 | 1124.361 | 570 | 1240 | 1296.2963 | 0
2016-05-16 20:00 | 2409 | 1114.953 | 589 | 1240 | 1296.2963 | 0
2016-05-16 21:00 | 2409 | 1092.693 | 423 | 1240 | 1238.9381 | 0
2016-05-16 22:00 | 2744 | 918.745 | 321 | 1240 | 1238.9381 | 0
2016-05-16 23:00 | 2744 | 874.3 | 321 | 1240 | 1440 | 0
2016-05-17 | 2744 | 703.893 | 442 | 1240 | 1430.7692 | 0
2016-05-17 01:00 | 2744 | 666.767 | 534 | 1240 | 1430.7692 | 0
2016-05-17 02:00 | 3084 | 677.08 | 321 | 1240 | 1430.7692 | 0
2016-05-17 03:00 | 3084 | 664.44 | 339 | 1240 | 1430.7692 | 0
2016-05-17 04:00 | 3084 | 667.4 | 366 | 1240 | 1430.7692 | 0
2016-05-17 05:00 | 3084 | 669.636 | 493 | 1240 | 1430.7692 | 0
2016-05-17 06:00 | 2925 | 731.538 | 642 | 1240 | 1430.7692 | 0
2016-05-17 07:00 | 2925 | 804.56 | 490 | 1240 | 1430.7692 | 0
2016-05-17 08:00 | 2925 | 843.68 | 568 | 1240 | 1440 | 0
2016-05-17 09:00 | 2925 | 848.331 | 530 | 1240 | 1440 | 0
2016-05-17 10:00 | 2519 | 907.915 | 592 | 1240 | 1238.9381 | 0
2016-05-17 11:00 | 2519 | 1062.369 | 519 | 1240 | 1296.2963 | 0
2016-05-17 12:00 | 2519 | 1114.092 | 601 | 1240 | 1296.2963 | 0
2016-05-17 13:00 | 2519 | 1218.602 | 617 | 1240 | 1000 | 0
2016-05-17 14:00 | 2685 | 1257.19 | 614 | 1240 | 1000 | 0
2016-05-17 15:00 | 2685 | 1269.202 | 511 | 1240 | 1000 | 0
2016-05-17 16:00 | 2685 | 1253.23 | 500 | 1240 | 1000 | 0
2016-05-17 17:00 | 2685 | 1159.284 | 384 | 1240 | 1296.2963 | 0
2016-05-17 18:00 | 2409 | 1105.041 | 321 | 1240 | 1296.2963 | 0
2016-05-17 19:00 | 2409 | 950.703 | 570 | 1240 | 1238.9381 | 0
2016-05-17 20:00 | 2409 | 937.327 | 589 | 1240 | 1238.9381 | 0
2016-05-17 21:00 | 2409 | 951.78 | 423 | 1240 | 1440 | 0
2016-05-17 22:00 | 2744 | 871.8 | 321 | 1240 | 1430.7692 | 0
2016-05-17 23:00 | 2744 | 745.351 | 321 | 1240 | 1521.4286 | 0
2016-05-18 | 2744 | 737.34 | 442 | 1240 | 1521.4286 | 0
2016-05-18 01:00 | 2744 | 698.66 | 534 | 1240 | 1521.4286 | 0
2016-05-18 02:00 | 3084 | 674.82 | 321 | 1240 | 1521.4286 | 0
2016-05-18 03:00 | 3084 | 662.06 | 339 | 1240 | 1521.4286 | 0
2016-05-18 04:00 | 3084 | 664.54 | 366 | 1240 | 1521.4286 | 0
2016-05-18 05:00 | 3084 | 699.6 | 493 | 1240 | 1521.4286 | 0
2016-05-18 06:00 | 2925 | 730.569 | 642 | 1240 | 1521.4286 | 0
2016-05-18 07:00 | 2925 | 754.471 | 490 | 1240 | 1521.4286 | 0
2016-05-18 08:00 | 2925 | 816.64 | 568 | 1240 | 1521.4286 | 0
2016-05-18 09:00 | 2925 | 849.64 | 530 | 1240 | 1430.7692 | 0
2016-05-18 10:00 | 2519 | 886.82 | 592 | 1240 | 1430.7692 | 0
2016-05-18 11:00 | 2519 | 925.32 | 519 | 1240 | 1440 | 0
2016-05-18 12:00 | 2519 | 918.042 | 601 | 1240 | 1440 | 0
2016-05-18 13:00 | 2519 | 959.424 | 617 | 1240 | 1440 | 0
2016-05-18 14:00 | 2685 | 994.403 | 614 | 1240 | 1238.9381 | 0
2016-05-18 15:00 | 2685 | 1129.254 | 511 | 1240 | 1238.9381 | 0
2016-05-18 16:00 | 2685 | 1156.68 | 500 | 1240 | 1238.9381 | 0
2016-05-18 17:00 | 2685 | 1053.36 | 384 | 1240 | 1238.9381 | 0
2016-05-18 18:00 | 2409 | 1027.615 | 321 | 1240 | 1440 | 0
2016-05-18 19:00 | 2409 | 1054.62 | 570 | 1240 | 1430.7692 | 0
2016-05-18 20:00 | 2409 | 1041.64 | 589 | 1240 | 1430.7692 | 0
2016-05-18 21:00 | 2409 | 1020.42 | 423 | 1240 | 1430.7692 | 0
2016-05-18 22:00 | 2744 | 889.409 | 321 | 1240 | 1521.4286 | 0
2016-05-18 23:00 | 2744 | 847.22 | 321 | 1240 | 1673.3333 | 0
2016-05-19 | 2744 | 667.206 | 442 | 1240 | 1730 | 0
2016-05-19 01:00 | 2744 | 633.744 | 534 | 1240 | 1730 | 0
2016-05-19 02:00 | 3084 | 612.18 | 321 | 1240 | 1730 | 0
2016-05-19 03:00 | 3084 | 598.23 | 339 | 1240 | 1730 | 0
2016-05-19 04:00 | 3084 | 601.02 | 366 | 1240 | 1730 | 0
2016-05-19 05:00 | 3084 | 630.198 | 493 | 1240 | 1730 | 0
2016-05-19 06:00 | 2925 | 764.44 | 642 | 1240 | 1730 | 0
2016-05-19 07:00 | 2925 | 796.7 | 490 | 1240 | 1673.3333 | 0
2016-05-19 08:00 | 2925 | 824.02 | 568 | 1240 | 1673.3333 | 0
2016-05-19 09:00 | 2925 | 820.648 | 530 | 1240 | 1521.4286 | 0
2016-05-19 10:00 | 2519 | 865.222 | 592 | 1240 | 1430.7692 | 0
2016-05-19 11:00 | 2519 | 952.46 | 519 | 1240 | 1430.7692 | 0
2016-05-19 12:00 | 2519 | 991.26 | 601 | 1240 | 1430.7692 | 0
2016-05-19 13:00 | 2519 | 977.493 | 617 | 1240 | 1440 | 0
2016-05-19 14:00 | 2685 | 1008.52 | 614 | 1240 | 1440 | 0
2016-05-19 15:00 | 2685 | 1089.02 | 511 | 1240 | 1440 | 0
2016-05-19 16:00 | 2685 | 1052.372 | 500 | 1240 | 1440 | 0
2016-05-19 17:00 | 2685 | 1054.348 | 384 | 1240 | 1440 | 0
2016-05-19 18:00 | 2409 | 1081.8 | 321 | 1240 | 1238.9381 | 0
2016-05-19 19:00 | 2409 | 1001.053 | 570 | 1240 | 1238.9381 | 0
2016-05-19 20:00 | 2409 | 1086.624 | 589 | 1240 | 1238.9381 | 0
2016-05-19 21:00 | 2409 | 961.248 | 423 | 1240 | 1238.9381 | 0
2016-05-19 22:00 | 2744 | 933.98 | 321 | 1240 | 1440 | 0
2016-05-19 23:00 | 2744 | 848.92 | 321 | 1240 | 1430.7692 | 0
2016-05-20 | 2744 | 746.757 | 442 | 1240 | 1430.7692 | 0
2016-05-20 01:00 | 2744 | 746.5 | 534 | 1240 | 1521.4286 | 0
2016-05-20 02:00 | 3084 | 720.32 | 321 | 1240 | 1521.4286 | 0
2016-05-20 03:00 | 3084 | 706.58 | 339 | 1240 | 1521.4286 | 0
2016-05-20 04:00 | 3084 | 707.1 | 366 | 1240 | 1521.4286 | 0
2016-05-20 05:00 | 3084 | 740.8 | 493 | 1240 | 1521.4286 | 0
2016-05-20 06:00 | 2925 | 766.042 | 642 | 1240 | 1521.4286 | 0
2016-05-20 07:00 | 2925 | 794.466 | 490 | 1240 | 1521.4286 | 0
2016-05-20 08:00 | 2925 | 860.96 | 568 | 1240 | 1430.7692 | 0
2016-05-20 09:00 | 2925 | 896.96 | 530 | 1240 | 1430.7692 | 0
2016-05-20 10:00 | 2519 | 889.751 | 592 | 1240 | 1440 | 0
2016-05-20 11:00 | 2519 | 918.764 | 519 | 1240 | 1440 | 0
2016-05-20 12:00 | 2519 | 945.174 | 601 | 1240 | 1238.9381 | 0
2016-05-20 13:00 | 2519 | 1072.953 | 617 | 1240 | 1238.9381 | 0
2016-05-20 14:00 | 2685 | 1095.885 | 614 | 1240 | 1238.9381 | 0
2016-05-20 15:00 | 2685 | 1123.836 | 511 | 1240 | 1296.2963 | 0
2016-05-20 16:00 | 2685 | 1150.128 | 500 | 1240 | 1296.2963 | 0
2016-05-20 17:00 | 2685 | 1152.858 | 384 | 1240 | 1296.2963 | 0
2016-05-20 18:00 | 2409 | 1120.602 | 321 | 1240 | 1238.9381 | 0
2016-05-20 19:00 | 2409 | 1088.346 | 570 | 1240 | 1238.9381 | 0
2016-05-20 20:00 | 2409 | 965.884 | 589 | 1240 | 1238.9381 | 0
2016-05-20 21:00 | 2409 | 940.766 | 423 | 1240 | 1440 | 0
2016-05-20 22:00 | 2744 | 918.98 | 321 | 1240 | 1430.7692 | 0
2016-05-20 23:00 | 2744 | 793.63 | 321 | 1240 | 1430.7692 | 0
2016-05-21 | 2744 | 764.427 | 442 | 1240 | 1521.4286 | 0
2016-05-21 01:00 | 2744 | 762.02 | 534 | 1240 | 1521.4286 | 0
2016-05-21 02:00 | 3084 | 733.72 | 321 | 1240 | 1521.4286 | 0
2016-05-21 03:00 | 3084 | 717.38 | 339 | 1240 | 1521.4286 | 0
2016-05-21 04:00 | 3084 | 718.14 | 366 | 1240 | 1521.4286 | 0
2016-05-21 05:00 | 3084 | 753.56 | 493 | 1240 | 1521.4286 | 0
2016-05-21 06:00 | 2925 | 785.08 | 642 | 1240 | 1521.4286 | 0
2016-05-21 07:00 | 2925 | 860.36 | 490 | 1240 | 1430.7692 | 0
2016-05-21 08:00 | 2925 | 885.66 | 568 | 1240 | 1430.7692 | 0
2016-05-21 09:00 | 2925 | 926.36 | 530 | 1240 | 1440 | 0
2016-05-21 10:00 | 2519 | 927.333 | 592 | 1240 | 1440 | 0
2016-05-21 11:00 | 2519 | 969.019 | 519 | 1240 | 1440 | 0
2016-05-21 12:00 | 2519 | 1009.66 | 601 | 1240 | 1238.9381 | 0
2016-05-21 13:00 | 2519 | 1166.55 | 617 | 1240 | 1296.2963 | 0
2016-05-21 14:00 | 2685 | 1214.934 | 614 | 1240 | 1296.2963 | 0
2016-05-21 15:00 | 2685 | 1251.054 | 511 | 1240 | 1296.2963 | 0
2016-05-21 16:00 | 2685 | 1274.574 | 500 | 1240 | 1296.2963 | 0
2016-05-21 17:00 | 2685 | 1269.345 | 384 | 1240 | 1296.2963 | 0
2016-05-21 18:00 | 2409 | 1222.977 | 321 | 1240 | 1296.2963 | 0
2016-05-21 19:00 | 2409 | 1064.57 | 570 | 1240 | 1238.9381 | 0
2016-05-21 20:00 | 2409 | 1088.92 | 589 | 1240 | 1440 | 0
2016-05-21 21:00 | 2409 | 1059.88 | 423 | 1240 | 1430.7692 | 0
2016-05-21 22:00 | 2744 | 996.26 | 321 | 1240 | 1430.7692 | 0
2016-05-21 23:00 | 2744 | 873.677 | 321 | 1240 | 1521.4286 | 0
2016-05-22 | 2744 | 844.55 | 442 | 1240 | 1521.4286 | 0
2016-05-22 01:00 | 2744 | 841.3 | 534 | 1240 | 1521.4286 | 0
2016-05-22 02:00 | 3084 | 807.94 | 321 | 1240 | 1521.4286 | 0
2016-05-22 03:00 | 3084 | 708.84 | 339 | 1240 | 1521.4286 | 0
2016-05-22 04:00 | 3084 | 699.534 | 366 | 1240 | 1521.4286 | 0
2016-05-22 05:00 | 3084 | 779.16 | 493 | 1240 | 1521.4286 | 0
2016-05-22 06:00 | 2925 | 799.74 | 642 | 1240 | 1673.3333 | 0
2016-05-22 07:00 | 2925 | 820.3 | 490 | 1240 | 1673.3333 | 0
2016-05-22 08:00 | 2925 | 873.98 | 568 | 1240 | 1521.4286 | 0
2016-05-22 09:00 | 2925 | 889.276 | 530 | 1240 | 1521.4286 | 0
2016-05-22 10:00 | 2519 | 940.88 | 592 | 1240 | 1521.4286 | 0
2016-05-22 11:00 | 2519 | 984.219 | 519 | 1240 | 1521.4286 | 0
2016-05-22 12:00 | 2519 | 1081.66 | 601 | 1240 | 1430.7692 | 0
2016-05-22 13:00 | 2519 | 1118.76 | 617 | 1240 | 1440 | 0
2016-05-22 14:00 | 2685 | 1094.818 | 614 | 1240 | 1440 | 0
2016-05-22 15:00 | 2685 | 1119.195 | 511 | 1240 | 1440 | 0
2016-05-22 16:00 | 2685 | 1128.41 | 500 | 1240 | 1440 | 0
2016-05-22 17:00 | 2685 | 1119.746 | 384 | 1240 | 1440 | 0
2016-05-22 18:00 | 2409 | 1088.358 | 321 | 1240 | 1440 | 0
2016-05-22 19:00 | 2409 | 1112.58 | 570 | 1240 | 1440 | 0
2016-05-22 20:00 | 2409 | 1100.46 | 589 | 1240 | 1430.7692 | 0
2016-05-22 21:00 | 2409 | 1082.64 | 423 | 1240 | 1430.7692 | 0
2016-05-22 22:00 | 2744 | 1026.72 | 321 | 1240 | 1430.7692 | 0
2016-05-22 23:00 | 2744 | 912.057 | 321 | 1240 | 1521.4286 | 0
2016-05-23 | 2744 | 908.92 | 442 | 1240 | 1521.4286 | 0
2016-05-23 01:00 | 2744 | 862.88 | 534 | 1240 | 1521.4286 | 0
2016-05-23 02:00 | 3084 | 831.86 | 321 | 1240 | 1673.3333 | 0
2016-05-23 03:00 | 3084 | 811 | 339 | 1240 | 1673.3333 | 0
2016-05-23 04:00 | 3084 | 796.58 | 366 | 1240 | 1673.3333 | 0
2016-05-23 05:00 | 3084 | 795.42 | 493 | 1240 | 1673.3333 | 0
2016-05-23 06:00 | 2925 | 795.44 | 642 | 1240 | 1673.3333 | 0
2016-05-23 07:00 | 2925 | 810.3 | 490 | 1240 | 1673.3333 | 0
2016-05-23 08:00 | 2925 | 869.48 | 568 | 1240 | 1673.3333 | 0
2016-05-23 09:00 | 2925 | 893.684 | 530 | 1240 | 1521.4286 | 0
2016-05-23 10:00 | 2519 | 952.413 | 592 | 1240 | 1521.4286 | 0
2016-05-23 11:00 | 2519 | 1005.803 | 519 | 1240 | 1430.7692 | 0
2016-05-23 12:00 | 2519 | 1110.56 | 601 | 1240 | 1430.7692 | 0
2016-05-23 13:00 | 2519 | 1154.54 | 617 | 1240 | 1440 | 0
2016-05-23 14:00 | 2685 | 1133.464 | 614 | 1240 | 1238.9381 | 0
2016-05-23 15:00 | 2685 | 1158.449 | 511 | 1240 | 1238.9381 | 0
2016-05-23 16:00 | 2685 | 1292.067 | 500 | 1240 | 1238.9381 | 0
2016-05-23 17:00 | 2685 | 1289.568 | 384 | 1240 | 1238.9381 | 0
2016-05-23 18:00 | 2409 | 1135.402 | 321 | 1240 | 1238.9381 | 0
2016-05-23 19:00 | 2409 | 1104.052 | 570 | 1240 | 1238.9381 | 0
2016-05-23 20:00 | 2409 | 1089.061 | 589 | 1240 | 1238.9381 | 0
2016-05-23 21:00 | 2409 | 1074.203 | 423 | 1240 | 1440 | 0
2016-05-23 22:00 | 2744 | 1065.08 | 321 | 1240 | 1440 | 0
2016-05-23 23:00 | 2744 | 929.138 | 321 | 1240 | 1430.7692 | 0
2016-05-24 | 2744 | 845.62 | 442 | 1240 | 1521.4286 | 0
2016-05-24 01:00 | 2744 | 720.864 | 534 | 1240 | 1521.4286 | 0
2016-05-24 02:00 | 3084 | 692.676 | 321 | 1240 | 1521.4286 | 0
2016-05-24 03:00 | 3084 | 679.104 | 339 | 1240 | 1521.4286 | 0
2016-05-24 04:00 | 3084 | 682.506 | 366 | 1240 | 1521.4286 | 0
2016-05-24 05:00 | 3084 | 792.48 | 493 | 1240 | 1521.4286 | 0
2016-05-24 06:00 | 2925 | 815.651 | 642 | 1240 | 1521.4286 | 0
2016-05-24 07:00 | 2925 | 890.94 | 490 | 1240 | 1521.4286 | 0
2016-05-24 08:00 | 2925 | 871.378 | 568 | 1240 | 1521.4286 | 0
2016-05-24 09:00 | 2925 | 913.824 | 530 | 1240 | 1521.4286 | 0
2016-05-24 10:00 | 2519 | 956.802 | 592 | 1240 | 1430.7692 | 0
2016-05-24 11:00 | 2519 | 1059.2 | 519 | 1240 | 1430.7692 | 0
2016-05-24 12:00 | 2519 | 1103.86 | 601 | 1240 | 1440 | 0
2016-05-24 13:00 | 2519 | 1083.722 | 617 | 1240 | 1238.9381 | 0
2016-05-24 14:00 | 2685 | 1233.582 | 614 | 1240 | 1296.2963 | 0
2016-05-24 15:00 | 2685 | 1263.465 | 511 | 1240 | 1296.2963 | 0
2016-05-24 16:00 | 2685 | 1272.768 | 500 | 1240 | 1296.2963 | 0
2016-05-24 17:00 | 2685 | 1261.911 | 384 | 1240 | 1238.9381 | 0
2016-05-24 18:00 | 2409 | 1105.952 | 321 | 1240 | 1238.9381 | 0
2016-05-24 19:00 | 2409 | 1070.175 | 570 | 1240 | 1238.9381 | 0
2016-05-24 20:00 | 2409 | 1050.681 | 589 | 1240 | 1238.9381 | 0
2016-05-24 21:00 | 2409 | 1023.549 | 423 | 1240 | 1238.9381 | 0
2016-05-24 22:00 | 2744 | 995.7 | 321 | 1240 | 1430.7692 | 0
2016-05-24 23:00 | 2744 | 857.052 | 321 | 1240 | 1430.7692 | 0
2016-05-25 | 2744 | 775.143 | 442 | 1240 | 1430.7692 | 0
2016-05-25 01:00 | 2744 | 733.286 | 534 | 1240 | 1430.7692 | 0
2016-05-25 02:00 | 3084 | 743.14 | 321 | 1240 | 1430.7692 | 0
2016-05-25 03:00 | 3084 | 726.68 | 339 | 1240 | 1430.7692 | 0
2016-05-25 04:00 | 3084 | 726.76 | 366 | 1240 | 1430.7692 | 0
2016-05-25 05:00 | 3084 | 723.064 | 493 | 1240 | 1430.7692 | 0
2016-05-25 06:00 | 2925 | 823.04 | 642 | 1240 | 1430.7692 | 0
2016-05-25 07:00 | 2925 | 855.5 | 490 | 1240 | 1430.7692 | 0
2016-05-25 08:00 | 2925 | 883.6 | 568 | 1240 | 1430.7692 | 0
2016-05-25 09:00 | 2925 | 877.534 | 530 | 1240 | 1440 | 0
2016-05-25 10:00 | 2519 | 921.329 | 592 | 1240 | 1440 | 0
2016-05-25 11:00 | 2519 | 960.203 | 519 | 1240 | 1238.9381 | 0
2016-05-25 12:00 | 2519 | 990.071 | 601 | 1240 | 1238.9381 | 0
2016-05-25 13:00 | 2519 | 1131.522 | 617 | 1240 | 1296.2963 | 0
2016-05-25 14:00 | 2685 | 1170.099 | 614 | 1240 | 1296.2963 | 0
2016-05-25 15:00 | 2685 | 1198.386 | 511 | 1240 | 1296.2963 | 0
2016-05-25 16:00 | 2685 | 1215.123 | 500 | 1240 | 1296.2963 | 0
2016-05-25 17:00 | 2685 | 1197.924 | 384 | 1240 | 1296.2963 | 0
2016-05-25 18:00 | 2409 | 1162.938 | 321 | 1240 | 1238.9381 | 0
2016-05-25 19:00 | 2409 | 1020.528 | 570 | 1240 | 1238.9381 | 0
2016-05-25 20:00 | 2409 | 1004.093 | 589 | 1240 | 1440 | 0
2016-05-25 21:00 | 2409 | 974.016 | 423 | 1240 | 1440 | 0
2016-05-25 22:00 | 2744 | 948.16 | 321 | 1240 | 1430.7692 | 0
2016-05-25 23:00 | 2744 | 809.419 | 321 | 1240 | 1430.7692 | 0
2016-05-26 | 2744 | 745.2 | 442 | 1240 | 1430.7692 | 0
2016-05-26 01:00 | 2744 | 703.4 | 534 | 1240 | 1430.7692 | 0
2016-05-26 02:00 | 3084 | 678.16 | 321 | 1240 | 1430.7692 | 0
2016-05-26 03:00 | 3084 | 663.86 | 339 | 1240 | 1430.7692 | 0
2016-05-26 04:00 | 3084 | 665.86 | 366 | 1240 | 1430.7692 | 0
2016-05-26 05:00 | 3084 | 660.668 | 493 | 1240 | 1430.7692 | 0
2016-05-26 06:00 | 2925 | 717.079 | 642 | 1240 | 1430.7692 | 0
2016-05-26 07:00 | 2925 | 786.44 | 490 | 1240 | 1430.7692 | 0
2016-05-26 08:00 | 2925 | 823.38 | 568 | 1240 | 1430.7692 | 0
2016-05-26 09:00 | 2925 | 873.36 | 530 | 1240 | 1440 | 0
2016-05-26 10:00 | 2519 | 890.549 | 592 | 1240 | 1440 | 0
2016-05-26 11:00 | 2519 | 944.49 | 519 | 1240 | 1238.9381 | 0
2016-05-26 12:00 | 2519 | 988.19 | 601 | 1240 | 1238.9381 | 0
2016-05-26 13:00 | 2519 | 1142.295 | 617 | 1240 | 1296.2963 | 0
2016-05-26 14:00 | 2685 | 1180.536 | 614 | 1240 | 1296.2963 | 0
2016-05-26 15:00 | 2685 | 1267.772 | 511 | 1240 | 1296.2963 | 0
2016-05-26 16:00 | 2685 | 1281.94 | 500 | 1240 | 1000 | 0
2016-05-26 17:00 | 2685 | 1274.812 | 384 | 1240 | 1000 | 0
2016-05-26 18:00 | 2409 | 1174.446 | 321 | 1240 | 1296.2963 | 0
2016-05-26 19:00 | 2409 | 1132.026 | 570 | 1240 | 1296.2963 | 0
2016-05-26 20:00 | 2409 | 995.372 | 589 | 1240 | 1238.9381 | 0
2016-05-26 21:00 | 2409 | 965.143 | 423 | 1240 | 1440 | 0
2016-05-26 22:00 | 2744 | 936.78 | 321 | 1240 | 1430.7692 | 0
2016-05-26 23:00 | 2744 | 800.375 | 321 | 1240 | 1521.4286 | 0
2016-05-27 | 2744 | 768.12 | 442 | 1240 | 1430.7692 | 0
2016-05-27 01:00 | 2744 | 722.84 | 534 | 1240 | 1430.7692 | 0
2016-05-27 02:00 | 3084 | 690.98 | 321 | 1240 | 1430.7692 | 0
2016-05-27 03:00 | 3084 | 672.38 | 339 | 1240 | 1430.7692 | 0
2016-05-27 04:00 | 3084 | 669.16 | 366 | 1240 | 1430.7692 | 0
2016-05-27 05:00 | 3084 | 698.14 | 493 | 1240 | 1521.4286 | 0
2016-05-27 06:00 | 2925 | 718.086 | 642 | 1240 | 1521.4286 | 0
2016-05-27 07:00 | 2925 | 789.32 | 490 | 1240 | 1521.4286 | 0
2016-05-27 08:00 | 2925 | 827.88 | 568 | 1240 | 1430.7692 | 0
2016-05-27 09:00 | 2925 | 837.615 | 530 | 1240 | 1440 | 0
2016-05-27 10:00 | 2519 | 899.65 | 592 | 1240 | 1440 | 0
2016-05-27 11:00 | 2519 | 1058.673 | 519 | 1240 | 1238.9381 | 0
2016-05-27 12:00 | 2519 | 1118.145 | 601 | 1240 | 1296.2963 | 0
2016-05-27 13:00 | 2519 | 1226.566 | 617 | 1240 | 1296.2963 | 0
2016-05-27 14:00 | 2685 | 1267.31 | 614 | 1240 | 1000 | 0
2016-05-27 15:00 | 2685 | 1293.006 | 511 | 1240 | 1000 | 0
2016-05-27 16:00 | 2685 | 1305.92 | 500 | 1240 | 1000 | 0
2016-05-27 17:00 | 2685 | 1288.452 | 384 | 1240 | 1000 | 0
2016-05-27 18:00 | 2409 | 1239.722 | 321 | 1240 | 1000 | 0
2016-05-27 19:00 | 2409 | 1136.835 | 570 | 1240 | 1296.2963 | 0
2016-05-27 20:00 | 2409 | 1108.212 | 589 | 1240 | 1238.9381 | 0
2016-05-27 21:00 | 2409 | 974.529 | 423 | 1240 | 1440 | 0
2016-05-27 22:00 | 2744 | 944.82 | 321 | 1240 | 1430.7692 | 0
2016-05-27 23:00 | 2744 | 810.369 | 321 | 1240 | 1430.7692 | 0
2016-05-28 | 2744 | 752.286 | 442 | 1240 | 1430.7692 | 0
2016-05-28 01:00 | 2744 | 744.42 | 534 | 1240 | 1430.7692 | 0
2016-05-28 02:00 | 3084 | 712.88 | 321 | 1240 | 1430.7692 | 0
2016-05-28 03:00 | 3084 | 692.94 | 339 | 1240 | 1430.7692 | 0
2016-05-28 04:00 | 3084 | 690.3 | 366 | 1240 | 1430.7692 | 0
2016-05-28 05:00 | 3084 | 715.72 | 493 | 1240 | 1430.7692 | 0
2016-05-28 06:00 | 2925 | 727.966 | 642 | 1240 | 1430.7692 | 0
2016-05-28 07:00 | 2925 | 805.36 | 490 | 1240 | 1430.7692 | 0
2016-05-28 08:00 | 2925 | 854.32 | 568 | 1240 | 1440 | 0
2016-05-28 09:00 | 2925 | 873.107 | 530 | 1240 | 1440 | 0
2016-05-28 10:00 | 2519 | 1044.33 | 592 | 1240 | 1238.9381 | 0
2016-05-28 11:00 | 2519 | 1114.071 | 519 | 1240 | 1296.2963 | 0
2016-05-28 12:00 | 2519 | 1225.994 | 601 | 1240 | 1000 | 0
2016-05-28 13:00 | 2519 | 1279.058 | 617 | 1240 | 1040 | 0
2016-05-28 14:00 | 2685 | 1320 | 614 | 1240 | 1040 | 0
2016-05-28 15:00 | 2685 | 1343.672 | 511 | 1240 | 1040 | 0
2016-05-28 16:00 | 2685 | 1351.02 | 500 | 1240 | 1040 | 0
2016-05-28 17:00 | 2685 | 1336.786 | 384 | 1240 | 1040 | 0
2016-05-28 18:00 | 2409 | 1282.512 | 321 | 1240 | 1040 | 0
2016-05-28 19:00 | 2409 | 1228.238 | 570 | 1240 | 1000 | 0
2016-05-28 20:00 | 2409 | 1125.264 | 589 | 1240 | 1296.2963 | 0
2016-05-28 21:00 | 2409 | 980.78 | 423 | 1240 | 1238.9381 | 0
2016-05-28 22:00 | 2744 | 964.82 | 321 | 1240 | 1440 | 0
2016-05-28 23:00 | 2744 | 887 | 321 | 1240 | 1430.7692 | 0
2016-05-29 | 2744 | 821.864 | 442 | 1240 | 1430.7692 | 0
2016-05-29 01:00 | 2744 | 800.166 | 534 | 1240 | 1430.7692 | 0
2016-05-29 02:00 | 3084 | 758.461 | 321 | 1240 | 1430.7692 | 0
2016-05-29 03:00 | 3084 | 768.36 | 339 | 1240 | 1430.7692 | 0
2016-05-29 04:00 | 3084 | 752.04 | 366 | 1240 | 1430.7692 | 0
2016-05-29 05:00 | 3084 | 751.06 | 493 | 1240 | 1430.7692 | 0
2016-05-29 06:00 | 2925 | 752.22 | 642 | 1240 | 1430.7692 | 0
2016-05-29 07:00 | 2925 | 739.062 | 490 | 1240 | 1430.7692 | 0
2016-05-29 08:00 | 2925 | 854.8 | 568 | 1240 | 1430.7692 | 0
2016-05-29 09:00 | 2925 | 899.498 | 530 | 1240 | 1440 | 0
2016-05-29 10:00 | 2519 | 1089.249 | 592 | 1240 | 1238.9381 | 0
2016-05-29 11:00 | 2519 | 1229.25 | 519 | 1240 | 1296.2963 | 0
2016-05-29 12:00 | 2519 | 1299.21 | 601 | 1240 | 1040 | 0
2016-05-29 13:00 | 2519 | 1345.432 | 617 | 1240 | 1040 | 0
2016-05-29 14:00 | 2685 | 1375.66 | 614 | 1240 | 1040 | 0
2016-05-29 15:00 | 2685 | 1397.726 | 511 | 1240 | 1040 | 0
2016-05-29 16:00 | 2685 | 1404.106 | 500 | 1240 | 1040 | 0
2016-05-29 17:00 | 2685 | 1389.608 | 384 | 1240 | 1040 | 0
2016-05-29 18:00 | 2409 | 1344.662 | 321 | 1240 | 1040 | 0
2016-05-29 19:00 | 2409 | 1299.716 | 570 | 1240 | 1000 | 0
2016-05-29 20:00 | 2409 | 1202.229 | 589 | 1240 | 1238.9381 | 0
2016-05-29 21:00 | 2409 | 1055.127 | 423 | 1240 | 1238.9381 | 0
2016-05-29 22:00 | 2744 | 1038.34 | 321 | 1240 | 1440 | 0
2016-05-29 23:00 | 2744 | 965.18 | 321 | 1240 | 1430.7692 | 0
2016-05-30 | 2744 | 868.129 | 442 | 1240 | 1430.7692 | 0
2016-05-30 01:00 | 2744 | 817.38 | 534 | 1240 | 1430.7692 | 0
2016-05-30 02:00 | 3084 | 780.862 | 321 | 1240 | 1430.7692 | 0
2016-05-30 03:00 | 3084 | 794.82 | 339 | 1240 | 1430.7692 | 0
2016-05-30 04:00 | 3084 | 776.46 | 366 | 1240 | 1430.7692 | 0
2016-05-30 05:00 | 3084 | 769.3 | 493 | 1240 | 1430.7692 | 0
2016-05-30 06:00 | 2925 | 762.88 | 642 | 1240 | 1430.7692 | 0
2016-05-30 07:00 | 2925 | 740.316 | 490 | 1240 | 1430.7692 | 0
2016-05-30 08:00 | 2925 | 848.12 | 568 | 1240 | 1430.7692 | 0
2016-05-30 09:00 | 2925 | 886.54 | 530 | 1240 | 1440 | 0
2016-05-30 10:00 | 2519 | 966.378 | 592 | 1240 | 1238.9381 | 0
2016-05-30 11:00 | 2519 | 1148.826 | 519 | 1240 | 1296.2963 | 0
2016-05-30 12:00 | 2519 | 1279.212 | 601 | 1240 | 1000 | 0
2016-05-30 13:00 | 2519 | 1340.614 | 617 | 1240 | 1040 | 0
2016-05-30 14:00 | 2685 | 1382.986 | 614 | 1240 | 1040 | 0
2016-05-30 15:00 | 2685 | 1406.394 | 511 | 1240 | 1040 | 0
2016-05-30 16:00 | 2685 | 1416.074 | 500 | 1240 | 1040 | 0
2016-05-30 17:00 | 2685 | 1400.85 | 384 | 1240 | 1040 | 0
2016-05-30 18:00 | 2409 | 1348.71 | 321 | 1240 | 1040 | 0
2016-05-30 19:00 | 2409 | 1296.57 | 570 | 1240 | 1040 | 0
2016-05-30 20:00 | 2409 | 1204.686 | 589 | 1240 | 1296.2963 | 0
2016-05-30 21:00 | 2409 | 1173.753 | 423 | 1240 | 1238.9381 | 0
2016-05-30 22:00 | 2744 | 998.374 | 321 | 1240 | 1440 | 0
2016-05-30 23:00 | 2744 | 974.14 | 321 | 1240 | 1440 | 0
2016-05-31 | 2744 | 832.865 | 442 | 1240 | 1430.7692 | 0
2016-05-31 01:00 | 2744 | 786.543 | 534 | 1240 | 1430.7692 | 0
2016-05-31 02:00 | 3084 | 753.54 | 321 | 1240 | 1430.7692 | 0
2016-05-31 03:00 | 3084 | 731.234 | 339 | 1240 | 1430.7692 | 0
2016-05-31 04:00 | 3084 | 720.499 | 366 | 1240 | 1430.7692 | 0
2016-05-31 05:00 | 3084 | 726.313 | 493 | 1240 | 1430.7692 | 0
2016-05-31 06:00 | 2925 | 730.74 | 642 | 1240 | 1430.7692 | 0
2016-05-31 07:00 | 2925 | 743.679 | 490 | 1240 | 1430.7692 | 0
2016-05-31 08:00 | 2925 | 844.84 | 568 | 1240 | 1440 | 0
2016-05-31 09:00 | 2925 | 880.251 | 530 | 1240 | 1238.9381 | 0
2016-05-31 10:00 | 2519 | 1062.726 | 592 | 1240 | 1296.2963 | 0
2016-05-31 11:00 | 2519 | 1198.362 | 519 | 1240 | 1296.2963 | 0
2016-05-31 12:00 | 2519 | 1269.664 | 601 | 1240 | 1000 | 0
2016-05-31 13:00 | 2519 | 1326.908 | 617 | 1240 | 1040 | 0
2016-05-31 14:00 | 2685 | 1374.186 | 614 | 1240 | 1040 | 0
2016-05-31 15:00 | 2685 | 1413.17 | 511 | 1240 | 1040 | 0
2016-05-31 16:00 | 2685 | 1435.808 | 500 | 1240 | 1040 | 0
2016-05-31 17:00 | 2685 | 1434.004 | 384 | 1240 | 1040 | 0
2016-05-31 18:00 | 2409 | 1394.36 | 321 | 1240 | 1040 | 0
2016-05-31 19:00 | 2409 | 1354.716 | 570 | 1240 | 1040 | 0
2016-05-31 20:00 | 2409 | 1320.418 | 589 | 1240 | 1000 | 0
2016-05-31 21:00 | 2409 | 1227.975 | 423 | 1240 | 1296.2963 | 0
2016-05-31 22:00 | 2744 | 1026.874 | 321 | 1240 | 1440 | 0
2016-05-31 23:00 | 2744 | 979.82 | 321 | 1240 | 1430.7692 | 0
2016-06-01 | 2261 | 820.192 | 462 | 1240 | 1430.7692 | 0
2016-06-01 01:00 | 2261 | 813.5 | 378 | 1240 | 1430.7692 | 0
2016-06-01 02:00 | 2900 | 779.14 | 348 | 1240 | 1430.7692 | 0
2016-06-01 03:00 | 2900 | 759.36 | 363 | 1240 | 1430.7692 | 0
2016-06-01 04:00 | 2900 | 756.94 | 393 | 1240 | 1430.7692 | 0
2016-06-01 05:00 | 2900 | 784.7 | 498 | 1240 | 1430.7692 | 0
2016-06-01 06:00 | 2751 | 796.727 | 542 | 1240 | 1430.7692 | 0
2016-06-01 07:00 | 2751 | 878.26 | 454 | 1240 | 1430.7692 | 0
2016-06-01 08:00 | 2751 | 933.64 | 629 | 1240 | 1440 | 0
2016-06-01 09:00 | 2751 | 947.302 | 667 | 1240 | 1238.9381 | 0
2016-06-01 10:00 | 2303 | 1016.652 | 701 | 1240 | 1238.9381 | 0
2016-06-01 11:00 | 2303 | 1078.345 | 643 | 1240 | 1238.9381 | 0
2016-06-01 12:00 | 2303 | 1253.364 | 612 | 1240 | 1296.2963 | 0
2016-06-01 13:00 | 2303 | 1374.208 | 687 | 1240 | 1040 | 0
2016-06-01 14:00 | 1871 | 1423.972 | 526 | 1240 | 1040 | 0
2016-06-01 15:00 | 1871 | 1444.498 | 457 | 1240 | 1040 | 0
2016-06-01 16:00 | 1871 | 1458.49 | 537 | 1240 | 1040 | 0
2016-06-01 17:00 | 1871 | 1447.732 | 506 | 1240 | 1040 | 0
2016-06-01 18:00 | 1938 | 1412.07 | 348 | 1240 | 1040 | 0
2016-06-01 19:00 | 1938 | 1361.316 | 348 | 1240 | 1040 | 0
2016-06-01 20:00 | 1938 | 1257.165 | 348 | 1240 | 1000 | 0
2016-06-01 21:00 | 1938 | 1221.822 | 360 | 1240 | 1296.2963 | 0
2016-06-01 22:00 | 2261 | 1022.124 | 348 | 1240 | 1440 | 0
2016-06-01 23:00 | 2261 | 974.24 | 348 | 1240 | 1430.7692 | 0
2016-06-02 | 2261 | 790.4 | 462 | 1240 | 1430.7692 | 0
2016-06-02 01:00 | 2261 | 784.14 | 378 | 1240 | 1430.7692 | 0
2016-06-02 02:00 | 2900 | 750.96 | 348 | 1240 | 1521.4286 | 0
2016-06-02 03:00 | 2900 | 731.76 | 363 | 1240 | 1521.4286 | 0
2016-06-02 04:00 | 2900 | 730.56 | 393 | 1240 | 1521.4286 | 0
2016-06-02 05:00 | 2900 | 759.1 | 498 | 1240 | 1521.4286 | 0
2016-06-02 06:00 | 2751 | 766.84 | 542 | 1240 | 1521.4286 | 0
2016-06-02 07:00 | 2751 | 798.57 | 454 | 1240 | 1521.4286 | 0
2016-06-02 08:00 | 2751 | 837.672 | 629 | 1240 | 1430.7692 | 0
2016-06-02 09:00 | 2751 | 933.42 | 667 | 1240 | 1440 | 0
2016-06-02 10:00 | 2303 | 944.851 | 701 | 1240 | 1440 | 0
2016-06-02 11:00 | 2303 | 1110.648 | 643 | 1240 | 1296.2963 | 0
2016-06-02 12:00 | 2303 | 1225.356 | 612 | 1240 | 1000 | 0
2016-06-02 13:00 | 2303 | 1285.108 | 687 | 1240 | 1040 | 0
2016-06-02 14:00 | 1871 | 1323.894 | 526 | 1240 | 1040 | 0
2016-06-02 15:00 | 1871 | 1342 | 457 | 1240 | 1040 | 0
2016-06-02 16:00 | 1871 | 1334.982 | 537 | 1240 | 1040 | 0
2016-06-02 17:00 | 1871 | 1298.66 | 506 | 1240 | 1040 | 0
2016-06-02 18:00 | 1938 | 1236.158 | 348 | 1240 | 1000 | 0
2016-06-02 19:00 | 1938 | 1120.287 | 348 | 1240 | 1296.2963 | 0
2016-06-02 20:00 | 1938 | 971.166 | 348 | 1240 | 1238.9381 | 0
2016-06-02 21:00 | 1938 | 974.56 | 360 | 1240 | 1440 | 0
2016-06-02 22:00 | 2261 | 912.2 | 348 | 1240 | 1430.7692 | 0
2016-06-02 23:00 | 2261 | 789.165 | 348 | 1240 | 1430.7692 | 0
2016-06-03 | 2261 | 819.08 | 462 | 1240 | 1430.7692 | 0
2016-06-03 01:00 | 2261 | 731.842 | 378 | 1240 | 1430.7692 | 0
2016-06-03 02:00 | 2900 | 698.25 | 348 | 1240 | 1430.7692 | 0
2016-06-03 03:00 | 2900 | 677.996 | 363 | 1240 | 1430.7692 | 0
2016-06-03 04:00 | 2900 | 677.749 | 393 | 1240 | 1430.7692 | 0
2016-06-03 05:00 | 2900 | 705.185 | 498 | 1240 | 1430.7692 | 0
2016-06-03 06:00 | 2751 | 793.9 | 542 | 1240 | 1430.7692 | 0
2016-06-03 07:00 | 2751 | 825.54 | 454 | 1240 | 1430.7692 | 0
2016-06-03 08:00 | 2751 | 858.42 | 629 | 1240 | 1440 | 0
2016-06-03 09:00 | 2751 | 859.579 | 667 | 1240 | 1440 | 0
2016-06-03 10:00 | 2303 | 905.502 | 701 | 1240 | 1238.9381 | 0
2016-06-03 11:00 | 2303 | 1049.223 | 643 | 1240 | 1238.9381 | 0
2016-06-03 12:00 | 2303 | 1081.689 | 612 | 1240 | 1296.2963 | 0
2016-06-03 13:00 | 2303 | 1099.77 | 687 | 1240 | 1000 | 0
2016-06-03 14:00 | 1871 | 1166.77 | 526 | 1240 | 1000 | 0
2016-06-03 15:00 | 1871 | 1180.124 | 457 | 1240 | 1000 | 0
2016-06-03 16:00 | 1871 | 1176.472 | 537 | 1240 | 1000 | 0
2016-06-03 17:00 | 1871 | 1107.96 | 506 | 1240 | 1000 | 0
2016-06-03 18:00 | 1938 | 1080.429 | 348 | 1240 | 1296.2963 | 0
2016-06-03 19:00 | 1938 | 1052.898 | 348 | 1240 | 1296.2963 | 0
2016-06-03 20:00 | 1938 | 951.178 | 348 | 1240 | 1238.9381 | 0
2016-06-03 21:00 | 1938 | 936.624 | 360 | 1240 | 1440 | 0
2016-06-03 22:00 | 2261 | 921.3 | 348 | 1240 | 1440 | 0
2016-06-03 23:00 | 2261 | 802.826 | 348 | 1240 | 1430.7692 | 0
2016-06-04 | 2261 | 756.485 | 462 | 1240 | 1430.7692 | 0
2016-06-04 01:00 | 2261 | 753.98 | 378 | 1240 | 1430.7692 | 0
2016-06-04 02:00 | 2900 | 724.96 | 348 | 1240 | 1430.7692 | 0
2016-06-04 03:00 | 2900 | 708.5 | 363 | 1240 | 1430.7692 | 0
2016-06-04 04:00 | 2900 | 714.02 | 393 | 1240 | 1430.7692 | 0
2016-06-04 05:00 | 2900 | 699.865 | 498 | 1240 | 1430.7692 | 0
2016-06-04 06:00 | 2751 | 744.724 | 542 | 1240 | 1430.7692 | 0
2016-06-04 07:00 | 2751 | 820.2 | 454 | 1240 | 1430.7692 | 0
2016-06-04 08:00 | 2751 | 873.48 | 629 | 1240 | 1440 | 0
2016-06-04 09:00 | 2751 | 885.248 | 667 | 1240 | 1238.9381 | 0
2016-06-04 10:00 | 2303 | 1049.601 | 701 | 1240 | 1296.2963 | 0
2016-06-04 11:00 | 2303 | 1125.768 | 643 | 1240 | 1000 | 0
2016-06-04 12:00 | 2303 | 1242.23 | 612 | 1240 | 1040 | 0
2016-06-04 13:00 | 2303 | 1306.954 | 687 | 1240 | 900 | 0
2016-06-04 14:00 | 1871 | 1362.46 | 526 | 1240 | 900 | 0
2016-06-04 15:00 | 1871 | 1405.646 | 457 | 1240 | 900 | 0
2016-06-04 16:00 | 1871 | 1426.7 | 537 | 1240 | 900 | 0
2016-06-04 17:00 | 1871 | 1416.14 | 506 | 1240 | 900 | 0
2016-06-04 18:00 | 1938 | 1366.618 | 348 | 1240 | 900 | 0
2016-06-04 19:00 | 1938 | 1317.096 | 348 | 1240 | 1040 | 0
2016-06-04 20:00 | 1938 | 1209.285 | 348 | 1240 | 1296.2963 | 0
2016-06-04 21:00 | 1938 | 1059.25 | 360 | 1240 | 1238.9381 | 0
2016-06-04 22:00 | 2261 | 1044.56 | 348 | 1240 | 1440 | 0
2016-06-04 23:00 | 2261 | 960.44 | 348 | 1240 | 1430.7692 | 0
2016-06-05 | 2261 | 873.924 | 462 | 1240 | 1430.7692 | 0
2016-06-05 01:00 | 2261 | 818.729 | 378 | 1240 | 1430.7692 | 0
2016-06-05 02:00 | 2900 | 779.437 | 348 | 1240 | 1430.7692 | 0
2016-06-05 03:00 | 2900 | 797.7 | 363 | 1240 | 1430.7692 | 0
2016-06-05 04:00 | 2900 | 783.58 | 393 | 1240 | 1430.7692 | 0
2016-06-05 05:00 | 2900 | 783.6 | 498 | 1240 | 1430.7692 | 0
2016-06-05 06:00 | 2751 | 791.08 | 542 | 1240 | 1430.7692 | 0
2016-06-05 07:00 | 2751 | 779.19 | 454 | 1240 | 1430.7692 | 0
2016-06-05 08:00 | 2751 | 893.96 | 629 | 1240 | 1430.7692 | 0
2016-06-05 09:00 | 2751 | 930.069 | 667 | 1240 | 1238.9381 | 0
2016-06-05 10:00 | 2303 | 1118.628 | 701 | 1240 | 1296.2963 | 0
2016-06-05 11:00 | 2303 | 1261.26 | 643 | 1240 | 1000 | 0
2016-06-05 12:00 | 2303 | 1325.984 | 612 | 1240 | 900 | 0
2016-06-05 13:00 | 2303 | 1382.04 | 687 | 1240 | 900 | 0
2016-06-05 14:00 | 1871 | 1428.834 | 526 | 1240 | 900 | 0
2016-06-05 15:00 | 1871 | 1443.794 | 457 | 1240 | 900 | 0
2016-06-05 16:00 | 1871 | 1458.27 | 537 | 1240 | 900 | 0
2016-06-05 17:00 | 1871 | 1451.01 | 506 | 1240 | 900 | 0
2016-06-05 18:00 | 1938 | 1421.42 | 348 | 1240 | 900 | 0
2016-06-05 19:00 | 1938 | 1376.694 | 348 | 1240 | 900 | 0
2016-06-05 20:00 | 1938 | 1331.066 | 348 | 1240 | 1040 | 0
2016-06-05 21:00 | 1938 | 1300.552 | 360 | 1240 | 1000 | 0
2016-06-05 22:00 | 2261 | 1172.724 | 348 | 1240 | 1296.2963 | 0
2016-06-05 23:00 | 2261 | 988.798 | 348 | 1240 | 1238.9381 | 0
2016-06-06 | 2261 | 972.08 | 462 | 1240 | 1440 | 0
2016-06-06 01:00 | 2261 | 918.76 | 378 | 1240 | 1440 | 0
2016-06-06 02:00 | 2900 | 836.513 | 348 | 1240 | 1440 | 0
2016-06-06 03:00 | 2900 | 811.452 | 363 | 1240 | 1440 | 0
2016-06-06 04:00 | 2900 | 795.397 | 393 | 1240 | 1440 | 0
2016-06-06 05:00 | 2900 | 790.704 | 498 | 1240 | 1440 | 0
2016-06-06 06:00 | 2751 | 829.44 | 542 | 1240 | 1440 | 0
2016-06-06 07:00 | 2751 | 840.78 | 454 | 1240 | 1440 | 0
2016-06-06 08:00 | 2751 | 857.356 | 629 | 1240 | 1440 | 0
2016-06-06 09:00 | 2751 | 929.309 | 667 | 1240 | 1238.9381 | 0
2016-06-06 10:00 | 2303 | 1116.948 | 701 | 1240 | 1000 | 0
2016-06-06 11:00 | 2303 | 1257.014 | 643 | 1240 | 1040 | 0
2016-06-06 12:00 | 2303 | 1333.068 | 612 | 1240 | 1040 | 0
2016-06-06 13:00 | 2303 | 1394.14 | 687 | 1240 | 1040 | 0
2016-06-06 14:00 | 1871 | 1426.48 | 526 | 1240 | 900 | 0
2016-06-06 15:00 | 1871 | 1460.338 | 457 | 1240 | 900 | 0
2016-06-06 16:00 | 1871 | 1474.946 | 537 | 1240 | 900 | 0
2016-06-06 17:00 | 1871 | 1457.83 | 506 | 1240 | 900 | 0
2016-06-06 18:00 | 1938 | 1432.31 | 348 | 1240 | 1040 | 0
2016-06-06 19:00 | 1938 | 1391.654 | 348 | 1240 | 1040 | 0
2016-06-06 20:00 | 1938 | 1356.85 | 348 | 1240 | 1000 | 0
2016-06-06 21:00 | 1938 | 1268.568 | 360 | 1240 | 1000 | 0
2016-06-06 22:00 | 2261 | 1191.141 | 348 | 1240 | 1238.9381 | 0
2016-06-06 23:00 | 2261 | 990.033 | 348 | 1240 | 1238.9381 | 0
2016-06-07 | 2261 | 918.6 | 462 | 1240 | 1440 | 0
2016-06-07 01:00 | 2261 | 868.68 | 378 | 1240 | 1440 | 0
2016-06-07 02:00 | 2900 | 793.972 | 348 | 1240 | 1440 | 0
2016-06-07 03:00 | 2900 | 775.2 | 363 | 1240 | 1440 | 0
2016-06-07 04:00 | 2900 | 774.459 | 393 | 1240 | 1440 | 0
2016-06-07 05:00 | 2900 | 842.36 | 498 | 1240 | 1440 | 0
2016-06-07 06:00 | 2751 | 885.3 | 542 | 1240 | 1440 | 0
2016-06-07 07:00 | 2751 | 875.729 | 454 | 1240 | 1238.9381 | 0
2016-06-07 08:00 | 2751 | 926.896 | 629 | 1240 | 1238.9381 | 0
2016-06-07 09:00 | 2751 | 1089.606 | 667 | 1240 | 1296.2963 | 0
2016-06-07 10:00 | 2303 | 1214.752 | 701 | 1240 | 1000 | 0
2016-06-07 11:00 | 2303 | 1280.092 | 643 | 1240 | 1040 | 0
2016-06-07 12:00 | 2303 | 1341.23 | 612 | 1240 | 900 | 0
2016-06-07 13:00 | 2303 | 1386.396 | 687 | 1240 | 900 | 0
2016-06-07 14:00 | 1871 | 1409.496 | 526 | 1240 | 900 | 0
2016-06-07 15:00 | 1871 | 1421.728 | 457 | 1240 | 900 | 0
2016-06-07 16:00 | 1871 | 1419.44 | 537 | 1240 | 900 | 0
2016-06-07 17:00 | 1871 | 1411.982 | 506 | 1240 | 900 | 0
2016-06-07 18:00 | 1938 | 1374.428 | 348 | 1240 | 900 | 0
2016-06-07 19:00 | 1938 | 1336.874 | 348 | 1240 | 1000 | 0
2016-06-07 20:00 | 1938 | 1246.392 | 348 | 1240 | 1296.2963 | 0
2016-06-07 21:00 | 1938 | 1219.386 | 360 | 1240 | 1238.9381 | 0
2016-06-07 22:00 | 2261 | 1032.308 | 348 | 1240 | 1440 | 0
2016-06-07 23:00 | 2261 | 999.06 | 348 | 1240 | 1440 | 0
2016-06-08 | 2261 | 931.76 | 462 | 1240 | 1430.7692 | 0
2016-06-08 01:00 | 2261 | 837.083 | 378 | 1240 | 1430.7692 | 0
2016-06-08 02:00 | 2900 | 802.883 | 348 | 1240 | 1430.7692 | 0
2016-06-08 03:00 | 2900 | 821.84 | 363 | 1240 | 1430.7692 | 0
2016-06-08 04:00 | 2900 | 815.82 | 393 | 1240 | 1430.7692 | 0
2016-06-08 05:00 | 2900 | 798.494 | 498 | 1240 | 1430.7692 | 0
2016-06-08 06:00 | 2751 | 838.793 | 542 | 1240 | 1430.7692 | 0
2016-06-08 07:00 | 2751 | 914.8 | 454 | 1240 | 1430.7692 | 0
2016-06-08 08:00 | 2751 | 910.537 | 629 | 1240 | 1440 | 0
2016-06-08 09:00 | 2751 | 962.141 | 667 | 1240 | 1238.9381 | 0
2016-06-08 10:00 | 2303 | 1010.496 | 701 | 1240 | 1238.9381 | 0
2016-06-08 11:00 | 2303 | 1031.624 | 643 | 1240 | 1296.2963 | 0
2016-06-08 12:00 | 2303 | 1165.29 | 612 | 1240 | 1296.2963 | 0
2016-06-08 13:00 | 2303 | 1197.084 | 687 | 1240 | 1000 | 0
2016-06-08 14:00 | 1871 | 1286.494 | 526 | 1240 | 1040 | 0
2016-06-08 15:00 | 1871 | 1314.61 | 457 | 1240 | 1040 | 0
2016-06-08 16:00 | 1871 | 1333.42 | 537 | 1240 | 1040 | 0
2016-06-08 17:00 | 1871 | 1325.852 | 506 | 1240 | 1040 | 0
2016-06-08 18:00 | 1938 | 1280.114 | 348 | 1240 | 1000 | 0
2016-06-08 19:00 | 1938 | 1178.289 | 348 | 1240 | 1000 | 0
2016-06-08 20:00 | 1938 | 1041.124 | 348 | 1240 | 1296.2963 | 0
2016-06-08 21:00 | 1938 | 1025.202 | 360 | 1240 | 1238.9381 | 0
2016-06-08 22:00 | 2261 | 1008.22 | 348 | 1240 | 1238.9381 | 0
2016-06-08 23:00 | 2261 | 883.405 | 348 | 1240 | 1430.7692 | 0
2016-06-09 | 2261 | 812.76 | 462 | 1240 | 1430.7692 | 0
2016-06-09 01:00 | 2261 | 772.96 | 378 | 1240 | 1430.7692 | 0
2016-06-09 02:00 | 2900 | 747.28 | 348 | 1240 | 1430.7692 | 0
2016-06-09 03:00 | 2900 | 733.88 | 363 | 1240 | 1430.7692 | 0
2016-06-09 04:00 | 2900 | 737.2 | 393 | 1240 | 1430.7692 | 0
2016-06-09 05:00 | 2900 | 729.22 | 498 | 1240 | 1430.7692 | 0
2016-06-09 06:00 | 2751 | 775.029 | 542 | 1240 | 1430.7692 | 0
2016-06-09 07:00 | 2751 | 805.752 | 454 | 1240 | 1430.7692 | 0
2016-06-09 08:00 | 2751 | 888.24 | 629 | 1240 | 1430.7692 | 0
2016-06-09 09:00 | 2751 | 932.34 | 667 | 1240 | 1440 | 0
2016-06-09 10:00 | 2303 | 932.368 | 701 | 1240 | 1440 | 0
2016-06-09 11:00 | 2303 | 974.757 | 643 | 1240 | 1238.9381 | 0
2016-06-09 12:00 | 2303 | 1006.107 | 612 | 1240 | 1238.9381 | 0
2016-06-09 13:00 | 2303 | 1134.126 | 687 | 1240 | 1296.2963 | 0
2016-06-09 14:00 | 1871 | 1149.54 | 526 | 1240 | 1296.2963 | 0
2016-06-09 15:00 | 1871 | 1161.258 | 457 | 1240 | 1296.2963 | 0
2016-06-09 16:00 | 1871 | 1168.608 | 537 | 1240 | 1296.2963 | 0
2016-06-09 17:00 | 1871 | 1163.295 | 506 | 1240 | 1296.2963 | 0
2016-06-09 18:00 | 1938 | 1131.816 | 348 | 1240 | 1296.2963 | 0
2016-06-09 19:00 | 1938 | 995.543 | 348 | 1240 | 1238.9381 | 0
2016-06-09 20:00 | 1938 | 980.229 | 348 | 1240 | 1238.9381 | 0
2016-06-09 21:00 | 1938 | 967.081 | 360 | 1240 | 1440 | 0
2016-06-09 22:00 | 2261 | 959.78 | 348 | 1240 | 1430.7692 | 0
2016-06-09 23:00 | 2261 | 843.809 | 348 | 1240 | 1430.7692 | 0
2016-06-10 | 2261 | 781.052 | 462 | 1240 | 1430.7692 | 0
2016-06-10 01:00 | 2261 | 782.92 | 378 | 1240 | 1430.7692 | 0
2016-06-10 02:00 | 2900 | 759.72 | 348 | 1240 | 1430.7692 | 0
2016-06-10 03:00 | 2900 | 748.22 | 363 | 1240 | 1430.7692 | 0
2016-06-10 04:00 | 2900 | 749.92 | 393 | 1240 | 1430.7692 | 0
2016-06-10 05:00 | 2900 | 739.67 | 498 | 1240 | 1430.7692 | 0
2016-06-10 06:00 | 2751 | 785.574 | 542 | 1240 | 1430.7692 | 0
2016-06-10 07:00 | 2751 | 812.136 | 454 | 1240 | 1430.7692 | 0
2016-06-10 08:00 | 2751 | 845.5 | 629 | 1240 | 1430.7692 | 0
2016-06-10 09:00 | 2751 | 888.193 | 667 | 1240 | 1430.7692 | 0
2016-06-10 10:00 | 2303 | 986.56 | 701 | 1240 | 1430.7692 | 0
2016-06-10 11:00 | 2303 | 1042.16 | 643 | 1240 | 1440 | 0
2016-06-10 12:00 | 2303 | 1033.258 | 612 | 1240 | 1440 | 0
2016-06-10 13:00 | 2303 | 1077.927 | 687 | 1240 | 1238.9381 | 0
2016-06-10 14:00 | 1871 | 1233.477 | 526 | 1240 | 1296.2963 | 0
2016-06-10 15:00 | 1871 | 1264.662 | 457 | 1240 | 1296.2963 | 0
2016-06-10 16:00 | 1871 | 1280.37 | 537 | 1240 | 1296.2963 | 0
2016-06-10 17:00 | 1871 | 1272.999 | 506 | 1240 | 1296.2963 | 0
2016-06-10 18:00 | 1938 | 1233.456 | 348 | 1240 | 1296.2963 | 0
2016-06-10 19:00 | 1938 | 1080.188 | 348 | 1240 | 1238.9381 | 0
2016-06-10 20:00 | 1938 | 1050.624 | 348 | 1240 | 1238.9381 | 0
2016-06-10 21:00 | 1938 | 1085.98 | 360 | 1240 | 1440 | 0
2016-06-10 22:00 | 2261 | 969.038 | 348 | 1240 | 1430.7692 | 0
2016-06-10 23:00 | 2261 | 893.456 | 348 | 1240 | 1430.7692 | 0
2016-06-11 | 2261 | 884.469 | 462 | 1240 | 1521.4286 | 0
2016-06-11 01:00 | 2261 | 884.56 | 378 | 1240 | 1521.4286 | 0
2016-06-11 02:00 | 2900 | 854.02 | 348 | 1240 | 1521.4286 | 0
2016-06-11 03:00 | 2900 | 838.62 | 363 | 1240 | 1521.4286 | 0
2016-06-11 04:00 | 2900 | 837.4 | 393 | 1240 | 1521.4286 | 0
2016-06-11 05:00 | 2900 | 865.7 | 498 | 1240 | 1521.4286 | 0
2016-06-11 06:00 | 2751 | 861.175 | 542 | 1240 | 1521.4286 | 0
2016-06-11 07:00 | 2751 | 890.055 | 454 | 1240 | 1430.7692 | 0
2016-06-11 08:00 | 2751 | 984.68 | 629 | 1240 | 1430.7692 | 0
2016-06-11 09:00 | 2751 | 1037.46 | 667 | 1240 | 1430.7692 | 0
2016-06-11 10:00 | 2303 | 1098.64 | 701 | 1240 | 1440 | 0
2016-06-11 11:00 | 2303 | 1097.725 | 643 | 1240 | 1440 | 0
2016-06-11 12:00 | 2303 | 1258.719 | 612 | 1240 | 1296.2963 | 0
2016-06-11 13:00 | 2303 | 1303.89 | 687 | 1240 | 1000 | 0
2016-06-11 14:00 | 1871 | 1402.456 | 526 | 1240 | 1000 | 0
2016-06-11 15:00 | 1871 | 1424.588 | 457 | 1240 | 1000 | 0
2016-06-11 16:00 | 1871 | 1420.034 | 537 | 1240 | 1000 | 0
2016-06-11 17:00 | 1871 | 1421.772 | 506 | 1240 | 1000 | 0
2016-06-11 18:00 | 1938 | 1308.972 | 348 | 1240 | 1000 | 0
2016-06-11 19:00 | 1938 | 1140.703 | 348 | 1240 | 1238.9381 | 0
2016-06-11 20:00 | 1938 | 1108.27 | 348 | 1240 | 1440 | 0
2016-06-11 21:00 | 1938 | 1091.721 | 360 | 1240 | 1440 | 0
2016-06-11 22:00 | 2261 | 1090.12 | 348 | 1240 | 1430.7692 | 0
2016-06-11 23:00 | 2261 | 969.285 | 348 | 1240 | 1430.7692 | 0
2016-06-12 | 2261 | 942.837 | 462 | 1240 | 1521.4286 | 0
2016-06-12 01:00 | 2261 | 897.541 | 378 | 1240 | 1521.4286 | 0
2016-06-12 02:00 | 2900 | 908.3 | 348 | 1240 | 1521.4286 | 0
2016-06-12 03:00 | 2900 | 887.74 | 363 | 1240 | 1521.4286 | 0
2016-06-12 04:00 | 2900 | 878.4 | 393 | 1240 | 1521.4286 | 0
2016-06-12 05:00 | 2900 | 881.34 | 498 | 1240 | 1521.4286 | 0
2016-06-12 06:00 | 2751 | 841.054 | 542 | 1240 | 1521.4286 | 0
2016-06-12 07:00 | 2751 | 865.222 | 454 | 1240 | 1521.4286 | 0
2016-06-12 08:00 | 2751 | 926.041 | 629 | 1240 | 1430.7692 | 0
2016-06-12 09:00 | 2751 | 987.981 | 667 | 1240 | 1430.7692 | 0
2016-06-12 10:00 | 2303 | 1110.72 | 701 | 1240 | 1440 | 0
2016-06-12 11:00 | 2303 | 1170.18 | 643 | 1240 | 1440 | 0
2016-06-12 12:00 | 2303 | 1153.224 | 612 | 1240 | 1238.9381 | 0
2016-06-12 13:00 | 2303 | 1183.225 | 687 | 1240 | 1238.9381 | 0
2016-06-12 14:00 | 1871 | 1339.296 | 526 | 1240 | 1296.2963 | 0
2016-06-12 15:00 | 1871 | 1364.601 | 457 | 1240 | 1296.2963 | 0
2016-06-12 16:00 | 1871 | 1364.727 | 537 | 1240 | 1296.2963 | 0
2016-06-12 17:00 | 1871 | 1363.782 | 506 | 1240 | 1296.2963 | 0
2016-06-12 18:00 | 1938 | 1343.937 | 348 | 1240 | 1296.2963 | 0
2016-06-12 19:00 | 1938 | 1184.935 | 348 | 1240 | 1296.2963 | 0
2016-06-12 20:00 | 1938 | 1152.198 | 348 | 1240 | 1238.9381 | 0
2016-06-12 21:00 | 1938 | 1132.362 | 360 | 1240 | 1238.9381 | 0
2016-06-12 22:00 | 2261 | 1132.54 | 348 | 1240 | 1440 | 0
2016-06-12 23:00 | 2261 | 1064.56 | 348 | 1240 | 1430.7692 | 0
2016-06-13 | 2261 | 964.763 | 462 | 1240 | 1430.7692 | 0
2016-06-13 01:00 | 2261 | 919.695 | 378 | 1240 | 1430.7692 | 0
2016-06-13 02:00 | 2900 | 932.18 | 348 | 1240 | 1430.7692 | 0
2016-06-13 03:00 | 2900 | 907.14 | 363 | 1240 | 1430.7692 | 0
2016-06-13 04:00 | 2900 | 890.2 | 393 | 1240 | 1430.7692 | 0
2016-06-13 05:00 | 2900 | 882.8 | 498 | 1240 | 1430.7692 | 0
2016-06-13 06:00 | 2751 | 875.48 | 542 | 1240 | 1430.7692 | 0
2016-06-13 07:00 | 2751 | 844.075 | 454 | 1240 | 1430.7692 | 0
2016-06-13 08:00 | 2751 | 948.64 | 629 | 1240 | 1430.7692 | 0
2016-06-13 09:00 | 2751 | 975.194 | 667 | 1240 | 1440 | 0
2016-06-13 10:00 | 2303 | 1040.972 | 701 | 1240 | 1238.9381 | 0
2016-06-13 11:00 | 2303 | 1098.732 | 643 | 1240 | 1238.9381 | 0
2016-06-13 12:00 | 2303 | 1277.85 | 612 | 1240 | 1296.2963 | 0
2016-06-13 13:00 | 2303 | 1327.704 | 687 | 1240 | 1000 | 0
2016-06-13 14:00 | 1871 | 1419.154 | 526 | 1240 | 1040 | 0
2016-06-13 15:00 | 1871 | 1447.204 | 457 | 1240 | 1040 | 0
2016-06-13 16:00 | 1871 | 1465.244 | 537 | 1240 | 1040 | 0
2016-06-13 17:00 | 1871 | 1463.088 | 506 | 1240 | 1040 | 0
2016-06-13 18:00 | 1938 | 1426.876 | 348 | 1240 | 1040 | 0
2016-06-13 19:00 | 1938 | 1405.8 | 348 | 1240 | 1040 | 0
2016-06-13 20:00 | 1938 | 1365.914 | 348 | 1240 | 1040 | 0
2016-06-13 21:00 | 1938 | 1341.23 | 360 | 1240 | 1040 | 0
2016-06-13 22:00 | 2261 | 1207.857 | 348 | 1240 | 1000 | 0
2016-06-13 23:00 | 2261 | 1005.898 | 348 | 1240 | 1238.9381 | 0
2016-06-14 | 2261 | 938.1 | 462 | 1240 | 1440 | 0
2016-06-14 01:00 | 2261 | 849.699 | 378 | 1240 | 1440 | 0
2016-06-14 02:00 | 2900 | 864.28 | 348 | 1240 | 1440 | 0
2016-06-14 03:00 | 2900 | 846.28 | 363 | 1240 | 1440 | 0
2016-06-14 04:00 | 2900 | 845.26 | 393 | 1240 | 1440 | 0
2016-06-14 05:00 | 2900 | 871.04 | 498 | 1240 | 1440 | 0
2016-06-14 06:00 | 2751 | 906.98 | 542 | 1240 | 1440 | 0
2016-06-14 07:00 | 2751 | 943.9 | 454 | 1240 | 1440 | 0
2016-06-14 08:00 | 2751 | 949.943 | 629 | 1240 | 1238.9381 | 0
2016-06-14 09:00 | 2751 | 1010.42 | 667 | 1240 | 1238.9381 | 0
2016-06-14 10:00 | 2303 | 1075.343 | 701 | 1240 | 1296.2963 | 0
2016-06-14 11:00 | 2303 | 1258.572 | 643 | 1240 | 1000 | 0
2016-06-14 12:00 | 2303 | 1375.528 | 612 | 1240 | 1040 | 0
2016-06-14 13:00 | 2303 | 1428.944 | 687 | 1240 | 900 | 0
2016-06-14 14:00 | 1871 | 1453.562 | 526 | 1240 | 900 | 0
2016-06-14 15:00 | 1871 | 1477.674 | 457 | 1240 | 900 | 0
2016-06-14 16:00 | 1871 | 1490.148 | 537 | 1240 | 900 | 0
2016-06-14 17:00 | 1871 | 1475.254 | 506 | 1240 | 900 | 0
2016-06-14 18:00 | 1938 | 1423.73 | 348 | 1240 | 900 | 0
2016-06-14 19:00 | 1938 | 1387.32 | 348 | 1240 | 900 | 0
2016-06-14 20:00 | 1938 | 1338.656 | 348 | 1240 | 1040 | 0
2016-06-14 21:00 | 1938 | 1305.59 | 360 | 1240 | 1040 | 0
2016-06-14 22:00 | 2261 | 1163.757 | 348 | 1240 | 1296.2963 | 0
2016-06-14 23:00 | 2261 | 961.438 | 348 | 1240 | 1238.9381 | 0
2016-06-15 | 2261 | 937.76 | 462 | 1240 | 1440 | 0
2016-06-15 01:00 | 2261 | 887.54 | 378 | 1240 | 1440 | 0
2016-06-15 02:00 | 2900 | 801.439 | 348 | 1240 | 1440 | 0
2016-06-15 03:00 | 2900 | 774.611 | 363 | 1240 | 1440 | 0
2016-06-15 04:00 | 2900 | 766.574 | 393 | 1240 | 1440 | 0
2016-06-15 05:00 | 2900 | 788.994 | 498 | 1240 | 1440 | 0
2016-06-15 06:00 | 2751 | 867.5 | 542 | 1240 | 1440 | 0
2016-06-15 07:00 | 2751 | 901.22 | 454 | 1240 | 1440 | 0
2016-06-15 08:00 | 2751 | 954.52 | 629 | 1240 | 1440 | 0
2016-06-15 09:00 | 2751 | 962.084 | 667 | 1240 | 1238.9381 | 0
2016-06-15 10:00 | 2303 | 1132.551 | 701 | 1240 | 1296.2963 | 0
2016-06-15 11:00 | 2303 | 1202.376 | 643 | 1240 | 1296.2963 | 0
2016-06-15 12:00 | 2303 | 1245.468 | 612 | 1240 | 1000 | 0
2016-06-15 13:00 | 2303 | 1357.07 | 687 | 1240 | 1040 | 0
2016-06-15 14:00 | 1871 | 1401.686 | 526 | 1240 | 1040 | 0
2016-06-15 15:00 | 1871 | 1418.494 | 457 | 1240 | 1040 | 0
2016-06-15 16:00 | 1871 | 1438.272 | 537 | 1240 | 1040 | 0
2016-06-15 17:00 | 1871 | 1432.904 | 506 | 1240 | 1040 | 0
2016-06-15 18:00 | 1938 | 1411.014 | 348 | 1240 | 1040 | 0
2016-06-15 19:00 | 1938 | 1373.988 | 348 | 1240 | 1040 | 0
2016-06-15 20:00 | 1938 | 1268.358 | 348 | 1240 | 1000 | 0
2016-06-15 21:00 | 1938 | 1235.556 | 360 | 1240 | 1296.2963 | 0
2016-06-15 22:00 | 2261 | 1042.264 | 348 | 1240 | 1238.9381 | 0
2016-06-15 23:00 | 2261 | 1004.8 | 348 | 1240 | 1440 | 0
2016-06-16 | 2261 | 841.111 | 462 | 1240 | 1430.7692 | 0
2016-06-16 01:00 | 2261 | 797.392 | 378 | 1240 | 1430.7692 | 0
2016-06-16 02:00 | 2900 | 805.92 | 348 | 1240 | 1430.7692 | 0
2016-06-16 03:00 | 2900 | 786.7 | 363 | 1240 | 1430.7692 | 0
2016-06-16 04:00 | 2900 | 784 | 393 | 1240 | 1430.7692 | 0
2016-06-16 05:00 | 2900 | 769.006 | 498 | 1240 | 1430.7692 | 0
2016-06-16 06:00 | 2751 | 803.206 | 542 | 1240 | 1430.7692 | 0
2016-06-16 07:00 | 2751 | 882.86 | 454 | 1240 | 1430.7692 | 0
2016-06-16 08:00 | 2751 | 937.08 | 629 | 1240 | 1440 | 0
2016-06-16 09:00 | 2751 | 1003.62 | 667 | 1240 | 1440 | 0
2016-06-16 10:00 | 2303 | 1021.231 | 701 | 1240 | 1238.9381 | 0
2016-06-16 11:00 | 2303 | 1081.993 | 643 | 1240 | 1238.9381 | 0
2016-06-16 12:00 | 2303 | 1252.86 | 612 | 1240 | 1296.2963 | 0
2016-06-16 13:00 | 2303 | 1304.919 | 687 | 1240 | 1000 | 0
2016-06-16 14:00 | 1871 | 1406.306 | 526 | 1240 | 1000 | 0
2016-06-16 15:00 | 1871 | 1420.232 | 457 | 1240 | 1000 | 0
2016-06-16 16:00 | 1871 | 1423.532 | 537 | 1240 | 1000 | 0
2016-06-16 17:00 | 1871 | 1412.092 | 506 | 1240 | 1040 | 0
2016-06-16 18:00 | 1938 | 1370.864 | 348 | 1240 | 1000 | 0
2016-06-16 19:00 | 1938 | 1269.177 | 348 | 1240 | 1296.2963 | 0
2016-06-16 20:00 | 1938 | 1106.598 | 348 | 1240 | 1238.9381 | 0
2016-06-16 21:00 | 1938 | 1082.658 | 360 | 1240 | 1440 | 0
2016-06-16 22:00 | 2261 | 1065.82 | 348 | 1240 | 1440 | 0
2016-06-16 23:00 | 2261 | 971.28 | 348 | 1240 | 1430.7692 | 0
2016-06-17 | 2261 | 858.268 | 462 | 1240 | 1430.7692 | 0
2016-06-17 01:00 | 2261 | 809.78 | 378 | 1240 | 1430.7692 | 0
2016-06-17 02:00 | 2900 | 816.36 | 348 | 1240 | 1430.7692 | 0
2016-06-17 03:00 | 2900 | 793.8 | 363 | 1240 | 1430.7692 | 0
2016-06-17 04:00 | 2900 | 789.44 | 393 | 1240 | 1430.7692 | 0
2016-06-17 05:00 | 2900 | 810.62 | 498 | 1240 | 1430.7692 | 0
2016-06-17 06:00 | 2751 | 802.465 | 542 | 1240 | 1430.7692 | 0
2016-06-17 07:00 | 2751 | 834.613 | 454 | 1240 | 1430.7692 | 0
2016-06-17 08:00 | 2751 | 892.848 | 629 | 1240 | 1430.7692 | 0
2016-06-17 09:00 | 2751 | 1004.16 | 667 | 1240 | 1430.7692 | 0
2016-06-17 10:00 | 2303 | 1074.42 | 701 | 1240 | 1440 | 0
2016-06-17 11:00 | 2303 | 1081.518 | 643 | 1240 | 1440 | 0
2016-06-17 12:00 | 2303 | 1134.984 | 612 | 1240 | 1238.9381 | 0
2016-06-17 13:00 | 2303 | 1362.372 | 687 | 1240 | 1000 | 0
2016-06-17 14:00 | 1871 | 1394.294 | 526 | 1240 | 1040 | 0
2016-06-17 15:00 | 1871 | 1412.356 | 457 | 1240 | 1040 | 0
2016-06-17 16:00 | 1871 | 1418.142 | 537 | 1240 | 1040 | 0
2016-06-17 17:00 | 1871 | 1410.53 | 506 | 1240 | 1040 | 0
2016-06-17 18:00 | 1938 | 1303.386 | 348 | 1240 | 1000 | 0
2016-06-17 19:00 | 1938 | 1260.357 | 348 | 1240 | 1296.2963 | 0
2016-06-17 20:00 | 1938 | 1103.14 | 348 | 1240 | 1238.9381 | 0
2016-06-17 21:00 | 1938 | 1079.067 | 360 | 1240 | 1440 | 0
2016-06-17 22:00 | 2261 | 1060.06 | 348 | 1240 | 1440 | 0
2016-06-17 23:00 | 2261 | 931.456 | 348 | 1240 | 1430.7692 | 0
2016-06-18 | 2261 | 903.545 | 462 | 1240 | 1430.7692 | 0
2016-06-18 01:00 | 2261 | 854.582 | 378 | 1240 | 1430.7692 | 0
2016-06-18 02:00 | 2900 | 865.84 | 348 | 1240 | 1430.7692 | 0
2016-06-18 03:00 | 2900 | 845.16 | 363 | 1240 | 1430.7692 | 0
2016-06-18 04:00 | 2900 | 839.62 | 393 | 1240 | 1430.7692 | 0
2016-06-18 05:00 | 2900 | 819.185 | 498 | 1240 | 1430.7692 | 0
2016-06-18 06:00 | 2751 | 848.825 | 542 | 1240 | 1430.7692 | 0
2016-06-18 07:00 | 2751 | 884.146 | 454 | 1240 | 1430.7692 | 0
2016-06-18 08:00 | 2751 | 993.88 | 629 | 1240 | 1430.7692 | 0
2016-06-18 09:00 | 2751 | 1061.2 | 667 | 1240 | 1440 | 0
2016-06-18 10:00 | 2303 | 1077.889 | 701 | 1240 | 1238.9381 | 0
2016-06-18 11:00 | 2303 | 1256.493 | 643 | 1240 | 1296.2963 | 0
2016-06-18 12:00 | 2303 | 1380.94 | 612 | 1240 | 1040 | 0
2016-06-18 13:00 | 2303 | 1420.672 | 687 | 1240 | 900 | 0
2016-06-18 14:00 | 1871 | 1458.16 | 526 | 1240 | 900 | 0
2016-06-18 15:00 | 1871 | 1482.712 | 457 | 1240 | 900 | 0
2016-06-18 16:00 | 1871 | 1487.266 | 537 | 1240 | 900 | 0
2016-06-18 17:00 | 1871 | 1473.956 | 506 | 1240 | 900 | 0
2016-06-18 18:00 | 1938 | 1421.904 | 348 | 1240 | 1040 | 0
2016-06-18 19:00 | 1938 | 1384.966 | 348 | 1240 | 1000 | 0
2016-06-18 20:00 | 1938 | 1276.989 | 348 | 1240 | 1296.2963 | 0
2016-06-18 21:00 | 1938 | 1129.55 | 360 | 1240 | 1238.9381 | 0
2016-06-18 22:00 | 2261 | 1066.66 | 348 | 1240 | 1440 | 0
2016-06-18 23:00 | 2261 | 1041.36 | 348 | 1240 | 1430.7692 | 0
2016-06-19 | 2261 | 1005.5 | 462 | 1240 | 1430.7692 | 0
2016-06-19 01:00 | 2261 | 901.436 | 378 | 1240 | 1430.7692 | 0
2016-06-19 02:00 | 2900 | 866.932 | 348 | 1240 | 1430.7692 | 0
2016-06-19 03:00 | 2900 | 840.18 | 363 | 1240 | 1430.7692 | 0
2016-06-19 04:00 | 2900 | 824.087 | 393 | 1240 | 1430.7692 | 0
2016-06-19 05:00 | 2900 | 821.731 | 498 | 1240 | 1430.7692 | 0
2016-06-19 06:00 | 2751 | 817.437 | 542 | 1240 | 1430.7692 | 0
2016-06-19 07:00 | 2751 | 840.256 | 454 | 1240 | 1430.7692 | 0
2016-06-19 08:00 | 2751 | 954 | 629 | 1240 | 1430.7692 | 0
2016-06-19 09:00 | 2751 | 977.854 | 667 | 1240 | 1238.9381 | 0
2016-06-19 10:00 | 2303 | 1163.526 | 701 | 1240 | 1296.2963 | 0
2016-06-19 11:00 | 2303 | 1299.76 | 643 | 1240 | 1000 | 0
2016-06-19 12:00 | 2303 | 1366.992 | 612 | 1240 | 1040 | 0
2016-06-19 13:00 | 2303 | 1417.46 | 687 | 1240 | 900 | 0
2016-06-19 14:00 | 1871 | 1442.628 | 526 | 1240 | 900 | 0
2016-06-19 15:00 | 1871 | 1471.206 | 457 | 1240 | 900 | 0
2016-06-19 16:00 | 1871 | 1487.904 | 537 | 1240 | 900 | 0
2016-06-19 17:00 | 1871 | 1479.72 | 506 | 1240 | 900 | 0
2016-06-19 18:00 | 1938 | 1438.91 | 348 | 1240 | 900 | 0
2016-06-19 19:00 | 1938 | 1413.214 | 348 | 1240 | 1040 | 0
2016-06-19 20:00 | 1938 | 1299.627 | 348 | 1240 | 1296.2963 | 0
2016-06-19 21:00 | 1938 | 1266.216 | 360 | 1240 | 1296.2963 | 0
2016-06-19 22:00 | 2261 | 1079.067 | 348 | 1240 | 1238.9381 | 0
2016-06-19 23:00 | 2261 | 1004.074 | 348 | 1240 | 1440 | 0
2016-06-20 | 2261 | 1010.44 | 462 | 1240 | 1440 | 0
2016-06-20 01:00 | 2261 | 953.76 | 378 | 1240 | 1440 | 0
2016-06-20 02:00 | 2900 | 862.581 | 348 | 1240 | 1440 | 0
2016-06-20 03:00 | 2900 | 830.49 | 363 | 1240 | 1440 | 0
2016-06-20 04:00 | 2900 | 808.982 | 393 | 1240 | 1440 | 0
2016-06-20 05:00 | 2900 | 800.147 | 498 | 1240 | 1440 | 0
2016-06-20 06:00 | 2751 | 791.046 | 542 | 1240 | 1440 | 0
2016-06-20 07:00 | 2751 | 812.288 | 454 | 1240 | 1440 | 0
2016-06-20 08:00 | 2751 | 933.9 | 629 | 1240 | 1440 | 0
2016-06-20 09:00 | 2751 | 963.661 | 667 | 1240 | 1238.9381 | 0
2016-06-20 10:00 | 2303 | 1149.477 | 701 | 1240 | 1296.2963 | 0
2016-06-20 11:00 | 2303 | 1227.975 | 643 | 1240 | 1000 | 0
2016-06-20 12:00 | 2303 | 1357.224 | 612 | 1240 | 1040 | 0
2016-06-20 13:00 | 2303 | 1412.664 | 687 | 1240 | 1040 | 0
2016-06-20 14:00 | 1871 | 1442.408 | 526 | 1240 | 1040 | 0
2016-06-20 15:00 | 1871 | 1475.694 | 457 | 1240 | 1040 | 0
2016-06-20 16:00 | 1871 | 1495.494 | 537 | 1240 | 1040 | 0
2016-06-20 17:00 | 1871 | 1494.922 | 506 | 1240 | 1040 | 0
2016-06-20 18:00 | 1938 | 1455.916 | 348 | 1240 | 1040 | 0
2016-06-20 19:00 | 1938 | 1432.002 | 348 | 1240 | 1000 | 0
2016-06-20 20:00 | 1938 | 1323.714 | 348 | 1240 | 1296.2963 | 0
2016-06-20 21:00 | 1938 | 1298.409 | 360 | 1240 | 1296.2963 | 0
2016-06-20 22:00 | 2261 | 1103.292 | 348 | 1240 | 1238.9381 | 0
2016-06-20 23:00 | 2261 | 1012.7 | 348 | 1240 | 1440 | 0
2016-06-21 | 2261 | 936.08 | 462 | 1240 | 1430.7692 | 0
2016-06-21 01:00 | 2261 | 841.035 | 378 | 1240 | 1430.7692 | 0
2016-06-21 02:00 | 2900 | 810.806 | 348 | 1240 | 1430.7692 | 0
2016-06-21 03:00 | 2900 | 790.856 | 363 | 1240 | 1430.7692 | 0
2016-06-21 04:00 | 2900 | 788.082 | 393 | 1240 | 1430.7692 | 0
2016-06-21 05:00 | 2900 | 808.716 | 498 | 1240 | 1430.7692 | 0
2016-06-21 06:00 | 2751 | 877.64 | 542 | 1240 | 1430.7692 | 0
2016-06-21 07:00 | 2751 | 914.9 | 454 | 1240 | 1430.7692 | 0
2016-06-21 08:00 | 2751 | 928.15 | 629 | 1240 | 1440 | 0
2016-06-21 09:00 | 2751 | 996.645 | 667 | 1240 | 1238.9381 | 0
2016-06-21 10:00 | 2303 | 1183.308 | 701 | 1240 | 1296.2963 | 0
2016-06-21 11:00 | 2303 | 1321.254 | 643 | 1240 | 1000 | 0
2016-06-21 12:00 | 2303 | 1388.222 | 612 | 1240 | 900 | 0
2016-06-21 13:00 | 2303 | 1434.598 | 687 | 1240 | 900 | 0
2016-06-21 14:00 | 1871 | 1481.766 | 526 | 1240 | 900 | 0
2016-06-21 15:00 | 1871 | 1511.18 | 457 | 1240 | 900 | 0
2016-06-21 16:00 | 1871 | 1522.818 | 537 | 1240 | 900 | 0
2016-06-21 17:00 | 1871 | 1510.146 | 506 | 1240 | 900 | 0
2016-06-21 18:00 | 1938 | 1464.408 | 348 | 1240 | 1040 | 0
2016-06-21 19:00 | 1938 | 1418.648 | 348 | 1240 | 1000 | 0
2016-06-21 20:00 | 1938 | 1320.144 | 348 | 1240 | 1296.2963 | 0
2016-06-21 21:00 | 1938 | 1290.324 | 360 | 1240 | 1296.2963 | 0
2016-06-21 22:00 | 2261 | 1086.933 | 348 | 1240 | 1238.9381 | 0
2016-06-21 23:00 | 2261 | 1047.54 | 348 | 1240 | 1440 | 0
2016-06-22 | 2261 | 956.94 | 462 | 1240 | 1440 | 0
2016-06-22 01:00 | 2261 | 859.997 | 378 | 1240 | 1440 | 0
2016-06-22 02:00 | 2900 | 820.515 | 348 | 1240 | 1440 | 0
2016-06-22 03:00 | 2900 | 794.2 | 363 | 1240 | 1440 | 0
2016-06-22 04:00 | 2900 | 788.595 | 393 | 1240 | 1440 | 0
2016-06-22 05:00 | 2900 | 807.88 | 498 | 1240 | 1440 | 0
2016-06-22 06:00 | 2751 | 882.34 | 542 | 1240 | 1440 | 0
2016-06-22 07:00 | 2751 | 924.94 | 454 | 1240 | 1440 | 0
2016-06-22 08:00 | 2751 | 937.935 | 629 | 1240 | 1440 | 0
2016-06-22 09:00 | 2751 | 1114.092 | 667 | 1240 | 1238.9381 | 0
2016-06-22 10:00 | 2303 | 1254.528 | 701 | 1240 | 1000 | 0
2016-06-22 11:00 | 2303 | 1335.444 | 643 | 1240 | 1040 | 0
2016-06-22 12:00 | 2303 | 1398.628 | 612 | 1240 | 1040 | 0
2016-06-22 13:00 | 2303 | 1439.086 | 687 | 1240 | 900 | 0
2016-06-22 14:00 | 1871 | 1482.756 | 526 | 1240 | 900 | 0
2016-06-22 15:00 | 1871 | 1502.402 | 457 | 1240 | 900 | 0
2016-06-22 16:00 | 1871 | 1503.546 | 537 | 1240 | 900 | 0
2016-06-22 17:00 | 1871 | 1480.358 | 506 | 1240 | 900 | 0
2016-06-22 18:00 | 1938 | 1435.698 | 348 | 1240 | 900 | 0
2016-06-22 19:00 | 1938 | 1406.174 | 348 | 1240 | 1000 | 0
2016-06-22 20:00 | 1938 | 1295.07 | 348 | 1240 | 1296.2963 | 0
2016-06-22 21:00 | 1938 | 1266.93 | 360 | 1240 | 1296.2963 | 0
2016-06-22 22:00 | 2261 | 1076.559 | 348 | 1240 | 1440 | 0
2016-06-22 23:00 | 2261 | 1038.4 | 348 | 1240 | 1440 | 0
2016-06-23 | 2261 | 880.175 | 462 | 1240 | 1430.7692 | 0
2016-06-23 01:00 | 2261 | 830.908 | 378 | 1240 | 1430.7692 | 0
2016-06-23 02:00 | 2900 | 836.7 | 348 | 1240 | 1430.7692 | 0
2016-06-23 03:00 | 2900 | 811.58 | 363 | 1240 | 1430.7692 | 0
2016-06-23 04:00 | 2900 | 763.876 | 393 | 1240 | 1430.7692 | 0
2016-06-23 05:00 | 2900 | 783.845 | 498 | 1240 | 1430.7692 | 0
2016-06-23 06:00 | 2751 | 864.46 | 542 | 1240 | 1430.7692 | 0
2016-06-23 07:00 | 2751 | 894.5 | 454 | 1240 | 1440 | 0
2016-06-23 08:00 | 2751 | 903.222 | 629 | 1240 | 1238.9381 | 0
2016-06-23 09:00 | 2751 | 1075.809 | 667 | 1240 | 1296.2963 | 0
2016-06-23 10:00 | 2303 | 1154.979 | 701 | 1240 | 1000 | 0
2016-06-23 11:00 | 2303 | 1285.24 | 643 | 1240 | 900 | 0
2016-06-23 12:00 | 2303 | 1344.728 | 612 | 1240 | 900 | 0
2016-06-23 13:00 | 2303 | 1390.752 | 687 | 1240 | 900 | 0
2016-06-23 14:00 | 1871 | 1423.928 | 526 | 1240 | 900 | 0
2016-06-23 15:00 | 1871 | 1421.904 | 457 | 1240 | 900 | 0
2016-06-23 16:00 | 1871 | 1423.422 | 537 | 1240 | 900 | 0
2016-06-23 17:00 | 1871 | 1429.076 | 506 | 1240 | 900 | 0
2016-06-23 18:00 | 1938 | 1390.62 | 348 | 1240 | 1040 | 0
2016-06-23 19:00 | 1938 | 1352.164 | 348 | 1240 | 1000 | 0
2016-06-23 20:00 | 1938 | 1247.589 | 348 | 1240 | 1000 | 0
2016-06-23 21:00 | 1938 | 1220.919 | 360 | 1240 | 1296.2963 | 0
2016-06-23 22:00 | 2261 | 1142.19 | 348 | 1240 | 1296.2963 | 0
2016-06-23 23:00 | 2261 | 949.031 | 348 | 1240 | 1238.9381 | 0
2016-06-24 | 2261 | 933.16 | 462 | 1240 | 1440 | 0
2016-06-24 01:00 | 2261 | 882.68 | 378 | 1240 | 1440 | 0
2016-06-24 02:00 | 2900 | 804.346 | 348 | 1240 | 1440 | 0
2016-06-24 03:00 | 2900 | 784.776 | 363 | 1240 | 1440 | 0
2016-06-24 04:00 | 2900 | 777.575 | 393 | 1240 | 1440 | 0
2016-06-24 05:00 | 2900 | 839.44 | 498 | 1240 | 1440 | 0
2016-06-24 06:00 | 2751 | 875.52 | 542 | 1240 | 1440 | 0
2016-06-24 07:00 | 2751 | 854.962 | 454 | 1240 | 1440 | 0
2016-06-24 08:00 | 2751 | 892.696 | 629 | 1240 | 1238.9381 | 0
2016-06-24 09:00 | 2751 | 1044.666 | 667 | 1240 | 1296.2963 | 0
2016-06-24 10:00 | 2303 | 1111.383 | 701 | 1240 | 1000 | 0
2016-06-24 11:00 | 2303 | 1233.298 | 643 | 1240 | 1040 | 0
2016-06-24 12:00 | 2303 | 1288.32 | 612 | 1240 | 1040 | 0
2016-06-24 13:00 | 2303 | 1335.224 | 687 | 1240 | 1040 | 0
2016-06-24 14:00 | 1871 | 1363.67 | 526 | 1240 | 900 | 0
2016-06-24 15:00 | 1871 | 1375.242 | 457 | 1240 | 900 | 0
2016-06-24 16:00 | 1871 | 1379.18 | 537 | 1240 | 900 | 0
2016-06-24 17:00 | 1871 | 1368.576 | 506 | 1240 | 900 | 0
2016-06-24 18:00 | 1938 | 1321.276 | 348 | 1240 | 1040 | 0
2016-06-24 19:00 | 1938 | 1273.954 | 348 | 1240 | 1000 | 0
2016-06-24 20:00 | 1938 | 1180.515 | 348 | 1240 | 1296.2963 | 0
2016-06-24 21:00 | 1938 | 1153.635 | 360 | 1240 | 1296.2963 | 0
2016-06-24 22:00 | 2261 | 978.5 | 348 | 1240 | 1238.9381 | 0
2016-06-24 23:00 | 2261 | 948.34 | 348 | 1240 | 1440 | 0
2016-06-25 | 2261 | 940.82 | 462 | 1240 | 1440 | 0
2016-06-25 01:00 | 2261 | 890.8 | 378 | 1240 | 1440 | 0
2016-06-25 02:00 | 2900 | 857.8 | 348 | 1240 | 1440 | 0
2016-06-25 03:00 | 2900 | 797.012 | 363 | 1240 | 1440 | 0
2016-06-25 04:00 | 2900 | 796.651 | 393 | 1240 | 1440 | 0
2016-06-25 05:00 | 2900 | 864.92 | 498 | 1240 | 1440 | 0
2016-06-25 06:00 | 2751 | 899.76 | 542 | 1240 | 1440 | 0
2016-06-25 07:00 | 2751 | 934.62 | 454 | 1240 | 1440 | 0
2016-06-25 08:00 | 2751 | 945.877 | 629 | 1240 | 1238.9381 | 0
2016-06-25 09:00 | 2751 | 1120.686 | 667 | 1240 | 1296.2963 | 0
2016-06-25 10:00 | 2303 | 1254.814 | 701 | 1240 | 1000 | 0
2016-06-25 11:00 | 2303 | 1321.87 | 643 | 1240 | 900 | 0
2016-06-25 12:00 | 2303 | 1369.698 | 612 | 1240 | 900 | 0
2016-06-25 13:00 | 2303 | 1406.592 | 687 | 1240 | 900 | 0
2016-06-25 14:00 | 1871 | 1423.73 | 526 | 1240 | 900 | 0
2016-06-25 15:00 | 1871 | 1420.826 | 457 | 1240 | 900 | 0
2016-06-25 16:00 | 1871 | 1422.564 | 537 | 1240 | 900 | 0
2016-06-25 17:00 | 1871 | 1422.168 | 506 | 1240 | 900 | 0
2016-06-25 18:00 | 1938 | 1379.752 | 348 | 1240 | 900 | 0
2016-06-25 19:00 | 1938 | 1337.336 | 348 | 1240 | 1040 | 0
2016-06-25 20:00 | 1938 | 1234.821 | 348 | 1240 | 1000 | 0
2016-06-25 21:00 | 1938 | 1211.847 | 360 | 1240 | 1000 | 0
2016-06-25 22:00 | 2261 | 1033.866 | 348 | 1240 | 1238.9381 | 0
2016-06-25 23:00 | 2261 | 963.015 | 348 | 1240 | 1238.9381 | 0
2016-06-26 | 2261 | 961.98 | 462 | 1240 | 1440 | 0
2016-06-26 01:00 | 2261 | 914.8 | 378 | 1240 | 1440 | 0
2016-06-26 02:00 | 2900 | 878.96 | 348 | 1240 | 1440 | 0
2016-06-26 03:00 | 2900 | 813.58 | 363 | 1240 | 1440 | 0
2016-06-26 04:00 | 2900 | 804.289 | 393 | 1240 | 1440 | 0
2016-06-26 05:00 | 2900 | 806.854 | 498 | 1240 | 1440 | 0
2016-06-26 06:00 | 2751 | 807.823 | 542 | 1240 | 1440 | 0
2016-06-26 07:00 | 2751 | 876.68 | 454 | 1240 | 1440 | 0
2016-06-26 08:00 | 2751 | 958.6 | 629 | 1240 | 1238.9381 | 0
2016-06-26 09:00 | 2751 | 996.55 | 667 | 1240 | 1296.2963 | 0
2016-06-26 10:00 | 2303 | 1193.598 | 701 | 1240 | 1000 | 0
2016-06-26 11:00 | 2303 | 1331.616 | 643 | 1240 | 1040 | 0
2016-06-26 12:00 | 2303 | 1402.742 | 612 | 1240 | 900 | 0
2016-06-26 13:00 | 2303 | 1439.724 | 687 | 1240 | 900 | 0
2016-06-26 14:00 | 1871 | 1476.794 | 526 | 1240 | 900 | 0
2016-06-26 15:00 | 1871 | 1500.356 | 457 | 1240 | 900 | 0
2016-06-26 16:00 | 1871 | 1511.576 | 537 | 1240 | 900 | 0
2016-06-26 17:00 | 1871 | 1502.952 | 506 | 1240 | 900 | 0
2016-06-26 18:00 | 1938 | 1463.66 | 348 | 1240 | 900 | 0
2016-06-26 19:00 | 1938 | 1424.346 | 348 | 1240 | 1040 | 0
2016-06-26 20:00 | 1938 | 1386.572 | 348 | 1240 | 1000 | 0
2016-06-26 21:00 | 1938 | 1286.88 | 360 | 1240 | 1000 | 0
2016-06-26 22:00 | 2261 | 1213.401 | 348 | 1240 | 1238.9381 | 0
2016-06-26 23:00 | 2261 | 1024.499 | 348 | 1240 | 1238.9381 | 0
2016-06-27 | 2261 | 1013.64 | 462 | 1240 | 1440 | 0
2016-06-27 01:00 | 2261 | 953.96 | 378 | 1240 | 1440 | 0
2016-06-27 02:00 | 2900 | 867.73 | 348 | 1240 | 1440 | 0
2016-06-27 03:00 | 2900 | 839.895 | 363 | 1240 | 1440 | 0
2016-06-27 04:00 | 2900 | 820.648 | 393 | 1240 | 1440 | 0
2016-06-27 05:00 | 2900 | 812.934 | 498 | 1240 | 1440 | 0
2016-06-27 06:00 | 2751 | 802.161 | 542 | 1240 | 1440 | 0
2016-06-27 07:00 | 2751 | 817.627 | 454 | 1240 | 1440 | 0
2016-06-27 08:00 | 2751 | 934.14 | 629 | 1240 | 1440 | 0
2016-06-27 09:00 | 2751 | 971.546 | 667 | 1240 | 1440 | 0
2016-06-27 10:00 | 2303 | 1161.447 | 701 | 1240 | 1296.2963 | 0
2016-06-27 11:00 | 2303 | 1303.258 | 643 | 1240 | 1000 | 0
2016-06-27 12:00 | 2303 | 1379.378 | 612 | 1240 | 900 | 0
2016-06-27 13:00 | 2303 | 1428.064 | 687 | 1240 | 900 | 0
2016-06-27 14:00 | 1871 | 1476.244 | 526 | 1240 | 900 | 0
2016-06-27 15:00 | 1871 | 1509.2 | 457 | 1240 | 900 | 0
2016-06-27 16:00 | 1871 | 1526.338 | 537 | 1240 | 900 | 0
2016-06-27 17:00 | 1871 | 1525.854 | 506 | 1240 | 900 | 0
2016-06-27 18:00 | 1938 | 1487.112 | 348 | 1240 | 900 | 0
2016-06-27 19:00 | 1938 | 1448.37 | 348 | 1240 | 900 | 0
2016-06-27 20:00 | 1938 | 1415.436 | 348 | 1240 | 900 | 0
2016-06-27 21:00 | 1938 | 1383.58 | 360 | 1240 | 900 | 0
2016-06-27 22:00 | 2261 | 1300.332 | 348 | 1240 | 1040 | 0
2016-06-27 23:00 | 2261 | 1142.295 | 348 | 1240 | 1296.2963 | 0
2016-06-28 | 2261 | 921.804 | 462 | 1240 | 1238.9381 | 0
2016-06-28 01:00 | 2261 | 870.865 | 378 | 1240 | 1238.9381 | 0
2016-06-28 02:00 | 2900 | 837.045 | 348 | 1240 | 1238.9381 | 0
2016-06-28 03:00 | 2900 | 861.64 | 363 | 1240 | 1238.9381 | 0
2016-06-28 04:00 | 2900 | 858.18 | 393 | 1240 | 1238.9381 | 0
2016-06-28 05:00 | 2900 | 839.439 | 498 | 1240 | 1238.9381 | 0
2016-06-28 06:00 | 2751 | 873.354 | 542 | 1240 | 1238.9381 | 0
2016-06-28 07:00 | 2751 | 904.495 | 454 | 1240 | 1238.9381 | 0
2016-06-28 08:00 | 2751 | 1064.217 | 629 | 1240 | 1296.2963 | 0
2016-06-28 09:00 | 2751 | 1199.66 | 667 | 1240 | 1040 | 0
2016-06-28 10:00 | 2303 | 1280.29 | 701 | 1240 | 900 | 0
2016-06-28 11:00 | 2303 | 1352.56 | 643 | 1240 | 900 | 0
2016-06-28 12:00 | 2303 | 1399.508 | 612 | 1240 | 900 | 0
2016-06-28 13:00 | 2303 | 1426.942 | 687 | 1240 | 900 | 0
2016-06-28 14:00 | 1871 | 1456.884 | 526 | 1240 | 900 | 0
2016-06-28 15:00 | 1871 | 1457.148 | 457 | 1240 | 900 | 0
2016-06-28 16:00 | 1871 | 1424.698 | 537 | 1240 | 900 | 0
2016-06-28 17:00 | 1871 | 1392.952 | 506 | 1240 | 900 | 0
2016-06-28 18:00 | 1938 | 1342.484 | 348 | 1240 | 1040 | 0
2016-06-28 19:00 | 1938 | 1292.038 | 348 | 1240 | 1040 | 0
2016-06-28 20:00 | 1938 | 1255.65 | 348 | 1240 | 1040 | 0
2016-06-28 21:00 | 1938 | 1225.906 | 360 | 1240 | 1040 | 0
2016-06-28 22:00 | 2261 | 1105.986 | 348 | 1240 | 1000 | 0
2016-06-28 23:00 | 2261 | 923.989 | 348 | 1240 | 1238.9381 | 0
2016-06-29 | 2261 | 875.596 | 462 | 1240 | 1238.9381 | 0
2016-06-29 01:00 | 2261 | 879.84 | 378 | 1240 | 1238.9381 | 0
2016-06-29 02:00 | 2900 | 852.02 | 348 | 1240 | 1238.9381 | 0
2016-06-29 03:00 | 2900 | 836.8 | 363 | 1240 | 1238.9381 | 0
2016-06-29 04:00 | 2900 | 837.64 | 393 | 1240 | 1238.9381 | 0
2016-06-29 05:00 | 2900 | 866.06 | 498 | 1240 | 1238.9381 | 0
2016-06-29 06:00 | 2751 | 862.106 | 542 | 1240 | 1238.9381 | 0
2016-06-29 07:00 | 2751 | 891.898 | 454 | 1240 | 1238.9381 | 0
2016-06-29 08:00 | 2751 | 1033.599 | 629 | 1240 | 1296.2963 | 0
2016-06-29 09:00 | 2751 | 1091.916 | 667 | 1240 | 1000 | 0
2016-06-29 10:00 | 2303 | 1151.052 | 701 | 1240 | 1000 | 0
2016-06-29 11:00 | 2303 | 1259.258 | 643 | 1240 | 1000 | 0
2016-06-29 12:00 | 2303 | 1302.158 | 612 | 1240 | 1000 | 0
2016-06-29 13:00 | 2303 | 1345.168 | 687 | 1240 | 1000 | 0
2016-06-29 14:00 | 1871 | 1376.584 | 526 | 1240 | 1000 | 0
2016-06-29 15:00 | 1871 | 1329.951 | 457 | 1240 | 1000 | 0
2016-06-29 16:00 | 1871 | 1329.783 | 537 | 1240 | 1000 | 0
2016-06-29 17:00 | 1871 | 1305.087 | 506 | 1240 | 1000 | 0
2016-06-29 18:00 | 1938 | 1137.226 | 348 | 1240 | 1296.2963 | 0
2016-06-29 19:00 | 1938 | 1093.64 | 348 | 1240 | 1296.2963 | 0
2016-06-29 20:00 | 1938 | 1078.915 | 348 | 1240 | 1296.2963 | 0
2016-06-29 21:00 | 1938 | 1178.793 | 360 | 1240 | 1296.2963 | 0
2016-06-29 22:00 | 2261 | 1109.136 | 348 | 1240 | 1238.9381 | 0
2016-06-29 23:00 | 2261 | 926.117 | 348 | 1240 | 1238.9381 | 0
2016-06-30 | 2261 | 894.14 | 462 | 1240 | 1440 | 0
2016-06-30 01:00 | 2261 | 851.66 | 378 | 1240 | 1440 | 0
2016-06-30 02:00 | 2900 | 783.959 | 348 | 1240 | 1440 | 0
2016-06-30 03:00 | 2900 | 770.317 | 363 | 1240 | 1440 | 0
2016-06-30 04:00 | 2900 | 772.578 | 393 | 1240 | 1440 | 0
2016-06-30 05:00 | 2900 | 842.2 | 498 | 1240 | 1440 | 0
2016-06-30 06:00 | 2751 | 877.8 | 542 | 1240 | 1440 | 0
2016-06-30 07:00 | 2751 | 902.54 | 454 | 1240 | 1440 | 0
2016-06-30 08:00 | 2751 | 893.969 | 629 | 1240 | 1440 | 0
2016-06-30 09:00 | 2751 | 941.659 | 667 | 1240 | 1238.9381 | 0
2016-06-30 10:00 | 2303 | 986.423 | 701 | 1240 | 1238.9381 | 0
2016-06-30 11:00 | 2303 | 1024.613 | 643 | 1240 | 1238.9381 | 0
2016-06-30 12:00 | 2303 | 1052.923 | 612 | 1240 | 1238.9381 | 0
2016-06-30 13:00 | 2303 | 1075.647 | 687 | 1240 | 1238.9381 | 0
2016-06-30 14:00 | 1871 | 1095.635 | 526 | 1240 | 1238.9381 | 0
2016-06-30 15:00 | 1871 | 1099.986 | 457 | 1240 | 1238.9381 | 0
2016-06-30 16:00 | 1871 | 1089.764 | 537 | 1240 | 1440 | 0
2016-06-30 17:00 | 1871 | 1067.838 | 506 | 1240 | 1440 | 0
2016-06-30 18:00 | 1938 | 1035.69 | 348 | 1240 | 1440 | 0
2016-06-30 19:00 | 1938 | 1056.36 | 348 | 1240 | 1440 | 0
2016-06-30 20:00 | 1938 | 991.42 | 348 | 1240 | 1440 | 0
2016-06-30 21:00 | 1938 | 978.481 | 360 | 1240 | 1440 | 0
2016-06-30 22:00 | 2261 | 978.24 | 348 | 1240 | 1430.7692 | 0
2016-06-30 23:00 | 2261 | 911.68 | 348 | 1240 | 1430.7692 | 0
2016-07-01 | 1752 | 815.005 | 589 | 1240 | 1430.7692 | 0
2016-07-01 01:00 | 1752 | 780.387 | 364 | 1240 | 1430.7692 | 0
2016-07-01 02:00 | 2311 | 757.245 | 364 | 1240 | 1430.7692 | 0
2016-07-01 03:00 | 2311 | 745.75 | 364 | 1240 | 1430.7692 | 0
2016-07-01 04:00 | 2311 | 749.455 | 435 | 1240 | 1430.7692 | 0
2016-07-01 05:00 | 2311 | 776.587 | 441 | 1240 | 1430.7692 | 0
2016-07-01 06:00 | 2144 | 862.92 | 537 | 1240 | 1430.7692 | 0
2016-07-01 07:00 | 2144 | 890.82 | 492 | 1240 | 1430.7692 | 0
2016-07-01 08:00 | 2144 | 876.375 | 673 | 1240 | 1440 | 0
2016-07-01 09:00 | 2144 | 909.397 | 704 | 1240 | 1440 | 0
2016-07-01 10:00 | 2322 | 1045.422 | 784 | 1240 | 1238.9381 | 0
2016-07-01 11:00 | 2322 | 1081.038 | 663 | 1240 | 1238.9381 | 0
2016-07-01 12:00 | 2322 | 1104.915 | 657 | 1240 | 1296.2963 | 0
2016-07-01 13:00 | 2322 | 1121.064 | 564 | 1240 | 1296.2963 | 0
2016-07-01 14:00 | 2123 | 1129.8 | 497 | 1240 | 1296.2963 | 0
2016-07-01 15:00 | 2123 | 1029.496 | 451 | 1240 | 1296.2963 | 0
2016-07-01 16:00 | 2123 | 1148.868 | 471 | 1240 | 1296.2963 | 0
2016-07-01 17:00 | 2123 | 1041.181 | 465 | 1240 | 1238.9381 | 0
2016-07-01 18:00 | 2559 | 1024.1 | 364 | 1240 | 1238.9381 | 0
2016-07-01 19:00 | 2559 | 1007.019 | 374 | 1240 | 1238.9381 | 0
2016-07-01 20:00 | 2559 | 1002.326 | 364 | 1240 | 1238.9381 | 0
2016-07-01 21:00 | 2559 | 994.764 | 416 | 1240 | 1238.9381 | 0
2016-07-01 22:00 | 1752 | 947.739 | 364 | 1240 | 1440 | 0
2016-07-01 23:00 | 1752 | 881.961 | 364 | 1240 | 1440 | 0
2016-07-02 | 1752 | 905.4 | 589 | 1240 | 1440 | 0
2016-07-02 01:00 | 1752 | 889.88 | 364 | 1240 | 1440 | 0
2016-07-02 02:00 | 2311 | 864.96 | 364 | 1240 | 1440 | 0
2016-07-02 03:00 | 2311 | 849.56 | 364 | 1240 | 1440 | 0
2016-07-02 04:00 | 2311 | 850.6 | 435 | 1240 | 1440 | 0
2016-07-02 05:00 | 2311 | 877.98 | 441 | 1240 | 1440 | 0
2016-07-02 06:00 | 2144 | 873.259 | 537 | 1240 | 1440 | 0
2016-07-02 07:00 | 2144 | 902.082 | 492 | 1240 | 1238.9381 | 0
2016-07-02 08:00 | 2144 | 936.947 | 673 | 1240 | 1296.2963 | 0
2016-07-02 09:00 | 2144 | 1079.127 | 704 | 1240 | 1296.2963 | 0
2016-07-02 10:00 | 2322 | 1121.652 | 784 | 1240 | 1296.2963 | 0
2016-07-02 11:00 | 2322 | 1159.389 | 663 | 1240 | 1296.2963 | 0
2016-07-02 12:00 | 2322 | 1186.962 | 657 | 1240 | 1000 | 0
2016-07-02 13:00 | 2322 | 1255.474 | 564 | 1240 | 1000 | 0
2016-07-02 14:00 | 2123 | 1198.533 | 497 | 1240 | 1000 | 0
2016-07-02 15:00 | 2123 | 1183.329 | 451 | 1240 | 1296.2963 | 0
2016-07-02 16:00 | 2123 | 1171.842 | 471 | 1240 | 1238.9381 | 0
2016-07-02 17:00 | 2123 | 1035.747 | 465 | 1240 | 1238.9381 | 0
2016-07-02 18:00 | 2559 | 1005.233 | 364 | 1240 | 1238.9381 | 0
2016-07-02 19:00 | 2559 | 974.719 | 374 | 1240 | 1238.9381 | 0
2016-07-02 20:00 | 2559 | 977.284 | 364 | 1240 | 1238.9381 | 0
2016-07-02 21:00 | 2559 | 1080.261 | 416 | 1240 | 1238.9381 | 0
2016-07-02 22:00 | 1752 | 943.958 | 364 | 1240 | 1238.9381 | 0
2016-07-02 23:00 | 1752 | 893.684 | 364 | 1240 | 1440 | 0
2016-07-03 | 1752 | 915.68 | 589 | 1240 | 1440 | 0
2016-07-03 01:00 | 1752 | 878.9 | 364 | 1240 | 1440 | 0
2016-07-03 02:00 | 2311 | 850.18 | 364 | 1240 | 1440 | 0
2016-07-03 03:00 | 2311 | 835.14 | 364 | 1240 | 1440 | 0
2016-07-03 04:00 | 2311 | 786.372 | 435 | 1240 | 1440 | 0
2016-07-03 05:00 | 2311 | 794.979 | 441 | 1240 | 1440 | 0
2016-07-03 06:00 | 2144 | 851.88 | 537 | 1240 | 1440 | 0
2016-07-03 07:00 | 2144 | 827.697 | 492 | 1240 | 1440 | 0
2016-07-03 08:00 | 2144 | 880.441 | 673 | 1240 | 1440 | 0
2016-07-03 09:00 | 2144 | 996.72 | 704 | 1240 | 1440 | 0
2016-07-03 10:00 | 2322 | 1010.097 | 784 | 1240 | 1238.9381 | 0
2016-07-03 11:00 | 2322 | 1063.525 | 663 | 1240 | 1238.9381 | 0
2016-07-03 12:00 | 2322 | 1094.134 | 657 | 1240 | 1238.9381 | 0
2016-07-03 13:00 | 2322 | 1109.619 | 564 | 1240 | 1238.9381 | 0
2016-07-03 14:00 | 2123 | 1116.364 | 497 | 1240 | 1238.9381 | 0
2016-07-03 15:00 | 2123 | 1126.985 | 451 | 1240 | 1238.9381 | 0
2016-07-03 16:00 | 2123 | 1249.479 | 471 | 1240 | 1238.9381 | 0
2016-07-03 17:00 | 2123 | 1241.457 | 465 | 1240 | 1238.9381 | 0
2016-07-03 18:00 | 2559 | 1091.189 | 364 | 1240 | 1238.9381 | 0
2016-07-03 19:00 | 2559 | 1059.174 | 374 | 1240 | 1238.9381 | 0
2016-07-03 20:00 | 2559 | 1040.155 | 364 | 1240 | 1238.9381 | 0
2016-07-03 21:00 | 2559 | 1032.346 | 416 | 1240 | 1238.9381 | 0
2016-07-03 22:00 | 1752 | 995.011 | 364 | 1240 | 1440 | 0
2016-07-03 23:00 | 1752 | 998.42 | 364 | 1240 | 1440 | 0
2016-07-04 | 1752 | 853.708 | 589 | 1240 | 1521.4286 | 0
2016-07-04 01:00 | 1752 | 816.62 | 364 | 1240 | 1521.4286 | 0
2016-07-04 02:00 | 2311 | 829.84 | 364 | 1240 | 1521.4286 | 0
2016-07-04 03:00 | 2311 | 809.76 | 364 | 1240 | 1521.4286 | 0
2016-07-04 04:00 | 2311 | 797.76 | 435 | 1240 | 1521.4286 | 0
2016-07-04 05:00 | 2311 | 796.8 | 441 | 1240 | 1521.4286 | 0
2016-07-04 06:00 | 2144 | 796.7 | 537 | 1240 | 1521.4286 | 0
2016-07-04 07:00 | 2144 | 808.72 | 492 | 1240 | 1521.4286 | 0
2016-07-04 08:00 | 2144 | 824.049 | 673 | 1240 | 1521.4286 | 0
2016-07-04 09:00 | 2144 | 937.68 | 704 | 1240 | 1430.7692 | 0
2016-07-04 10:00 | 2322 | 959.671 | 784 | 1240 | 1440 | 0
2016-07-04 11:00 | 2322 | 1023.416 | 663 | 1240 | 1440 | 0
2016-07-04 12:00 | 2322 | 1078.649 | 657 | 1240 | 1238.9381 | 0
2016-07-04 13:00 | 2322 | 1236.711 | 564 | 1240 | 1000 | 0
2016-07-04 14:00 | 2123 | 1272.348 | 497 | 1240 | 1000 | 0
2016-07-04 15:00 | 2123 | 1293.621 | 451 | 1240 | 1000 | 0
2016-07-04 16:00 | 2123 | 1366.662 | 471 | 1240 | 1000 | 0
2016-07-04 17:00 | 2123 | 1361.03 | 465 | 1240 | 1000 | 0
2016-07-04 18:00 | 2559 | 1255.233 | 364 | 1240 | 1296.2963 | 0
2016-07-04 19:00 | 2559 | 1211.322 | 374 | 1240 | 1296.2963 | 0
2016-07-04 20:00 | 2559 | 1166.046 | 364 | 1240 | 1296.2963 | 0
2016-07-04 21:00 | 2559 | 1027.045 | 416 | 1240 | 1238.9381 | 0
2016-07-04 22:00 | 1752 | 988.266 | 364 | 1240 | 1238.9381 | 0
2016-07-04 23:00 | 1752 | 945.022 | 364 | 1240 | 1440 | 0
2016-07-05 | 1752 | 883.842 | 589 | 1240 | 1430.7692 | 0
2016-07-05 01:00 | 1752 | 841.054 | 364 | 1240 | 1430.7692 | 0
2016-07-05 02:00 | 2311 | 810.217 | 364 | 1240 | 1430.7692 | 0
2016-07-05 03:00 | 2311 | 789.982 | 364 | 1240 | 1430.7692 | 0
2016-07-05 04:00 | 2311 | 782.724 | 435 | 1240 | 1430.7692 | 0
2016-07-05 05:00 | 2311 | 789.336 | 441 | 1240 | 1430.7692 | 0
2016-07-05 06:00 | 2144 | 793.801 | 537 | 1240 | 1430.7692 | 0
2016-07-05 07:00 | 2144 | 806.189 | 492 | 1240 | 1430.7692 | 0
2016-07-05 08:00 | 2144 | 856.444 | 673 | 1240 | 1430.7692 | 0
2016-07-05 09:00 | 2144 | 979.26 | 704 | 1240 | 1440 | 0
2016-07-05 10:00 | 2322 | 1009.565 | 784 | 1240 | 1238.9381 | 0
2016-07-05 11:00 | 2322 | 1195.761 | 663 | 1240 | 1296.2963 | 0
2016-07-05 12:00 | 2322 | 1323.52 | 657 | 1240 | 1040 | 0
2016-07-05 13:00 | 2322 | 1382.084 | 564 | 1240 | 900 | 0
2016-07-05 14:00 | 2123 | 1423.994 | 497 | 1240 | 900 | 0
2016-07-05 15:00 | 2123 | 1454.838 | 451 | 1240 | 900 | 0
2016-07-05 16:00 | 2123 | 1474.594 | 471 | 1240 | 900 | 0
2016-07-05 17:00 | 2123 | 1466.586 | 465 | 1240 | 900 | 0
2016-07-05 18:00 | 2559 | 1423.686 | 364 | 1240 | 900 | 0
2016-07-05 19:00 | 2559 | 1380.786 | 374 | 1240 | 900 | 0
2016-07-05 20:00 | 2559 | 1335.202 | 364 | 1240 | 1040 | 0
2016-07-05 21:00 | 2559 | 1303.654 | 416 | 1240 | 1040 | 0
2016-07-05 22:00 | 1752 | 1165.983 | 364 | 1240 | 1296.2963 | 0
2016-07-05 23:00 | 1752 | 1069.257 | 364 | 1240 | 1296.2963 | 0
2016-07-06 | 1752 | 855.095 | 589 | 1240 | 1440 | 0
2016-07-06 01:00 | 1752 | 847.56 | 364 | 1240 | 1440 | 0
2016-07-06 02:00 | 2311 | 816.44 | 364 | 1240 | 1440 | 0
2016-07-06 03:00 | 2311 | 797.24 | 364 | 1240 | 1440 | 0
2016-07-06 04:00 | 2311 | 793.94 | 435 | 1240 | 1440 | 0
2016-07-06 05:00 | 2311 | 817.86 | 441 | 1240 | 1440 | 0
2016-07-06 06:00 | 2144 | 855.64 | 537 | 1240 | 1440 | 0
2016-07-06 07:00 | 2144 | 844.683 | 492 | 1240 | 1238.9381 | 0
2016-07-06 08:00 | 2144 | 906.395 | 673 | 1240 | 1238.9381 | 0
2016-07-06 09:00 | 2144 | 1080.408 | 704 | 1240 | 1296.2963 | 0
2016-07-06 10:00 | 2322 | 1222.848 | 784 | 1240 | 1000 | 0
2016-07-06 11:00 | 2322 | 1308.89 | 663 | 1240 | 900 | 0
2016-07-06 12:00 | 2322 | 1373.79 | 657 | 1240 | 900 | 0
2016-07-06 13:00 | 2322 | 1424.06 | 564 | 1240 | 900 | 0
2016-07-06 14:00 | 2123 | 1451.714 | 497 | 1240 | 900 | 0
2016-07-06 15:00 | 2123 | 1459.502 | 451 | 1240 | 900 | 0
2016-07-06 16:00 | 2123 | 1452.11 | 471 | 1240 | 900 | 0
2016-07-06 17:00 | 2123 | 1430.55 | 465 | 1240 | 900 | 0
2016-07-06 18:00 | 2559 | 1390.95 | 364 | 1240 | 900 | 0
2016-07-06 19:00 | 2559 | 1351.372 | 374 | 1240 | 900 | 0
2016-07-06 20:00 | 2559 | 1304.666 | 364 | 1240 | 1040 | 0
2016-07-06 21:00 | 2559 | 1271.446 | 416 | 1240 | 1040 | 0
2016-07-06 22:00 | 1752 | 1132.341 | 364 | 1240 | 1000 | 0
2016-07-06 23:00 | 1752 | 939.683 | 364 | 1240 | 1238.9381 | 0
2016-07-07 | 1752 | 883.72 | 589 | 1240 | 1440 | 0
2016-07-07 01:00 | 1752 | 832.58 | 364 | 1240 | 1440 | 0
2016-07-07 02:00 | 2311 | 800.14 | 364 | 1240 | 1440 | 0
2016-07-07 03:00 | 2311 | 742.083 | 364 | 1240 | 1440 | 0
2016-07-07 04:00 | 2311 | 738.853 | 435 | 1240 | 1440 | 0
2016-07-07 05:00 | 2311 | 800.92 | 441 | 1240 | 1440 | 0
2016-07-07 06:00 | 2144 | 838.32 | 537 | 1240 | 1440 | 0
2016-07-07 07:00 | 2144 | 863.38 | 492 | 1240 | 1440 | 0
2016-07-07 08:00 | 2144 | 867.141 | 673 | 1240 | 1238.9381 | 0
2016-07-07 09:00 | 2144 | 1022.259 | 704 | 1240 | 1296.2963 | 0
2016-07-07 10:00 | 2322 | 1089.711 | 784 | 1240 | 1000 | 0
2016-07-07 11:00 | 2322 | 1206.26 | 663 | 1240 | 1040 | 0
2016-07-07 12:00 | 2322 | 1246.102 | 657 | 1240 | 1040 | 0
2016-07-07 13:00 | 2322 | 1282.556 | 564 | 1240 | 1040 | 0
2016-07-07 14:00 | 2123 | 1314.522 | 497 | 1240 | 1040 | 0
2016-07-07 15:00 | 2123 | 1346.026 | 451 | 1240 | 1040 | 0
2016-07-07 16:00 | 2123 | 1353.726 | 471 | 1240 | 1040 | 0
2016-07-07 17:00 | 2123 | 1335.026 | 465 | 1240 | 1040 | 0
2016-07-07 18:00 | 2559 | 1297.692 | 364 | 1240 | 1000 | 0
2016-07-07 19:00 | 2559 | 1203.069 | 374 | 1240 | 1296.2963 | 0
2016-07-07 20:00 | 2559 | 1057.008 | 364 | 1240 | 1296.2963 | 0
2016-07-07 21:00 | 2559 | 1139.796 | 416 | 1240 | 1296.2963 | 0
2016-07-07 22:00 | 1752 | 966.91 | 364 | 1240 | 1238.9381 | 0
2016-07-07 23:00 | 1752 | 891.917 | 364 | 1240 | 1440 | 0
2016-07-08 | 1752 | 887.7 | 589 | 1240 | 1440 | 0
2016-07-08 01:00 | 1752 | 843.64 | 364 | 1240 | 1440 | 0
2016-07-08 02:00 | 2311 | 813.02 | 364 | 1240 | 1440 | 0
2016-07-08 03:00 | 2311 | 798.04 | 364 | 1240 | 1440 | 0
2016-07-08 04:00 | 2311 | 799.62 | 435 | 1240 | 1440 | 0
2016-07-08 05:00 | 2311 | 825 | 441 | 1240 | 1440 | 0
2016-07-08 06:00 | 2144 | 867.2 | 537 | 1240 | 1440 | 0
2016-07-08 07:00 | 2144 | 846.374 | 492 | 1240 | 1440 | 0
2016-07-08 08:00 | 2144 | 872.138 | 673 | 1240 | 1440 | 0
2016-07-08 09:00 | 2144 | 905.692 | 704 | 1240 | 1238.9381 | 0
2016-07-08 10:00 | 2322 | 943.996 | 784 | 1240 | 1238.9381 | 0
2016-07-08 11:00 | 2322 | 984.656 | 663 | 1240 | 1238.9381 | 0
2016-07-08 12:00 | 2322 | 1008.862 | 657 | 1240 | 1238.9381 | 0
2016-07-08 13:00 | 2322 | 1146.558 | 564 | 1240 | 1238.9381 | 0
2016-07-08 14:00 | 2123 | 1158.99 | 497 | 1240 | 1238.9381 | 0
2016-07-08 15:00 | 2123 | 1160.964 | 451 | 1240 | 1238.9381 | 0
2016-07-08 16:00 | 2123 | 1140.951 | 471 | 1240 | 1238.9381 | 0
2016-07-08 17:00 | 2123 | 1003.086 | 465 | 1240 | 1238.9381 | 0
2016-07-08 18:00 | 2559 | 987.145 | 364 | 1240 | 1238.9381 | 0
2016-07-08 19:00 | 2559 | 971.185 | 374 | 1240 | 1238.9381 | 0
2016-07-08 20:00 | 2559 | 967.119 | 364 | 1240 | 1238.9381 | 0
2016-07-08 21:00 | 2559 | 953.876 | 416 | 1240 | 1238.9381 | 0
2016-07-08 22:00 | 1752 | 907.744 | 364 | 1240 | 1440 | 0
2016-07-08 23:00 | 1752 | 889.98 | 364 | 1240 | 1440 | 0
2016-07-09 | 1752 | 864.64 | 589 | 1240 | 1440 | 0
2016-07-09 01:00 | 1752 | 827.1 | 364 | 1240 | 1440 | 0
2016-07-09 02:00 | 2311 | 802.94 | 364 | 1240 | 1440 | 0
2016-07-09 03:00 | 2311 | 788.7 | 364 | 1240 | 1440 | 0
2016-07-09 04:00 | 2311 | 790.8 | 435 | 1240 | 1440 | 0
2016-07-09 05:00 | 2311 | 817.8 | 441 | 1240 | 1440 | 0
2016-07-09 06:00 | 2144 | 861.36 | 537 | 1240 | 1440 | 0
2016-07-09 07:00 | 2144 | 844.797 | 492 | 1240 | 1440 | 0
2016-07-09 08:00 | 2144 | 891.252 | 673 | 1240 | 1440 | 0
2016-07-09 09:00 | 2144 | 945.611 | 704 | 1240 | 1238.9381 | 0
2016-07-09 10:00 | 2322 | 1115.919 | 784 | 1240 | 1296.2963 | 0
2016-07-09 11:00 | 2322 | 1175.769 | 663 | 1240 | 1296.2963 | 0
2016-07-09 12:00 | 2322 | 1278.838 | 657 | 1240 | 1000 | 0
2016-07-09 13:00 | 2322 | 1321.188 | 564 | 1240 | 1040 | 0
2016-07-09 14:00 | 2123 | 1340.79 | 497 | 1240 | 1040 | 0
2016-07-09 15:00 | 2123 | 1352.472 | 451 | 1240 | 1040 | 0
2016-07-09 16:00 | 2123 | 1355.75 | 471 | 1240 | 1040 | 0
2016-07-09 17:00 | 2123 | 1330.538 | 465 | 1240 | 1040 | 0
2016-07-09 18:00 | 2559 | 1278.552 | 364 | 1240 | 1000 | 0
2016-07-09 19:00 | 2559 | 1170.813 | 374 | 1240 | 1000 | 0
2016-07-09 20:00 | 2559 | 1140.51 | 364 | 1240 | 1000 | 0
2016-07-09 21:00 | 2559 | 1118.397 | 416 | 1240 | 1296.2963 | 0
2016-07-09 22:00 | 1752 | 1061.697 | 364 | 1240 | 1238.9381 | 0
2016-07-09 23:00 | 1752 | 897.921 | 364 | 1240 | 1238.9381 | 0
2016-07-10 | 1752 | 863.816 | 589 | 1240 | 1238.9381 | 0
2016-07-10 01:00 | 1752 | 860.76 | 364 | 1240 | 1440 | 0
2016-07-10 02:00 | 2311 | 828.4 | 364 | 1240 | 1440 | 0
2016-07-10 03:00 | 2311 | 805.6 | 364 | 1240 | 1440 | 0
2016-07-10 04:00 | 2311 | 796.12 | 435 | 1240 | 1440 | 0
2016-07-10 05:00 | 2311 | 802.14 | 441 | 1240 | 1440 | 0
2016-07-10 06:00 | 2144 | 816.48 | 537 | 1240 | 1440 | 0
2016-07-10 07:00 | 2144 | 832.68 | 492 | 1240 | 1440 | 0
2016-07-10 08:00 | 2144 | 848.179 | 673 | 1240 | 1238.9381 | 0
2016-07-10 09:00 | 2144 | 919.771 | 704 | 1240 | 1238.9381 | 0
2016-07-10 10:00 | 2322 | 1101.093 | 784 | 1240 | 1000 | 0
2016-07-10 11:00 | 2322 | 1233.1 | 663 | 1240 | 1040 | 0
2016-07-10 12:00 | 2322 | 1304.49 | 657 | 1240 | 900 | 0
2016-07-10 13:00 | 2322 | 1354.144 | 564 | 1240 | 900 | 0
2016-07-10 14:00 | 2123 | 1389.278 | 497 | 1240 | 900 | 0
2016-07-10 15:00 | 2123 | 1403.974 | 451 | 1240 | 900 | 0
2016-07-10 16:00 | 2123 | 1406.922 | 471 | 1240 | 900 | 0
2016-07-10 17:00 | 2123 | 1403.996 | 465 | 1240 | 900 | 0
2016-07-10 18:00 | 2559 | 1367.806 | 364 | 1240 | 900 | 0
2016-07-10 19:00 | 2559 | 1331.616 | 374 | 1240 | 900 | 0
2016-07-10 20:00 | 2559 | 1294.414 | 364 | 1240 | 1040 | 0
2016-07-10 21:00 | 2559 | 1270.104 | 416 | 1240 | 1000 | 0
2016-07-10 22:00 | 1752 | 1147.629 | 364 | 1240 | 1296.2963 | 0
2016-07-10 23:00 | 1752 | 970.026 | 364 | 1240 | 1238.9381 | 0
2016-07-11 | 1752 | 954.56 | 589 | 1240 | 1440 | 0
2016-07-11 01:00 | 1752 | 903.76 | 364 | 1240 | 1430.7692 | 0
2016-07-11 02:00 | 2311 | 824.125 | 364 | 1240 | 1430.7692 | 0
2016-07-11 03:00 | 2311 | 799.71 | 364 | 1240 | 1430.7692 | 0
2016-07-11 04:00 | 2311 | 784.738 | 435 | 1240 | 1430.7692 | 0
2016-07-11 05:00 | 2311 | 781.204 | 441 | 1240 | 1430.7692 | 0
2016-07-11 06:00 | 2144 | 780.178 | 537 | 1240 | 1430.7692 | 0
2016-07-11 07:00 | 2144 | 789.431 | 492 | 1240 | 1430.7692 | 0
2016-07-11 08:00 | 2144 | 902 | 673 | 1240 | 1430.7692 | 0
2016-07-11 09:00 | 2144 | 992.36 | 704 | 1240 | 1440 | 0
2016-07-11 10:00 | 2322 | 1027.197 | 784 | 1240 | 1238.9381 | 0
2016-07-11 11:00 | 2322 | 1219.386 | 663 | 1240 | 1296.2963 | 0
2016-07-11 12:00 | 2322 | 1354.32 | 657 | 1240 | 1000 | 0
2016-07-11 13:00 | 2322 | 1411.19 | 564 | 1240 | 1040 | 0
2016-07-11 14:00 | 2123 | 1456.246 | 497 | 1240 | 900 | 0
2016-07-11 15:00 | 2123 | 1472.02 | 451 | 1240 | 900 | 0
2016-07-11 16:00 | 2123 | 1492.832 | 471 | 1240 | 900 | 0
2016-07-11 17:00 | 2123 | 1496.88 | 465 | 1240 | 900 | 0
2016-07-11 18:00 | 2559 | 1472.262 | 364 | 1240 | 900 | 0
2016-07-11 19:00 | 2559 | 1432.53 | 374 | 1240 | 900 | 0
2016-07-11 20:00 | 2559 | 1379.334 | 364 | 1240 | 1040 | 0
2016-07-11 21:00 | 2559 | 1287.258 | 416 | 1240 | 1000 | 0
2016-07-11 22:00 | 1752 | 1208.529 | 364 | 1240 | 1296.2963 | 0
2016-07-11 23:00 | 1752 | 1007.133 | 364 | 1240 | 1440 | 0
2016-07-12 | 1752 | 880.365 | 589 | 1240 | 1430.7692 | 0
2016-07-12 01:00 | 1752 | 834.366 | 364 | 1240 | 1430.7692 | 0
2016-07-12 02:00 | 2311 | 804.137 | 364 | 1240 | 1430.7692 | 0
2016-07-12 03:00 | 2311 | 788.177 | 364 | 1240 | 1430.7692 | 0
2016-07-12 04:00 | 2311 | 789.393 | 435 | 1240 | 1430.7692 | 0
2016-07-12 05:00 | 2311 | 812.573 | 441 | 1240 | 1430.7692 | 0
2016-07-12 06:00 | 2144 | 847.932 | 537 | 1240 | 1430.7692 | 0
2016-07-12 07:00 | 2144 | 926.36 | 492 | 1240 | 1430.7692 | 0
2016-07-12 08:00 | 2144 | 987.44 | 673 | 1240 | 1440 | 0
2016-07-12 09:00 | 2144 | 1005.48 | 704 | 1240 | 1440 | 0
2016-07-12 10:00 | 2322 | 1190.007 | 784 | 1240 | 1296.2963 | 0
2016-07-12 11:00 | 2322 | 1314.83 | 663 | 1240 | 1000 | 0
2016-07-12 12:00 | 2322 | 1380.742 | 657 | 1240 | 1040 | 0
2016-07-12 13:00 | 2322 | 1430.968 | 564 | 1240 | 900 | 0
2016-07-12 14:00 | 2123 | 1467.4 | 497 | 1240 | 900 | 0
2016-07-12 15:00 | 2123 | 1474.22 | 451 | 1240 | 900 | 0
2016-07-12 16:00 | 2123 | 1482.096 | 471 | 1240 | 900 | 0
2016-07-12 17:00 | 2123 | 1467.466 | 465 | 1240 | 900 | 0
2016-07-12 18:00 | 2559 | 1440.978 | 364 | 1240 | 900 | 0
2016-07-12 19:00 | 2559 | 1399.376 | 374 | 1240 | 900 | 0
2016-07-12 20:00 | 2559 | 1355.926 | 364 | 1240 | 1040 | 0
2016-07-12 21:00 | 2559 | 1325.676 | 416 | 1240 | 1040 | 0
2016-07-12 22:00 | 1752 | 1182.636 | 364 | 1240 | 1296.2963 | 0
2016-07-12 23:00 | 1752 | 986.29 | 364 | 1240 | 1238.9381 | 0
2016-07-13 | 1752 | 942.76 | 589 | 1240 | 1440 | 0
2016-07-13 01:00 | 1752 | 896.18 | 364 | 1240 | 1440 | 0
2016-07-13 02:00 | 2311 | 823.365 | 364 | 1240 | 1440 | 0
2016-07-13 03:00 | 2311 | 809.419 | 364 | 1240 | 1440 | 0
2016-07-13 04:00 | 2311 | 807.063 | 435 | 1240 | 1440 | 0
2016-07-13 05:00 | 2311 | 831.345 | 441 | 1240 | 1440 | 0
2016-07-13 06:00 | 2144 | 909.5 | 537 | 1240 | 1440 | 0
2016-07-13 07:00 | 2144 | 932.22 | 492 | 1240 | 1440 | 0
2016-07-13 08:00 | 2144 | 930.905 | 673 | 1240 | 1440 | 0
2016-07-13 09:00 | 2144 | 993.814 | 704 | 1240 | 1238.9381 | 0
2016-07-13 10:00 | 2322 | 1173.48 | 784 | 1240 | 1296.2963 | 0
2016-07-13 11:00 | 2322 | 1305.854 | 663 | 1240 | 1040 | 0
2016-07-13 12:00 | 2322 | 1370.93 | 657 | 1240 | 900 | 0
2016-07-13 13:00 | 2322 | 1421.508 | 564 | 1240 | 900 | 0
2016-07-13 14:00 | 2123 | 1461.856 | 497 | 1240 | 900 | 0
2016-07-13 15:00 | 2123 | 1471.404 | 451 | 1240 | 900 | 0
2016-07-13 16:00 | 2123 | 1480.798 | 471 | 1240 | 900 | 0
2016-07-13 17:00 | 2123 | 1469.798 | 465 | 1240 | 900 | 0
2016-07-13 18:00 | 2559 | 1440.736 | 364 | 1240 | 900 | 0
2016-07-13 19:00 | 2559 | 1396.56 | 374 | 1240 | 1040 | 0
2016-07-13 20:00 | 2559 | 1354.54 | 364 | 1240 | 1000 | 0
2016-07-13 21:00 | 2559 | 1320.726 | 416 | 1240 | 1000 | 0
2016-07-13 22:00 | 1752 | 1179.696 | 364 | 1240 | 1238.9381 | 0
2016-07-13 23:00 | 1752 | 983.193 | 364 | 1240 | 1440 | 0
2016-07-14 | 1752 | 861.441 | 589 | 1240 | 1430.7692 | 0
2016-07-14 01:00 | 1752 | 816.582 | 364 | 1240 | 1430.7692 | 0
2016-07-14 02:00 | 2311 | 787.512 | 364 | 1240 | 1430.7692 | 0
2016-07-14 03:00 | 2311 | 770.241 | 364 | 1240 | 1430.7692 | 0
2016-07-14 04:00 | 2311 | 767.752 | 435 | 1240 | 1430.7692 | 0
2016-07-14 05:00 | 2311 | 789.488 | 441 | 1240 | 1430.7692 | 0
2016-07-14 06:00 | 2144 | 825.721 | 537 | 1240 | 1430.7692 | 0
2016-07-14 07:00 | 2144 | 893.12 | 492 | 1240 | 1430.7692 | 0
2016-07-14 08:00 | 2144 | 938.96 | 673 | 1240 | 1430.7692 | 0
2016-07-14 09:00 | 2144 | 1002.1 | 704 | 1240 | 1440 | 0
2016-07-14 10:00 | 2322 | 1017.431 | 784 | 1240 | 1238.9381 | 0
2016-07-14 11:00 | 2322 | 1190.763 | 663 | 1240 | 1296.2963 | 0
2016-07-14 12:00 | 2322 | 1239.588 | 657 | 1240 | 1296.2963 | 0
2016-07-14 13:00 | 2322 | 1294.986 | 564 | 1240 | 1000 | 0
2016-07-14 14:00 | 2123 | 1403.952 | 497 | 1240 | 1040 | 0
2016-07-14 15:00 | 2123 | 1434.51 | 451 | 1240 | 1040 | 0
2016-07-14 16:00 | 2123 | 1446.324 | 471 | 1240 | 1040 | 0
2016-07-14 17:00 | 2123 | 1442.848 | 465 | 1240 | 1040 | 0
2016-07-14 18:00 | 2559 | 1403.864 | 364 | 1240 | 1040 | 0
2016-07-14 19:00 | 2559 | 1302.861 | 374 | 1240 | 1000 | 0
2016-07-14 20:00 | 2559 | 1253.007 | 364 | 1240 | 1296.2963 | 0
2016-07-14 21:00 | 2559 | 1221.339 | 416 | 1240 | 1296.2963 | 0
2016-07-14 22:00 | 1752 | 1029.42 | 364 | 1240 | 1440 | 0
2016-07-14 23:00 | 1752 | 995.9 | 364 | 1240 | 1430.7692 | 0
2016-07-15 | 1752 | 854.563 | 589 | 1240 | 1430.7692 | 0
2016-07-15 01:00 | 1752 | 807.139 | 364 | 1240 | 1430.7692 | 0
2016-07-15 02:00 | 2311 | 776.72 | 364 | 1240 | 1430.7692 | 0
2016-07-15 03:00 | 2311 | 795 | 364 | 1240 | 1430.7692 | 0
2016-07-15 04:00 | 2311 | 788.26 | 435 | 1240 | 1430.7692 | 0
2016-07-15 05:00 | 2311 | 764.693 | 441 | 1240 | 1430.7692 | 0
2016-07-15 06:00 | 2144 | 792.566 | 537 | 1240 | 1430.7692 | 0
2016-07-15 07:00 | 2144 | 855.66 | 492 | 1240 | 1430.7692 | 0
2016-07-15 08:00 | 2144 | 910.94 | 673 | 1240 | 1440 | 0
2016-07-15 09:00 | 2144 | 930.012 | 704 | 1240 | 1238.9381 | 0
2016-07-15 10:00 | 2322 | 1102.668 | 784 | 1240 | 1296.2963 | 0
2016-07-15 11:00 | 2322 | 1166.214 | 663 | 1240 | 1000 | 0
2016-07-15 12:00 | 2322 | 1221.906 | 657 | 1240 | 1000 | 0
2016-07-15 13:00 | 2322 | 1338.282 | 564 | 1240 | 1000 | 0
2016-07-15 14:00 | 2123 | 1379.202 | 497 | 1240 | 1040 | 0
2016-07-15 15:00 | 2123 | 1404.216 | 451 | 1240 | 1040 | 0
2016-07-15 16:00 | 2123 | 1415.458 | 471 | 1240 | 1040 | 0
2016-07-15 17:00 | 2123 | 1409.298 | 465 | 1240 | 1040 | 0
2016-07-15 18:00 | 2559 | 1370.072 | 364 | 1240 | 1040 | 0
2016-07-15 19:00 | 2559 | 1330.868 | 374 | 1240 | 1040 | 0
2016-07-15 20:00 | 2559 | 1284.58 | 364 | 1240 | 1040 | 0
2016-07-15 21:00 | 2559 | 1248.896 | 416 | 1240 | 1000 | 0
2016-07-15 22:00 | 1752 | 1110.816 | 364 | 1240 | 1238.9381 | 0
2016-07-15 23:00 | 1752 | 922.716 | 364 | 1240 | 1440 | 0
2016-07-16 | 1752 | 940.94 | 589 | 1240 | 1440 | 0
2016-07-16 01:00 | 1752 | 885.2 | 364 | 1240 | 1440 | 0
2016-07-16 02:00 | 2311 | 803.662 | 364 | 1240 | 1440 | 0
2016-07-16 03:00 | 2311 | 778.81 | 364 | 1240 | 1440 | 0
2016-07-16 04:00 | 2311 | 771.818 | 435 | 1240 | 1440 | 0
2016-07-16 05:00 | 2311 | 787.056 | 441 | 1240 | 1440 | 0
2016-07-16 06:00 | 2144 | 859.74 | 537 | 1240 | 1440 | 0
2016-07-16 07:00 | 2144 | 880.64 | 492 | 1240 | 1440 | 0
2016-07-16 08:00 | 2144 | 891.1 | 673 | 1240 | 1238.9381 | 0
2016-07-16 09:00 | 2144 | 1059.702 | 704 | 1240 | 1296.2963 | 0
2016-07-16 10:00 | 2322 | 1145.025 | 784 | 1240 | 1296.2963 | 0
2016-07-16 11:00 | 2322 | 1275.56 | 663 | 1240 | 1000 | 0
2016-07-16 12:00 | 2322 | 1338.876 | 657 | 1240 | 900 | 0
2016-07-16 13:00 | 2322 | 1402.324 | 564 | 1240 | 900 | 0
2016-07-16 14:00 | 2123 | 1449.646 | 497 | 1240 | 900 | 0
2016-07-16 15:00 | 2123 | 1462.582 | 451 | 1240 | 900 | 0
2016-07-16 16:00 | 2123 | 1470.81 | 471 | 1240 | 900 | 0
2016-07-16 17:00 | 2123 | 1462.076 | 465 | 1240 | 900 | 0
2016-07-16 18:00 | 2559 | 1431.518 | 364 | 1240 | 900 | 0
2016-07-16 19:00 | 2559 | 1385.868 | 374 | 1240 | 900 | 0
2016-07-16 20:00 | 2559 | 1335.884 | 364 | 1240 | 1040 | 0
2016-07-16 21:00 | 2559 | 1294.282 | 416 | 1240 | 1040 | 0
2016-07-16 22:00 | 1752 | 1156.281 | 364 | 1240 | 1296.2963 | 0
2016-07-16 23:00 | 1752 | 967.556 | 364 | 1240 | 1238.9381 | 0
2016-07-17 | 1752 | 932.539 | 589 | 1240 | 1440 | 0
2016-07-17 01:00 | 1752 | 920.7 | 364 | 1240 | 1440 | 0
2016-07-17 02:00 | 2311 | 876.1 | 364 | 1240 | 1440 | 0
2016-07-17 03:00 | 2311 | 801.914 | 364 | 1240 | 1440 | 0
2016-07-17 04:00 | 2311 | 782.99 | 435 | 1240 | 1440 | 0
2016-07-17 05:00 | 2311 | 779.76 | 441 | 1240 | 1440 | 0
2016-07-17 06:00 | 2144 | 780.729 | 537 | 1240 | 1440 | 0
2016-07-17 07:00 | 2144 | 834.82 | 492 | 1240 | 1440 | 0
2016-07-17 08:00 | 2144 | 861.194 | 673 | 1240 | 1440 | 0
2016-07-17 09:00 | 2144 | 1046.136 | 704 | 1240 | 1238.9381 | 0
2016-07-17 10:00 | 2322 | 1196.734 | 784 | 1240 | 1000 | 0
2016-07-17 11:00 | 2322 | 1285.724 | 663 | 1240 | 1040 | 0
2016-07-17 12:00 | 2322 | 1360.876 | 657 | 1240 | 900 | 0
2016-07-17 13:00 | 2322 | 1414.49 | 564 | 1240 | 900 | 0
2016-07-17 14:00 | 2123 | 1455.146 | 497 | 1240 | 900 | 0
2016-07-17 15:00 | 2123 | 1470.172 | 451 | 1240 | 900 | 0
2016-07-17 16:00 | 2123 | 1486.738 | 471 | 1240 | 900 | 0
2016-07-17 17:00 | 2123 | 1475.276 | 465 | 1240 | 900 | 0
2016-07-17 18:00 | 2559 | 1441.176 | 364 | 1240 | 900 | 0
2016-07-17 19:00 | 2559 | 1391.94 | 374 | 1240 | 900 | 0
2016-07-17 20:00 | 2559 | 1337.842 | 364 | 1240 | 1040 | 0
2016-07-17 21:00 | 2559 | 1294.722 | 416 | 1240 | 1000 | 0
2016-07-17 22:00 | 1752 | 1159.326 | 364 | 1240 | 1238.9381 | 0
2016-07-17 23:00 | 1752 | 975.194 | 364 | 1240 | 1440 | 0
2016-07-18 | 1752 | 956.441 | 589 | 1240 | 1440 | 0
2016-07-18 01:00 | 1752 | 951.18 | 364 | 1240 | 1440 | 0
2016-07-18 02:00 | 2311 | 905.02 | 364 | 1240 | 1440 | 0
2016-07-18 03:00 | 2311 | 828.476 | 364 | 1240 | 1440 | 0
2016-07-18 04:00 | 2311 | 809.115 | 435 | 1240 | 1440 | 0
2016-07-18 05:00 | 2311 | 801.819 | 441 | 1240 | 1440 | 0
2016-07-18 06:00 | 2144 | 798.095 | 537 | 1240 | 1440 | 0
2016-07-18 07:00 | 2144 | 849.5 | 492 | 1240 | 1440 | 0
2016-07-18 08:00 | 2144 | 874.665 | 673 | 1240 | 1440 | 0
2016-07-18 09:00 | 2144 | 1062.285 | 704 | 1240 | 1296.2963 | 0
2016-07-18 10:00 | 2322 | 1150.863 | 784 | 1240 | 1296.2963 | 0
2016-07-18 11:00 | 2322 | 1293.534 | 663 | 1240 | 1040 | 0
2016-07-18 12:00 | 2322 | 1371.106 | 657 | 1240 | 900 | 0
2016-07-18 13:00 | 2322 | 1427.184 | 564 | 1240 | 900 | 0
2016-07-18 14:00 | 2123 | 1453.166 | 497 | 1240 | 900 | 0
2016-07-18 15:00 | 2123 | 1469.908 | 451 | 1240 | 900 | 0
2016-07-18 16:00 | 2123 | 1464.914 | 471 | 1240 | 900 | 0
2016-07-18 17:00 | 2123 | 1474.396 | 465 | 1240 | 900 | 0
2016-07-18 18:00 | 2559 | 1432.552 | 364 | 1240 | 900 | 0
2016-07-18 19:00 | 2559 | 1390.686 | 374 | 1240 | 1040 | 0
2016-07-18 20:00 | 2559 | 1348.204 | 364 | 1240 | 1040 | 0
2016-07-18 21:00 | 2559 | 1324.444 | 416 | 1240 | 1000 | 0
2016-07-18 22:00 | 1752 | 1190.616 | 364 | 1240 | 1238.9381 | 0
2016-07-18 23:00 | 1752 | 998.184 | 364 | 1240 | 1440 | 0
2016-07-19 | 1752 | 921.48 | 589 | 1240 | 1440 | 0
2016-07-19 01:00 | 1752 | 830.452 | 364 | 1240 | 1440 | 0
2016-07-19 02:00 | 2311 | 798.836 | 364 | 1240 | 1440 | 0
2016-07-19 03:00 | 2311 | 780.292 | 364 | 1240 | 1440 | 0
2016-07-19 04:00 | 2311 | 778.202 | 435 | 1240 | 1440 | 0
2016-07-19 05:00 | 2311 | 800.888 | 441 | 1240 | 1440 | 0
2016-07-19 06:00 | 2144 | 880.9 | 537 | 1240 | 1440 | 0
2016-07-19 07:00 | 2144 | 906.78 | 492 | 1240 | 1440 | 0
2016-07-19 08:00 | 2144 | 910.081 | 673 | 1240 | 1238.9381 | 0
2016-07-19 09:00 | 2144 | 1069.152 | 704 | 1240 | 1296.2963 | 0
2016-07-19 10:00 | 2322 | 1145.319 | 784 | 1240 | 1000 | 0
2016-07-19 11:00 | 2322 | 1272.7 | 663 | 1240 | 1040 | 0
2016-07-19 12:00 | 2322 | 1334.19 | 657 | 1240 | 900 | 0
2016-07-19 13:00 | 2322 | 1380.214 | 564 | 1240 | 900 | 0
2016-07-19 14:00 | 2123 | 1413.434 | 497 | 1240 | 900 | 0
2016-07-19 15:00 | 2123 | 1437.392 | 451 | 1240 | 900 | 0
2016-07-19 16:00 | 2123 | 1444.454 | 471 | 1240 | 900 | 0
2016-07-19 17:00 | 2123 | 1431.43 | 465 | 1240 | 900 | 0
2016-07-19 18:00 | 2559 | 1393.414 | 364 | 1240 | 900 | 0
2016-07-19 19:00 | 2559 | 1355.398 | 374 | 1240 | 1040 | 0
2016-07-19 20:00 | 2559 | 1256.997 | 364 | 1240 | 1000 | 0
2016-07-19 21:00 | 2559 | 1234.464 | 416 | 1240 | 1296.2963 | 0
2016-07-19 22:00 | 1752 | 1158.402 | 364 | 1240 | 1238.9381 | 0
2016-07-19 23:00 | 1752 | 967.195 | 364 | 1240 | 1440 | 0
2016-07-20 | 1752 | 922.5 | 589 | 1240 | 1440 | 0
2016-07-20 01:00 | 1752 | 829.882 | 364 | 1240 | 1440 | 0
2016-07-20 02:00 | 2311 | 799.064 | 364 | 1240 | 1440 | 0
2016-07-20 03:00 | 2311 | 780.349 | 364 | 1240 | 1440 | 0
2016-07-20 04:00 | 2311 | 777.157 | 435 | 1240 | 1440 | 0
2016-07-20 05:00 | 2311 | 798.133 | 441 | 1240 | 1440 | 0
2016-07-20 06:00 | 2144 | 877.56 | 537 | 1240 | 1440 | 0
2016-07-20 07:00 | 2144 | 902.72 | 492 | 1240 | 1440 | 0
2016-07-20 08:00 | 2144 | 905.844 | 673 | 1240 | 1440 | 0
2016-07-20 09:00 | 2144 | 967.632 | 704 | 1240 | 1238.9381 | 0
2016-07-20 10:00 | 2322 | 1141.77 | 784 | 1240 | 1296.2963 | 0
2016-07-20 11:00 | 2322 | 1213.716 | 663 | 1240 | 1000 | 0
2016-07-20 12:00 | 2322 | 1334.894 | 657 | 1240 | 1040 | 0
2016-07-20 13:00 | 2322 | 1387.892 | 564 | 1240 | 1040 | 0
2016-07-20 14:00 | 2123 | 1410.046 | 497 | 1240 | 1040 | 0
2016-07-20 15:00 | 2123 | 1418.648 | 451 | 1240 | 1040 | 0
2016-07-20 16:00 | 2123 | 1423.312 | 471 | 1240 | 1040 | 0
2016-07-20 17:00 | 2123 | 1415.634 | 465 | 1240 | 1040 | 0
2016-07-20 18:00 | 2559 | 1379.95 | 364 | 1240 | 1000 | 0
2016-07-20 19:00 | 2559 | 1283.184 | 374 | 1240 | 1000 | 0
2016-07-20 20:00 | 2559 | 1242.57 | 364 | 1240 | 1000 | 0
2016-07-20 21:00 | 2559 | 1215.963 | 416 | 1240 | 1296.2963 | 0
2016-07-20 22:00 | 1752 | 1139.292 | 364 | 1240 | 1238.9381 | 0
2016-07-20 23:00 | 1752 | 948.138 | 364 | 1240 | 1440 | 0
2016-07-21 | 1752 | 844.303 | 589 | 1240 | 1430.7692 | 0
2016-07-21 01:00 | 1752 | 799.881 | 364 | 1240 | 1430.7692 | 0
2016-07-21 02:00 | 2311 | 768.379 | 364 | 1240 | 1430.7692 | 0
2016-07-21 03:00 | 2311 | 787.04 | 364 | 1240 | 1430.7692 | 0
2016-07-21 04:00 | 2311 | 742.919 | 435 | 1240 | 1430.7692 | 0
2016-07-21 05:00 | 2311 | 761.216 | 441 | 1240 | 1430.7692 | 0
2016-07-21 06:00 | 2144 | 798.095 | 537 | 1240 | 1430.7692 | 0
2016-07-21 07:00 | 2144 | 864.7 | 492 | 1240 | 1430.7692 | 0
2016-07-21 08:00 | 2144 | 919.8 | 673 | 1240 | 1440 | 0
2016-07-21 09:00 | 2144 | 939.968 | 704 | 1240 | 1238.9381 | 0
2016-07-21 10:00 | 2322 | 1115.037 | 784 | 1240 | 1296.2963 | 0
2016-07-21 11:00 | 2322 | 1177.092 | 663 | 1240 | 1296.2963 | 0
2016-07-21 12:00 | 2322 | 1229.025 | 657 | 1240 | 1000 | 0
2016-07-21 13:00 | 2322 | 1273.881 | 564 | 1240 | 1000 | 0
2016-07-21 14:00 | 2123 | 1368.202 | 497 | 1240 | 1000 | 0
2016-07-21 15:00 | 2123 | 1386.022 | 451 | 1240 | 1000 | 0
2016-07-21 16:00 | 2123 | 1389.344 | 471 | 1240 | 1000 | 0
2016-07-21 17:00 | 2123 | 1307.397 | 465 | 1240 | 1000 | 0
2016-07-21 18:00 | 2559 | 1265.082 | 364 | 1240 | 1296.2963 | 0
2016-07-21 19:00 | 2559 | 1222.767 | 374 | 1240 | 1238.9381 | 0
2016-07-21 20:00 | 2559 | 1074.963 | 364 | 1240 | 1238.9381 | 0
2016-07-21 21:00 | 2559 | 1165.794 | 416 | 1240 | 1238.9381 | 0
2016-07-21 22:00 | 1752 | 991.021 | 364 | 1240 | 1440 | 0
2016-07-21 23:00 | 1752 | 963.5 | 364 | 1240 | 1430.7692 | 0
2016-07-22 | 1752 | 870.2 | 589 | 1240 | 1430.7692 | 0
2016-07-22 01:00 | 1752 | 829.217 | 364 | 1240 | 1430.7692 | 0
2016-07-22 02:00 | 2311 | 797.544 | 364 | 1240 | 1430.7692 | 0
2016-07-22 03:00 | 2311 | 778.411 | 364 | 1240 | 1430.7692 | 0
2016-07-22 04:00 | 2311 | 773.832 | 435 | 1240 | 1430.7692 | 0
2016-07-22 05:00 | 2311 | 792.699 | 441 | 1240 | 1430.7692 | 0
2016-07-22 06:00 | 2144 | 869.12 | 537 | 1240 | 1430.7692 | 0
2016-07-22 07:00 | 2144 | 892.3 | 492 | 1240 | 1430.7692 | 0
2016-07-22 08:00 | 2144 | 894.805 | 673 | 1240 | 1440 | 0
2016-07-22 09:00 | 2144 | 955.32 | 704 | 1240 | 1238.9381 | 0
2016-07-22 10:00 | 2322 | 1128.12 | 784 | 1240 | 1238.9381 | 0
2016-07-22 11:00 | 2322 | 1191.183 | 663 | 1240 | 1296.2963 | 0
2016-07-22 12:00 | 2322 | 1301.168 | 657 | 1240 | 1040 | 0
2016-07-22 13:00 | 2322 | 1347.302 | 564 | 1240 | 1040 | 0
2016-07-22 14:00 | 2123 | 1376.034 | 497 | 1240 | 1040 | 0
2016-07-22 15:00 | 2123 | 1392.182 | 451 | 1240 | 1040 | 0
2016-07-22 16:00 | 2123 | 1394.03 | 471 | 1240 | 1040 | 0
2016-07-22 17:00 | 2123 | 1369.83 | 465 | 1240 | 1040 | 0
2016-07-22 18:00 | 2559 | 1330.538 | 364 | 1240 | 1000 | 0
2016-07-22 19:00 | 2559 | 1232.574 | 374 | 1240 | 1296.2963 | 0
2016-07-22 20:00 | 2559 | 1203.783 | 364 | 1240 | 1238.9381 | 0
2016-07-22 21:00 | 2559 | 1065.33 | 416 | 1240 | 1238.9381 | 0
2016-07-22 22:00 | 1752 | 1002.934 | 364 | 1240 | 1440 | 0
2016-07-22 23:00 | 1752 | 979.36 | 364 | 1240 | 1440 | 0
2016-07-23 | 1752 | 961.18 | 589 | 1240 | 1440 | 0
2016-07-23 01:00 | 1752 | 911.68 | 364 | 1240 | 1440 | 0
2016-07-23 02:00 | 2311 | 834.271 | 364 | 1240 | 1440 | 0
2016-07-23 03:00 | 2311 | 814.017 | 364 | 1240 | 1440 | 0
2016-07-23 04:00 | 2311 | 809.704 | 435 | 1240 | 1440 | 0
2016-07-23 05:00 | 2311 | 832.618 | 441 | 1240 | 1440 | 0
2016-07-23 06:00 | 2144 | 916.74 | 537 | 1240 | 1440 | 0
2016-07-23 07:00 | 2144 | 942.28 | 492 | 1240 | 1440 | 0
2016-07-23 08:00 | 2144 | 950.019 | 673 | 1240 | 1440 | 0
2016-07-23 09:00 | 2144 | 1015.721 | 704 | 1240 | 1238.9381 | 0
2016-07-23 10:00 | 2322 | 1192.506 | 784 | 1240 | 1296.2963 | 0
2016-07-23 11:00 | 2322 | 1258.845 | 663 | 1240 | 1296.2963 | 0
2016-07-23 12:00 | 2322 | 1316.448 | 657 | 1240 | 1000 | 0
2016-07-23 13:00 | 2322 | 1431.936 | 564 | 1240 | 1040 | 0
2016-07-23 14:00 | 2123 | 1468.192 | 497 | 1240 | 1040 | 0
2016-07-23 15:00 | 2123 | 1468.588 | 451 | 1240 | 1040 | 0
2016-07-23 16:00 | 2123 | 1473.054 | 471 | 1240 | 1040 | 0
2016-07-23 17:00 | 2123 | 1429.912 | 465 | 1240 | 1040 | 0
2016-07-23 18:00 | 2559 | 1311.219 | 364 | 1240 | 1000 | 0
2016-07-23 19:00 | 2559 | 1257.543 | 374 | 1240 | 1296.2963 | 0
2016-07-23 20:00 | 2559 | 1106.769 | 364 | 1240 | 1238.9381 | 0
2016-07-23 21:00 | 2559 | 1081.518 | 416 | 1240 | 1238.9381 | 0
2016-07-23 22:00 | 1752 | 1016.063 | 364 | 1240 | 1238.9381 | 0
2016-07-23 23:00 | 1752 | 1000.9 | 364 | 1240 | 1440 | 0
2016-07-24 | 1752 | 974.64 | 589 | 1240 | 1440 | 0
2016-07-24 01:00 | 1752 | 923.9 | 364 | 1240 | 1440 | 0
2016-07-24 02:00 | 2311 | 837.767 | 364 | 1240 | 1440 | 0
2016-07-24 03:00 | 2311 | 813.618 | 364 | 1240 | 1440 | 0
2016-07-24 04:00 | 2311 | 799.14 | 435 | 1240 | 1440 | 0
2016-07-24 05:00 | 2311 | 799.539 | 441 | 1240 | 1440 | 0
2016-07-24 06:00 | 2144 | 808.678 | 537 | 1240 | 1440 | 0
2016-07-24 07:00 | 2144 | 814.891 | 492 | 1240 | 1440 | 0
2016-07-24 08:00 | 2144 | 921.38 | 673 | 1240 | 1440 | 0
2016-07-24 09:00 | 2144 | 955.776 | 704 | 1240 | 1238.9381 | 0
2016-07-24 10:00 | 2322 | 1145.172 | 784 | 1240 | 1296.2963 | 0
2016-07-24 11:00 | 2322 | 1225.728 | 663 | 1240 | 1000 | 0
2016-07-24 12:00 | 2322 | 1353.462 | 657 | 1240 | 1040 | 0
2016-07-24 13:00 | 2322 | 1413.346 | 564 | 1240 | 1040 | 0
2016-07-24 14:00 | 2123 | 1457.632 | 497 | 1240 | 1040 | 0
2016-07-24 15:00 | 2123 | 1472.636 | 451 | 1240 | 1040 | 0
2016-07-24 16:00 | 2123 | 1488.014 | 471 | 1240 | 1040 | 0
2016-07-24 17:00 | 2123 | 1472.042 | 465 | 1240 | 1040 | 0
2016-07-24 18:00 | 2559 | 1430.99 | 364 | 1240 | 1040 | 0
2016-07-24 19:00 | 2559 | 1374.802 | 374 | 1240 | 1000 | 0
2016-07-24 20:00 | 2559 | 1326.182 | 364 | 1240 | 1000 | 0
2016-07-24 21:00 | 2559 | 1280.598 | 416 | 1240 | 1000 | 0
2016-07-24 22:00 | 1752 | 1143.072 | 364 | 1240 | 1296.2963 | 0
2016-07-24 23:00 | 1752 | 962.502 | 364 | 1240 | 1440 | 0
2016-07-25 | 1752 | 913.634 | 589 | 1240 | 1440 | 0
2016-07-25 01:00 | 1752 | 909.72 | 364 | 1240 | 1440 | 0
2016-07-25 02:00 | 2311 | 869.82 | 364 | 1240 | 1440 | 0
2016-07-25 03:00 | 2311 | 795.91 | 364 | 1240 | 1440 | 0
2016-07-25 04:00 | 2311 | 775.504 | 435 | 1240 | 1440 | 0
2016-07-25 05:00 | 2311 | 768.151 | 441 | 1240 | 1440 | 0
2016-07-25 06:00 | 2144 | 765.035 | 537 | 1240 | 1440 | 0
2016-07-25 07:00 | 2144 | 812.2 | 492 | 1240 | 1440 | 0
2016-07-25 08:00 | 2144 | 880.18 | 673 | 1240 | 1440 | 0
2016-07-25 09:00 | 2144 | 921.234 | 704 | 1240 | 1238.9381 | 0
2016-07-25 10:00 | 2322 | 1120.308 | 784 | 1240 | 1296.2963 | 0
2016-07-25 11:00 | 2322 | 1275.78 | 663 | 1240 | 1040 | 0
2016-07-25 12:00 | 2322 | 1370.49 | 657 | 1240 | 1040 | 0
2016-07-25 13:00 | 2322 | 1439.746 | 564 | 1240 | 900 | 0
2016-07-25 14:00 | 2123 | 1473.428 | 497 | 1240 | 900 | 0
2016-07-25 15:00 | 2123 | 1500.356 | 451 | 1240 | 900 | 0
2016-07-25 16:00 | 2123 | 1508.782 | 471 | 1240 | 900 | 0
2016-07-25 17:00 | 2123 | 1499.168 | 465 | 1240 | 900 | 0
2016-07-25 18:00 | 2559 | 1466.96 | 364 | 1240 | 900 | 0
2016-07-25 19:00 | 2559 | 1419.66 | 374 | 1240 | 900 | 0
2016-07-25 20:00 | 2559 | 1377.156 | 364 | 1240 | 1040 | 0
2016-07-25 21:00 | 2559 | 1334.41 | 416 | 1240 | 1040 | 0
2016-07-25 22:00 | 1752 | 1190.238 | 364 | 1240 | 1000 | 0
2016-07-25 23:00 | 1752 | 988.361 | 364 | 1240 | 1238.9381 | 0
2016-07-26 | 1752 | 949.56 | 589 | 1240 | 1440 | 0
2016-07-26 01:00 | 1752 | 900.88 | 364 | 1240 | 1440 | 0
2016-07-26 02:00 | 2311 | 868.02 | 364 | 1240 | 1440 | 0
2016-07-26 03:00 | 2311 | 806.607 | 364 | 1240 | 1440 | 0
2016-07-26 04:00 | 2311 | 848.14 | 435 | 1240 | 1440 | 0
2016-07-26 05:00 | 2311 | 872.96 | 441 | 1240 | 1440 | 0
2016-07-26 06:00 | 2144 | 916.82 | 537 | 1240 | 1440 | 0
2016-07-26 07:00 | 2144 | 894.862 | 492 | 1240 | 1440 | 0
2016-07-26 08:00 | 2144 | 1036.476 | 673 | 1240 | 1238.9381 | 0
2016-07-26 09:00 | 2144 | 1101.807 | 704 | 1240 | 1296.2963 | 0
2016-07-26 10:00 | 2322 | 1236.928 | 784 | 1240 | 1040 | 0
2016-07-26 11:00 | 2322 | 1322.068 | 663 | 1240 | 900 | 0
2016-07-26 12:00 | 2322 | 1398.584 | 657 | 1240 | 900 | 0
2016-07-26 13:00 | 2322 | 1460.228 | 564 | 1240 | 900 | 0
2016-07-26 14:00 | 2123 | 1472.174 | 497 | 1240 | 900 | 0
2016-07-26 15:00 | 2123 | 1427.536 | 451 | 1240 | 900 | 0
2016-07-26 16:00 | 2123 | 1364.33 | 471 | 1240 | 900 | 0
2016-07-26 17:00 | 2123 | 1322.838 | 465 | 1240 | 1040 | 0
2016-07-26 18:00 | 2559 | 1282.27 | 364 | 1240 | 1000 | 0
2016-07-26 19:00 | 2559 | 1185.24 | 374 | 1240 | 1000 | 0
2016-07-26 20:00 | 2559 | 1163.442 | 364 | 1240 | 1296.2963 | 0
2016-07-26 21:00 | 2559 | 1137.003 | 416 | 1240 | 1296.2963 | 0
2016-07-26 22:00 | 1752 | 969 | 364 | 1240 | 1238.9381 | 0
2016-07-26 23:00 | 1752 | 893.646 | 364 | 1240 | 1440 | 0
2016-07-27 | 1752 | 863.52 | 589 | 1240 | 1440 | 0
2016-07-27 01:00 | 1752 | 781.47 | 364 | 1240 | 1440 | 0
2016-07-27 02:00 | 2311 | 755.174 | 364 | 1240 | 1440 | 0
2016-07-27 03:00 | 2311 | 741.361 | 364 | 1240 | 1440 | 0
2016-07-27 04:00 | 2311 | 744.382 | 435 | 1240 | 1440 | 0
2016-07-27 05:00 | 2311 | 814.42 | 441 | 1240 | 1440 | 0
2016-07-27 06:00 | 2144 | 863.88 | 537 | 1240 | 1440 | 0
2016-07-27 07:00 | 2144 | 845.082 | 492 | 1240 | 1440 | 0
2016-07-27 08:00 | 2144 | 879.016 | 673 | 1240 | 1238.9381 | 0
2016-07-27 09:00 | 2144 | 923.628 | 704 | 1240 | 1238.9381 | 0
2016-07-27 10:00 | 2322 | 1088.934 | 784 | 1240 | 1296.2963 | 0
2016-07-27 11:00 | 2322 | 1213.014 | 663 | 1240 | 1040 | 0
2016-07-27 12:00 | 2322 | 1272.018 | 657 | 1240 | 1040 | 0
2016-07-27 13:00 | 2322 | 1320.88 | 564 | 1240 | 1040 | 0
2016-07-27 14:00 | 2123 | 1359.116 | 497 | 1240 | 1040 | 0
2016-07-27 15:00 | 2123 | 1382.546 | 451 | 1240 | 1040 | 0
2016-07-27 16:00 | 2123 | 1387.474 | 471 | 1240 | 1040 | 0
2016-07-27 17:00 | 2123 | 1371.634 | 465 | 1240 | 1040 | 0
2016-07-27 18:00 | 2559 | 1328.756 | 364 | 1240 | 1000 | 0
2016-07-27 19:00 | 2559 | 1227.45 | 374 | 1240 | 1296.2963 | 0
2016-07-27 20:00 | 2559 | 1199.583 | 364 | 1240 | 1296.2963 | 0
2016-07-27 21:00 | 2559 | 1063.088 | 416 | 1240 | 1238.9381 | 0
2016-07-27 22:00 | 1752 | 996.968 | 364 | 1240 | 1440 | 0
2016-07-27 23:00 | 1752 | 965.4 | 364 | 1240 | 1440 | 0
2016-07-28 | 1752 | 809.552 | 589 | 1240 | 1430.7692 | 0
2016-07-28 01:00 | 1752 | 769.082 | 364 | 1240 | 1430.7692 | 0
2016-07-28 02:00 | 2311 | 741.532 | 364 | 1240 | 1430.7692 | 0
2016-07-28 03:00 | 2311 | 766.38 | 364 | 1240 | 1430.7692 | 0
2016-07-28 04:00 | 2311 | 730.36 | 435 | 1240 | 1430.7692 | 0
2016-07-28 05:00 | 2311 | 756.732 | 441 | 1240 | 1430.7692 | 0
2016-07-28 06:00 | 2144 | 847.32 | 537 | 1240 | 1430.7692 | 0
2016-07-28 07:00 | 2144 | 863.36 | 492 | 1240 | 1440 | 0
2016-07-28 08:00 | 2144 | 902.78 | 673 | 1240 | 1440 | 0
2016-07-28 09:00 | 2144 | 914.85 | 704 | 1240 | 1238.9381 | 0
2016-07-28 10:00 | 2322 | 973.807 | 784 | 1240 | 1238.9381 | 0
2016-07-28 11:00 | 2322 | 1128.078 | 663 | 1240 | 1296.2963 | 0
2016-07-28 12:00 | 2322 | 1152.312 | 657 | 1240 | 1000 | 0
2016-07-28 13:00 | 2322 | 1183.602 | 564 | 1240 | 1000 | 0
2016-07-28 14:00 | 2123 | 1267.508 | 497 | 1240 | 1000 | 0
2016-07-28 15:00 | 2123 | 1289.662 | 451 | 1240 | 1000 | 0
2016-07-28 16:00 | 2123 | 1302.092 | 471 | 1240 | 1000 | 0
2016-07-28 17:00 | 2123 | 1294.392 | 465 | 1240 | 1000 | 0
2016-07-28 18:00 | 2559 | 1193.745 | 364 | 1240 | 1000 | 0
2016-07-28 19:00 | 2559 | 1151.934 | 374 | 1240 | 1296.2963 | 0
2016-07-28 20:00 | 2559 | 1130.367 | 364 | 1240 | 1296.2963 | 0
2016-07-28 21:00 | 2559 | 1006.924 | 416 | 1240 | 1238.9381 | 0
2016-07-28 22:00 | 1752 | 937.422 | 364 | 1240 | 1440 | 0
2016-07-28 23:00 | 1752 | 908.74 | 364 | 1240 | 1430.7692 | 0
2016-07-29 | 1752 | 794.39 | 589 | 1240 | 1430.7692 | 0
2016-07-29 01:00 | 1752 | 753.901 | 364 | 1240 | 1430.7692 | 0
2016-07-29 02:00 | 2311 | 727.985 | 364 | 1240 | 1430.7692 | 0
2016-07-29 03:00 | 2311 | 714.001 | 364 | 1240 | 1430.7692 | 0
2016-07-29 04:00 | 2311 | 715.445 | 435 | 1240 | 1430.7692 | 0
2016-07-29 05:00 | 2311 | 739.575 | 441 | 1240 | 1430.7692 | 0
2016-07-29 06:00 | 2144 | 821.28 | 537 | 1240 | 1430.7692 | 0
2016-07-29 07:00 | 2144 | 845.24 | 492 | 1240 | 1430.7692 | 0
2016-07-29 08:00 | 2144 | 886.74 | 673 | 1240 | 1440 | 0
2016-07-29 09:00 | 2144 | 904.305 | 704 | 1240 | 1238.9381 | 0
2016-07-29 10:00 | 2322 | 1080.135 | 784 | 1240 | 1296.2963 | 0
2016-07-29 11:00 | 2322 | 1153.425 | 663 | 1240 | 1000 | 0
2016-07-29 12:00 | 2322 | 1212.477 | 657 | 1240 | 1000 | 0
2016-07-29 13:00 | 2322 | 1327.986 | 564 | 1240 | 1000 | 0
2016-07-29 14:00 | 2123 | 1370.996 | 497 | 1240 | 1040 | 0
2016-07-29 15:00 | 2123 | 1397.198 | 451 | 1240 | 1040 | 0
2016-07-29 16:00 | 2123 | 1401.686 | 471 | 1240 | 1040 | 0
2016-07-29 17:00 | 2123 | 1380.786 | 465 | 1240 | 1000 | 0
2016-07-29 18:00 | 2559 | 1274.826 | 364 | 1240 | 1000 | 0
2016-07-29 19:00 | 2559 | 1231.65 | 374 | 1240 | 1296.2963 | 0
2016-07-29 20:00 | 2559 | 1196.643 | 364 | 1240 | 1296.2963 | 0
2016-07-29 21:00 | 2559 | 1054.576 | 416 | 1240 | 1238.9381 | 0
2016-07-29 22:00 | 1752 | 985.568 | 364 | 1240 | 1238.9381 | 0
2016-07-29 23:00 | 1752 | 954.76 | 364 | 1240 | 1440 | 0
2016-07-30 | 1752 | 916.46 | 589 | 1240 | 1430.7692 | 0
2016-07-30 01:00 | 1752 | 824.771 | 364 | 1240 | 1430.7692 | 0
2016-07-30 02:00 | 2311 | 793.079 | 364 | 1240 | 1430.7692 | 0
2016-07-30 03:00 | 2311 | 773.642 | 364 | 1240 | 1430.7692 | 0
2016-07-30 04:00 | 2311 | 769.348 | 435 | 1240 | 1430.7692 | 0
2016-07-30 05:00 | 2311 | 788.804 | 441 | 1240 | 1430.7692 | 0
2016-07-30 06:00 | 2144 | 819.812 | 537 | 1240 | 1430.7692 | 0
2016-07-30 07:00 | 2144 | 886.42 | 492 | 1240 | 1440 | 0
2016-07-30 08:00 | 2144 | 949.72 | 673 | 1240 | 1440 | 0
2016-07-30 09:00 | 2144 | 972.952 | 704 | 1240 | 1238.9381 | 0
2016-07-30 10:00 | 2322 | 1161.615 | 784 | 1240 | 1000 | 0
2016-07-30 11:00 | 2322 | 1294.656 | 663 | 1240 | 1040 | 0
2016-07-30 12:00 | 2322 | 1361.58 | 657 | 1240 | 900 | 0
2016-07-30 13:00 | 2322 | 1425.908 | 564 | 1240 | 900 | 0
2016-07-30 14:00 | 2123 | 1474.088 | 497 | 1240 | 900 | 0
2016-07-30 15:00 | 2123 | 1494.416 | 451 | 1240 | 900 | 0
2016-07-30 16:00 | 2123 | 1509.816 | 471 | 1240 | 900 | 0
2016-07-30 17:00 | 2123 | 1500.532 | 465 | 1240 | 900 | 0
2016-07-30 18:00 | 2559 | 1462.01 | 364 | 1240 | 900 | 0
2016-07-30 19:00 | 2559 | 1408.352 | 374 | 1240 | 900 | 0
2016-07-30 20:00 | 2559 | 1356.476 | 364 | 1240 | 1040 | 0
2016-07-30 21:00 | 2559 | 1314.016 | 416 | 1240 | 1000 | 0
2016-07-30 22:00 | 1752 | 1173.06 | 364 | 1240 | 1238.9381 | 0
2016-07-30 23:00 | 1752 | 983.801 | 364 | 1240 | 1440 | 0
2016-07-31 | 1752 | 998.04 | 589 | 1240 | 1440 | 0
2016-07-31 01:00 | 1752 | 939.94 | 364 | 1240 | 1440 | 0
2016-07-31 02:00 | 2311 | 852.055 | 364 | 1240 | 1440 | 0
2016-07-31 03:00 | 2311 | 822.681 | 364 | 1240 | 1440 | 0
2016-07-31 04:00 | 2311 | 806.55 | 435 | 1240 | 1440 | 0
2016-07-31 05:00 | 2311 | 803.795 | 441 | 1240 | 1440 | 0
2016-07-31 06:00 | 2144 | 849.9 | 537 | 1240 | 1440 | 0
2016-07-31 07:00 | 2144 | 859.8 | 492 | 1240 | 1440 | 0
2016-07-31 08:00 | 2144 | 919.98 | 673 | 1240 | 1440 | 0
2016-07-31 09:00 | 2144 | 950.817 | 704 | 1240 | 1238.9381 | 0
2016-07-31 10:00 | 2322 | 1143.849 | 784 | 1240 | 1000 | 0
2016-07-31 11:00 | 2322 | 1289.662 | 663 | 1240 | 1040 | 0
2016-07-31 12:00 | 2322 | 1368.334 | 657 | 1240 | 900 | 0
2016-07-31 13:00 | 2322 | 1434.048 | 564 | 1240 | 900 | 0
2016-07-31 14:00 | 2123 | 1474.726 | 497 | 1240 | 900 | 0
2016-07-31 15:00 | 2123 | 1513.644 | 451 | 1240 | 900 | 0
2016-07-31 16:00 | 2123 | 1537.492 | 471 | 1240 | 900 | 0
2016-07-31 17:00 | 2123 | 1535.666 | 465 | 1240 | 900 | 0
2016-07-31 18:00 | 2559 | 1489.532 | 364 | 1240 | 900 | 0
2016-07-31 19:00 | 2559 | 1458.512 | 374 | 1240 | 900 | 0
2016-07-31 20:00 | 2559 | 1396.45 | 364 | 1240 | 1040 | 0
2016-07-31 21:00 | 2559 | 1344.222 | 416 | 1240 | 1000 | 0
2016-07-31 22:00 | 1752 | 1082.981 | 364 | 1240 | 1238.9381 | 0
2016-07-31 23:00 | 1752 | 1004.416 | 364 | 1240 | 1440 | 0
2016-08-01 | 1994 | 1014.34 | 647 | 1240 | 1440 | 0
2016-08-01 01:00 | 1994 | 955.68 | 374 | 1240 | 1440 | 0
2016-08-01 02:00 | 2308 | 908 | 374 | 1240 | 1440 | 0
2016-08-01 03:00 | 2308 | 829.825 | 394 | 1240 | 1440 | 0
2016-08-01 04:00 | 2308 | 806.987 | 374 | 1240 | 1440 | 0
2016-08-01 05:00 | 2308 | 796.423 | 560 | 1240 | 1440 | 0
2016-08-01 06:00 | 2483 | 790.476 | 641 | 1240 | 1440 | 0
2016-08-01 07:00 | 2483 | 834.9 | 549 | 1240 | 1440 | 0
2016-08-01 08:00 | 2483 | 857.394 | 615 | 1240 | 1440 | 0
2016-08-01 09:00 | 2483 | 1044.582 | 810 | 1240 | 1238.9381 | 0
2016-08-01 10:00 | 2674 | 1203.532 | 766 | 1240 | 1000 | 0
2016-08-01 11:00 | 2674 | 1312.564 | 747 | 1240 | 900 | 0
2016-08-01 12:00 | 2674 | 1414.49 | 766 | 1240 | 900 | 0
2016-08-01 13:00 | 2674 | 1498.332 | 733 | 1240 | 900 | 0
2016-08-01 14:00 | 3275 | 1545.874 | 561 | 1240 | 900 | 0
2016-08-01 15:00 | 3275 | 1587.982 | 457 | 1240 | 900 | 0
2016-08-01 16:00 | 3275 | 1612.688 | 498 | 1240 | 900 | 0
2016-08-01 17:00 | 3275 | 1614.866 | 386 | 1240 | 900 | 0
2016-08-01 18:00 | 3174 | 1572.362 | 374 | 1240 | 900 | 0
2016-08-01 19:00 | 3174 | 1529.836 | 374 | 1240 | 900 | 0
2016-08-01 20:00 | 3174 | 1483.416 | 374 | 1240 | 900 | 0
2016-08-01 21:00 | 3174 | 1436.424 | 374 | 1240 | 1040 | 0
2016-08-01 22:00 | 1994 | 1274.637 | 374 | 1240 | 1000 | 0
2016-08-01 23:00 | 1994 | 1057.198 | 374 | 1240 | 1238.9381 | 0
2016-08-02 | 1994 | 971.84 | 647 | 1240 | 1440 | 0
2016-08-02 01:00 | 1994 | 869.326 | 374 | 1240 | 1440 | 0
2016-08-02 02:00 | 2308 | 830.129 | 374 | 1240 | 1440 | 0
2016-08-02 03:00 | 2308 | 804.213 | 394 | 1240 | 1440 | 0
2016-08-02 04:00 | 2308 | 794.827 | 374 | 1240 | 1440 | 0
2016-08-02 05:00 | 2308 | 810.198 | 560 | 1240 | 1440 | 0
2016-08-02 06:00 | 2483 | 885.36 | 641 | 1240 | 1440 | 0
2016-08-02 07:00 | 2483 | 908.62 | 549 | 1240 | 1440 | 0
2016-08-02 08:00 | 2483 | 920.911 | 615 | 1240 | 1238.9381 | 0
2016-08-02 09:00 | 2483 | 1101.681 | 810 | 1240 | 1296.2963 | 0
2016-08-02 10:00 | 2674 | 1253.912 | 766 | 1240 | 1000 | 0
2016-08-02 11:00 | 2674 | 1349.128 | 747 | 1240 | 1040 | 0
2016-08-02 12:00 | 2674 | 1437.37 | 766 | 1240 | 900 | 0
2016-08-02 13:00 | 2674 | 1513.908 | 733 | 1240 | 900 | 0
2016-08-02 14:00 | 3275 | 1556.918 | 561 | 1240 | 900 | 0
2016-08-02 15:00 | 3275 | 1590.842 | 457 | 1240 | 900 | 0
2016-08-02 16:00 | 3275 | 1603.602 | 498 | 1240 | 900 | 0
2016-08-02 17:00 | 3275 | 1593.306 | 386 | 1240 | 900 | 0
2016-08-02 18:00 | 3174 | 1546.908 | 374 | 1240 | 900 | 0
2016-08-02 19:00 | 3174 | 1515.624 | 374 | 1240 | 900 | 0
2016-08-02 20:00 | 3174 | 1466.168 | 374 | 1240 | 900 | 0
2016-08-02 21:00 | 3174 | 1418.054 | 374 | 1240 | 1040 | 0
2016-08-02 22:00 | 1994 | 1258.887 | 374 | 1240 | 1296.2963 | 0
2016-08-02 23:00 | 1994 | 1043.765 | 374 | 1240 | 1238.9381 | 0
2016-08-03 | 1994 | 990.64 | 647 | 1240 | 1440 | 0
2016-08-03 01:00 | 1994 | 885.609 | 374 | 1240 | 1440 | 0
2016-08-03 02:00 | 2308 | 845.842 | 374 | 1240 | 1440 | 0
2016-08-03 03:00 | 2308 | 822.092 | 394 | 1240 | 1440 | 0
2016-08-03 04:00 | 2308 | 811.11 | 374 | 1240 | 1440 | 0
2016-08-03 05:00 | 2308 | 825.284 | 560 | 1240 | 1440 | 0
2016-08-03 06:00 | 2483 | 899.08 | 641 | 1240 | 1440 | 0
2016-08-03 07:00 | 2483 | 919.66 | 549 | 1240 | 1440 | 0
2016-08-03 08:00 | 2483 | 926.231 | 615 | 1240 | 1238.9381 | 0
2016-08-03 09:00 | 2483 | 1105.86 | 810 | 1240 | 1296.2963 | 0
2016-08-03 10:00 | 2674 | 1256.354 | 766 | 1240 | 1040 | 0
2016-08-03 11:00 | 2674 | 1348.072 | 747 | 1240 | 900 | 0
2016-08-03 12:00 | 2674 | 1428.306 | 766 | 1240 | 900 | 0
2016-08-03 13:00 | 2674 | 1501.94 | 733 | 1240 | 900 | 0
2016-08-03 14:00 | 3275 | 1536.304 | 561 | 1240 | 900 | 0
2016-08-03 15:00 | 3275 | 1561.758 | 457 | 1240 | 900 | 0
2016-08-03 16:00 | 3275 | 1566.07 | 498 | 1240 | 900 | 0
2016-08-03 17:00 | 3275 | 1552.892 | 386 | 1240 | 900 | 0
2016-08-03 18:00 | 3174 | 1521.586 | 374 | 1240 | 900 | 0
2016-08-03 19:00 | 3174 | 1475.166 | 374 | 1240 | 900 | 0
2016-08-03 20:00 | 3174 | 1431.958 | 374 | 1240 | 1040 | 0
2016-08-03 21:00 | 3174 | 1388.464 | 374 | 1240 | 1000 | 0
2016-08-03 22:00 | 1994 | 1238.37 | 374 | 1240 | 1296.2963 | 0
2016-08-03 23:00 | 1994 | 1028.736 | 374 | 1240 | 1238.9381 | 0
2016-08-04 | 1994 | 961.68 | 647 | 1240 | 1440 | 0
2016-08-04 01:00 | 1994 | 909.12 | 374 | 1240 | 1440 | 0
2016-08-04 02:00 | 2308 | 828.4 | 374 | 1240 | 1440 | 0
2016-08-04 03:00 | 2308 | 806.949 | 394 | 1240 | 1440 | 0
2016-08-04 04:00 | 2308 | 800.128 | 374 | 1240 | 1440 | 0
2016-08-04 05:00 | 2308 | 818.653 | 560 | 1240 | 1440 | 0
2016-08-04 06:00 | 2483 | 898.02 | 641 | 1240 | 1440 | 0
2016-08-04 07:00 | 2483 | 873.62 | 549 | 1240 | 1440 | 0
2016-08-04 08:00 | 2483 | 920.607 | 615 | 1240 | 1238.9381 | 0
2016-08-04 09:00 | 2483 | 1092 | 810 | 1240 | 1296.2963 | 0
2016-08-04 10:00 | 2674 | 1230.57 | 766 | 1240 | 1000 | 0
2016-08-04 11:00 | 2674 | 1313.004 | 747 | 1240 | 900 | 0
2016-08-04 12:00 | 2674 | 1384.174 | 766 | 1240 | 900 | 0
2016-08-04 13:00 | 2674 | 1446.654 | 733 | 1240 | 900 | 0
2016-08-04 14:00 | 3275 | 1494.482 | 561 | 1240 | 900 | 0
2016-08-04 15:00 | 3275 | 1516.46 | 457 | 1240 | 900 | 0
2016-08-04 16:00 | 3275 | 1524.424 | 498 | 1240 | 900 | 0
2016-08-04 17:00 | 3275 | 1517.472 | 386 | 1240 | 900 | 0
2016-08-04 18:00 | 3174 | 1475.32 | 374 | 1240 | 900 | 0
2016-08-04 19:00 | 3174 | 1433.168 | 374 | 1240 | 900 | 0
2016-08-04 20:00 | 3174 | 1389.146 | 374 | 1240 | 1040 | 0
2016-08-04 21:00 | 3174 | 1343.188 | 374 | 1240 | 1040 | 0
2016-08-04 22:00 | 1994 | 1244.342 | 374 | 1240 | 1000 | 0
2016-08-04 23:00 | 1994 | 990.109 | 374 | 1240 | 1238.9381 | 0
2016-08-05 | 1994 | 973.3 | 647 | 1240 | 1440 | 0
2016-08-05 01:00 | 1994 | 918.12 | 374 | 1240 | 1440 | 0
2016-08-05 02:00 | 2308 | 877.42 | 374 | 1240 | 1440 | 0
2016-08-05 03:00 | 2308 | 851.94 | 394 | 1240 | 1440 | 0
2016-08-05 04:00 | 2308 | 841.8 | 374 | 1240 | 1440 | 0
2016-08-05 05:00 | 2308 | 859.34 | 560 | 1240 | 1440 | 0
2016-08-05 06:00 | 2483 | 896.44 | 641 | 1240 | 1440 | 0
2016-08-05 07:00 | 2483 | 911.52 | 549 | 1240 | 1440 | 0
2016-08-05 08:00 | 2483 | 917.244 | 615 | 1240 | 1238.9381 | 0
2016-08-05 09:00 | 2483 | 1093.113 | 810 | 1240 | 1296.2963 | 0
2016-08-05 10:00 | 2674 | 1237.764 | 766 | 1240 | 1040 | 0
2016-08-05 11:00 | 2674 | 1324.07 | 747 | 1240 | 900 | 0
2016-08-05 12:00 | 2674 | 1399.31 | 766 | 1240 | 900 | 0
2016-08-05 13:00 | 2674 | 1464.232 | 733 | 1240 | 900 | 0
2016-08-05 14:00 | 3275 | 1507.484 | 561 | 1240 | 900 | 0
2016-08-05 15:00 | 3275 | 1513.226 | 457 | 1240 | 900 | 0
2016-08-05 16:00 | 3275 | 1517.472 | 498 | 1240 | 900 | 0
2016-08-05 17:00 | 3275 | 1522.334 | 386 | 1240 | 900 | 0
2016-08-05 18:00 | 3174 | 1476.86 | 374 | 1240 | 900 | 0
2016-08-05 19:00 | 3174 | 1431.364 | 374 | 1240 | 900 | 0
2016-08-05 20:00 | 3174 | 1396.186 | 374 | 1240 | 900 | 0
2016-08-05 21:00 | 3174 | 1353.396 | 374 | 1240 | 1040 | 0
2016-08-05 22:00 | 1994 | 1202.145 | 374 | 1240 | 1000 | 0
2016-08-05 23:00 | 1994 | 1109.346 | 374 | 1240 | 1296.2963 | 0
2016-08-06 | 1994 | 984.086 | 647 | 1240 | 1296.2963 | 0
2016-08-06 01:00 | 1994 | 927.96 | 374 | 1240 | 1296.2963 | 0
2016-08-06 02:00 | 2308 | 890.948 | 374 | 1240 | 1238.9381 | 0
2016-08-06 03:00 | 2308 | 907.16 | 394 | 1240 | 1238.9381 | 0
2016-08-06 04:00 | 2308 | 897.42 | 374 | 1240 | 1238.9381 | 0
2016-08-06 05:00 | 2308 | 870.485 | 560 | 1240 | 1238.9381 | 0
2016-08-06 06:00 | 2483 | 902.12 | 641 | 1240 | 1238.9381 | 0
2016-08-06 07:00 | 2483 | 915.914 | 549 | 1240 | 1296.2963 | 0
2016-08-06 08:00 | 2483 | 1070.013 | 615 | 1240 | 1000 | 0
2016-08-06 09:00 | 2483 | 1203.576 | 810 | 1240 | 1040 | 0
2016-08-06 10:00 | 2674 | 1300.794 | 766 | 1240 | 900 | 0
2016-08-06 11:00 | 2674 | 1391.148 | 747 | 1240 | 900 | 0
2016-08-06 12:00 | 2674 | 1467.532 | 766 | 1240 | 900 | 0
2016-08-06 13:00 | 2674 | 1521.674 | 733 | 1240 | 900 | 0
2016-08-06 14:00 | 3275 | 1570.778 | 561 | 1240 | 900 | 0
2016-08-06 15:00 | 3275 | 1592.514 | 457 | 1240 | 900 | 0
2016-08-06 16:00 | 3275 | 1580.436 | 498 | 1240 | 900 | 0
2016-08-06 17:00 | 3275 | 1535.204 | 386 | 1240 | 900 | 0
2016-08-06 18:00 | 3174 | 1480.842 | 374 | 1240 | 900 | 0
2016-08-06 19:00 | 3174 | 1411.344 | 374 | 1240 | 900 | 0
2016-08-06 20:00 | 3174 | 1368.29 | 374 | 1240 | 900 | 0
2016-08-06 21:00 | 3174 | 1320.352 | 374 | 1240 | 1040 | 0
2016-08-06 22:00 | 1994 | 1182.888 | 374 | 1240 | 1000 | 0
2016-08-06 23:00 | 1994 | 1098.699 | 374 | 1240 | 1296.2963 | 0
2016-08-07 | 1994 | 979.583 | 647 | 1240 | 1238.9381 | 0
2016-08-07 01:00 | 1994 | 929.86 | 374 | 1240 | 1238.9381 | 0
2016-08-07 02:00 | 2308 | 936.22 | 374 | 1240 | 1238.9381 | 0
2016-08-07 03:00 | 2308 | 907.58 | 394 | 1240 | 1238.9381 | 0
2016-08-07 04:00 | 2308 | 892.6 | 374 | 1240 | 1238.9381 | 0
2016-08-07 05:00 | 2308 | 892.52 | 560 | 1240 | 1238.9381 | 0
2016-08-07 06:00 | 2483 | 902.58 | 641 | 1240 | 1238.9381 | 0
2016-08-07 07:00 | 2483 | 911.02 | 549 | 1240 | 1238.9381 | 0
2016-08-07 08:00 | 2483 | 921.386 | 615 | 1240 | 1238.9381 | 0
2016-08-07 09:00 | 2483 | 1104.999 | 810 | 1240 | 1296.2963 | 0
2016-08-07 10:00 | 2674 | 1258.158 | 766 | 1240 | 1040 | 0
2016-08-07 11:00 | 2674 | 1353.462 | 747 | 1240 | 900 | 0
2016-08-07 12:00 | 2674 | 1436.578 | 766 | 1240 | 900 | 0
2016-08-07 13:00 | 2674 | 1498.376 | 733 | 1240 | 900 | 0
2016-08-07 14:00 | 3275 | 1526.888 | 561 | 1240 | 900 | 0
2016-08-07 15:00 | 3275 | 1554.96 | 457 | 1240 | 900 | 0
2016-08-07 16:00 | 3275 | 1564.31 | 498 | 1240 | 900 | 0
2016-08-07 17:00 | 3275 | 1552.892 | 386 | 1240 | 900 | 0
2016-08-07 18:00 | 3174 | 1526.558 | 374 | 1240 | 900 | 0
2016-08-07 19:00 | 3174 | 1485.132 | 374 | 1240 | 900 | 0
2016-08-07 20:00 | 3174 | 1445.774 | 374 | 1240 | 900 | 0
2016-08-07 21:00 | 3174 | 1404.26 | 374 | 1240 | 1040 | 0
2016-08-07 22:00 | 1994 | 1267.245 | 374 | 1240 | 1000 | 0
2016-08-07 23:00 | 1994 | 1184.085 | 374 | 1240 | 1296.2963 | 0
2016-08-08 | 1994 | 1005.822 | 647 | 1240 | 1440 | 0
2016-08-08 01:00 | 1994 | 1001.38 | 374 | 1240 | 1440 | 0
2016-08-08 02:00 | 2308 | 959.92 | 374 | 1240 | 1440 | 0
2016-08-08 03:00 | 2308 | 928.72 | 394 | 1240 | 1440 | 0
2016-08-08 04:00 | 2308 | 861.517 | 374 | 1240 | 1440 | 0
2016-08-08 05:00 | 2308 | 852.682 | 560 | 1240 | 1440 | 0
2016-08-08 06:00 | 2483 | 893.84 | 641 | 1240 | 1440 | 0
2016-08-08 07:00 | 2483 | 894.9 | 549 | 1240 | 1440 | 0
2016-08-08 08:00 | 2483 | 915.192 | 615 | 1240 | 1238.9381 | 0
2016-08-08 09:00 | 2483 | 1104.327 | 810 | 1240 | 1238.9381 | 0
2016-08-08 10:00 | 2674 | 1197.861 | 766 | 1240 | 1000 | 0
2016-08-08 11:00 | 2674 | 1349.392 | 747 | 1240 | 1040 | 0
2016-08-08 12:00 | 2674 | 1430.462 | 766 | 1240 | 900 | 0
2016-08-08 13:00 | 2674 | 1492.678 | 733 | 1240 | 900 | 0
2016-08-08 14:00 | 3275 | 1520.948 | 561 | 1240 | 900 | 0
2016-08-08 15:00 | 3275 | 1549.966 | 457 | 1240 | 900 | 0
2016-08-08 16:00 | 3275 | 1563.65 | 498 | 1240 | 900 | 0
2016-08-08 17:00 | 3275 | 1560.46 | 386 | 1240 | 900 | 0
2016-08-08 18:00 | 3174 | 1520.948 | 374 | 1240 | 900 | 0
2016-08-08 19:00 | 3174 | 1496.55 | 374 | 1240 | 900 | 0
2016-08-08 20:00 | 3174 | 1460.822 | 374 | 1240 | 1040 | 0
2016-08-08 21:00 | 3174 | 1422.366 | 374 | 1240 | 1040 | 0
2016-08-08 22:00 | 1994 | 1271.718 | 374 | 1240 | 1000 | 0
2016-08-08 23:00 | 1994 | 1172.955 | 374 | 1240 | 1238.9381 | 0
2016-08-09 | 1994 | 984.3 | 647 | 1240 | 1440 | 0
2016-08-09 01:00 | 1994 | 932.42 | 374 | 1240 | 1440 | 0
2016-08-09 02:00 | 2308 | 897.86 | 374 | 1240 | 1440 | 0
2016-08-09 03:00 | 2308 | 833.739 | 394 | 1240 | 1440 | 0
2016-08-09 04:00 | 2308 | 828.913 | 374 | 1240 | 1440 | 0
2016-08-09 05:00 | 2308 | 891.94 | 560 | 1240 | 1440 | 0
2016-08-09 06:00 | 2483 | 935.36 | 641 | 1240 | 1440 | 0
2016-08-09 07:00 | 2483 | 909.378 | 549 | 1240 | 1238.9381 | 0
2016-08-09 08:00 | 2483 | 1064.595 | 615 | 1240 | 1296.2963 | 0
2016-08-09 09:00 | 2483 | 1143.723 | 810 | 1240 | 1000 | 0
2016-08-09 10:00 | 2674 | 1293.974 | 766 | 1240 | 1040 | 0
2016-08-09 11:00 | 2674 | 1380.94 | 747 | 1240 | 900 | 0
2016-08-09 12:00 | 2674 | 1457.94 | 766 | 1240 | 900 | 0
2016-08-09 13:00 | 2674 | 1521.894 | 733 | 1240 | 900 | 0
2016-08-09 14:00 | 3275 | 1555.642 | 561 | 1240 | 900 | 0
2016-08-09 15:00 | 3275 | 1586.97 | 457 | 1240 | 900 | 0
2016-08-09 16:00 | 3275 | 1594.186 | 498 | 1240 | 900 | 0
2016-08-09 17:00 | 3275 | 1574.386 | 386 | 1240 | 900 | 0
2016-08-09 18:00 | 3174 | 1523.786 | 374 | 1240 | 900 | 0
2016-08-09 19:00 | 3174 | 1488.322 | 374 | 1240 | 900 | 0
2016-08-09 20:00 | 3174 | 1448.568 | 374 | 1240 | 900 | 0
2016-08-09 21:00 | 3174 | 1400.036 | 374 | 1240 | 900 | 0
2016-08-09 22:00 | 1994 | 1299.694 | 374 | 1240 | 1000 | 0
2016-08-09 23:00 | 1994 | 1137.381 | 374 | 1240 | 1296.2963 | 0
2016-08-10 | 1994 | 924.787 | 647 | 1240 | 1440 | 0
2016-08-10 01:00 | 1994 | 920.1 | 374 | 1240 | 1440 | 0
2016-08-10 02:00 | 2308 | 879.86 | 374 | 1240 | 1440 | 0
2016-08-10 03:00 | 2308 | 812.782 | 394 | 1240 | 1440 | 0
2016-08-10 04:00 | 2308 | 806.93 | 374 | 1240 | 1440 | 0
2016-08-10 05:00 | 2308 | 868.04 | 560 | 1240 | 1440 | 0
2016-08-10 06:00 | 2483 | 914.54 | 641 | 1240 | 1440 | 0
2016-08-10 07:00 | 2483 | 934.6 | 549 | 1240 | 1440 | 0
2016-08-10 08:00 | 2483 | 940.88 | 615 | 1240 | 1238.9381 | 0
2016-08-10 09:00 | 2483 | 1119.699 | 810 | 1240 | 1000 | 0
2016-08-10 10:00 | 2674 | 1267.332 | 766 | 1240 | 1040 | 0
2016-08-10 11:00 | 2674 | 1358.126 | 747 | 1240 | 900 | 0
2016-08-10 12:00 | 2674 | 1435.544 | 766 | 1240 | 900 | 0
2016-08-10 13:00 | 2674 | 1498.002 | 733 | 1240 | 900 | 0
2016-08-10 14:00 | 3275 | 1529.352 | 561 | 1240 | 900 | 0
2016-08-10 15:00 | 3275 | 1552.276 | 457 | 1240 | 900 | 0
2016-08-10 16:00 | 3275 | 1558.04 | 498 | 1240 | 900 | 0
2016-08-10 17:00 | 3275 | 1545.236 | 386 | 1240 | 900 | 0
2016-08-10 18:00 | 3174 | 1515.976 | 374 | 1240 | 900 | 0
2016-08-10 19:00 | 3174 | 1471.624 | 374 | 1240 | 900 | 0
2016-08-10 20:00 | 3174 | 1433.85 | 374 | 1240 | 900 | 0
2016-08-10 21:00 | 3174 | 1381.16 | 374 | 1240 | 900 | 0
2016-08-10 22:00 | 1994 | 1281.28 | 374 | 1240 | 1040 | 0
2016-08-10 23:00 | 1994 | 1122.324 | 374 | 1240 | 1296.2963 | 0
2016-08-11 | 1994 | 962.6 | 647 | 1240 | 1440 | 0
2016-08-11 01:00 | 1994 | 913.02 | 374 | 1240 | 1440 | 0
2016-08-11 02:00 | 2308 | 877.58 | 374 | 1240 | 1440 | 0
2016-08-11 03:00 | 2308 | 812.345 | 394 | 1240 | 1440 | 0
2016-08-11 04:00 | 2308 | 803.016 | 374 | 1240 | 1440 | 0
2016-08-11 05:00 | 2308 | 863.28 | 560 | 1240 | 1440 | 0
2016-08-11 06:00 | 2483 | 901.06 | 641 | 1240 | 1440 | 0
2016-08-11 07:00 | 2483 | 871.72 | 549 | 1240 | 1440 | 0
2016-08-11 08:00 | 2483 | 919.6 | 615 | 1240 | 1238.9381 | 0
2016-08-11 09:00 | 2483 | 1097.733 | 810 | 1240 | 1000 | 0
2016-08-11 10:00 | 2674 | 1248.654 | 766 | 1240 | 1040 | 0
2016-08-11 11:00 | 2674 | 1341.516 | 747 | 1240 | 900 | 0
2016-08-11 12:00 | 2674 | 1412.642 | 766 | 1240 | 900 | 0
2016-08-11 13:00 | 2674 | 1469.556 | 733 | 1240 | 900 | 0
2016-08-11 14:00 | 3275 | 1499.278 | 561 | 1240 | 900 | 0
2016-08-11 15:00 | 3275 | 1511.246 | 457 | 1240 | 900 | 0
2016-08-11 16:00 | 3275 | 1509.772 | 498 | 1240 | 900 | 0
2016-08-11 17:00 | 3275 | 1493.294 | 386 | 1240 | 900 | 0
2016-08-11 18:00 | 3174 | 1443.53 | 374 | 1240 | 900 | 0
2016-08-11 19:00 | 3174 | 1393.788 | 374 | 1240 | 900 | 0
2016-08-11 20:00 | 3174 | 1364.154 | 374 | 1240 | 1040 | 0
2016-08-11 21:00 | 3174 | 1315.446 | 374 | 1240 | 1040 | 0
2016-08-11 22:00 | 1994 | 1168.818 | 374 | 1240 | 1296.2963 | 0
2016-08-11 23:00 | 1994 | 976.182 | 374 | 1240 | 1238.9381 | 0
2016-08-12 | 1994 | 921.937 | 647 | 1240 | 1238.9381 | 0
2016-08-12 01:00 | 1994 | 874.038 | 374 | 1240 | 1440 | 0
2016-08-12 02:00 | 2308 | 883.9 | 374 | 1240 | 1440 | 0
2016-08-12 03:00 | 2308 | 862.36 | 394 | 1240 | 1440 | 0
2016-08-12 04:00 | 2308 | 857.14 | 374 | 1240 | 1440 | 0
2016-08-12 05:00 | 2308 | 880.02 | 560 | 1240 | 1440 | 0
2016-08-12 06:00 | 2483 | 918.64 | 641 | 1240 | 1440 | 0
2016-08-12 07:00 | 2483 | 887.984 | 549 | 1240 | 1440 | 0
2016-08-12 08:00 | 2483 | 924.445 | 615 | 1240 | 1238.9381 | 0
2016-08-12 09:00 | 2483 | 1096.599 | 810 | 1240 | 1296.2963 | 0
2016-08-12 10:00 | 2674 | 1242.054 | 766 | 1240 | 1040 | 0
2016-08-12 11:00 | 2674 | 1325.148 | 747 | 1240 | 900 | 0
2016-08-12 12:00 | 2674 | 1397 | 766 | 1240 | 900 | 0
2016-08-12 13:00 | 2674 | 1453.342 | 733 | 1240 | 900 | 0
2016-08-12 14:00 | 3275 | 1488.806 | 561 | 1240 | 900 | 0
2016-08-12 15:00 | 3275 | 1512.852 | 457 | 1240 | 900 | 0
2016-08-12 16:00 | 3275 | 1519.32 | 498 | 1240 | 900 | 0
2016-08-12 17:00 | 3275 | 1506.956 | 386 | 1240 | 900 | 0
2016-08-12 18:00 | 3174 | 1462.164 | 374 | 1240 | 900 | 0
2016-08-12 19:00 | 3174 | 1417.372 | 374 | 1240 | 900 | 0
2016-08-12 20:00 | 3174 | 1386.704 | 374 | 1240 | 900 | 0
2016-08-12 21:00 | 3174 | 1339.448 | 374 | 1240 | 1000 | 0
2016-08-12 22:00 | 1994 | 1190.112 | 374 | 1240 | 1238.9381 | 0
2016-08-12 23:00 | 1994 | 994.916 | 374 | 1240 | 1440 | 0
2016-08-13 | 1994 | 979.564 | 647 | 1240 | 1440 | 0
2016-08-13 01:00 | 1994 | 978.3 | 374 | 1240 | 1440 | 0
2016-08-13 02:00 | 2308 | 937.66 | 374 | 1240 | 1440 | 0
2016-08-13 03:00 | 2308 | 911.58 | 394 | 1240 | 1440 | 0
2016-08-13 04:00 | 2308 | 904.96 | 374 | 1240 | 1440 | 0
2016-08-13 05:00 | 2308 | 924.36 | 560 | 1240 | 1440 | 0
2016-08-13 06:00 | 2483 | 963.04 | 641 | 1240 | 1440 | 0
2016-08-13 07:00 | 2483 | 929.746 | 549 | 1240 | 1440 | 0
2016-08-13 08:00 | 2483 | 981.141 | 615 | 1240 | 1238.9381 | 0
2016-08-13 09:00 | 2483 | 1166.571 | 810 | 1240 | 1296.2963 | 0
2016-08-13 10:00 | 2674 | 1316.832 | 766 | 1240 | 1000 | 0
2016-08-13 11:00 | 2674 | 1404.48 | 747 | 1240 | 900 | 0
2016-08-13 12:00 | 2674 | 1481.392 | 766 | 1240 | 900 | 0
2016-08-13 13:00 | 2674 | 1534.39 | 733 | 1240 | 900 | 0
2016-08-13 14:00 | 3275 | 1582.24 | 561 | 1240 | 900 | 0
2016-08-13 15:00 | 3275 | 1602.766 | 457 | 1240 | 900 | 0
2016-08-13 16:00 | 3275 | 1602.48 | 498 | 1240 | 900 | 0
2016-08-13 17:00 | 3275 | 1578.412 | 386 | 1240 | 900 | 0
2016-08-13 18:00 | 3174 | 1521.432 | 374 | 1240 | 900 | 0
2016-08-13 19:00 | 3174 | 1479.566 | 374 | 1240 | 900 | 0
2016-08-13 20:00 | 3174 | 1442.122 | 374 | 1240 | 900 | 0
2016-08-13 21:00 | 3174 | 1393.59 | 374 | 1240 | 1040 | 0
2016-08-13 22:00 | 1994 | 1248.03 | 374 | 1240 | 1296.2963 | 0
2016-08-13 23:00 | 1994 | 1053.436 | 374 | 1240 | 1238.9381 | 0
2016-08-14 | 1994 | 1003.219 | 647 | 1240 | 1440 | 0
2016-08-14 01:00 | 1994 | 998.96 | 374 | 1240 | 1440 | 0
2016-08-14 02:00 | 2308 | 958.08 | 374 | 1240 | 1440 | 0
2016-08-14 03:00 | 2308 | 928.28 | 394 | 1240 | 1440 | 0
2016-08-14 04:00 | 2308 | 914.16 | 374 | 1240 | 1440 | 0
2016-08-14 05:00 | 2308 | 914.44 | 560 | 1240 | 1440 | 0
2016-08-14 06:00 | 2483 | 924.78 | 641 | 1240 | 1440 | 0
2016-08-14 07:00 | 2483 | 931.28 | 549 | 1240 | 1440 | 0
2016-08-14 08:00 | 2483 | 943.749 | 615 | 1240 | 1238.9381 | 0
2016-08-14 09:00 | 2483 | 1138.578 | 810 | 1240 | 1296.2963 | 0
2016-08-14 10:00 | 2674 | 1295.646 | 766 | 1240 | 1040 | 0
2016-08-14 11:00 | 2674 | 1386.154 | 747 | 1240 | 900 | 0
2016-08-14 12:00 | 2674 | 1460.734 | 766 | 1240 | 900 | 0
2016-08-14 13:00 | 2674 | 1514.458 | 733 | 1240 | 900 | 0
2016-08-14 14:00 | 3275 | 1539.494 | 561 | 1240 | 900 | 0
2016-08-14 15:00 | 3275 | 1566.29 | 457 | 1240 | 900 | 0
2016-08-14 16:00 | 3275 | 1580.326 | 498 | 1240 | 900 | 0
2016-08-14 17:00 | 3275 | 1572.406 | 386 | 1240 | 900 | 0
2016-08-14 18:00 | 3174 | 1529.814 | 374 | 1240 | 900 | 0
2016-08-14 19:00 | 3174 | 1502.314 | 374 | 1240 | 900 | 0
2016-08-14 20:00 | 3174 | 1465.926 | 374 | 1240 | 900 | 0
2016-08-14 21:00 | 3174 | 1417.724 | 374 | 1240 | 1040 | 0
2016-08-14 22:00 | 1994 | 1335.62 | 374 | 1240 | 1000 | 0
2016-08-14 23:00 | 1994 | 1195.908 | 374 | 1240 | 1296.2963 | 0
2016-08-15 | 1994 | 997.462 | 647 | 1240 | 1238.9381 | 0
2016-08-15 01:00 | 1994 | 945.82 | 374 | 1240 | 1238.9381 | 0
2016-08-15 02:00 | 2308 | 953.6 | 374 | 1240 | 1238.9381 | 0
2016-08-15 03:00 | 2308 | 924.52 | 394 | 1240 | 1440 | 0
2016-08-15 04:00 | 2308 | 902.22 | 374 | 1240 | 1440 | 0
2016-08-15 05:00 | 2308 | 893.3 | 560 | 1240 | 1440 | 0
2016-08-15 06:00 | 2483 | 891.62 | 641 | 1240 | 1440 | 0
2016-08-15 07:00 | 2483 | 889.44 | 549 | 1240 | 1440 | 0
2016-08-15 08:00 | 2483 | 903.203 | 615 | 1240 | 1238.9381 | 0
2016-08-15 09:00 | 2483 | 1087.905 | 810 | 1240 | 1296.2963 | 0
2016-08-15 10:00 | 2674 | 1238.006 | 766 | 1240 | 1040 | 0
2016-08-15 11:00 | 2674 | 1333.09 | 747 | 1240 | 900 | 0
2016-08-15 12:00 | 2674 | 1416.8 | 766 | 1240 | 900 | 0
2016-08-15 13:00 | 2674 | 1480.688 | 733 | 1240 | 900 | 0
2016-08-15 14:00 | 3275 | 1522.972 | 561 | 1240 | 900 | 0
2016-08-15 15:00 | 3275 | 1536.744 | 457 | 1240 | 900 | 0
2016-08-15 16:00 | 3275 | 1551.22 | 498 | 1240 | 900 | 0
2016-08-15 17:00 | 3275 | 1549.526 | 386 | 1240 | 900 | 0
2016-08-15 18:00 | 3174 | 1524.952 | 374 | 1240 | 900 | 0
2016-08-15 19:00 | 3174 | 1485.286 | 374 | 1240 | 900 | 0
2016-08-15 20:00 | 3174 | 1454.024 | 374 | 1240 | 900 | 0
2016-08-15 21:00 | 3174 | 1405.118 | 374 | 1240 | 1040 | 0
2016-08-15 22:00 | 1994 | 1312.058 | 374 | 1240 | 1040 | 0
2016-08-15 23:00 | 1994 | 1159.956 | 374 | 1240 | 1000 | 0
2016-08-16 | 1994 | 947.321 | 647 | 1240 | 1238.9381 | 0
2016-08-16 01:00 | 1994 | 896.724 | 374 | 1240 | 1238.9381 | 0
2016-08-16 02:00 | 2308 | 864.12 | 374 | 1240 | 1238.9381 | 0
2016-08-16 03:00 | 2308 | 844.626 | 394 | 1240 | 1238.9381 | 0
2016-08-16 04:00 | 2308 | 839.306 | 374 | 1240 | 1238.9381 | 0
2016-08-16 05:00 | 2308 | 857.831 | 560 | 1240 | 1238.9381 | 0
2016-08-16 06:00 | 2483 | 897.085 | 641 | 1240 | 1238.9381 | 0
2016-08-16 07:00 | 2483 | 909.017 | 549 | 1240 | 1238.9381 | 0
2016-08-16 08:00 | 2483 | 1051.365 | 615 | 1240 | 1296.2963 | 0
2016-08-16 09:00 | 2483 | 1181.906 | 810 | 1240 | 1000 | 0
2016-08-16 10:00 | 2674 | 1275.89 | 766 | 1240 | 900 | 0
2016-08-16 11:00 | 2674 | 1373.064 | 747 | 1240 | 900 | 0
2016-08-16 12:00 | 2674 | 1461.702 | 766 | 1240 | 900 | 0
2016-08-16 13:00 | 2674 | 1524.512 | 733 | 1240 | 900 | 0
2016-08-16 14:00 | 3275 | 1574.386 | 561 | 1240 | 900 | 0
2016-08-16 15:00 | 3275 | 1582.262 | 457 | 1240 | 900 | 0
2016-08-16 16:00 | 3275 | 1549.438 | 498 | 1240 | 900 | 0
2016-08-16 17:00 | 3275 | 1514.832 | 386 | 1240 | 900 | 0
2016-08-16 18:00 | 3174 | 1475.452 | 374 | 1240 | 900 | 0
2016-08-16 19:00 | 3174 | 1420.958 | 374 | 1240 | 900 | 0
2016-08-16 20:00 | 3174 | 1389.168 | 374 | 1240 | 900 | 0
2016-08-16 21:00 | 3174 | 1334.938 | 374 | 1240 | 1040 | 0
2016-08-16 22:00 | 1994 | 1236.444 | 374 | 1240 | 1000 | 0
2016-08-16 23:00 | 1994 | 1086.624 | 374 | 1240 | 1296.2963 | 0
2016-08-17 | 1994 | 906.547 | 647 | 1240 | 1238.9381 | 0
2016-08-17 01:00 | 1994 | 905.74 | 374 | 1240 | 1238.9381 | 0
2016-08-17 02:00 | 2308 | 870.52 | 374 | 1240 | 1238.9381 | 0
2016-08-17 03:00 | 2308 | 849 | 394 | 1240 | 1238.9381 | 0
2016-08-17 04:00 | 2308 | 843.82 | 374 | 1240 | 1238.9381 | 0
2016-08-17 05:00 | 2308 | 867.66 | 560 | 1240 | 1238.9381 | 0
2016-08-17 06:00 | 2483 | 869.972 | 641 | 1240 | 1238.9381 | 0
2016-08-17 07:00 | 2483 | 882.74 | 549 | 1240 | 1238.9381 | 0
2016-08-17 08:00 | 2483 | 921.006 | 615 | 1240 | 1238.9381 | 0
2016-08-17 09:00 | 2483 | 1090.026 | 810 | 1240 | 1296.2963 | 0
2016-08-17 10:00 | 2674 | 1177.428 | 766 | 1240 | 1000 | 0
2016-08-17 11:00 | 2674 | 1325.434 | 747 | 1240 | 1040 | 0
2016-08-17 12:00 | 2674 | 1411.19 | 766 | 1240 | 900 | 0
2016-08-17 13:00 | 2674 | 1484.34 | 733 | 1240 | 900 | 0
2016-08-17 14:00 | 3275 | 1520.64 | 561 | 1240 | 900 | 0
2016-08-17 15:00 | 3275 | 1551.726 | 457 | 1240 | 900 | 0
2016-08-17 16:00 | 3275 | 1553.662 | 498 | 1240 | 900 | 0
2016-08-17 17:00 | 3275 | 1528.208 | 386 | 1240 | 900 | 0
2016-08-17 18:00 | 3174 | 1484.714 | 374 | 1240 | 900 | 0
2016-08-17 19:00 | 3174 | 1426.106 | 374 | 1240 | 900 | 0
2016-08-17 20:00 | 3174 | 1397.264 | 374 | 1240 | 900 | 0
2016-08-17 21:00 | 3174 | 1345.894 | 374 | 1240 | 1040 | 0
2016-08-17 22:00 | 1994 | 1197.21 | 374 | 1240 | 1296.2963 | 0
2016-08-17 23:00 | 1994 | 1000.35 | 374 | 1240 | 1238.9381 | 0
2016-08-18 | 1994 | 943.72 | 647 | 1240 | 1238.9381 | 0
2016-08-18 01:00 | 1994 | 894.38 | 374 | 1240 | 1238.9381 | 0
2016-08-18 02:00 | 2308 | 862.7 | 374 | 1240 | 1238.9381 | 0
2016-08-18 03:00 | 2308 | 842.08 | 394 | 1240 | 1238.9381 | 0
2016-08-18 04:00 | 2308 | 837.9 | 374 | 1240 | 1238.9381 | 0
2016-08-18 05:00 | 2308 | 860.8 | 560 | 1240 | 1238.9381 | 0
2016-08-18 06:00 | 2483 | 860.225 | 641 | 1240 | 1238.9381 | 0
2016-08-18 07:00 | 2483 | 875.026 | 549 | 1240 | 1238.9381 | 0
2016-08-18 08:00 | 2483 | 905.578 | 615 | 1240 | 1238.9381 | 0
2016-08-18 09:00 | 2483 | 1064.448 | 810 | 1240 | 1296.2963 | 0
2016-08-18 10:00 | 2674 | 1188.77 | 766 | 1240 | 1000 | 0
2016-08-18 11:00 | 2674 | 1257.916 | 747 | 1240 | 1040 | 0
2016-08-18 12:00 | 2674 | 1316.92 | 766 | 1240 | 900 | 0
2016-08-18 13:00 | 2674 | 1372.734 | 733 | 1240 | 900 | 0
2016-08-18 14:00 | 3275 | 1418.56 | 561 | 1240 | 900 | 0
2016-08-18 15:00 | 3275 | 1446.126 | 457 | 1240 | 900 | 0
2016-08-18 16:00 | 3275 | 1456.972 | 498 | 1240 | 900 | 0
2016-08-18 17:00 | 3275 | 1442.804 | 386 | 1240 | 900 | 0
2016-08-18 18:00 | 3174 | 1395.658 | 374 | 1240 | 900 | 0
2016-08-18 19:00 | 3174 | 1348.49 | 374 | 1240 | 900 | 0
2016-08-18 20:00 | 3174 | 1322.706 | 374 | 1240 | 1040 | 0
2016-08-18 21:00 | 3174 | 1212.603 | 374 | 1240 | 1000 | 0
2016-08-18 22:00 | 1994 | 1131.375 | 374 | 1240 | 1296.2963 | 0
2016-08-18 23:00 | 1994 | 944.167 | 374 | 1240 | 1238.9381 | 0
2016-08-19 | 1994 | 931.08 | 647 | 1240 | 1238.9381 | 0
2016-08-19 01:00 | 1994 | 884.1 | 374 | 1240 | 1238.9381 | 0
2016-08-19 02:00 | 2308 | 851.6 | 374 | 1240 | 1238.9381 | 0
2016-08-19 03:00 | 2308 | 832.28 | 394 | 1240 | 1238.9381 | 0
2016-08-19 04:00 | 2308 | 787.512 | 374 | 1240 | 1238.9381 | 0
2016-08-19 05:00 | 2308 | 852.3 | 560 | 1240 | 1238.9381 | 0
2016-08-19 06:00 | 2483 | 896.3 | 641 | 1240 | 1238.9381 | 0
2016-08-19 07:00 | 2483 | 864.842 | 549 | 1240 | 1238.9381 | 0
2016-08-19 08:00 | 2483 | 906.167 | 615 | 1240 | 1238.9381 | 0
2016-08-19 09:00 | 2483 | 1076.355 | 810 | 1240 | 1296.2963 | 0
2016-08-19 10:00 | 2674 | 1155.588 | 766 | 1240 | 1000 | 0
2016-08-19 11:00 | 2674 | 1290.52 | 747 | 1240 | 900 | 0
2016-08-19 12:00 | 2674 | 1353.132 | 766 | 1240 | 900 | 0
2016-08-19 13:00 | 2674 | 1404.172 | 733 | 1240 | 900 | 0
2016-08-19 14:00 | 3275 | 1441.11 | 561 | 1240 | 900 | 0
2016-08-19 15:00 | 3275 | 1470.7 | 457 | 1240 | 900 | 0
2016-08-19 16:00 | 3275 | 1472.174 | 498 | 1240 | 900 | 0
2016-08-19 17:00 | 3275 | 1436.16 | 386 | 1240 | 900 | 0
2016-08-19 18:00 | 3174 | 1384.086 | 374 | 1240 | 900 | 0
2016-08-19 19:00 | 3174 | 1332.012 | 374 | 1240 | 1040 | 0
2016-08-19 20:00 | 3174 | 1253.616 | 374 | 1240 | 1296.2963 | 0
2016-08-19 21:00 | 3174 | 1212.036 | 374 | 1240 | 1238.9381 | 0
2016-08-19 22:00 | 1994 | 1029.059 | 374 | 1240 | 1440 | 0
2016-08-19 23:00 | 1994 | 1004.74 | 374 | 1240 | 1440 | 0
2016-08-20 | 1994 | 973.94 | 647 | 1240 | 1430.7692 | 0
2016-08-20 01:00 | 1994 | 881.923 | 374 | 1240 | 1430.7692 | 0
2016-08-20 02:00 | 2308 | 852.036 | 374 | 1240 | 1430.7692 | 0
2016-08-20 03:00 | 2308 | 832.732 | 394 | 1240 | 1430.7692 | 0
2016-08-20 04:00 | 2308 | 831.744 | 374 | 1240 | 1430.7692 | 0
2016-08-20 05:00 | 2308 | 856.368 | 560 | 1240 | 1430.7692 | 0
2016-08-20 06:00 | 2483 | 949.22 | 641 | 1240 | 1430.7692 | 0
2016-08-20 07:00 | 2483 | 966.52 | 549 | 1240 | 1430.7692 | 0
2016-08-20 08:00 | 2483 | 1009.54 | 615 | 1240 | 1430.7692 | 0
2016-08-20 09:00 | 2483 | 1030.199 | 810 | 1240 | 1238.9381 | 0
2016-08-20 10:00 | 2674 | 1222.788 | 766 | 1240 | 1296.2963 | 0
2016-08-20 11:00 | 2674 | 1355.42 | 747 | 1240 | 1040 | 0
2016-08-20 12:00 | 2674 | 1414.314 | 766 | 1240 | 900 | 0
2016-08-20 13:00 | 2674 | 1469.82 | 733 | 1240 | 900 | 0
2016-08-20 14:00 | 3275 | 1506.89 | 561 | 1240 | 900 | 0
2016-08-20 15:00 | 3275 | 1519.386 | 457 | 1240 | 900 | 0
2016-08-20 16:00 | 3275 | 1519.606 | 498 | 1240 | 900 | 0
2016-08-20 17:00 | 3275 | 1503.018 | 386 | 1240 | 900 | 0
2016-08-20 18:00 | 3174 | 1448.458 | 374 | 1240 | 900 | 0
2016-08-20 19:00 | 3174 | 1393.898 | 374 | 1240 | 900 | 0
2016-08-20 20:00 | 3174 | 1363.34 | 374 | 1240 | 1040 | 0
2016-08-20 21:00 | 3174 | 1259.559 | 374 | 1240 | 1296.2963 | 0
2016-08-20 22:00 | 1994 | 1072.151 | 374 | 1240 | 1238.9381 | 0
2016-08-20 23:00 | 1994 | 1000.122 | 374 | 1240 | 1440 | 0
2016-08-21 | 1994 | 978.709 | 647 | 1240 | 1440 | 0
2016-08-21 01:00 | 1994 | 975.98 | 374 | 1240 | 1440 | 0
2016-08-21 02:00 | 2308 | 938.56 | 374 | 1240 | 1440 | 0
2016-08-21 03:00 | 2308 | 909.04 | 394 | 1240 | 1440 | 0
2016-08-21 04:00 | 2308 | 892.7 | 374 | 1240 | 1440 | 0
2016-08-21 05:00 | 2308 | 895.12 | 560 | 1240 | 1440 | 0
2016-08-21 06:00 | 2483 | 907.94 | 641 | 1240 | 1440 | 0
2016-08-21 07:00 | 2483 | 915.74 | 549 | 1240 | 1440 | 0
2016-08-21 08:00 | 2483 | 931.779 | 615 | 1240 | 1440 | 0
2016-08-21 09:00 | 2483 | 1123.395 | 810 | 1240 | 1238.9381 | 0
2016-08-21 10:00 | 2674 | 1270.522 | 766 | 1240 | 1000 | 0
2016-08-21 11:00 | 2674 | 1351.592 | 747 | 1240 | 900 | 0
2016-08-21 12:00 | 2674 | 1420.166 | 766 | 1240 | 900 | 0
2016-08-21 13:00 | 2674 | 1478.532 | 733 | 1240 | 900 | 0
2016-08-21 14:00 | 3275 | 1525.81 | 561 | 1240 | 900 | 0
2016-08-21 15:00 | 3275 | 1545.148 | 457 | 1240 | 900 | 0
2016-08-21 16:00 | 3275 | 1561.67 | 498 | 1240 | 900 | 0
2016-08-21 17:00 | 3275 | 1554.784 | 386 | 1240 | 900 | 0
2016-08-21 18:00 | 3174 | 1523.698 | 374 | 1240 | 900 | 0
2016-08-21 19:00 | 3174 | 1477.476 | 374 | 1240 | 900 | 0
2016-08-21 20:00 | 3174 | 1441.066 | 374 | 1240 | 900 | 0
2016-08-21 21:00 | 3174 | 1385.164 | 374 | 1240 | 900 | 0
2016-08-21 22:00 | 1994 | 1301.212 | 374 | 1240 | 1000 | 0
2016-08-21 23:00 | 1994 | 1160.25 | 374 | 1240 | 1296.2963 | 0
2016-08-22 | 1994 | 990.071 | 647 | 1240 | 1238.9381 | 0
2016-08-22 01:00 | 1994 | 936.263 | 374 | 1240 | 1238.9381 | 0
2016-08-22 02:00 | 2308 | 945.12 | 374 | 1240 | 1238.9381 | 0
2016-08-22 03:00 | 2308 | 916.4 | 394 | 1240 | 1238.9381 | 0
2016-08-22 04:00 | 2308 | 897.22 | 374 | 1240 | 1238.9381 | 0
2016-08-22 05:00 | 2308 | 891.22 | 560 | 1240 | 1238.9381 | 0
2016-08-22 06:00 | 2483 | 891.88 | 641 | 1240 | 1238.9381 | 0
2016-08-22 07:00 | 2483 | 890.56 | 549 | 1240 | 1238.9381 | 0
2016-08-22 08:00 | 2483 | 901.056 | 615 | 1240 | 1238.9381 | 0
2016-08-22 09:00 | 2483 | 1090.446 | 810 | 1240 | 1296.2963 | 0
2016-08-22 10:00 | 2674 | 1243.55 | 766 | 1240 | 1040 | 0
2016-08-22 11:00 | 2674 | 1336.038 | 747 | 1240 | 900 | 0
2016-08-22 12:00 | 2674 | 1426.898 | 766 | 1240 | 900 | 0
2016-08-22 13:00 | 2674 | 1503.832 | 733 | 1240 | 900 | 0
2016-08-22 14:00 | 3275 | 1545.676 | 561 | 1240 | 900 | 0
2016-08-22 15:00 | 3275 | 1584.88 | 457 | 1240 | 900 | 0
2016-08-22 16:00 | 3275 | 1607.056 | 498 | 1240 | 900 | 0
2016-08-22 17:00 | 3275 | 1611.06 | 386 | 1240 | 900 | 0
2016-08-22 18:00 | 3174 | 1573.902 | 374 | 1240 | 900 | 0
2016-08-22 19:00 | 3174 | 1536.722 | 374 | 1240 | 900 | 0
2016-08-22 20:00 | 3174 | 1522.818 | 374 | 1240 | 900 | 0
2016-08-22 21:00 | 3174 | 1456.598 | 374 | 1240 | 900 | 0
2016-08-22 22:00 | 1994 | 1345.784 | 374 | 1240 | 900 | 0
2016-08-22 23:00 | 1994 | 1174.719 | 374 | 1240 | 1000 | 0
2016-08-23 | 1994 | 954.731 | 647 | 1240 | 1238.9381 | 0
2016-08-23 01:00 | 1994 | 904.495 | 374 | 1240 | 1238.9381 | 0
2016-08-23 02:00 | 2308 | 918.02 | 374 | 1240 | 1238.9381 | 0
2016-08-23 03:00 | 2308 | 897.86 | 394 | 1240 | 1238.9381 | 0
2016-08-23 04:00 | 2308 | 892.22 | 374 | 1240 | 1238.9381 | 0
2016-08-23 05:00 | 2308 | 918.22 | 560 | 1240 | 1238.9381 | 0
2016-08-23 06:00 | 2483 | 926.972 | 641 | 1240 | 1238.9381 | 0
2016-08-23 07:00 | 2483 | 930.411 | 549 | 1240 | 1238.9381 | 0
2016-08-23 08:00 | 2483 | 1065.267 | 615 | 1240 | 1296.2963 | 0
2016-08-23 09:00 | 2483 | 1199.506 | 810 | 1240 | 1000 | 0
2016-08-23 10:00 | 2674 | 1297.164 | 766 | 1240 | 900 | 0
2016-08-23 11:00 | 2674 | 1399.024 | 747 | 1240 | 900 | 0
2016-08-23 12:00 | 2674 | 1497.21 | 766 | 1240 | 900 | 0
2016-08-23 13:00 | 2674 | 1563.892 | 733 | 1240 | 900 | 0
2016-08-23 14:00 | 3275 | 1618.936 | 561 | 1240 | 900 | 0
2016-08-23 15:00 | 3275 | 1641.618 | 457 | 1240 | 900 | 0
2016-08-23 16:00 | 3275 | 1643.4 | 498 | 1240 | 900 | 0
2016-08-23 17:00 | 3275 | 1606.088 | 386 | 1240 | 900 | 0
2016-08-23 18:00 | 3174 | 1546.622 | 374 | 1240 | 900 | 0
2016-08-23 19:00 | 3174 | 1502.27 | 374 | 1240 | 900 | 0
2016-08-23 20:00 | 3174 | 1472.724 | 374 | 1240 | 900 | 0
2016-08-23 21:00 | 3174 | 1401.862 | 374 | 1240 | 900 | 0
2016-08-23 22:00 | 1994 | 1294.216 | 374 | 1240 | 1040 | 0
2016-08-23 23:00 | 1994 | 1133.139 | 374 | 1240 | 1296.2963 | 0
2016-08-24 | 1994 | 957.885 | 647 | 1240 | 1238.9381 | 0
2016-08-24 01:00 | 1994 | 908.029 | 374 | 1240 | 1238.9381 | 0
2016-08-24 02:00 | 2308 | 918.98 | 374 | 1240 | 1238.9381 | 0
2016-08-24 03:00 | 2308 | 894.52 | 394 | 1240 | 1238.9381 | 0
2016-08-24 04:00 | 2308 | 889.44 | 374 | 1240 | 1238.9381 | 0
2016-08-24 05:00 | 2308 | 915.5 | 560 | 1240 | 1238.9381 | 0
2016-08-24 06:00 | 2483 | 927.675 | 641 | 1240 | 1238.9381 | 0
2016-08-24 07:00 | 2483 | 933.907 | 549 | 1240 | 1238.9381 | 0
2016-08-24 08:00 | 2483 | 965.922 | 615 | 1240 | 1238.9381 | 0
2016-08-24 09:00 | 2483 | 1144.374 | 810 | 1240 | 1000 | 0
2016-08-24 10:00 | 2674 | 1290.102 | 766 | 1240 | 1000 | 0
2016-08-24 11:00 | 2674 | 1369.61 | 747 | 1240 | 1040 | 0
2016-08-24 12:00 | 2674 | 1441.33 | 766 | 1240 | 1040 | 0
2016-08-24 13:00 | 2674 | 1501.104 | 733 | 1240 | 1040 | 0
2016-08-24 14:00 | 3275 | 1520.244 | 561 | 1240 | 1040 | 0
2016-08-24 15:00 | 3275 | 1514.7 | 457 | 1240 | 1040 | 0
2016-08-24 16:00 | 3275 | 1513.446 | 498 | 1240 | 1040 | 0
2016-08-24 17:00 | 3275 | 1464.584 | 386 | 1240 | 1040 | 0
2016-08-24 18:00 | 3174 | 1410.332 | 374 | 1240 | 1040 | 0
2016-08-24 19:00 | 3174 | 1294.461 | 374 | 1240 | 1000 | 0
2016-08-24 20:00 | 3174 | 1281.714 | 374 | 1240 | 1000 | 0
2016-08-24 21:00 | 3174 | 1235.64 | 374 | 1240 | 1296.2963 | 0
2016-08-24 22:00 | 1994 | 1035.424 | 374 | 1240 | 1238.9381 | 0
2016-08-24 23:00 | 1994 | 1001.66 | 374 | 1240 | 1440 | 0
2016-08-25 | 1994 | 901.9 | 647 | 1240 | 1440 | 0
2016-08-25 01:00 | 1994 | 816.981 | 374 | 1240 | 1440 | 0
2016-08-25 02:00 | 2308 | 788.044 | 374 | 1240 | 1440 | 0
2016-08-25 03:00 | 2308 | 770.488 | 394 | 1240 | 1440 | 0
2016-08-25 04:00 | 2308 | 767.619 | 374 | 1240 | 1440 | 0
2016-08-25 05:00 | 2308 | 797.373 | 560 | 1240 | 1440 | 0
2016-08-25 06:00 | 2483 | 901.72 | 641 | 1240 | 1440 | 0
2016-08-25 07:00 | 2483 | 913.4 | 549 | 1240 | 1440 | 0
2016-08-25 08:00 | 2483 | 879.168 | 615 | 1240 | 1440 | 0
2016-08-25 09:00 | 2483 | 915.705 | 810 | 1240 | 1238.9381 | 0
2016-08-25 10:00 | 2674 | 958.702 | 766 | 1240 | 1238.9381 | 0
2016-08-25 11:00 | 2674 | 996.816 | 747 | 1240 | 1238.9381 | 0
2016-08-25 12:00 | 2674 | 1142.988 | 766 | 1240 | 1296.2963 | 0
2016-08-25 13:00 | 2674 | 1186.038 | 733 | 1240 | 1296.2963 | 0
2016-08-25 14:00 | 3275 | 1216.593 | 561 | 1240 | 1000 | 0
2016-08-25 15:00 | 3275 | 1298.968 | 457 | 1240 | 1000 | 0
2016-08-25 16:00 | 3275 | 1311.222 | 498 | 1240 | 1000 | 0
2016-08-25 17:00 | 3275 | 1300.948 | 386 | 1240 | 1000 | 0
2016-08-25 18:00 | 3174 | 1210.146 | 374 | 1240 | 1000 | 0
2016-08-25 19:00 | 3174 | 1178.478 | 374 | 1240 | 1000 | 0
2016-08-25 20:00 | 3174 | 1175.139 | 374 | 1240 | 1000 | 0
2016-08-25 21:00 | 3174 | 1133.181 | 374 | 1240 | 1296.2963 | 0
2016-08-25 22:00 | 1994 | 950.228 | 374 | 1240 | 1238.9381 | 0
2016-08-25 23:00 | 1994 | 871.606 | 374 | 1240 | 1440 | 0
2016-08-26 | 1994 | 823.24 | 647 | 1240 | 1440 | 0
2016-08-26 01:00 | 1994 | 744.553 | 374 | 1240 | 1440 | 0
2016-08-26 02:00 | 2308 | 718.162 | 374 | 1240 | 1440 | 0
2016-08-26 03:00 | 2308 | 702.164 | 394 | 1240 | 1440 | 0
2016-08-26 04:00 | 2308 | 702.525 | 374 | 1240 | 1440 | 0
2016-08-26 05:00 | 2308 | 730.151 | 560 | 1240 | 1440 | 0
2016-08-26 06:00 | 2483 | 831.62 | 641 | 1240 | 1440 | 0
2016-08-26 07:00 | 2483 | 842.76 | 549 | 1240 | 1440 | 0
2016-08-26 08:00 | 2483 | 865.34 | 615 | 1240 | 1440 | 0
2016-08-26 09:00 | 2483 | 865.659 | 810 | 1240 | 1440 | 0
2016-08-26 10:00 | 2674 | 919.733 | 766 | 1240 | 1238.9381 | 0
2016-08-26 11:00 | 2674 | 1078.938 | 747 | 1240 | 1296.2963 | 0
2016-08-26 12:00 | 2674 | 1138.284 | 766 | 1240 | 1000 | 0
2016-08-26 13:00 | 2674 | 1252.35 | 733 | 1240 | 1040 | 0
2016-08-26 14:00 | 3275 | 1299.056 | 561 | 1240 | 1040 | 0
2016-08-26 15:00 | 3275 | 1329.57 | 457 | 1240 | 900 | 0
2016-08-26 16:00 | 3275 | 1343.012 | 498 | 1240 | 900 | 0
2016-08-26 17:00 | 3275 | 1330.956 | 386 | 1240 | 900 | 0
2016-08-26 18:00 | 3174 | 1287 | 374 | 1240 | 1040 | 0
2016-08-26 19:00 | 3174 | 1243.044 | 374 | 1240 | 1040 | 0
2016-08-26 20:00 | 3174 | 1171.506 | 374 | 1240 | 1000 | 0
2016-08-26 21:00 | 3174 | 1115.541 | 374 | 1240 | 1296.2963 | 0
2016-08-26 22:00 | 1994 | 926.421 | 374 | 1240 | 1238.9381 | 0
2016-08-26 23:00 | 1994 | 888.26 | 374 | 1240 | 1440 | 0
2016-08-27 | 1994 | 861.08 | 647 | 1240 | 1440 | 0
2016-08-27 01:00 | 1994 | 800.66 | 374 | 1240 | 1440 | 0
2016-08-27 02:00 | 2308 | 769.386 | 374 | 1240 | 1440 | 0
2016-08-27 03:00 | 2308 | 749.037 | 394 | 1240 | 1440 | 0
2016-08-27 04:00 | 2308 | 744.914 | 374 | 1240 | 1440 | 0
2016-08-27 05:00 | 2308 | 773.11 | 560 | 1240 | 1440 | 0
2016-08-27 06:00 | 2483 | 878.66 | 641 | 1240 | 1440 | 0
2016-08-27 07:00 | 2483 | 891.06 | 549 | 1240 | 1440 | 0
2016-08-27 08:00 | 2483 | 870.048 | 615 | 1240 | 1440 | 0
2016-08-27 09:00 | 2483 | 926.098 | 810 | 1240 | 1238.9381 | 0
2016-08-27 10:00 | 2674 | 1096.893 | 766 | 1240 | 1296.2963 | 0
2016-08-27 11:00 | 2674 | 1168.923 | 747 | 1240 | 1000 | 0
2016-08-27 12:00 | 2674 | 1295.118 | 766 | 1240 | 1040 | 0
2016-08-27 13:00 | 2674 | 1361.734 | 733 | 1240 | 900 | 0
2016-08-27 14:00 | 3275 | 1414.71 | 561 | 1240 | 900 | 0
2016-08-27 15:00 | 3275 | 1455.872 | 457 | 1240 | 900 | 0
2016-08-27 16:00 | 3275 | 1478.29 | 498 | 1240 | 900 | 0
2016-08-27 17:00 | 3275 | 1464.958 | 386 | 1240 | 900 | 0
2016-08-27 18:00 | 3174 | 1399.904 | 374 | 1240 | 900 | 0
2016-08-27 19:00 | 3174 | 1334.85 | 374 | 1240 | 1040 | 0
2016-08-27 20:00 | 3174 | 1230.18 | 374 | 1240 | 1296.2963 | 0
2016-08-27 21:00 | 3174 | 1053.379 | 374 | 1240 | 1238.9381 | 0
2016-08-27 22:00 | 1994 | 1026.94 | 374 | 1240 | 1440 | 0
2016-08-27 23:00 | 1994 | 944.1 | 374 | 1240 | 1430.7692 | 0
2016-08-28 | 1994 | 858.686 | 647 | 1240 | 1521.4286 | 0
2016-08-28 01:00 | 1994 | 807.899 | 374 | 1240 | 1521.4286 | 0
2016-08-28 02:00 | 2308 | 769.348 | 374 | 1240 | 1521.4286 | 0
2016-08-28 03:00 | 2308 | 782.98 | 394 | 1240 | 1521.4286 | 0
2016-08-28 04:00 | 2308 | 768.32 | 374 | 1240 | 1521.4286 | 0
2016-08-28 05:00 | 2308 | 769.5 | 560 | 1240 | 1521.4286 | 0
2016-08-28 06:00 | 2483 | 743.717 | 641 | 1240 | 1521.4286 | 0
2016-08-28 07:00 | 2483 | 748.391 | 549 | 1240 | 1521.4286 | 0
2016-08-28 08:00 | 2483 | 803.301 | 615 | 1240 | 1430.7692 | 0
2016-08-28 09:00 | 2483 | 885.856 | 810 | 1240 | 1440 | 0
2016-08-28 10:00 | 2674 | 979.374 | 766 | 1240 | 1238.9381 | 0
2016-08-28 11:00 | 2674 | 1177.365 | 747 | 1240 | 1296.2963 | 0
2016-08-28 12:00 | 2674 | 1320.132 | 766 | 1240 | 1040 | 0
2016-08-28 13:00 | 2674 | 1393.942 | 733 | 1240 | 900 | 0
2016-08-28 14:00 | 3275 | 1448.634 | 561 | 1240 | 900 | 0
2016-08-28 15:00 | 3275 | 1493.822 | 457 | 1240 | 900 | 0
2016-08-28 16:00 | 3275 | 1517.846 | 498 | 1240 | 900 | 0
2016-08-28 17:00 | 3275 | 1514.304 | 386 | 1240 | 900 | 0
2016-08-28 18:00 | 3174 | 1464.188 | 374 | 1240 | 900 | 0
2016-08-28 19:00 | 3174 | 1414.072 | 374 | 1240 | 900 | 0
2016-08-28 20:00 | 3174 | 1384.328 | 374 | 1240 | 1000 | 0
2016-08-28 21:00 | 3174 | 1259.244 | 374 | 1240 | 1296.2963 | 0
2016-08-28 22:00 | 1994 | 1064.874 | 374 | 1240 | 1238.9381 | 0
2016-08-28 23:00 | 1994 | 1044.44 | 374 | 1240 | 1440 | 0
2016-08-29 | 1994 | 970.84 | 647 | 1240 | 1430.7692 | 0
2016-08-29 01:00 | 1994 | 877.781 | 374 | 1240 | 1430.7692 | 0
2016-08-29 02:00 | 2308 | 842.517 | 374 | 1240 | 1430.7692 | 0
2016-08-29 03:00 | 2308 | 817.855 | 394 | 1240 | 1430.7692 | 0
2016-08-29 04:00 | 2308 | 801.116 | 374 | 1240 | 1430.7692 | 0
2016-08-29 05:00 | 2308 | 795.796 | 560 | 1240 | 1430.7692 | 0
2016-08-29 06:00 | 2483 | 799.368 | 641 | 1240 | 1430.7692 | 0
2016-08-29 07:00 | 2483 | 797.62 | 549 | 1240 | 1430.7692 | 0
2016-08-29 08:00 | 2483 | 899.02 | 615 | 1240 | 1440 | 0
2016-08-29 09:00 | 2483 | 937.023 | 810 | 1240 | 1238.9381 | 0
2016-08-29 10:00 | 2674 | 1131.501 | 766 | 1240 | 1296.2963 | 0
2016-08-29 11:00 | 2674 | 1281.566 | 747 | 1240 | 1000 | 0
2016-08-29 12:00 | 2674 | 1365.562 | 766 | 1240 | 900 | 0
2016-08-29 13:00 | 2674 | 1436.138 | 733 | 1240 | 900 | 0
2016-08-29 14:00 | 3275 | 1477.96 | 561 | 1240 | 900 | 0
2016-08-29 15:00 | 3275 | 1506.384 | 457 | 1240 | 900 | 0
2016-08-29 16:00 | 3275 | 1519.342 | 498 | 1240 | 900 | 0
2016-08-29 17:00 | 3275 | 1512.39 | 386 | 1240 | 900 | 0
2016-08-29 18:00 | 3174 | 1471.448 | 374 | 1240 | 900 | 0
2016-08-29 19:00 | 3174 | 1430.528 | 374 | 1240 | 900 | 0
2016-08-29 20:00 | 3174 | 1415.876 | 374 | 1240 | 1040 | 0
2016-08-29 21:00 | 3174 | 1297.737 | 374 | 1240 | 1296.2963 | 0
2016-08-29 22:00 | 1994 | 1211.448 | 374 | 1240 | 1238.9381 | 0
2016-08-29 23:00 | 1994 | 1010.344 | 374 | 1240 | 1440 | 0
2016-08-30 | 1994 | 965.5 | 647 | 1240 | 1440 | 0
2016-08-30 01:00 | 1994 | 878.351 | 374 | 1240 | 1440 | 0
2016-08-30 02:00 | 2308 | 851.048 | 374 | 1240 | 1440 | 0
2016-08-30 03:00 | 2308 | 840.332 | 394 | 1240 | 1440 | 0
2016-08-30 04:00 | 2308 | 889.44 | 374 | 1240 | 1440 | 0
2016-08-30 05:00 | 2308 | 924.86 | 560 | 1240 | 1440 | 0
2016-08-30 06:00 | 2483 | 944.946 | 641 | 1240 | 1238.9381 | 0
2016-08-30 07:00 | 2483 | 962.939 | 549 | 1240 | 1238.9381 | 0
2016-08-30 08:00 | 2483 | 985.245 | 615 | 1240 | 1238.9381 | 0
2016-08-30 09:00 | 2483 | 1148.784 | 810 | 1240 | 1296.2963 | 0
2016-08-30 10:00 | 2674 | 1217.265 | 766 | 1240 | 1000 | 0
2016-08-30 11:00 | 2674 | 1271.928 | 747 | 1240 | 1000 | 0
2016-08-30 12:00 | 2674 | 1373.064 | 766 | 1240 | 1000 | 0
2016-08-30 13:00 | 2674 | 1413.896 | 733 | 1240 | 1040 | 0
2016-08-30 14:00 | 3275 | 1449.074 | 561 | 1240 | 1040 | 0
2016-08-30 15:00 | 3275 | 1476.64 | 457 | 1240 | 900 | 0
2016-08-30 16:00 | 3275 | 1494.35 | 498 | 1240 | 900 | 0
2016-08-30 17:00 | 3275 | 1487.992 | 386 | 1240 | 900 | 0
2016-08-30 18:00 | 3174 | 1452.198 | 374 | 1240 | 1040 | 0
2016-08-30 19:00 | 3174 | 1416.426 | 374 | 1240 | 1040 | 0
2016-08-30 20:00 | 3174 | 1408.33 | 374 | 1240 | 1000 | 0
2016-08-30 21:00 | 3174 | 1285.074 | 374 | 1240 | 1296.2963 | 0
2016-08-30 22:00 | 1994 | 1190.154 | 374 | 1240 | 1238.9381 | 0
2016-08-30 23:00 | 1994 | 988.817 | 374 | 1240 | 1440 | 0
2016-08-31 | 1994 | 959.74 | 647 | 1240 | 1440 | 0
2016-08-31 01:00 | 1994 | 870.143 | 374 | 1240 | 1440 | 0
2016-08-31 02:00 | 2308 | 842.65 | 374 | 1240 | 1440 | 0
2016-08-31 03:00 | 2308 | 826.196 | 394 | 1240 | 1440 | 0
2016-08-31 04:00 | 2308 | 826.804 | 374 | 1240 | 1440 | 0
2016-08-31 05:00 | 2308 | 902.28 | 560 | 1240 | 1440 | 0
2016-08-31 06:00 | 2483 | 922.811 | 641 | 1240 | 1440 | 0
2016-08-31 07:00 | 2483 | 935.978 | 549 | 1240 | 1440 | 0
2016-08-31 08:00 | 2483 | 963.319 | 615 | 1240 | 1440 | 0
2016-08-31 09:00 | 2483 | 1131.48 | 810 | 1240 | 1238.9381 | 0
2016-08-31 10:00 | 2674 | 1257.256 | 766 | 1240 | 1000 | 0
2016-08-31 11:00 | 2674 | 1326.38 | 747 | 1240 | 1040 | 0
2016-08-31 12:00 | 2674 | 1382.766 | 766 | 1240 | 900 | 0
2016-08-31 13:00 | 2674 | 1432.244 | 733 | 1240 | 900 | 0
2016-08-31 14:00 | 3275 | 1466.894 | 561 | 1240 | 900 | 0
2016-08-31 15:00 | 3275 | 1494.24 | 457 | 1240 | 900 | 0
2016-08-31 16:00 | 3275 | 1509.046 | 498 | 1240 | 900 | 0
2016-08-31 17:00 | 3275 | 1495.384 | 386 | 1240 | 900 | 0
2016-08-31 18:00 | 3174 | 1453.892 | 374 | 1240 | 900 | 0
2016-08-31 19:00 | 3174 | 1412.422 | 374 | 1240 | 900 | 0
2016-08-31 20:00 | 3174 | 1404.942 | 374 | 1240 | 900 | 0
2016-08-31 21:00 | 3174 | 1344.816 | 374 | 1240 | 1000 | 0
2016-08-31 22:00 | 1994 | 1185.45 | 374 | 1240 | 1296.2963 | 0
2016-08-31 23:00 | 1994 | 984.314 | 374 | 1240 | 1238.9381 | 0
2016-09-01 | 2144 | 922.54 | 746 | 1240 | 1238.9381 | 0
2016-09-01 01:00 | 2144 | 877.96 | 332 | 1240 | 1238.9381 | 0
2016-09-01 02:00 | 2073 | 849.12 | 332 | 1240 | 1238.9381 | 0
2016-09-01 03:00 | 2073 | 831.72 | 377 | 1240 | 1238.9381 | 0
2016-09-01 04:00 | 2073 | 831.94 | 397 | 1240 | 1238.9381 | 0
2016-09-01 05:00 | 2073 | 863.02 | 537 | 1240 | 1440 | 0
2016-09-01 06:00 | 2067 | 883.329 | 668 | 1240 | 1440 | 0
2016-09-01 07:00 | 2067 | 896.496 | 462 | 1240 | 1440 | 0
2016-09-01 08:00 | 2067 | 913.083 | 433 | 1240 | 1440 | 0
2016-09-01 09:00 | 2067 | 963.262 | 562 | 1240 | 1238.9381 | 0
2016-09-01 10:00 | 1925 | 1131.207 | 627 | 1240 | 1296.2963 | 0
2016-09-01 11:00 | 1925 | 1254.594 | 626 | 1240 | 1040 | 0
2016-09-01 12:00 | 1925 | 1303.654 | 587 | 1240 | 900 | 0
2016-09-01 13:00 | 1925 | 1360.502 | 587 | 1240 | 900 | 0
2016-09-01 14:00 | 2474 | 1392.952 | 476 | 1240 | 900 | 0
2016-09-01 15:00 | 2474 | 1400.894 | 512 | 1240 | 900 | 0
2016-09-01 16:00 | 2474 | 1395.196 | 382 | 1240 | 900 | 0
2016-09-01 17:00 | 2474 | 1365.034 | 342 | 1240 | 900 | 0
2016-09-01 18:00 | 2257 | 1316.634 | 332 | 1240 | 900 | 0
2016-09-01 19:00 | 2257 | 1283.348 | 332 | 1240 | 1040 | 0
2016-09-01 20:00 | 2257 | 1212.981 | 413 | 1240 | 1296.2963 | 0
2016-09-01 21:00 | 2257 | 1050.491 | 332 | 1240 | 1238.9381 | 0
2016-09-01 22:00 | 2144 | 974.51 | 332 | 1240 | 1440 | 0
2016-09-01 23:00 | 2144 | 937.62 | 332 | 1240 | 1440 | 0
2016-09-02 | 2144 | 870.98 | 746 | 1240 | 1440 | 0
2016-09-02 01:00 | 2144 | 788.975 | 332 | 1240 | 1440 | 0
2016-09-02 02:00 | 2073 | 762.375 | 332 | 1240 | 1440 | 0
2016-09-02 03:00 | 2073 | 747.764 | 377 | 1240 | 1440 | 0
2016-09-02 04:00 | 2073 | 748.277 | 397 | 1240 | 1440 | 0
2016-09-02 05:00 | 2073 | 779.893 | 537 | 1240 | 1440 | 0
2016-09-02 06:00 | 2067 | 885.18 | 668 | 1240 | 1440 | 0
2016-09-02 07:00 | 2067 | 902.34 | 462 | 1240 | 1440 | 0
2016-09-02 08:00 | 2067 | 873.411 | 433 | 1240 | 1440 | 0
2016-09-02 09:00 | 2067 | 917.187 | 562 | 1240 | 1238.9381 | 0
2016-09-02 10:00 | 1925 | 1064.406 | 627 | 1240 | 1238.9381 | 0
2016-09-02 11:00 | 1925 | 1116.339 | 626 | 1240 | 1296.2963 | 0
2016-09-02 12:00 | 1925 | 1210.572 | 587 | 1240 | 1000 | 0
2016-09-02 13:00 | 1925 | 1253.01 | 587 | 1240 | 1040 | 0
2016-09-02 14:00 | 2474 | 1288.672 | 476 | 1240 | 1040 | 0
2016-09-02 15:00 | 2474 | 1309.352 | 512 | 1240 | 1040 | 0
2016-09-02 16:00 | 2474 | 1308.34 | 382 | 1240 | 1040 | 0
2016-09-02 17:00 | 2474 | 1300.53 | 342 | 1240 | 1040 | 0
2016-09-02 18:00 | 2257 | 1207.101 | 332 | 1240 | 1000 | 0
2016-09-02 19:00 | 2257 | 1172.808 | 332 | 1240 | 1296.2963 | 0
2016-09-02 20:00 | 2257 | 1052.809 | 413 | 1240 | 1296.2963 | 0
2016-09-02 21:00 | 2257 | 1006.221 | 332 | 1240 | 1238.9381 | 0
2016-09-02 22:00 | 2144 | 933.014 | 332 | 1240 | 1440 | 0
2016-09-02 23:00 | 2144 | 903.92 | 332 | 1240 | 1430.7692 | 0
2016-09-03 | 2144 | 845.481 | 746 | 1240 | 1430.7692 | 0
2016-09-03 01:00 | 2144 | 847.84 | 332 | 1240 | 1430.7692 | 0
2016-09-03 02:00 | 2073 | 818.92 | 332 | 1240 | 1430.7692 | 0
2016-09-03 03:00 | 2073 | 763.23 | 377 | 1240 | 1430.7692 | 0
2016-09-03 04:00 | 2073 | 764.655 | 397 | 1240 | 1430.7692 | 0
2016-09-03 05:00 | 2073 | 795.055 | 537 | 1240 | 1430.7692 | 0
2016-09-03 06:00 | 2067 | 902.22 | 668 | 1240 | 1430.7692 | 0
2016-09-03 07:00 | 2067 | 918.72 | 462 | 1240 | 1430.7692 | 0
2016-09-03 08:00 | 2067 | 877.401 | 433 | 1240 | 1430.7692 | 0
2016-09-03 09:00 | 2067 | 947.4 | 562 | 1240 | 1430.7692 | 0
2016-09-03 10:00 | 1925 | 980.46 | 627 | 1240 | 1430.7692 | 0
2016-09-03 11:00 | 1925 | 1006.74 | 626 | 1240 | 1430.7692 | 0
2016-09-03 12:00 | 1925 | 1034.18 | 587 | 1240 | 1440 | 0
2016-09-03 13:00 | 1925 | 1010.42 | 587 | 1240 | 1440 | 0
2016-09-03 14:00 | 2474 | 1033.885 | 476 | 1240 | 1238.9381 | 0
2016-09-03 15:00 | 2474 | 1057.635 | 512 | 1240 | 1238.9381 | 0
2016-09-03 16:00 | 2474 | 1068.313 | 382 | 1240 | 1238.9381 | 0
2016-09-03 17:00 | 2474 | 1054.861 | 342 | 1240 | 1238.9381 | 0
2016-09-03 18:00 | 2257 | 1015.531 | 332 | 1240 | 1238.9381 | 0
2016-09-03 19:00 | 2257 | 976.201 | 332 | 1240 | 1238.9381 | 0
2016-09-03 20:00 | 2257 | 967.993 | 413 | 1240 | 1238.9381 | 0
2016-09-03 21:00 | 2257 | 931.399 | 332 | 1240 | 1440 | 0
2016-09-03 22:00 | 2144 | 921.88 | 332 | 1240 | 1430.7692 | 0
2016-09-03 23:00 | 2144 | 858.62 | 332 | 1240 | 1430.7692 | 0
2016-09-04 | 2144 | 804.783 | 746 | 1240 | 1430.7692 | 0
2016-09-04 01:00 | 2144 | 796.005 | 332 | 1240 | 1430.7692 | 0
2016-09-04 02:00 | 2073 | 764.579 | 332 | 1240 | 1430.7692 | 0
2016-09-04 03:00 | 2073 | 745.807 | 377 | 1240 | 1430.7692 | 0
2016-09-04 04:00 | 2073 | 775.12 | 397 | 1240 | 1430.7692 | 0
2016-09-04 05:00 | 2073 | 741.893 | 537 | 1240 | 1430.7692 | 0
2016-09-04 06:00 | 2067 | 757.587 | 668 | 1240 | 1430.7692 | 0
2016-09-04 07:00 | 2067 | 763.572 | 462 | 1240 | 1430.7692 | 0
2016-09-04 08:00 | 2067 | 846.96 | 433 | 1240 | 1430.7692 | 0
2016-09-04 09:00 | 2067 | 912.08 | 562 | 1240 | 1440 | 0
2016-09-04 10:00 | 1925 | 933.603 | 627 | 1240 | 1238.9381 | 0
2016-09-04 11:00 | 1925 | 1103.571 | 626 | 1240 | 1296.2963 | 0
2016-09-04 12:00 | 1925 | 1166.697 | 587 | 1240 | 1000 | 0
2016-09-04 13:00 | 1925 | 1278.53 | 587 | 1240 | 1040 | 0
2016-09-04 14:00 | 2474 | 1306.932 | 476 | 1240 | 1040 | 0
2016-09-04 15:00 | 2474 | 1333.926 | 512 | 1240 | 1040 | 0
2016-09-04 16:00 | 2474 | 1342.286 | 382 | 1240 | 1040 | 0
2016-09-04 17:00 | 2474 | 1336.302 | 342 | 1240 | 1040 | 0
2016-09-04 18:00 | 2257 | 1309.154 | 332 | 1240 | 1040 | 0
2016-09-04 19:00 | 2257 | 1266.892 | 332 | 1240 | 1000 | 0
2016-09-04 20:00 | 2257 | 1197.462 | 413 | 1240 | 1296.2963 | 0
2016-09-04 21:00 | 2257 | 1033.049 | 332 | 1240 | 1238.9381 | 0
2016-09-04 22:00 | 2144 | 1021.44 | 332 | 1240 | 1440 | 0
2016-09-04 23:00 | 2144 | 950.94 | 332 | 1240 | 1430.7692 | 0
2016-09-05 | 2144 | 829.768 | 746 | 1240 | 1521.4286 | 0
2016-09-05 01:00 | 2144 | 830.14 | 332 | 1240 | 1521.4286 | 0
2016-09-05 02:00 | 2073 | 796.36 | 332 | 1240 | 1521.4286 | 0
2016-09-05 03:00 | 2073 | 771.8 | 377 | 1240 | 1521.4286 | 0
2016-09-05 04:00 | 2073 | 757.42 | 397 | 1240 | 1521.4286 | 0
2016-09-05 05:00 | 2073 | 756.06 | 537 | 1240 | 1521.4286 | 0
2016-09-05 06:00 | 2067 | 764.62 | 668 | 1240 | 1521.4286 | 0
2016-09-05 07:00 | 2067 | 763.56 | 462 | 1240 | 1521.4286 | 0
2016-09-05 08:00 | 2067 | 775.732 | 433 | 1240 | 1521.4286 | 0
2016-09-05 09:00 | 2067 | 896.32 | 562 | 1240 | 1430.7692 | 0
2016-09-05 10:00 | 1925 | 981.8 | 627 | 1240 | 1440 | 0
2016-09-05 11:00 | 1925 | 1011.997 | 626 | 1240 | 1238.9381 | 0
2016-09-05 12:00 | 1925 | 1198.344 | 587 | 1240 | 1296.2963 | 0
2016-09-05 13:00 | 1925 | 1309.33 | 587 | 1240 | 1000 | 0
2016-09-05 14:00 | 2474 | 1364.528 | 476 | 1240 | 1040 | 0
2016-09-05 15:00 | 2474 | 1407.01 | 512 | 1240 | 1040 | 0
2016-09-05 16:00 | 2474 | 1428.284 | 382 | 1240 | 1040 | 0
2016-09-05 17:00 | 2474 | 1424.148 | 342 | 1240 | 1040 | 0
2016-09-05 18:00 | 2257 | 1372.03 | 332 | 1240 | 1000 | 0
2016-09-05 19:00 | 2257 | 1259.916 | 332 | 1240 | 1296.2963 | 0
2016-09-05 20:00 | 2257 | 1237.488 | 413 | 1240 | 1238.9381 | 0
2016-09-05 21:00 | 2257 | 1084.52 | 332 | 1240 | 1440 | 0
2016-09-05 22:00 | 2144 | 1074.18 | 332 | 1240 | 1430.7692 | 0
2016-09-05 23:00 | 2144 | 1004.28 | 332 | 1240 | 1430.7692 | 0
2016-09-06 | 2144 | 869.174 | 746 | 1240 | 1521.4286 | 0
2016-09-06 01:00 | 2144 | 870.66 | 332 | 1240 | 1521.4286 | 0
2016-09-06 02:00 | 2073 | 839.12 | 332 | 1240 | 1521.4286 | 0
2016-09-06 03:00 | 2073 | 818.46 | 377 | 1240 | 1521.4286 | 0
2016-09-06 04:00 | 2073 | 809.78 | 397 | 1240 | 1521.4286 | 0
2016-09-06 05:00 | 2073 | 816.24 | 537 | 1240 | 1521.4286 | 0
2016-09-06 06:00 | 2067 | 830.7 | 668 | 1240 | 1521.4286 | 0
2016-09-06 07:00 | 2067 | 827.14 | 462 | 1240 | 1521.4286 | 0
2016-09-06 08:00 | 2067 | 829.597 | 433 | 1240 | 1521.4286 | 0
2016-09-06 09:00 | 2067 | 962.58 | 562 | 1240 | 1430.7692 | 0
2016-09-06 10:00 | 1925 | 1002.155 | 627 | 1240 | 1440 | 0
2016-09-06 11:00 | 1925 | 1064.893 | 626 | 1240 | 1238.9381 | 0
2016-09-06 12:00 | 1925 | 1231.797 | 587 | 1240 | 1296.2963 | 0
2016-09-06 13:00 | 1925 | 1319.56 | 587 | 1240 | 1000 | 0
2016-09-06 14:00 | 2474 | 1334.894 | 476 | 1240 | 1040 | 0
2016-09-06 15:00 | 2474 | 1347.61 | 512 | 1240 | 1040 | 0
2016-09-06 16:00 | 2474 | 1356.388 | 382 | 1240 | 1040 | 0
2016-09-06 17:00 | 2474 | 1355.332 | 342 | 1240 | 1040 | 0
2016-09-06 18:00 | 2257 | 1323.586 | 332 | 1240 | 1040 | 0
2016-09-06 19:00 | 2257 | 1247.568 | 332 | 1240 | 1000 | 0
2016-09-06 20:00 | 2257 | 1242.507 | 413 | 1240 | 1296.2963 | 0
2016-09-06 21:00 | 2257 | 1092.728 | 332 | 1240 | 1238.9381 | 0
2016-09-06 22:00 | 2144 | 1019.464 | 332 | 1240 | 1440 | 0
2016-09-06 23:00 | 2144 | 988.74 | 332 | 1240 | 1430.7692 | 0
2016-09-07 | 2144 | 845.823 | 746 | 1240 | 1430.7692 | 0
2016-09-07 01:00 | 2144 | 855.22 | 332 | 1240 | 1430.7692 | 0
2016-09-07 02:00 | 2073 | 831.84 | 332 | 1240 | 1430.7692 | 0
2016-09-07 03:00 | 2073 | 780.216 | 377 | 1240 | 1430.7692 | 0
2016-09-07 04:00 | 2073 | 790.286 | 397 | 1240 | 1430.7692 | 0
2016-09-07 05:00 | 2073 | 874.82 | 537 | 1240 | 1430.7692 | 0
2016-09-07 06:00 | 2067 | 900.239 | 668 | 1240 | 1440 | 0
2016-09-07 07:00 | 2067 | 930.639 | 462 | 1240 | 1238.9381 | 0
2016-09-07 08:00 | 2067 | 939.569 | 433 | 1240 | 1238.9381 | 0
2016-09-07 09:00 | 2067 | 956.384 | 562 | 1240 | 1238.9381 | 0
2016-09-07 10:00 | 1925 | 1075.473 | 627 | 1240 | 1238.9381 | 0
2016-09-07 11:00 | 1925 | 1086.54 | 626 | 1240 | 1238.9381 | 0
2016-09-07 12:00 | 1925 | 1102.017 | 587 | 1240 | 1238.9381 | 0
2016-09-07 13:00 | 1925 | 1003.333 | 587 | 1240 | 1238.9381 | 0
2016-09-07 14:00 | 2474 | 1006.696 | 476 | 1240 | 1238.9381 | 0
2016-09-07 15:00 | 2474 | 1009.508 | 512 | 1240 | 1238.9381 | 0
2016-09-07 16:00 | 2474 | 1014.353 | 382 | 1240 | 1440 | 0
2016-09-07 17:00 | 2474 | 1003.143 | 342 | 1240 | 1440 | 0
2016-09-07 18:00 | 2257 | 996.36 | 332 | 1240 | 1440 | 0
2016-09-07 19:00 | 2257 | 989.558 | 332 | 1240 | 1440 | 0
2016-09-07 20:00 | 2257 | 1006.62 | 413 | 1240 | 1440 | 0
2016-09-07 21:00 | 2257 | 979.108 | 332 | 1240 | 1440 | 0
2016-09-07 22:00 | 2144 | 970.52 | 332 | 1240 | 1440 | 0
2016-09-07 23:00 | 2144 | 901.42 | 332 | 1240 | 1430.7692 | 0
2016-09-08 | 2144 | 746.738 | 746 | 1240 | 1430.7692 | 0
2016-09-08 01:00 | 2144 | 720.1 | 332 | 1240 | 1430.7692 | 0
2016-09-08 02:00 | 2073 | 707.085 | 332 | 1240 | 1430.7692 | 0
2016-09-08 03:00 | 2073 | 702.696 | 377 | 1240 | 1430.7692 | 0
2016-09-08 04:00 | 2073 | 712.538 | 397 | 1240 | 1430.7692 | 0
2016-09-08 05:00 | 2073 | 748.695 | 537 | 1240 | 1430.7692 | 0
2016-09-08 06:00 | 2067 | 862.16 | 668 | 1240 | 1430.7692 | 0
2016-09-08 07:00 | 2067 | 888.7 | 462 | 1240 | 1440 | 0
2016-09-08 08:00 | 2067 | 898.82 | 433 | 1240 | 1440 | 0
2016-09-08 09:00 | 2067 | 882.569 | 562 | 1240 | 1440 | 0
2016-09-08 10:00 | 1925 | 918.878 | 627 | 1240 | 1440 | 0
2016-09-08 11:00 | 1925 | 948.423 | 626 | 1240 | 1238.9381 | 0
2016-09-08 12:00 | 1925 | 977.113 | 587 | 1240 | 1238.9381 | 0
2016-09-08 13:00 | 1925 | 1110.648 | 587 | 1240 | 1296.2963 | 0
2016-09-08 14:00 | 2474 | 1136.394 | 476 | 1240 | 1296.2963 | 0
2016-09-08 15:00 | 2474 | 1160.859 | 512 | 1240 | 1000 | 0
2016-09-08 16:00 | 2474 | 1236.488 | 382 | 1240 | 1000 | 0
2016-09-08 17:00 | 2474 | 1225.928 | 342 | 1240 | 1000 | 0
2016-09-08 18:00 | 2257 | 1144.542 | 332 | 1240 | 1000 | 0
2016-09-08 19:00 | 2257 | 1118.88 | 332 | 1240 | 1000 | 0
2016-09-08 20:00 | 2257 | 1123.122 | 413 | 1240 | 1296.2963 | 0
2016-09-08 21:00 | 2257 | 1081.332 | 332 | 1240 | 1238.9381 | 0
2016-09-08 22:00 | 2144 | 913.007 | 332 | 1240 | 1238.9381 | 0
2016-09-08 23:00 | 2144 | 888.42 | 332 | 1240 | 1440 | 0
2016-09-09 | 2144 | 816.2 | 746 | 1240 | 1440 | 0
2016-09-09 01:00 | 2144 | 745.674 | 332 | 1240 | 1440 | 0
2016-09-09 02:00 | 2073 | 728.935 | 332 | 1240 | 1440 | 0
2016-09-09 03:00 | 2073 | 720.461 | 377 | 1240 | 1440 | 0
2016-09-09 04:00 | 2073 | 725.249 | 397 | 1240 | 1440 | 0
2016-09-09 05:00 | 2073 | 757.321 | 537 | 1240 | 1440 | 0
2016-09-09 06:00 | 2067 | 865.6 | 668 | 1240 | 1440 | 0
2016-09-09 07:00 | 2067 | 885.36 | 462 | 1240 | 1440 | 0
2016-09-09 08:00 | 2067 | 901.28 | 433 | 1240 | 1440 | 0
2016-09-09 09:00 | 2067 | 945.36 | 562 | 1240 | 1440 | 0
2016-09-09 10:00 | 1925 | 953.211 | 627 | 1240 | 1238.9381 | 0
2016-09-09 11:00 | 1925 | 1005.1 | 626 | 1240 | 1238.9381 | 0
2016-09-09 12:00 | 1925 | 1164.471 | 587 | 1240 | 1296.2963 | 0
2016-09-09 13:00 | 1925 | 1275.648 | 587 | 1240 | 1040 | 0
2016-09-09 14:00 | 2474 | 1304.864 | 476 | 1240 | 1040 | 0
2016-09-09 15:00 | 2474 | 1327.172 | 512 | 1240 | 1040 | 0
2016-09-09 16:00 | 2474 | 1334.19 | 382 | 1240 | 1040 | 0
2016-09-09 17:00 | 2474 | 1319.318 | 342 | 1240 | 1040 | 0
2016-09-09 18:00 | 2257 | 1293.622 | 332 | 1240 | 1040 | 0
2016-09-09 19:00 | 2257 | 1195.887 | 332 | 1240 | 1296.2963 | 0
2016-09-09 20:00 | 2257 | 1187.928 | 413 | 1240 | 1238.9381 | 0
2016-09-09 21:00 | 2257 | 1026.418 | 332 | 1240 | 1440 | 0
2016-09-09 22:00 | 2144 | 992.32 | 332 | 1240 | 1430.7692 | 0
2016-09-09 23:00 | 2144 | 866.875 | 332 | 1240 | 1430.7692 | 0
2016-09-10 | 2144 | 850.269 | 746 | 1240 | 1430.7692 | 0
2016-09-10 01:00 | 2144 | 811.281 | 332 | 1240 | 1430.7692 | 0
2016-09-10 02:00 | 2073 | 825.74 | 332 | 1240 | 1430.7692 | 0
2016-09-10 03:00 | 2073 | 809.16 | 377 | 1240 | 1430.7692 | 0
2016-09-10 04:00 | 2073 | 810.36 | 397 | 1240 | 1430.7692 | 0
2016-09-10 05:00 | 2073 | 799.197 | 537 | 1240 | 1430.7692 | 0
2016-09-10 06:00 | 2067 | 911.64 | 668 | 1240 | 1430.7692 | 0
2016-09-10 07:00 | 2067 | 929.8 | 462 | 1240 | 1430.7692 | 0
2016-09-10 08:00 | 2067 | 951.92 | 433 | 1240 | 1430.7692 | 0
2016-09-10 09:00 | 2067 | 954.446 | 562 | 1240 | 1440 | 0
2016-09-10 10:00 | 1925 | 1016.576 | 627 | 1240 | 1238.9381 | 0
2016-09-10 11:00 | 1925 | 1189.461 | 626 | 1240 | 1296.2963 | 0
2016-09-10 12:00 | 1925 | 1307.46 | 587 | 1240 | 1000 | 0
2016-09-10 13:00 | 1925 | 1352.912 | 587 | 1240 | 1040 | 0
2016-09-10 14:00 | 2474 | 1397.132 | 476 | 1240 | 900 | 0
2016-09-10 15:00 | 2474 | 1427.932 | 512 | 1240 | 900 | 0
2016-09-10 16:00 | 2474 | 1440.582 | 382 | 1240 | 900 | 0
2016-09-10 17:00 | 2474 | 1421.288 | 342 | 1240 | 900 | 0
2016-09-10 18:00 | 2257 | 1361.162 | 332 | 1240 | 1040 | 0
2016-09-10 19:00 | 2257 | 1301.036 | 332 | 1240 | 1000 | 0
2016-09-10 20:00 | 2257 | 1286.318 | 413 | 1240 | 1000 | 0
2016-09-10 21:00 | 2257 | 1171.653 | 332 | 1240 | 1296.2963 | 0
2016-09-10 22:00 | 2144 | 1099.749 | 332 | 1240 | 1238.9381 | 0
2016-09-10 23:00 | 2144 | 930.373 | 332 | 1240 | 1238.9381 | 0
2016-09-11 | 2144 | 942.32 | 746 | 1240 | 1440 | 0
2016-09-11 01:00 | 2144 | 894.76 | 332 | 1240 | 1440 | 0
2016-09-11 02:00 | 2073 | 816.164 | 332 | 1240 | 1440 | 0
2016-09-11 03:00 | 2073 | 795.378 | 377 | 1240 | 1440 | 0
2016-09-11 04:00 | 2073 | 783.674 | 397 | 1240 | 1440 | 0
2016-09-11 05:00 | 2073 | 787.778 | 537 | 1240 | 1440 | 0
2016-09-11 06:00 | 2067 | 804.308 | 668 | 1240 | 1440 | 0
2016-09-11 07:00 | 2067 | 856.1 | 462 | 1240 | 1440 | 0
2016-09-11 08:00 | 2067 | 901.66 | 433 | 1240 | 1440 | 0
2016-09-11 09:00 | 2067 | 924.217 | 562 | 1240 | 1238.9381 | 0
2016-09-11 10:00 | 1925 | 1100.463 | 627 | 1240 | 1296.2963 | 0
2016-09-11 11:00 | 1925 | 1237.566 | 626 | 1240 | 1040 | 0
2016-09-11 12:00 | 1925 | 1300.904 | 587 | 1240 | 900 | 0
2016-09-11 13:00 | 1925 | 1366.508 | 587 | 1240 | 900 | 0
2016-09-11 14:00 | 2474 | 1416.822 | 476 | 1240 | 900 | 0
2016-09-11 15:00 | 2474 | 1450.526 | 512 | 1240 | 900 | 0
2016-09-11 16:00 | 2474 | 1464.056 | 382 | 1240 | 900 | 0
2016-09-11 17:00 | 2474 | 1452.88 | 342 | 1240 | 900 | 0
2016-09-11 18:00 | 2257 | 1402.06 | 332 | 1240 | 900 | 0
2016-09-11 19:00 | 2257 | 1351.262 | 332 | 1240 | 1040 | 0
2016-09-11 20:00 | 2257 | 1321.078 | 413 | 1240 | 1000 | 0
2016-09-11 21:00 | 2257 | 1210.44 | 332 | 1240 | 1296.2963 | 0
2016-09-11 22:00 | 2144 | 1130.136 | 332 | 1240 | 1238.9381 | 0
2016-09-11 23:00 | 2144 | 951.387 | 332 | 1240 | 1238.9381 | 0
2016-09-12 | 2144 | 907.725 | 746 | 1240 | 1440 | 0
2016-09-12 01:00 | 2144 | 904.44 | 332 | 1240 | 1440 | 0
2016-09-12 02:00 | 2073 | 867.22 | 332 | 1240 | 1440 | 0
2016-09-12 03:00 | 2073 | 841.64 | 377 | 1240 | 1440 | 0
2016-09-12 04:00 | 2073 | 783.56 | 397 | 1240 | 1440 | 0
2016-09-12 05:00 | 2073 | 779.798 | 537 | 1240 | 1440 | 0
2016-09-12 06:00 | 2067 | 828.1 | 668 | 1240 | 1440 | 0
2016-09-12 07:00 | 2067 | 830.9 | 462 | 1240 | 1440 | 0
2016-09-12 08:00 | 2067 | 838.869 | 433 | 1240 | 1440 | 0
2016-09-12 09:00 | 2067 | 919.41 | 562 | 1240 | 1238.9381 | 0
2016-09-12 10:00 | 1925 | 1108.968 | 627 | 1240 | 1000 | 0
2016-09-12 11:00 | 1925 | 1263.13 | 626 | 1240 | 1040 | 0
2016-09-12 12:00 | 1925 | 1333.618 | 587 | 1240 | 900 | 0
2016-09-12 13:00 | 1925 | 1396.802 | 587 | 1240 | 900 | 0
2016-09-12 14:00 | 2474 | 1439.174 | 476 | 1240 | 900 | 0
2016-09-12 15:00 | 2474 | 1464.958 | 512 | 1240 | 900 | 0
2016-09-12 16:00 | 2474 | 1470.59 | 382 | 1240 | 900 | 0
2016-09-12 17:00 | 2474 | 1456.752 | 342 | 1240 | 900 | 0
2016-09-12 18:00 | 2257 | 1411.256 | 332 | 1240 | 900 | 0
2016-09-12 19:00 | 2257 | 1365.782 | 332 | 1240 | 900 | 0
2016-09-12 20:00 | 2257 | 1345.542 | 413 | 1240 | 900 | 0
2016-09-12 21:00 | 2257 | 1297.648 | 332 | 1240 | 1040 | 0
2016-09-12 22:00 | 2144 | 1147.272 | 332 | 1240 | 1000 | 0
2016-09-12 23:00 | 2144 | 1054.032 | 332 | 1240 | 1296.2963 | 0
2016-09-13 | 2144 | 887.68 | 746 | 1240 | 1440 | 0
2016-09-13 01:00 | 2144 | 842.56 | 332 | 1240 | 1440 | 0
2016-09-13 02:00 | 2073 | 812.88 | 332 | 1240 | 1440 | 0
2016-09-13 03:00 | 2073 | 758.613 | 377 | 1240 | 1440 | 0
2016-09-13 04:00 | 2073 | 760.665 | 397 | 1240 | 1440 | 0
2016-09-13 05:00 | 2073 | 835.9 | 537 | 1240 | 1440 | 0
2016-09-13 06:00 | 2067 | 861.593 | 668 | 1240 | 1440 | 0
2016-09-13 07:00 | 2067 | 880.251 | 462 | 1240 | 1238.9381 | 0
2016-09-13 08:00 | 2067 | 900.296 | 433 | 1240 | 1238.9381 | 0
2016-09-13 09:00 | 2067 | 1053.801 | 562 | 1240 | 1238.9381 | 0
2016-09-13 10:00 | 1925 | 1127.322 | 627 | 1240 | 1296.2963 | 0
2016-09-13 11:00 | 1925 | 1256.09 | 626 | 1240 | 1040 | 0
2016-09-13 12:00 | 1925 | 1313.664 | 587 | 1240 | 900 | 0
2016-09-13 13:00 | 1925 | 1380.874 | 587 | 1240 | 900 | 0
2016-09-13 14:00 | 2474 | 1430.616 | 476 | 1240 | 900 | 0
2016-09-13 15:00 | 2474 | 1451.186 | 512 | 1240 | 900 | 0
2016-09-13 16:00 | 2474 | 1458.424 | 382 | 1240 | 900 | 0
2016-09-13 17:00 | 2474 | 1441.22 | 342 | 1240 | 900 | 0
2016-09-13 18:00 | 2257 | 1393.986 | 332 | 1240 | 900 | 0
2016-09-13 19:00 | 2257 | 1346.752 | 332 | 1240 | 1040 | 0
2016-09-13 20:00 | 2257 | 1326.49 | 413 | 1240 | 1000 | 0
2016-09-13 21:00 | 2257 | 1211.952 | 332 | 1240 | 1296.2963 | 0
2016-09-13 22:00 | 2144 | 1008.026 | 332 | 1240 | 1238.9381 | 0
2016-09-13 23:00 | 2144 | 968.58 | 332 | 1240 | 1440 | 0
2016-09-14 | 2144 | 889.32 | 746 | 1240 | 1440 | 0
2016-09-14 01:00 | 2144 | 800.983 | 332 | 1240 | 1440 | 0
2016-09-14 02:00 | 2073 | 770.279 | 332 | 1240 | 1440 | 0
2016-09-14 03:00 | 2073 | 752.248 | 377 | 1240 | 1440 | 0
2016-09-14 04:00 | 2073 | 750.12 | 397 | 1240 | 1440 | 0
2016-09-14 05:00 | 2073 | 781.603 | 537 | 1240 | 1440 | 0
2016-09-14 06:00 | 2067 | 893.58 | 668 | 1240 | 1440 | 0
2016-09-14 07:00 | 2067 | 914.86 | 462 | 1240 | 1440 | 0
2016-09-14 08:00 | 2067 | 889.751 | 433 | 1240 | 1440 | 0
2016-09-14 09:00 | 2067 | 948.613 | 562 | 1240 | 1238.9381 | 0
2016-09-14 10:00 | 1925 | 1121.904 | 627 | 1240 | 1296.2963 | 0
2016-09-14 11:00 | 1925 | 1250.37 | 626 | 1240 | 1000 | 0
2016-09-14 12:00 | 1925 | 1303.412 | 587 | 1240 | 1040 | 0
2016-09-14 13:00 | 1925 | 1366.398 | 587 | 1240 | 900 | 0
2016-09-14 14:00 | 2474 | 1414.468 | 476 | 1240 | 900 | 0
2016-09-14 15:00 | 2474 | 1441.814 | 512 | 1240 | 900 | 0
2016-09-14 16:00 | 2474 | 1450.636 | 382 | 1240 | 900 | 0
2016-09-14 17:00 | 2474 | 1432.134 | 342 | 1240 | 900 | 0
2016-09-14 18:00 | 2257 | 1377.508 | 332 | 1240 | 900 | 0
2016-09-14 19:00 | 2257 | 1322.882 | 332 | 1240 | 1040 | 0
2016-09-14 20:00 | 2257 | 1248.786 | 413 | 1240 | 1296.2963 | 0
2016-09-14 21:00 | 2257 | 1174.236 | 332 | 1240 | 1238.9381 | 0
2016-09-14 22:00 | 2144 | 979.564 | 332 | 1240 | 1440 | 0
2016-09-14 23:00 | 2144 | 936.8 | 332 | 1240 | 1430.7692 | 0
2016-09-15 | 2144 | 800.85 | 746 | 1240 | 1430.7692 | 0
2016-09-15 01:00 | 2144 | 797.08 | 332 | 1240 | 1430.7692 | 0
2016-09-15 02:00 | 2073 | 771.62 | 332 | 1240 | 1430.7692 | 0
2016-09-15 03:00 | 2073 | 754.64 | 377 | 1240 | 1430.7692 | 0
2016-09-15 04:00 | 2073 | 756.84 | 397 | 1240 | 1430.7692 | 0
2016-09-15 05:00 | 2073 | 749.284 | 537 | 1240 | 1430.7692 | 0
2016-09-15 06:00 | 2067 | 813.371 | 668 | 1240 | 1430.7692 | 0
2016-09-15 07:00 | 2067 | 826.994 | 462 | 1240 | 1430.7692 | 0
2016-09-15 08:00 | 2067 | 891.58 | 433 | 1240 | 1430.7692 | 0
2016-09-15 09:00 | 2067 | 948.26 | 562 | 1240 | 1440 | 0
2016-09-15 10:00 | 1925 | 967.461 | 627 | 1240 | 1238.9381 | 0
2016-09-15 11:00 | 1925 | 1135.449 | 626 | 1240 | 1296.2963 | 0
2016-09-15 12:00 | 1925 | 1197.672 | 587 | 1240 | 1000 | 0
2016-09-15 13:00 | 1925 | 1299.034 | 587 | 1240 | 1040 | 0
2016-09-15 14:00 | 2474 | 1343.276 | 476 | 1240 | 1040 | 0
2016-09-15 15:00 | 2474 | 1373.262 | 512 | 1240 | 1040 | 0
2016-09-15 16:00 | 2474 | 1384.68 | 382 | 1240 | 1040 | 0
2016-09-15 17:00 | 2474 | 1362.108 | 342 | 1240 | 1040 | 0
2016-09-15 18:00 | 2257 | 1303.94 | 332 | 1240 | 1040 | 0
2016-09-15 19:00 | 2257 | 1203.552 | 332 | 1240 | 1000 | 0
2016-09-15 20:00 | 2257 | 1176.462 | 413 | 1240 | 1296.2963 | 0
2016-09-15 21:00 | 2257 | 1006.069 | 332 | 1240 | 1440 | 0
2016-09-15 22:00 | 2144 | 972.34 | 332 | 1240 | 1430.7692 | 0
2016-09-15 23:00 | 2144 | 840.921 | 332 | 1240 | 1430.7692 | 0
2016-09-16 | 2144 | 776.568 | 746 | 1240 | 1430.7692 | 0
2016-09-16 01:00 | 2144 | 775.78 | 332 | 1240 | 1430.7692 | 0
2016-09-16 02:00 | 2073 | 747.16 | 332 | 1240 | 1430.7692 | 0
2016-09-16 03:00 | 2073 | 730.76 | 377 | 1240 | 1430.7692 | 0
2016-09-16 04:00 | 2073 | 729.3 | 397 | 1240 | 1430.7692 | 0
2016-09-16 05:00 | 2073 | 724.242 | 537 | 1240 | 1430.7692 | 0
2016-09-16 06:00 | 2067 | 829.76 | 668 | 1240 | 1430.7692 | 0
2016-09-16 07:00 | 2067 | 845.82 | 462 | 1240 | 1430.7692 | 0
2016-09-16 08:00 | 2067 | 865.8 | 433 | 1240 | 1440 | 0
2016-09-16 09:00 | 2067 | 871.91 | 562 | 1240 | 1238.9381 | 0
2016-09-16 10:00 | 1925 | 937.194 | 627 | 1240 | 1238.9381 | 0
2016-09-16 11:00 | 1925 | 1105.503 | 626 | 1240 | 1296.2963 | 0
2016-09-16 12:00 | 1925 | 1227.512 | 587 | 1240 | 1040 | 0
2016-09-16 13:00 | 1925 | 1293.864 | 587 | 1240 | 1040 | 0
2016-09-16 14:00 | 2474 | 1329.548 | 476 | 1240 | 900 | 0
2016-09-16 15:00 | 2474 | 1364 | 512 | 1240 | 1040 | 0
2016-09-16 16:00 | 2474 | 1379.026 | 382 | 1240 | 1040 | 0
2016-09-16 17:00 | 2474 | 1357.708 | 342 | 1240 | 1040 | 0
2016-09-16 18:00 | 2257 | 1305.26 | 332 | 1240 | 1040 | 0
2016-09-16 19:00 | 2257 | 1210.314 | 332 | 1240 | 1040 | 0
2016-09-16 20:00 | 2257 | 1186.164 | 413 | 1240 | 1296.2963 | 0
2016-09-16 21:00 | 2257 | 1118.67 | 332 | 1240 | 1296.2963 | 0
2016-09-16 22:00 | 2144 | 932.254 | 332 | 1240 | 1440 | 0
2016-09-16 23:00 | 2144 | 891.76 | 332 | 1240 | 1440 | 0
2016-09-17 | 2144 | 888.56 | 746 | 1240 | 1440 | 0
2016-09-17 01:00 | 2144 | 843.6 | 332 | 1240 | 1440 | 0
2016-09-17 02:00 | 2073 | 772.426 | 332 | 1240 | 1440 | 0
2016-09-17 03:00 | 2073 | 756.276 | 377 | 1240 | 1440 | 0
2016-09-17 04:00 | 2073 | 757.473 | 397 | 1240 | 1440 | 0
2016-09-17 05:00 | 2073 | 831.32 | 537 | 1240 | 1440 | 0
2016-09-17 06:00 | 2067 | 854.886 | 668 | 1240 | 1440 | 0
2016-09-17 07:00 | 2067 | 875.216 | 462 | 1240 | 1238.9381 | 0
2016-09-17 08:00 | 2067 | 894.026 | 433 | 1240 | 1238.9381 | 0
2016-09-17 09:00 | 2067 | 1054.83 | 562 | 1240 | 1296.2963 | 0
2016-09-17 10:00 | 1925 | 1189.1 | 627 | 1240 | 1000 | 0
2016-09-17 11:00 | 1925 | 1262.888 | 626 | 1240 | 1040 | 0
2016-09-17 12:00 | 1925 | 1311.2 | 587 | 1240 | 1040 | 0
2016-09-17 13:00 | 1925 | 1353.99 | 587 | 1240 | 900 | 0
2016-09-17 14:00 | 2474 | 1383.514 | 476 | 1240 | 900 | 0
2016-09-17 15:00 | 2474 | 1395.9 | 512 | 1240 | 900 | 0
2016-09-17 16:00 | 2474 | 1386.792 | 382 | 1240 | 900 | 0
2016-09-17 17:00 | 2474 | 1320.33 | 342 | 1240 | 1040 | 0
2016-09-17 18:00 | 2257 | 1278.244 | 332 | 1240 | 1000 | 0
2016-09-17 19:00 | 2257 | 1165.521 | 332 | 1240 | 1296.2963 | 0
2016-09-17 20:00 | 2257 | 1145.445 | 413 | 1240 | 1238.9381 | 0
2016-09-17 21:00 | 2257 | 992.332 | 332 | 1240 | 1238.9381 | 0
2016-09-17 22:00 | 2144 | 937.346 | 332 | 1240 | 1440 | 0
2016-09-17 23:00 | 2144 | 922.48 | 332 | 1240 | 1440 | 0
2016-09-18 | 2144 | 907.2 | 746 | 1240 | 1440 | 0
2016-09-18 01:00 | 2144 | 880.98 | 332 | 1240 | 1440 | 0
2016-09-18 02:00 | 2073 | 805.486 | 332 | 1240 | 1440 | 0
2016-09-18 03:00 | 2073 | 784.795 | 377 | 1240 | 1440 | 0
2016-09-18 04:00 | 2073 | 774.611 | 397 | 1240 | 1440 | 0
2016-09-18 05:00 | 2073 | 781.014 | 537 | 1240 | 1440 | 0
2016-09-18 06:00 | 2067 | 843.52 | 668 | 1240 | 1440 | 0
2016-09-18 07:00 | 2067 | 858.5 | 462 | 1240 | 1440 | 0
2016-09-18 08:00 | 2067 | 863.132 | 433 | 1240 | 1440 | 0
2016-09-18 09:00 | 2067 | 935.199 | 562 | 1240 | 1238.9381 | 0
2016-09-18 10:00 | 1925 | 1112.097 | 627 | 1240 | 1296.2963 | 0
2016-09-18 11:00 | 1925 | 1231.582 | 626 | 1240 | 1040 | 0
2016-09-18 12:00 | 1925 | 1279.344 | 587 | 1240 | 1040 | 0
2016-09-18 13:00 | 1925 | 1298.088 | 587 | 1240 | 1040 | 0
2016-09-18 14:00 | 2474 | 1318.152 | 476 | 1240 | 1040 | 0
2016-09-18 15:00 | 2474 | 1328.272 | 512 | 1240 | 1040 | 0
2016-09-18 16:00 | 2474 | 1323.278 | 382 | 1240 | 1040 | 0
2016-09-18 17:00 | 2474 | 1298.88 | 342 | 1240 | 1040 | 0
2016-09-18 18:00 | 2257 | 1224.531 | 332 | 1240 | 1040 | 0
2016-09-18 19:00 | 2257 | 1194.816 | 332 | 1240 | 1296.2963 | 0
2016-09-18 20:00 | 2257 | 1068.465 | 413 | 1240 | 1238.9381 | 0
2016-09-18 21:00 | 2257 | 1028.565 | 332 | 1240 | 1238.9381 | 0
2016-09-18 22:00 | 2144 | 973.389 | 332 | 1240 | 1238.9381 | 0
2016-09-18 23:00 | 2144 | 960.52 | 332 | 1240 | 1440 | 0
2016-09-19 | 2144 | 910.52 | 746 | 1240 | 1440 | 0
2016-09-19 01:00 | 2144 | 866.1 | 332 | 1240 | 1440 | 0
2016-09-19 02:00 | 2073 | 834 | 332 | 1240 | 1440 | 0
2016-09-19 03:00 | 2073 | 771.248 | 377 | 1240 | 1440 | 0
2016-09-19 04:00 | 2073 | 759.202 | 397 | 1240 | 1440 | 0
2016-09-19 05:00 | 2073 | 798.8 | 537 | 1240 | 1440 | 0
2016-09-19 06:00 | 2067 | 810.3 | 668 | 1240 | 1440 | 0
2016-09-19 07:00 | 2067 | 821.74 | 462 | 1240 | 1440 | 0
2016-09-19 08:00 | 2067 | 863.38 | 433 | 1240 | 1440 | 0
2016-09-19 09:00 | 2067 | 885.305 | 562 | 1240 | 1238.9381 | 0
2016-09-19 10:00 | 1925 | 1055.649 | 627 | 1240 | 1296.2963 | 0
2016-09-19 11:00 | 1925 | 1129.128 | 626 | 1240 | 1296.2963 | 0
2016-09-19 12:00 | 1925 | 1253.098 | 587 | 1240 | 1000 | 0
2016-09-19 13:00 | 1925 | 1301.652 | 587 | 1240 | 1000 | 0
2016-09-19 14:00 | 2474 | 1298.198 | 476 | 1240 | 1000 | 0
2016-09-19 15:00 | 2474 | 1299.122 | 512 | 1240 | 1000 | 0
2016-09-19 16:00 | 2474 | 1240.197 | 382 | 1240 | 1000 | 0
2016-09-19 17:00 | 2474 | 1241.667 | 342 | 1240 | 1000 | 0
2016-09-19 18:00 | 2257 | 1224.489 | 332 | 1240 | 1296.2963 | 0
2016-09-19 19:00 | 2257 | 1207.311 | 332 | 1240 | 1296.2963 | 0
2016-09-19 20:00 | 2257 | 1199.919 | 413 | 1240 | 1296.2963 | 0
2016-09-19 21:00 | 2257 | 1140.657 | 332 | 1240 | 1296.2963 | 0
2016-09-19 22:00 | 2144 | 958.607 | 332 | 1240 | 1238.9381 | 0
2016-09-19 23:00 | 2144 | 926.64 | 332 | 1240 | 1440 | 0
2016-09-20 | 2144 | 759.867 | 746 | 1240 | 1440 | 0
2016-09-20 01:00 | 2144 | 725.363 | 332 | 1240 | 1440 | 0
2016-09-20 02:00 | 2073 | 705.033 | 332 | 1240 | 1440 | 0
2016-09-20 03:00 | 2073 | 697.167 | 377 | 1240 | 1440 | 0
2016-09-20 04:00 | 2073 | 705.812 | 397 | 1240 | 1440 | 0
2016-09-20 05:00 | 2073 | 743.47 | 537 | 1240 | 1440 | 0
2016-09-20 06:00 | 2067 | 857.2 | 668 | 1240 | 1440 | 0
2016-09-20 07:00 | 2067 | 884.36 | 462 | 1240 | 1440 | 0
2016-09-20 08:00 | 2067 | 894.7 | 433 | 1240 | 1440 | 0
2016-09-20 09:00 | 2067 | 884.545 | 562 | 1240 | 1238.9381 | 0
2016-09-20 10:00 | 1925 | 930.031 | 627 | 1240 | 1238.9381 | 0
2016-09-20 11:00 | 1925 | 1084.377 | 626 | 1240 | 1296.2963 | 0
2016-09-20 12:00 | 1925 | 1139.607 | 587 | 1240 | 1296.2963 | 0
2016-09-20 13:00 | 1925 | 1193.367 | 587 | 1240 | 1000 | 0
2016-09-20 14:00 | 2474 | 1216.068 | 476 | 1240 | 1000 | 0
2016-09-20 15:00 | 2474 | 1222.137 | 512 | 1240 | 1000 | 0
2016-09-20 16:00 | 2474 | 1234.926 | 382 | 1240 | 1000 | 0
2016-09-20 17:00 | 2474 | 1219.701 | 342 | 1240 | 1000 | 0
2016-09-20 18:00 | 2257 | 1198.344 | 332 | 1240 | 1000 | 0
2016-09-20 19:00 | 2257 | 1176.987 | 332 | 1240 | 1296.2963 | 0
2016-09-20 20:00 | 2257 | 1051.289 | 413 | 1240 | 1296.2963 | 0
2016-09-20 21:00 | 2257 | 996.189 | 332 | 1240 | 1440 | 0
2016-09-20 22:00 | 2144 | 965.94 | 332 | 1240 | 1440 | 0
2016-09-20 23:00 | 2144 | 837.501 | 332 | 1240 | 1430.7692 | 0
2016-09-21 | 2144 | 751.64 | 746 | 1240 | 1430.7692 | 0
2016-09-21 01:00 | 2144 | 753.92 | 332 | 1240 | 1430.7692 | 0
2016-09-21 02:00 | 2073 | 730.4 | 332 | 1240 | 1430.7692 | 0
2016-09-21 03:00 | 2073 | 718.72 | 377 | 1240 | 1430.7692 | 0
2016-09-21 04:00 | 2073 | 724.2 | 397 | 1240 | 1430.7692 | 0
2016-09-21 05:00 | 2073 | 722.874 | 537 | 1240 | 1430.7692 | 0
2016-09-21 06:00 | 2067 | 835.1 | 668 | 1240 | 1430.7692 | 0
2016-09-21 07:00 | 2067 | 859.04 | 462 | 1240 | 1430.7692 | 0
2016-09-21 08:00 | 2067 | 866.54 | 433 | 1240 | 1430.7692 | 0
2016-09-21 09:00 | 2067 | 900.62 | 562 | 1240 | 1440 | 0
2016-09-21 10:00 | 1925 | 947.88 | 627 | 1240 | 1440 | 0
2016-09-21 11:00 | 1925 | 938.885 | 626 | 1240 | 1440 | 0
2016-09-21 12:00 | 1925 | 968.24 | 587 | 1240 | 1238.9381 | 0
2016-09-21 13:00 | 1925 | 1003.903 | 587 | 1240 | 1296.2963 | 0
2016-09-21 14:00 | 2474 | 1143.345 | 476 | 1240 | 1296.2963 | 0
2016-09-21 15:00 | 2474 | 1174.236 | 512 | 1240 | 1296.2963 | 0
2016-09-21 16:00 | 2474 | 1195.194 | 382 | 1240 | 1296.2963 | 0
2016-09-21 17:00 | 2474 | 1185.408 | 342 | 1240 | 1296.2963 | 0
2016-09-21 18:00 | 2257 | 1043.309 | 332 | 1240 | 1238.9381 | 0
2016-09-21 19:00 | 2257 | 1067.48 | 332 | 1240 | 1440 | 0
2016-09-21 20:00 | 2257 | 1058 | 413 | 1240 | 1440 | 0
2016-09-21 21:00 | 2257 | 1009.74 | 332 | 1240 | 1430.7692 | 0
2016-09-21 22:00 | 2144 | 886.122 | 332 | 1240 | 1430.7692 | 0
2016-09-21 23:00 | 2144 | 808.944 | 332 | 1240 | 1521.4286 | 0
2016-09-22 | 2144 | 746.72 | 746 | 1240 | 1521.4286 | 0
2016-09-22 01:00 | 2144 | 716.1 | 332 | 1240 | 1521.4286 | 0
2016-09-22 02:00 | 2073 | 695.62 | 332 | 1240 | 1521.4286 | 0
2016-09-22 03:00 | 2073 | 685.48 | 377 | 1240 | 1521.4286 | 0
2016-09-22 04:00 | 2073 | 691.1 | 397 | 1240 | 1521.4286 | 0
2016-09-22 05:00 | 2073 | 690.061 | 537 | 1240 | 1521.4286 | 0
2016-09-22 06:00 | 2067 | 757.815 | 668 | 1240 | 1430.7692 | 0
2016-09-22 07:00 | 2067 | 820.88 | 462 | 1240 | 1430.7692 | 0
2016-09-22 08:00 | 2067 | 792.205 | 433 | 1240 | 1430.7692 | 0
2016-09-22 09:00 | 2067 | 874.56 | 562 | 1240 | 1430.7692 | 0
2016-09-22 10:00 | 1925 | 924.98 | 627 | 1240 | 1430.7692 | 0
2016-09-22 11:00 | 1925 | 974.96 | 626 | 1240 | 1430.7692 | 0
2016-09-22 12:00 | 1925 | 1019.34 | 587 | 1240 | 1430.7692 | 0
2016-09-22 13:00 | 1925 | 1057.76 | 587 | 1240 | 1430.7692 | 0
2016-09-22 14:00 | 2474 | 1084.06 | 476 | 1240 | 1440 | 0
2016-09-22 15:00 | 2474 | 1106.06 | 512 | 1240 | 1440 | 0
2016-09-22 16:00 | 2474 | 1120.48 | 382 | 1240 | 1440 | 0
2016-09-22 17:00 | 2474 | 1106.34 | 342 | 1240 | 1440 | 0
2016-09-22 18:00 | 2257 | 1071.72 | 332 | 1240 | 1440 | 0
2016-09-22 19:00 | 2257 | 1037.1 | 332 | 1240 | 1440 | 0
2016-09-22 20:00 | 2257 | 1024.06 | 413 | 1240 | 1440 | 0
2016-09-22 21:00 | 2257 | 976.08 | 332 | 1240 | 1430.7692 | 0
2016-09-22 22:00 | 2144 | 859.769 | 332 | 1240 | 1521.4286 | 0
2016-09-22 23:00 | 2144 | 831.96 | 332 | 1240 | 1521.4286 | 0
2016-09-23 | 2144 | 780.28 | 746 | 1240 | 1673.3333 | 0
2016-09-23 01:00 | 2144 | 671.4 | 332 | 1240 | 1673.3333 | 0
2016-09-23 02:00 | 2073 | 654.57 | 332 | 1240 | 1673.3333 | 0
2016-09-23 03:00 | 2073 | 645.588 | 377 | 1240 | 1673.3333 | 0
2016-09-23 04:00 | 2073 | 649.908 | 397 | 1240 | 1673.3333 | 0
2016-09-23 05:00 | 2073 | 759.36 | 537 | 1240 | 1673.3333 | 0
2016-09-23 06:00 | 2067 | 790.077 | 668 | 1240 | 1521.4286 | 0
2016-09-23 07:00 | 2067 | 812.82 | 462 | 1240 | 1521.4286 | 0
2016-09-23 08:00 | 2067 | 866.58 | 433 | 1240 | 1521.4286 | 0
2016-09-23 09:00 | 2067 | 864.063 | 562 | 1240 | 1521.4286 | 0
2016-09-23 10:00 | 1925 | 914.28 | 627 | 1240 | 1521.4286 | 0
2016-09-23 11:00 | 1925 | 1011.94 | 626 | 1240 | 1430.7692 | 0
2016-09-23 12:00 | 1925 | 1052.04 | 587 | 1240 | 1430.7692 | 0
2016-09-23 13:00 | 1925 | 1036.602 | 587 | 1240 | 1440 | 0
2016-09-23 14:00 | 2474 | 1066.432 | 476 | 1240 | 1440 | 0
2016-09-23 15:00 | 2474 | 1200.969 | 512 | 1240 | 1238.9381 | 0
2016-09-23 16:00 | 2474 | 1214.157 | 382 | 1240 | 1296.2963 | 0
2016-09-23 17:00 | 2474 | 1199.373 | 342 | 1240 | 1296.2963 | 0
2016-09-23 18:00 | 2257 | 1163.4 | 332 | 1240 | 1296.2963 | 0
2016-09-23 19:00 | 2257 | 1127.427 | 332 | 1240 | 1238.9381 | 0
2016-09-23 20:00 | 2257 | 1116.024 | 413 | 1240 | 1238.9381 | 0
2016-09-23 21:00 | 2257 | 959.842 | 332 | 1240 | 1238.9381 | 0
2016-09-23 22:00 | 2144 | 892.411 | 332 | 1240 | 1440 | 0
2016-09-23 23:00 | 2144 | 861.24 | 332 | 1240 | 1440 | 0
2016-09-24 | 2144 | 855.38 | 746 | 1240 | 1440 | 0
2016-09-24 01:00 | 2144 | 793.896 | 332 | 1240 | 1440 | 0
2016-09-24 02:00 | 2073 | 767.79 | 332 | 1240 | 1440 | 0
2016-09-24 03:00 | 2073 | 754.756 | 377 | 1240 | 1440 | 0
2016-09-24 04:00 | 2073 | 760.418 | 397 | 1240 | 1440 | 0
2016-09-24 05:00 | 2073 | 836.26 | 537 | 1240 | 1440 | 0
2016-09-24 06:00 | 2067 | 861.707 | 668 | 1240 | 1440 | 0
2016-09-24 07:00 | 2067 | 884.963 | 462 | 1240 | 1238.9381 | 0
2016-09-24 08:00 | 2067 | 900.733 | 433 | 1240 | 1238.9381 | 0
2016-09-24 09:00 | 2067 | 1043.679 | 562 | 1240 | 1296.2963 | 0
2016-09-24 10:00 | 1925 | 1098.489 | 627 | 1240 | 1296.2963 | 0
2016-09-24 11:00 | 1925 | 1146.6 | 626 | 1240 | 1000 | 0
2016-09-24 12:00 | 1925 | 1243.66 | 587 | 1240 | 1040 | 0
2016-09-24 13:00 | 1925 | 1288.386 | 587 | 1240 | 1040 | 0
2016-09-24 14:00 | 2474 | 1312.432 | 476 | 1240 | 1040 | 0
2016-09-24 15:00 | 2474 | 1333.794 | 512 | 1240 | 1040 | 0
2016-09-24 16:00 | 2474 | 1329.328 | 382 | 1240 | 1040 | 0
2016-09-24 17:00 | 2474 | 1305.876 | 342 | 1240 | 1040 | 0
2016-09-24 18:00 | 2257 | 1259.742 | 332 | 1240 | 1040 | 0
2016-09-24 19:00 | 2257 | 1158.444 | 332 | 1240 | 1296.2963 | 0
2016-09-24 20:00 | 2257 | 1139.838 | 413 | 1240 | 1296.2963 | 0
2016-09-24 21:00 | 2257 | 986.461 | 332 | 1240 | 1238.9381 | 0
2016-09-24 22:00 | 2144 | 929.176 | 332 | 1240 | 1238.9381 | 0
2016-09-24 23:00 | 2144 | 910.58 | 332 | 1240 | 1440 | 0
2016-09-25 | 2144 | 897.68 | 746 | 1240 | 1440 | 0
2016-09-25 01:00 | 2144 | 852.44 | 332 | 1240 | 1440 | 0
2016-09-25 02:00 | 2073 | 821.4 | 332 | 1240 | 1440 | 0
2016-09-25 03:00 | 2073 | 800.52 | 377 | 1240 | 1440 | 0
2016-09-25 04:00 | 2073 | 749.683 | 397 | 1240 | 1440 | 0
2016-09-25 05:00 | 2073 | 795.58 | 537 | 1240 | 1440 | 0
2016-09-25 06:00 | 2067 | 819.3 | 668 | 1240 | 1440 | 0
2016-09-25 07:00 | 2067 | 835.42 | 462 | 1240 | 1440 | 0
2016-09-25 08:00 | 2067 | 834.252 | 433 | 1240 | 1440 | 0
2016-09-25 09:00 | 2067 | 894.9 | 562 | 1240 | 1238.9381 | 0
2016-09-25 10:00 | 1925 | 1052.205 | 627 | 1240 | 1296.2963 | 0
2016-09-25 11:00 | 1925 | 1102.479 | 626 | 1240 | 1296.2963 | 0
2016-09-25 12:00 | 1925 | 1142.589 | 587 | 1240 | 1000 | 0
2016-09-25 13:00 | 1925 | 1162.875 | 587 | 1240 | 1000 | 0
2016-09-25 14:00 | 2474 | 1234.926 | 476 | 1240 | 1000 | 0
2016-09-25 15:00 | 2474 | 1240.646 | 512 | 1240 | 1000 | 0
2016-09-25 16:00 | 2474 | 1237.94 | 382 | 1240 | 1000 | 0
2016-09-25 17:00 | 2474 | 1168.125 | 342 | 1240 | 1000 | 0
2016-09-25 18:00 | 2257 | 1145.319 | 332 | 1240 | 1296.2963 | 0
2016-09-25 19:00 | 2257 | 1122.513 | 332 | 1240 | 1296.2963 | 0
2016-09-25 20:00 | 2257 | 1106.826 | 413 | 1240 | 1296.2963 | 0
2016-09-25 21:00 | 2257 | 1061.109 | 332 | 1240 | 1296.2963 | 0
2016-09-25 22:00 | 2144 | 907.858 | 332 | 1240 | 1238.9381 | 0
2016-09-25 23:00 | 2144 | 850.174 | 332 | 1240 | 1238.9381 | 0
2016-09-26 | 2144 | 854.6 | 746 | 1240 | 1440 | 0
2016-09-26 01:00 | 2144 | 812.26 | 332 | 1240 | 1430.7692 | 0
2016-09-26 02:00 | 2073 | 741.551 | 332 | 1240 | 1430.7692 | 0
2016-09-26 03:00 | 2073 | 724.299 | 377 | 1240 | 1430.7692 | 0
2016-09-26 04:00 | 2073 | 714.514 | 397 | 1240 | 1430.7692 | 0
2016-09-26 05:00 | 2073 | 714.381 | 537 | 1240 | 1430.7692 | 0
2016-09-26 06:00 | 2067 | 727.073 | 668 | 1240 | 1430.7692 | 0
2016-09-26 07:00 | 2067 | 738.435 | 462 | 1240 | 1430.7692 | 0
2016-09-26 08:00 | 2067 | 774.174 | 433 | 1240 | 1430.7692 | 0
2016-09-26 09:00 | 2067 | 822.643 | 562 | 1240 | 1430.7692 | 0
2016-09-26 10:00 | 1925 | 865.564 | 627 | 1240 | 1430.7692 | 0
2016-09-26 11:00 | 1925 | 955.18 | 626 | 1240 | 1430.7692 | 0
2016-09-26 12:00 | 1925 | 992.8 | 587 | 1240 | 1440 | 0
2016-09-26 13:00 | 1925 | 968.791 | 587 | 1240 | 1440 | 0
2016-09-26 14:00 | 2474 | 986.746 | 476 | 1240 | 1440 | 0
2016-09-26 15:00 | 2474 | 1002.402 | 512 | 1240 | 1440 | 0
2016-09-26 16:00 | 2474 | 1011.237 | 382 | 1240 | 1440 | 0
2016-09-26 17:00 | 2474 | 1002.041 | 342 | 1240 | 1440 | 0
2016-09-26 18:00 | 2257 | 984.789 | 332 | 1240 | 1238.9381 | 0
2016-09-26 19:00 | 2257 | 967.537 | 332 | 1240 | 1238.9381 | 0
2016-09-26 20:00 | 2257 | 961.666 | 413 | 1240 | 1238.9381 | 0
2016-09-26 21:00 | 2257 | 914.109 | 332 | 1240 | 1238.9381 | 0
2016-09-26 22:00 | 2144 | 885.6 | 332 | 1240 | 1440 | 0
2016-09-26 23:00 | 2144 | 766.194 | 332 | 1240 | 1430.7692 | 0
2016-09-27 | 2144 | 713.583 | 746 | 1240 | 1430.7692 | 0
2016-09-27 01:00 | 2144 | 714.6 | 332 | 1240 | 1430.7692 | 0
2016-09-27 02:00 | 2073 | 692.72 | 332 | 1240 | 1521.4286 | 0
2016-09-27 03:00 | 2073 | 682.64 | 377 | 1240 | 1521.4286 | 0
2016-09-27 04:00 | 2073 | 691.36 | 397 | 1240 | 1521.4286 | 0
2016-09-27 05:00 | 2073 | 728.6 | 537 | 1240 | 1521.4286 | 0
2016-09-27 06:00 | 2067 | 760 | 668 | 1240 | 1521.4286 | 0
2016-09-27 07:00 | 2067 | 819.68 | 462 | 1240 | 1430.7692 | 0
2016-09-27 08:00 | 2067 | 825.72 | 433 | 1240 | 1430.7692 | 0
2016-09-27 09:00 | 2067 | 851.66 | 562 | 1240 | 1430.7692 | 0
2016-09-27 10:00 | 1925 | 882.4 | 627 | 1240 | 1440 | 0
2016-09-27 11:00 | 1925 | 861.802 | 626 | 1240 | 1440 | 0
2016-09-27 12:00 | 1925 | 883.082 | 587 | 1240 | 1440 | 0
2016-09-27 13:00 | 1925 | 910.062 | 587 | 1240 | 1238.9381 | 0
2016-09-27 14:00 | 2474 | 1032.549 | 476 | 1240 | 1238.9381 | 0
2016-09-27 15:00 | 2474 | 1059.744 | 512 | 1240 | 1296.2963 | 0
2016-09-27 16:00 | 2474 | 1080.051 | 382 | 1240 | 1296.2963 | 0
2016-09-27 17:00 | 2474 | 1077.468 | 342 | 1240 | 1296.2963 | 0
2016-09-27 18:00 | 2257 | 1056.111 | 332 | 1240 | 1296.2963 | 0
2016-09-27 19:00 | 2257 | 936.206 | 332 | 1240 | 1238.9381 | 0
2016-09-27 20:00 | 2257 | 931.285 | 413 | 1240 | 1238.9381 | 0
2016-09-27 21:00 | 2257 | 927.34 | 332 | 1240 | 1440 | 0
2016-09-27 22:00 | 2144 | 849.26 | 332 | 1240 | 1430.7692 | 0
2016-09-27 23:00 | 2144 | 731.937 | 332 | 1240 | 1521.4286 | 0
2016-09-28 | 2144 | 717.06 | 746 | 1240 | 1521.4286 | 0
2016-09-28 01:00 | 2144 | 687.34 | 332 | 1240 | 1521.4286 | 0
2016-09-28 02:00 | 2073 | 669.92 | 332 | 1240 | 1521.4286 | 0
2016-09-28 03:00 | 2073 | 661.16 | 377 | 1240 | 1521.4286 | 0
2016-09-28 04:00 | 2073 | 668.06 | 397 | 1240 | 1521.4286 | 0
2016-09-28 05:00 | 2073 | 708.34 | 537 | 1240 | 1521.4286 | 0
2016-09-28 06:00 | 2067 | 747.65 | 668 | 1240 | 1521.4286 | 0
2016-09-28 07:00 | 2067 | 766.574 | 462 | 1240 | 1521.4286 | 0
2016-09-28 08:00 | 2067 | 773.072 | 433 | 1240 | 1521.4286 | 0
2016-09-28 09:00 | 2067 | 847.26 | 562 | 1240 | 1430.7692 | 0
2016-09-28 10:00 | 1925 | 839.078 | 627 | 1240 | 1440 | 0
2016-09-28 11:00 | 1925 | 868.946 | 626 | 1240 | 1440 | 0
2016-09-28 12:00 | 1925 | 899.384 | 587 | 1240 | 1238.9381 | 0
2016-09-28 13:00 | 1925 | 941.26 | 587 | 1240 | 1238.9381 | 0
2016-09-28 14:00 | 2474 | 1087.506 | 476 | 1240 | 1296.2963 | 0
2016-09-28 15:00 | 2474 | 1132.425 | 512 | 1240 | 1000 | 0
2016-09-28 16:00 | 2474 | 1165.605 | 382 | 1240 | 1000 | 0
2016-09-28 17:00 | 2474 | 1227.754 | 342 | 1240 | 1000 | 0
2016-09-28 18:00 | 2257 | 1146.138 | 332 | 1240 | 1000 | 0
2016-09-28 19:00 | 2257 | 1120.329 | 332 | 1240 | 1000 | 0
2016-09-28 20:00 | 2257 | 1101.156 | 413 | 1240 | 1000 | 0
2016-09-28 21:00 | 2257 | 938.733 | 332 | 1240 | 1296.2963 | 0
2016-09-28 22:00 | 2144 | 904.08 | 332 | 1240 | 1440 | 0
2016-09-28 23:00 | 2144 | 817.92 | 332 | 1240 | 1430.7692 | 0
2016-09-29 | 2144 | 695.68 | 746 | 1240 | 1521.4286 | 0
2016-09-29 01:00 | 2144 | 662.6 | 332 | 1240 | 1521.4286 | 0
2016-09-29 02:00 | 2073 | 642.68 | 332 | 1240 | 1521.4286 | 0
2016-09-29 03:00 | 2073 | 631.4 | 377 | 1240 | 1521.4286 | 0
2016-09-29 04:00 | 2073 | 637.96 | 397 | 1240 | 1521.4286 | 0
2016-09-29 05:00 | 2073 | 674.06 | 537 | 1240 | 1521.4286 | 0
2016-09-29 06:00 | 2067 | 709.137 | 668 | 1240 | 1430.7692 | 0
2016-09-29 07:00 | 2067 | 727.301 | 462 | 1240 | 1430.7692 | 0
2016-09-29 08:00 | 2067 | 735.585 | 433 | 1240 | 1430.7692 | 0
2016-09-29 09:00 | 2067 | 811.4 | 562 | 1240 | 1440 | 0
2016-09-29 10:00 | 1925 | 855.98 | 627 | 1240 | 1440 | 0
2016-09-29 11:00 | 1925 | 854.259 | 626 | 1240 | 1238.9381 | 0
2016-09-29 12:00 | 1925 | 896.667 | 587 | 1240 | 1296.2963 | 0
2016-09-29 13:00 | 1925 | 1042.44 | 587 | 1240 | 1000 | 0
2016-09-29 14:00 | 2474 | 1089.102 | 476 | 1240 | 1000 | 0
2016-09-29 15:00 | 2474 | 1181.95 | 512 | 1240 | 1040 | 0
2016-09-29 16:00 | 2474 | 1209.78 | 382 | 1240 | 1040 | 0
2016-09-29 17:00 | 2474 | 1207.184 | 342 | 1240 | 1040 | 0
2016-09-29 18:00 | 2257 | 1114.47 | 332 | 1240 | 1040 | 0
2016-09-29 19:00 | 2257 | 1076.628 | 332 | 1240 | 1000 | 0
2016-09-29 20:00 | 2257 | 949.43 | 413 | 1240 | 1296.2963 | 0
2016-09-29 21:00 | 2257 | 937.84 | 332 | 1240 | 1238.9381 | 0
2016-09-29 22:00 | 2144 | 854.38 | 332 | 1240 | 1430.7692 | 0
2016-09-29 23:00 | 2144 | 731.804 | 332 | 1240 | 1521.4286 | 0
2016-09-30 | 2144 | 699.56 | 746 | 1240 | 1521.4286 | 0
2016-09-30 01:00 | 2144 | 665.26 | 332 | 1240 | 1521.4286 | 0
2016-09-30 02:00 | 2073 | 642.7 | 332 | 1240 | 1521.4286 | 0
2016-09-30 03:00 | 2073 | 633.18 | 377 | 1240 | 1521.4286 | 0
2016-09-30 04:00 | 2073 | 636.98 | 397 | 1240 | 1521.4286 | 0
2016-09-30 05:00 | 2073 | 672.32 | 537 | 1240 | 1521.4286 | 0
2016-09-30 06:00 | 2067 | 708.073 | 668 | 1240 | 1430.7692 | 0
2016-09-30 07:00 | 2067 | 726.56 | 462 | 1240 | 1430.7692 | 0
2016-09-30 08:00 | 2067 | 733.97 | 433 | 1240 | 1430.7692 | 0
2016-09-30 09:00 | 2067 | 809.58 | 562 | 1240 | 1440 | 0
2016-09-30 10:00 | 1925 | 854.36 | 627 | 1240 | 1440 | 0
2016-09-30 11:00 | 1925 | 854.696 | 626 | 1240 | 1440 | 0
2016-09-30 12:00 | 1925 | 899.289 | 587 | 1240 | 1238.9381 | 0
2016-09-30 13:00 | 1925 | 1051.302 | 587 | 1240 | 1296.2963 | 0
2016-09-30 14:00 | 2474 | 1096.2 | 476 | 1240 | 1296.2963 | 0
2016-09-30 15:00 | 2474 | 1133.139 | 512 | 1240 | 1000 | 0
2016-09-30 16:00 | 2474 | 1212.816 | 382 | 1240 | 1000 | 0
2016-09-30 17:00 | 2474 | 1199.264 | 342 | 1240 | 1000 | 0
2016-09-30 18:00 | 2257 | 1109.682 | 332 | 1240 | 1000 | 0
2016-09-30 19:00 | 2257 | 1074.633 | 332 | 1240 | 1296.2963 | 0
2016-09-30 20:00 | 2257 | 951.121 | 413 | 1240 | 1238.9381 | 0
2016-09-30 21:00 | 2257 | 896.173 | 332 | 1240 | 1440 | 0
2016-09-30 22:00 | 2144 | 863.92 | 332 | 1240 | 1430.7692 | 0
2016-09-30 23:00 | 2144 | 743.413 | 332 | 1240 | 1430.7692 | 0
2016-10-01 | 2421 | 710.448 | 677 | 1240 | 1430.7692 | 0
2016-10-01 01:00 | 2421 | 708.64 | 302 | 1240 | 1521.4286 | 0
2016-10-01 02:00 | 2595 | 682.32 | 391 | 1240 | 1521.4286 | 0
2016-10-01 03:00 | 2595 | 668.76 | 305 | 1240 | 1521.4286 | 0
2016-10-01 04:00 | 2595 | 671.3 | 302 | 1240 | 1521.4286 | 0
2016-10-01 05:00 | 2595 | 703.68 | 545 | 1240 | 1521.4286 | 0
2016-10-01 06:00 | 3002 | 735.87 | 695 | 1240 | 1430.7692 | 0
2016-10-01 07:00 | 3002 | 794.98 | 497 | 1240 | 1430.7692 | 0
2016-10-01 08:00 | 3002 | 804.38 | 333 | 1240 | 1430.7692 | 0
2016-10-01 09:00 | 3002 | 841.5 | 560 | 1240 | 1440 | 0
2016-10-01 10:00 | 3145 | 840.218 | 595 | 1240 | 1440 | 0
2016-10-01 11:00 | 3145 | 882.246 | 538 | 1240 | 1238.9381 | 0
2016-10-01 12:00 | 3145 | 925.091 | 497 | 1240 | 1238.9381 | 0
2016-10-01 13:00 | 3145 | 1073.373 | 473 | 1240 | 1296.2963 | 0
2016-10-01 14:00 | 2424 | 1118.418 | 534 | 1240 | 1000 | 0
2016-10-01 15:00 | 2424 | 1206.656 | 521 | 1240 | 1000 | 0
2016-10-01 16:00 | 2424 | 1223.376 | 394 | 1240 | 1000 | 0
2016-10-01 17:00 | 2424 | 1201.75 | 439 | 1240 | 1000 | 0
2016-10-01 18:00 | 2101 | 1097.334 | 524 | 1240 | 1000 | 0
2016-10-01 19:00 | 2101 | 947.796 | 453 | 1240 | 1296.2963 | 0
2016-10-01 20:00 | 2101 | 917.187 | 302 | 1240 | 1238.9381 | 0
2016-10-01 21:00 | 2101 | 912.32 | 302 | 1240 | 1440 | 0
2016-10-01 22:00 | 2421 | 808.089 | 302 | 1240 | 1430.7692 | 0
2016-10-01 23:00 | 2421 | 745.978 | 302 | 1240 | 1430.7692 | 0
2016-10-02 | 2421 | 735.547 | 677 | 1240 | 1430.7692 | 0
2016-10-02 01:00 | 2421 | 712.595 | 302 | 1240 | 1430.7692 | 0
2016-10-02 02:00 | 2595 | 720.48 | 391 | 1240 | 1430.7692 | 0
2016-10-02 03:00 | 2595 | 700.28 | 305 | 1240 | 1430.7692 | 0
2016-10-02 04:00 | 2595 | 690.96 | 302 | 1240 | 1430.7692 | 0
2016-10-02 05:00 | 2595 | 697.76 | 545 | 1240 | 1430.7692 | 0
2016-10-02 06:00 | 3002 | 684.741 | 695 | 1240 | 1430.7692 | 0
2016-10-02 07:00 | 3002 | 698.383 | 497 | 1240 | 1430.7692 | 0
2016-10-02 08:00 | 3002 | 730.854 | 333 | 1240 | 1430.7692 | 0
2016-10-02 09:00 | 3002 | 819.04 | 560 | 1240 | 1430.7692 | 0
2016-10-02 10:00 | 3145 | 865.44 | 595 | 1240 | 1440 | 0
2016-10-02 11:00 | 3145 | 860.168 | 538 | 1240 | 1440 | 0
2016-10-02 12:00 | 3145 | 898.947 | 497 | 1240 | 1238.9381 | 0
2016-10-02 13:00 | 3145 | 934.344 | 473 | 1240 | 1238.9381 | 0
2016-10-02 14:00 | 2424 | 1069.551 | 534 | 1240 | 1238.9381 | 0
2016-10-02 15:00 | 2424 | 1103.34 | 521 | 1240 | 1238.9381 | 0
2016-10-02 16:00 | 2424 | 1124.046 | 394 | 1240 | 1238.9381 | 0
2016-10-02 17:00 | 2424 | 1009.394 | 439 | 1240 | 1238.9381 | 0
2016-10-02 18:00 | 2101 | 983.269 | 524 | 1240 | 1238.9381 | 0
2016-10-02 19:00 | 2101 | 957.163 | 453 | 1240 | 1440 | 0
2016-10-02 20:00 | 2101 | 936.662 | 302 | 1240 | 1440 | 0
2016-10-02 21:00 | 2101 | 939.5 | 302 | 1240 | 1440 | 0
2016-10-02 22:00 | 2421 | 880.76 | 302 | 1240 | 1430.7692 | 0
2016-10-02 23:00 | 2421 | 775.827 | 302 | 1240 | 1521.4286 | 0
2016-10-03 | 2421 | 751.83 | 677 | 1240 | 1521.4286 | 0
2016-10-03 01:00 | 2421 | 747.46 | 302 | 1240 | 1521.4286 | 0
2016-10-03 02:00 | 2595 | 721 | 391 | 1240 | 1521.4286 | 0
2016-10-03 03:00 | 2595 | 703.64 | 305 | 1240 | 1521.4286 | 0
2016-10-03 04:00 | 2595 | 695.4 | 302 | 1240 | 1521.4286 | 0
2016-10-03 05:00 | 2595 | 696.92 | 545 | 1240 | 1521.4286 | 0
2016-10-03 06:00 | 3002 | 709.78 | 695 | 1240 | 1521.4286 | 0
2016-10-03 07:00 | 3002 | 715.98 | 497 | 1240 | 1521.4286 | 0
2016-10-03 08:00 | 3002 | 712.652 | 333 | 1240 | 1521.4286 | 0
2016-10-03 09:00 | 3002 | 756.542 | 560 | 1240 | 1521.4286 | 0
2016-10-03 10:00 | 3145 | 832.8 | 595 | 1240 | 1430.7692 | 0
2016-10-03 11:00 | 3145 | 863.94 | 538 | 1240 | 1430.7692 | 0
2016-10-03 12:00 | 3145 | 895.04 | 497 | 1240 | 1440 | 0
2016-10-03 13:00 | 3145 | 923.62 | 473 | 1240 | 1440 | 0
2016-10-03 14:00 | 2424 | 902.348 | 534 | 1240 | 1440 | 0
2016-10-03 15:00 | 2424 | 922.013 | 521 | 1240 | 1238.9381 | 0
2016-10-03 16:00 | 2424 | 932.767 | 394 | 1240 | 1238.9381 | 0
2016-10-03 17:00 | 2424 | 932.52 | 439 | 1240 | 1238.9381 | 0
2016-10-03 18:00 | 2101 | 927.77 | 524 | 1240 | 1238.9381 | 0
2016-10-03 19:00 | 2101 | 923.039 | 453 | 1240 | 1440 | 0
2016-10-03 20:00 | 2101 | 920.474 | 302 | 1240 | 1440 | 0
2016-10-03 21:00 | 2101 | 922.86 | 302 | 1240 | 1430.7692 | 0
2016-10-03 22:00 | 2421 | 811.319 | 302 | 1240 | 1521.4286 | 0
2016-10-03 23:00 | 2421 | 742.007 | 302 | 1240 | 1521.4286 | 0
2016-10-04 | 2421 | 696.58 | 677 | 1240 | 1521.4286 | 0
2016-10-04 01:00 | 2421 | 602.856 | 302 | 1240 | 1521.4286 | 0
2016-10-04 02:00 | 2595 | 588.654 | 391 | 1240 | 1521.4286 | 0
2016-10-04 03:00 | 2595 | 585.018 | 305 | 1240 | 1521.4286 | 0
2016-10-04 04:00 | 2595 | 661.2 | 302 | 1240 | 1521.4286 | 0
2016-10-04 05:00 | 2595 | 705.16 | 545 | 1240 | 1521.4286 | 0
2016-10-04 06:00 | 3002 | 746.928 | 695 | 1240 | 1521.4286 | 0
2016-10-04 07:00 | 3002 | 773.243 | 497 | 1240 | 1521.4286 | 0
2016-10-04 08:00 | 3002 | 775.542 | 333 | 1240 | 1521.4286 | 0
2016-10-04 09:00 | 3002 | 837.54 | 560 | 1240 | 1430.7692 | 0
2016-10-04 10:00 | 3145 | 862.8 | 595 | 1240 | 1430.7692 | 0
2016-10-04 11:00 | 3145 | 883.32 | 538 | 1240 | 1430.7692 | 0
2016-10-04 12:00 | 3145 | 904.26 | 497 | 1240 | 1430.7692 | 0
2016-10-04 13:00 | 3145 | 925.58 | 473 | 1240 | 1440 | 0
2016-10-04 14:00 | 2424 | 895.451 | 534 | 1240 | 1440 | 0
2016-10-04 15:00 | 2424 | 912.133 | 521 | 1240 | 1440 | 0
2016-10-04 16:00 | 2424 | 927.675 | 394 | 1240 | 1440 | 0
2016-10-04 17:00 | 2424 | 972.26 | 439 | 1240 | 1440 | 0
2016-10-04 18:00 | 2101 | 965.1 | 524 | 1240 | 1440 | 0
2016-10-04 19:00 | 2101 | 957.94 | 453 | 1240 | 1430.7692 | 0
2016-10-04 20:00 | 2101 | 951.4 | 302 | 1240 | 1430.7692 | 0
2016-10-04 21:00 | 2101 | 858.952 | 302 | 1240 | 1430.7692 | 0
2016-10-04 22:00 | 2421 | 784.871 | 302 | 1240 | 1521.4286 | 0
2016-10-04 23:00 | 2421 | 755.02 | 302 | 1240 | 1521.4286 | 0
2016-10-05 | 2421 | 643.23 | 677 | 1240 | 1521.4286 | 0
2016-10-05 01:00 | 2421 | 618.822 | 302 | 1240 | 1521.4286 | 0
2016-10-05 02:00 | 2595 | 605.898 | 391 | 1240 | 1521.4286 | 0
2016-10-05 03:00 | 2595 | 600.48 | 305 | 1240 | 1521.4286 | 0
2016-10-05 04:00 | 2595 | 608.382 | 302 | 1240 | 1521.4286 | 0
2016-10-05 05:00 | 2595 | 718.28 | 545 | 1240 | 1521.4286 | 0
2016-10-05 06:00 | 3002 | 760.076 | 695 | 1240 | 1521.4286 | 0
2016-10-05 07:00 | 3002 | 786.429 | 497 | 1240 | 1521.4286 | 0
2016-10-05 08:00 | 3002 | 784.985 | 333 | 1240 | 1521.4286 | 0
2016-10-05 09:00 | 3002 | 846.48 | 560 | 1240 | 1430.7692 | 0
2016-10-05 10:00 | 3145 | 869.9 | 595 | 1240 | 1430.7692 | 0
2016-10-05 11:00 | 3145 | 892.52 | 538 | 1240 | 1440 | 0
2016-10-05 12:00 | 3145 | 907.62 | 497 | 1240 | 1440 | 0
2016-10-05 13:00 | 3145 | 929.98 | 473 | 1240 | 1440 | 0
2016-10-05 14:00 | 2424 | 950.3 | 534 | 1240 | 1440 | 0
2016-10-05 15:00 | 2424 | 970.6 | 521 | 1240 | 1440 | 0
2016-10-05 16:00 | 2424 | 938.885 | 394 | 1240 | 1440 | 0
2016-10-05 17:00 | 2424 | 981.5 | 439 | 1240 | 1440 | 0
2016-10-05 18:00 | 2101 | 972.3 | 524 | 1240 | 1440 | 0
2016-10-05 19:00 | 2101 | 963.12 | 453 | 1240 | 1430.7692 | 0
2016-10-05 20:00 | 2101 | 959.02 | 302 | 1240 | 1430.7692 | 0
2016-10-05 21:00 | 2101 | 859.826 | 302 | 1240 | 1430.7692 | 0
2016-10-05 22:00 | 2421 | 792.604 | 302 | 1240 | 1521.4286 | 0
2016-10-05 23:00 | 2421 | 762.04 | 302 | 1240 | 1673.3333 | 0
2016-10-06 | 2421 | 578.502 | 677 | 1240 | 1673.3333 | 0
2016-10-06 01:00 | 2421 | 557.334 | 302 | 1240 | 1673.3333 | 0
2016-10-06 02:00 | 2595 | 545.166 | 391 | 1240 | 1673.3333 | 0
2016-10-06 03:00 | 2595 | 538.29 | 305 | 1240 | 1673.3333 | 0
2016-10-06 04:00 | 2595 | 544.68 | 302 | 1240 | 1673.3333 | 0
2016-10-06 05:00 | 2595 | 580.5 | 545 | 1240 | 1673.3333 | 0
2016-10-06 06:00 | 3002 | 718.32 | 695 | 1240 | 1673.3333 | 0
2016-10-06 07:00 | 3002 | 744.6 | 497 | 1240 | 1521.4286 | 0
2016-10-06 08:00 | 3002 | 736.48 | 333 | 1240 | 1521.4286 | 0
2016-10-06 09:00 | 3002 | 716.927 | 560 | 1240 | 1521.4286 | 0
2016-10-06 10:00 | 3145 | 738.397 | 595 | 1240 | 1430.7692 | 0
2016-10-06 11:00 | 3145 | 797.22 | 538 | 1240 | 1430.7692 | 0
2016-10-06 12:00 | 3145 | 815.44 | 497 | 1240 | 1430.7692 | 0
2016-10-06 13:00 | 3145 | 837.72 | 473 | 1240 | 1440 | 0
2016-10-06 14:00 | 2424 | 859.3 | 534 | 1240 | 1440 | 0
2016-10-06 15:00 | 2424 | 883.2 | 521 | 1240 | 1440 | 0
2016-10-06 16:00 | 2424 | 860.548 | 394 | 1240 | 1440 | 0
2016-10-06 17:00 | 2424 | 861.251 | 439 | 1240 | 1440 | 0
2016-10-06 18:00 | 2101 | 892.98 | 524 | 1240 | 1440 | 0
2016-10-06 19:00 | 2101 | 879.38 | 453 | 1240 | 1430.7692 | 0
2016-10-06 20:00 | 2101 | 821.484 | 302 | 1240 | 1430.7692 | 0
2016-10-06 21:00 | 2101 | 779.684 | 302 | 1240 | 1521.4286 | 0
2016-10-06 22:00 | 2421 | 750.94 | 302 | 1240 | 1673.3333 | 0
2016-10-06 23:00 | 2421 | 617.238 | 302 | 1240 | 1673.3333 | 0
2016-10-07 | 2421 | 569.52 | 677 | 1240 | 1730 | 0
2016-10-07 01:00 | 2421 | 548.982 | 302 | 1240 | 1673.3333 | 0
2016-10-07 02:00 | 2595 | 536.976 | 391 | 1240 | 1673.3333 | 0
2016-10-07 03:00 | 2595 | 531.882 | 305 | 1240 | 1673.3333 | 0
2016-10-07 04:00 | 2595 | 538.164 | 302 | 1240 | 1673.3333 | 0
2016-10-07 05:00 | 2595 | 570.528 | 545 | 1240 | 1673.3333 | 0
2016-10-07 06:00 | 3002 | 706.28 | 695 | 1240 | 1673.3333 | 0
2016-10-07 07:00 | 3002 | 728.88 | 497 | 1240 | 1521.4286 | 0
2016-10-07 08:00 | 3002 | 692.778 | 333 | 1240 | 1521.4286 | 0
2016-10-07 09:00 | 3002 | 713.165 | 560 | 1240 | 1521.4286 | 0
2016-10-07 10:00 | 3145 | 775.94 | 595 | 1240 | 1430.7692 | 0
2016-10-07 11:00 | 3145 | 801.52 | 538 | 1240 | 1430.7692 | 0
2016-10-07 12:00 | 3145 | 825.4 | 497 | 1240 | 1440 | 0
2016-10-07 13:00 | 3145 | 856.62 | 473 | 1240 | 1440 | 0
2016-10-07 14:00 | 2424 | 843.581 | 534 | 1240 | 1238.9381 | 0
2016-10-07 15:00 | 2424 | 871.644 | 521 | 1240 | 1238.9381 | 0
2016-10-07 16:00 | 2424 | 893.418 | 394 | 1240 | 1238.9381 | 0
2016-10-07 17:00 | 2424 | 890.15 | 439 | 1240 | 1238.9381 | 0
2016-10-07 18:00 | 2101 | 870.257 | 524 | 1240 | 1440 | 0
2016-10-07 19:00 | 2101 | 895.1 | 453 | 1240 | 1440 | 0
2016-10-07 20:00 | 2101 | 876.98 | 302 | 1240 | 1430.7692 | 0
2016-10-07 21:00 | 2101 | 784.301 | 302 | 1240 | 1521.4286 | 0
2016-10-07 22:00 | 2421 | 761.8 | 302 | 1240 | 1673.3333 | 0
2016-10-07 23:00 | 2421 | 624.132 | 302 | 1240 | 1673.3333 | 0
2016-10-08 | 2421 | 621.396 | 677 | 1240 | 1673.3333 | 0
2016-10-08 01:00 | 2421 | 597.168 | 302 | 1240 | 1673.3333 | 0
2016-10-08 02:00 | 2595 | 583.308 | 391 | 1240 | 1673.3333 | 0
2016-10-08 03:00 | 2595 | 575.55 | 305 | 1240 | 1673.3333 | 0
2016-10-08 04:00 | 2595 | 581.688 | 302 | 1240 | 1673.3333 | 0
2016-10-08 05:00 | 2595 | 613.404 | 545 | 1240 | 1673.3333 | 0
2016-10-08 06:00 | 3002 | 755.34 | 695 | 1240 | 1673.3333 | 0
2016-10-08 07:00 | 3002 | 744.743 | 497 | 1240 | 1521.4286 | 0
2016-10-08 08:00 | 3002 | 744.477 | 333 | 1240 | 1521.4286 | 0
2016-10-08 09:00 | 3002 | 769.025 | 560 | 1240 | 1430.7692 | 0
2016-10-08 10:00 | 3145 | 843.16 | 595 | 1240 | 1440 | 0
2016-10-08 11:00 | 3145 | 873.92 | 538 | 1240 | 1440 | 0
2016-10-08 12:00 | 3145 | 857.451 | 497 | 1240 | 1440 | 0
2016-10-08 13:00 | 3145 | 888.288 | 473 | 1240 | 1238.9381 | 0
2016-10-08 14:00 | 2424 | 921.025 | 534 | 1240 | 1296.2963 | 0
2016-10-08 15:00 | 2424 | 1048.425 | 521 | 1240 | 1296.2963 | 0
2016-10-08 16:00 | 2424 | 1070.097 | 394 | 1240 | 1296.2963 | 0
2016-10-08 17:00 | 2424 | 1059.912 | 439 | 1240 | 1296.2963 | 0
2016-10-08 18:00 | 2101 | 925.053 | 524 | 1240 | 1238.9381 | 0
2016-10-08 19:00 | 2101 | 938.06 | 453 | 1240 | 1440 | 0
2016-10-08 20:00 | 2101 | 909.14 | 302 | 1240 | 1430.7692 | 0
2016-10-08 21:00 | 2101 | 818.026 | 302 | 1240 | 1521.4286 | 0
2016-10-08 22:00 | 2421 | 808.3 | 302 | 1240 | 1673.3333 | 0
2016-10-08 23:00 | 2421 | 675.864 | 302 | 1240 | 1673.3333 | 0
2016-10-09 | 2421 | 661.842 | 677 | 1240 | 1673.3333 | 0
2016-10-09 01:00 | 2421 | 632.538 | 302 | 1240 | 1673.3333 | 0
2016-10-09 02:00 | 2595 | 616.104 | 391 | 1240 | 1673.3333 | 0
2016-10-09 03:00 | 2595 | 602.136 | 305 | 1240 | 1673.3333 | 0
2016-10-09 04:00 | 2595 | 598.212 | 302 | 1240 | 1673.3333 | 0
2016-10-09 05:00 | 2595 | 606.762 | 545 | 1240 | 1673.3333 | 0
2016-10-09 06:00 | 3002 | 629.964 | 695 | 1240 | 1673.3333 | 0
2016-10-09 07:00 | 3002 | 719.66 | 497 | 1240 | 1673.3333 | 0
2016-10-09 08:00 | 3002 | 751.38 | 333 | 1240 | 1521.4286 | 0
2016-10-09 09:00 | 3002 | 755.478 | 560 | 1240 | 1430.7692 | 0
2016-10-09 10:00 | 3145 | 837.78 | 595 | 1240 | 1440 | 0
2016-10-09 11:00 | 3145 | 875.28 | 538 | 1240 | 1440 | 0
2016-10-09 12:00 | 3145 | 864.747 | 497 | 1240 | 1238.9381 | 0
2016-10-09 13:00 | 3145 | 902.329 | 473 | 1240 | 1238.9381 | 0
2016-10-09 14:00 | 2424 | 1037.757 | 534 | 1240 | 1296.2963 | 0
2016-10-09 15:00 | 2424 | 1077.174 | 521 | 1240 | 1296.2963 | 0
2016-10-09 16:00 | 2424 | 1100.001 | 394 | 1240 | 1296.2963 | 0
2016-10-09 17:00 | 2424 | 1094.541 | 439 | 1240 | 1296.2963 | 0
2016-10-09 18:00 | 2101 | 1065.666 | 524 | 1240 | 1296.2963 | 0
2016-10-09 19:00 | 2101 | 938.068 | 453 | 1240 | 1238.9381 | 0
2016-10-09 20:00 | 2101 | 961.08 | 302 | 1240 | 1440 | 0
2016-10-09 21:00 | 2101 | 914.2 | 302 | 1240 | 1430.7692 | 0
2016-10-09 22:00 | 2421 | 817.684 | 302 | 1240 | 1521.4286 | 0
2016-10-09 23:00 | 2421 | 803.36 | 302 | 1240 | 1673.3333 | 0
2016-10-10 | 2421 | 758.76 | 677 | 1240 | 1673.3333 | 0
2016-10-10 01:00 | 2421 | 719.6 | 302 | 1240 | 1673.3333 | 0
2016-10-10 02:00 | 2595 | 626.76 | 391 | 1240 | 1673.3333 | 0
2016-10-10 03:00 | 2595 | 614.232 | 305 | 1240 | 1673.3333 | 0
2016-10-10 04:00 | 2595 | 607.986 | 302 | 1240 | 1673.3333 | 0
2016-10-10 05:00 | 2595 | 610.038 | 545 | 1240 | 1673.3333 | 0
2016-10-10 06:00 | 3002 | 692.02 | 695 | 1240 | 1673.3333 | 0
2016-10-10 07:00 | 3002 | 703.1 | 497 | 1240 | 1673.3333 | 0
2016-10-10 08:00 | 3002 | 740.08 | 333 | 1240 | 1673.3333 | 0
2016-10-10 09:00 | 3002 | 751.222 | 560 | 1240 | 1521.4286 | 0
2016-10-10 10:00 | 3145 | 798.513 | 595 | 1240 | 1521.4286 | 0
2016-10-10 11:00 | 3145 | 889.04 | 538 | 1240 | 1430.7692 | 0
2016-10-10 12:00 | 3145 | 939.34 | 497 | 1240 | 1440 | 0
2016-10-10 13:00 | 3145 | 937.802 | 473 | 1240 | 1440 | 0
2016-10-10 14:00 | 2424 | 976.372 | 534 | 1240 | 1238.9381 | 0
2016-10-10 15:00 | 2424 | 1006.791 | 521 | 1240 | 1238.9381 | 0
2016-10-10 16:00 | 2424 | 1132.467 | 394 | 1240 | 1238.9381 | 0
2016-10-10 17:00 | 2424 | 1022.086 | 439 | 1240 | 1238.9381 | 0
2016-10-10 18:00 | 2101 | 1007.969 | 524 | 1240 | 1238.9381 | 0
2016-10-10 19:00 | 2101 | 993.852 | 453 | 1240 | 1238.9381 | 0
2016-10-10 20:00 | 2101 | 973.104 | 302 | 1240 | 1238.9381 | 0
2016-10-10 21:00 | 2101 | 926.212 | 302 | 1240 | 1440 | 0
2016-10-10 22:00 | 2421 | 908.6 | 302 | 1240 | 1440 | 0
2016-10-10 23:00 | 2421 | 793.402 | 302 | 1240 | 1430.7692 | 0
2016-10-11 | 2421 | 712.22 | 677 | 1240 | 1430.7692 | 0
2016-10-11 01:00 | 2421 | 682.54 | 302 | 1240 | 1521.4286 | 0
2016-10-11 02:00 | 2595 | 664.96 | 391 | 1240 | 1521.4286 | 0
2016-10-11 03:00 | 2595 | 655.8 | 305 | 1240 | 1521.4286 | 0
2016-10-11 04:00 | 2595 | 663.08 | 302 | 1240 | 1521.4286 | 0
2016-10-11 05:00 | 2595 | 696.9 | 545 | 1240 | 1521.4286 | 0
2016-10-11 06:00 | 3002 | 718.827 | 695 | 1240 | 1521.4286 | 0
2016-10-11 07:00 | 3002 | 745.085 | 497 | 1240 | 1430.7692 | 0
2016-10-11 08:00 | 3002 | 762.128 | 333 | 1240 | 1430.7692 | 0
2016-10-11 09:00 | 3002 | 845.02 | 560 | 1240 | 1440 | 0
2016-10-11 10:00 | 3145 | 847.02 | 595 | 1240 | 1440 | 0
2016-10-11 11:00 | 3145 | 887.661 | 538 | 1240 | 1238.9381 | 0
2016-10-11 12:00 | 3145 | 1021.629 | 497 | 1240 | 1296.2963 | 0
2016-10-11 13:00 | 3145 | 1063.713 | 473 | 1240 | 1296.2963 | 0
2016-10-11 14:00 | 2424 | 1099.728 | 534 | 1240 | 1000 | 0
2016-10-11 15:00 | 2424 | 1127.133 | 521 | 1240 | 1000 | 0
2016-10-11 16:00 | 2424 | 1196.778 | 394 | 1240 | 1000 | 0
2016-10-11 17:00 | 2424 | 1123.878 | 439 | 1240 | 1000 | 0
2016-10-11 18:00 | 2101 | 1103.487 | 524 | 1240 | 1000 | 0
2016-10-11 19:00 | 2101 | 1083.096 | 453 | 1240 | 1296.2963 | 0
2016-10-11 20:00 | 2101 | 1057.035 | 302 | 1240 | 1238.9381 | 0
2016-10-11 21:00 | 2101 | 902.633 | 302 | 1240 | 1238.9381 | 0
2016-10-11 22:00 | 2421 | 874.06 | 302 | 1240 | 1440 | 0
2016-10-11 23:00 | 2421 | 794.38 | 302 | 1240 | 1430.7692 | 0
2016-10-12 | 2421 | 695.875 | 677 | 1240 | 1430.7692 | 0
2016-10-12 01:00 | 2421 | 662.625 | 302 | 1240 | 1430.7692 | 0
2016-10-12 02:00 | 2595 | 674.66 | 391 | 1240 | 1430.7692 | 0
2016-10-12 03:00 | 2595 | 662.44 | 305 | 1240 | 1430.7692 | 0
2016-10-12 04:00 | 2595 | 666.18 | 302 | 1240 | 1430.7692 | 0
2016-10-12 05:00 | 2595 | 665.057 | 545 | 1240 | 1430.7692 | 0
2016-10-12 06:00 | 3002 | 734.141 | 695 | 1240 | 1430.7692 | 0
2016-10-12 07:00 | 3002 | 798.42 | 497 | 1240 | 1430.7692 | 0
2016-10-12 08:00 | 3002 | 758.613 | 333 | 1240 | 1430.7692 | 0
2016-10-12 09:00 | 3002 | 833.54 | 560 | 1240 | 1440 | 0
2016-10-12 10:00 | 3145 | 832.922 | 595 | 1240 | 1440 | 0
2016-10-12 11:00 | 3145 | 871.72 | 538 | 1240 | 1238.9381 | 0
2016-10-12 12:00 | 3145 | 907.706 | 497 | 1240 | 1238.9381 | 0
2016-10-12 13:00 | 3145 | 1048.11 | 473 | 1240 | 1296.2963 | 0
2016-10-12 14:00 | 2424 | 1082.424 | 534 | 1240 | 1296.2963 | 0
2016-10-12 15:00 | 2424 | 1108.611 | 521 | 1240 | 1296.2963 | 0
2016-10-12 16:00 | 2424 | 1121.463 | 394 | 1240 | 1296.2963 | 0
2016-10-12 17:00 | 2424 | 1103.487 | 439 | 1240 | 1296.2963 | 0
2016-10-12 18:00 | 2101 | 1076.817 | 524 | 1240 | 1296.2963 | 0
2016-10-12 19:00 | 2101 | 950.133 | 453 | 1240 | 1238.9381 | 0
2016-10-12 20:00 | 2101 | 924.692 | 302 | 1240 | 1238.9381 | 0
2016-10-12 21:00 | 2101 | 914.9 | 302 | 1240 | 1440 | 0
2016-10-12 22:00 | 2421 | 795.492 | 302 | 1240 | 1430.7692 | 0
2016-10-12 23:00 | 2421 | 722.399 | 302 | 1240 | 1521.4286 | 0
2016-10-13 | 2421 | 679.54 | 677 | 1240 | 1521.4286 | 0
2016-10-13 01:00 | 2421 | 643.62 | 302 | 1240 | 1521.4286 | 0
2016-10-13 02:00 | 2595 | 561.294 | 391 | 1240 | 1521.4286 | 0
2016-10-13 03:00 | 2595 | 553.302 | 305 | 1240 | 1521.4286 | 0
2016-10-13 04:00 | 2595 | 557.622 | 302 | 1240 | 1521.4286 | 0
2016-10-13 05:00 | 2595 | 652.08 | 545 | 1240 | 1521.4286 | 0
2016-10-13 06:00 | 3002 | 724.72 | 695 | 1240 | 1521.4286 | 0
2016-10-13 07:00 | 3002 | 713.906 | 497 | 1240 | 1521.4286 | 0
2016-10-13 08:00 | 3002 | 714.21 | 333 | 1240 | 1521.4286 | 0
2016-10-13 09:00 | 3002 | 738.435 | 560 | 1240 | 1521.4286 | 0
2016-10-13 10:00 | 3145 | 813.62 | 595 | 1240 | 1430.7692 | 0
2016-10-13 11:00 | 3145 | 845.62 | 538 | 1240 | 1440 | 0
2016-10-13 12:00 | 3145 | 875.3 | 497 | 1240 | 1440 | 0
2016-10-13 13:00 | 3145 | 909.52 | 473 | 1240 | 1440 | 0
2016-10-13 14:00 | 2424 | 935.32 | 534 | 1240 | 1440 | 0
2016-10-13 15:00 | 2424 | 953.92 | 521 | 1240 | 1440 | 0
2016-10-13 16:00 | 2424 | 915.477 | 394 | 1240 | 1440 | 0
2016-10-13 17:00 | 2424 | 947.74 | 439 | 1240 | 1440 | 0
2016-10-13 18:00 | 2101 | 930.38 | 524 | 1240 | 1440 | 0
2016-10-13 19:00 | 2101 | 913.02 | 453 | 1240 | 1440 | 0
2016-10-13 20:00 | 2101 | 894.06 | 302 | 1240 | 1440 | 0
2016-10-13 21:00 | 2101 | 804.479 | 302 | 1240 | 1430.7692 | 0
2016-10-13 22:00 | 2421 | 738.663 | 302 | 1240 | 1430.7692 | 0
2016-10-13 23:00 | 2421 | 707.36 | 302 | 1240 | 1521.4286 | 0
2016-10-14 | 2421 | 680.04 | 677 | 1240 | 1521.4286 | 0
2016-10-14 01:00 | 2421 | 649.62 | 302 | 1240 | 1521.4286 | 0
2016-10-14 02:00 | 2595 | 567.468 | 391 | 1240 | 1521.4286 | 0
2016-10-14 03:00 | 2595 | 559.962 | 305 | 1240 | 1521.4286 | 0
2016-10-14 04:00 | 2595 | 626.98 | 302 | 1240 | 1521.4286 | 0
2016-10-14 05:00 | 2595 | 661.92 | 545 | 1240 | 1521.4286 | 0
2016-10-14 06:00 | 3002 | 697.338 | 695 | 1240 | 1521.4286 | 0
2016-10-14 07:00 | 3002 | 721.297 | 497 | 1240 | 1430.7692 | 0
2016-10-14 08:00 | 3002 | 716.813 | 333 | 1240 | 1430.7692 | 0
2016-10-14 09:00 | 3002 | 735.68 | 560 | 1240 | 1430.7692 | 0
2016-10-14 10:00 | 3145 | 801.1 | 595 | 1240 | 1430.7692 | 0
2016-10-14 11:00 | 3145 | 822.06 | 538 | 1240 | 1440 | 0
2016-10-14 12:00 | 3145 | 842.58 | 497 | 1240 | 1440 | 0
2016-10-14 13:00 | 3145 | 867.4 | 473 | 1240 | 1440 | 0
2016-10-14 14:00 | 2424 | 845.082 | 534 | 1240 | 1440 | 0
2016-10-14 15:00 | 2424 | 864.272 | 521 | 1240 | 1440 | 0
2016-10-14 16:00 | 2424 | 876.755 | 394 | 1240 | 1238.9381 | 0
2016-10-14 17:00 | 2424 | 867.103 | 439 | 1240 | 1238.9381 | 0
2016-10-14 18:00 | 2101 | 855.836 | 524 | 1240 | 1440 | 0
2016-10-14 19:00 | 2101 | 844.569 | 453 | 1240 | 1440 | 0
2016-10-14 20:00 | 2101 | 871.52 | 302 | 1240 | 1440 | 0
2016-10-14 21:00 | 2101 | 779.684 | 302 | 1240 | 1430.7692 | 0
2016-10-14 22:00 | 2421 | 754.98 | 302 | 1240 | 1673.3333 | 0
2016-10-14 23:00 | 2421 | 624.096 | 302 | 1240 | 1673.3333 | 0
2016-10-15 | 2421 | 623.358 | 677 | 1240 | 1730 | 0
2016-10-15 01:00 | 2421 | 622.71 | 302 | 1240 | 1730 | 0
2016-10-15 02:00 | 2595 | 606.618 | 391 | 1240 | 1730 | 0
2016-10-15 03:00 | 2595 | 601.776 | 305 | 1240 | 1730 | 0
2016-10-15 04:00 | 2595 | 608.382 | 302 | 1240 | 1730 | 0
2016-10-15 05:00 | 2595 | 717 | 545 | 1240 | 1673.3333 | 0
2016-10-15 06:00 | 3002 | 757.34 | 695 | 1240 | 1521.4286 | 0
2016-10-15 07:00 | 3002 | 786.068 | 497 | 1240 | 1521.4286 | 0
2016-10-15 08:00 | 3002 | 783.161 | 333 | 1240 | 1521.4286 | 0
2016-10-15 09:00 | 3002 | 843.78 | 560 | 1240 | 1430.7692 | 0
2016-10-15 10:00 | 3145 | 869.44 | 595 | 1240 | 1440 | 0
2016-10-15 11:00 | 3145 | 850.212 | 538 | 1240 | 1440 | 0
2016-10-15 12:00 | 3145 | 872.328 | 497 | 1240 | 1238.9381 | 0
2016-10-15 13:00 | 3145 | 903.412 | 473 | 1240 | 1238.9381 | 0
2016-10-15 14:00 | 2424 | 936.225 | 534 | 1240 | 1296.2963 | 0
2016-10-15 15:00 | 2424 | 1067.598 | 521 | 1240 | 1296.2963 | 0
2016-10-15 16:00 | 2424 | 1093.428 | 394 | 1240 | 1296.2963 | 0
2016-10-15 17:00 | 2424 | 1085.574 | 439 | 1240 | 1296.2963 | 0
2016-10-15 18:00 | 2101 | 1055.46 | 524 | 1240 | 1296.2963 | 0
2016-10-15 19:00 | 2101 | 927.694 | 453 | 1240 | 1238.9381 | 0
2016-10-15 20:00 | 2101 | 943.12 | 302 | 1240 | 1430.7692 | 0
2016-10-15 21:00 | 2101 | 852.796 | 302 | 1240 | 1521.4286 | 0
2016-10-15 22:00 | 2421 | 841.34 | 302 | 1240 | 1673.3333 | 0
2016-10-15 23:00 | 2421 | 783.26 | 302 | 1240 | 1673.3333 | 0
2016-10-16 | 2421 | 670.104 | 677 | 1240 | 1673.3333 | 0
2016-10-16 01:00 | 2421 | 639.072 | 302 | 1240 | 1730 | 0
2016-10-16 02:00 | 2595 | 617.004 | 391 | 1240 | 1730 | 0
2016-10-16 03:00 | 2595 | 605.196 | 305 | 1240 | 1730 | 0
2016-10-16 04:00 | 2595 | 602.802 | 302 | 1240 | 1730 | 0
2016-10-16 05:00 | 2595 | 612.666 | 545 | 1240 | 1730 | 0
2016-10-16 06:00 | 3002 | 706.64 | 695 | 1240 | 1673.3333 | 0
2016-10-16 07:00 | 3002 | 728.08 | 497 | 1240 | 1673.3333 | 0
2016-10-16 08:00 | 3002 | 720.974 | 333 | 1240 | 1521.4286 | 0
2016-10-16 09:00 | 3002 | 759.145 | 560 | 1240 | 1521.4286 | 0
2016-10-16 10:00 | 3145 | 833.18 | 595 | 1240 | 1430.7692 | 0
2016-10-16 11:00 | 3145 | 866.42 | 538 | 1240 | 1430.7692 | 0
2016-10-16 12:00 | 3145 | 894.56 | 497 | 1240 | 1440 | 0
2016-10-16 13:00 | 3145 | 922.6 | 473 | 1240 | 1440 | 0
2016-10-16 14:00 | 2424 | 906.794 | 534 | 1240 | 1238.9381 | 0
2016-10-16 15:00 | 2424 | 939.056 | 521 | 1240 | 1238.9381 | 0
2016-10-16 16:00 | 2424 | 959.804 | 394 | 1240 | 1238.9381 | 0
2016-10-16 17:00 | 2424 | 955.149 | 439 | 1240 | 1238.9381 | 0
2016-10-16 18:00 | 2101 | 937.688 | 524 | 1240 | 1238.9381 | 0
2016-10-16 19:00 | 2101 | 968.64 | 453 | 1240 | 1440 | 0
2016-10-16 20:00 | 2101 | 941.56 | 302 | 1240 | 1430.7692 | 0
2016-10-16 21:00 | 2101 | 853.613 | 302 | 1240 | 1521.4286 | 0
2016-10-16 22:00 | 2421 | 845.08 | 302 | 1240 | 1673.3333 | 0
2016-10-16 23:00 | 2421 | 789.38 | 302 | 1240 | 1673.3333 | 0
2016-10-17 | 2421 | 644.832 | 677 | 1240 | 1730 | 0
2016-10-17 01:00 | 2421 | 616.662 | 302 | 1240 | 1730 | 0
2016-10-17 02:00 | 2595 | 597.114 | 391 | 1240 | 1730 | 0
2016-10-17 03:00 | 2595 | 587.808 | 305 | 1240 | 1730 | 0
2016-10-17 04:00 | 2595 | 583.02 | 302 | 1240 | 1730 | 0
2016-10-17 05:00 | 2595 | 586.278 | 545 | 1240 | 1730 | 0
2016-10-17 06:00 | 3002 | 601.002 | 695 | 1240 | 1730 | 0
2016-10-17 07:00 | 3002 | 680.7 | 497 | 1240 | 1730 | 0
2016-10-17 08:00 | 3002 | 708.9 | 333 | 1240 | 1673.3333 | 0
2016-10-17 09:00 | 3002 | 715.198 | 560 | 1240 | 1521.4286 | 0
2016-10-17 10:00 | 3145 | 751.374 | 595 | 1240 | 1430.7692 | 0
2016-10-17 11:00 | 3145 | 831.08 | 538 | 1240 | 1430.7692 | 0
2016-10-17 12:00 | 3145 | 870.26 | 497 | 1240 | 1440 | 0
2016-10-17 13:00 | 3145 | 903.48 | 473 | 1240 | 1440 | 0
2016-10-17 14:00 | 2424 | 887.756 | 534 | 1240 | 1440 | 0
2016-10-17 15:00 | 2424 | 908.542 | 521 | 1240 | 1440 | 0
2016-10-17 16:00 | 2424 | 921.405 | 394 | 1240 | 1440 | 0
2016-10-17 17:00 | 2424 | 917.928 | 439 | 1240 | 1440 | 0
2016-10-17 18:00 | 2101 | 926.915 | 524 | 1240 | 1440 | 0
2016-10-17 19:00 | 2101 | 985.14 | 453 | 1240 | 1440 | 0
2016-10-17 20:00 | 2101 | 965.6 | 302 | 1240 | 1430.7692 | 0
2016-10-17 21:00 | 2101 | 876.508 | 302 | 1240 | 1521.4286 | 0
2016-10-17 22:00 | 2421 | 853.58 | 302 | 1240 | 1673.3333 | 0
2016-10-17 23:00 | 2421 | 785.66 | 302 | 1240 | 1730 | 0
2016-10-18 | 2421 | 584.208 | 677 | 1240 | 1730 | 0
2016-10-18 01:00 | 2421 | 559.926 | 302 | 1240 | 1730 | 0
2016-10-18 02:00 | 2595 | 545.796 | 391 | 1240 | 1730 | 0
2016-10-18 03:00 | 2595 | 541.926 | 305 | 1240 | 1730 | 0
2016-10-18 04:00 | 2595 | 551.7 | 302 | 1240 | 1730 | 0
2016-10-18 05:00 | 2595 | 586.242 | 545 | 1240 | 1730 | 0
2016-10-18 06:00 | 3002 | 724.42 | 695 | 1240 | 1673.3333 | 0
2016-10-18 07:00 | 3002 | 754.36 | 497 | 1240 | 1673.3333 | 0
2016-10-18 08:00 | 3002 | 754.1 | 333 | 1240 | 1673.3333 | 0
2016-10-18 09:00 | 3002 | 743.983 | 560 | 1240 | 1521.4286 | 0
2016-10-18 10:00 | 3145 | 784.225 | 595 | 1240 | 1521.4286 | 0
2016-10-18 11:00 | 3145 | 863.04 | 538 | 1240 | 1430.7692 | 0
2016-10-18 12:00 | 3145 | 895.88 | 497 | 1240 | 1440 | 0
2016-10-18 13:00 | 3145 | 887.623 | 473 | 1240 | 1440 | 0
2016-10-18 14:00 | 2424 | 918.802 | 534 | 1240 | 1238.9381 | 0
2016-10-18 15:00 | 2424 | 939.759 | 521 | 1240 | 1238.9381 | 0
2016-10-18 16:00 | 2424 | 951.273 | 394 | 1240 | 1238.9381 | 0
2016-10-18 17:00 | 2424 | 935.066 | 439 | 1240 | 1238.9381 | 0
2016-10-18 18:00 | 2101 | 921.538 | 524 | 1240 | 1238.9381 | 0
2016-10-18 19:00 | 2101 | 908.029 | 453 | 1240 | 1440 | 0
2016-10-18 20:00 | 2101 | 929.14 | 302 | 1240 | 1430.7692 | 0
2016-10-18 21:00 | 2101 | 835.24 | 302 | 1240 | 1430.7692 | 0
2016-10-18 22:00 | 2421 | 769.12 | 302 | 1240 | 1521.4286 | 0
2016-10-18 23:00 | 2421 | 737.4 | 302 | 1240 | 1521.4286 | 0
2016-10-19 | 2421 | 595.944 | 677 | 1240 | 1521.4286 | 0
2016-10-19 01:00 | 2421 | 566.64 | 302 | 1240 | 1521.4286 | 0
2016-10-19 02:00 | 2595 | 612.32 | 391 | 1240 | 1521.4286 | 0
2016-10-19 03:00 | 2595 | 541.926 | 305 | 1240 | 1521.4286 | 0
2016-10-19 04:00 | 2595 | 607.94 | 302 | 1240 | 1521.4286 | 0
2016-10-19 05:00 | 2595 | 641.64 | 545 | 1240 | 1521.4286 | 0
2016-10-19 06:00 | 3002 | 678.11 | 695 | 1240 | 1521.4286 | 0
2016-10-19 07:00 | 3002 | 708.149 | 497 | 1240 | 1521.4286 | 0
2016-10-19 08:00 | 3002 | 707.446 | 333 | 1240 | 1521.4286 | 0
2016-10-19 09:00 | 3002 | 734.141 | 560 | 1240 | 1430.7692 | 0
2016-10-19 10:00 | 3145 | 812.5 | 595 | 1240 | 1430.7692 | 0
2016-10-19 11:00 | 3145 | 849.52 | 538 | 1240 | 1440 | 0
2016-10-19 12:00 | 3145 | 845.215 | 497 | 1240 | 1238.9381 | 0
2016-10-19 13:00 | 3145 | 879.833 | 473 | 1240 | 1238.9381 | 0
2016-10-19 14:00 | 2424 | 910.879 | 534 | 1240 | 1238.9381 | 0
2016-10-19 15:00 | 2424 | 1033.263 | 521 | 1240 | 1238.9381 | 0
2016-10-19 16:00 | 2424 | 1047.291 | 394 | 1240 | 1238.9381 | 0
2016-10-19 17:00 | 2424 | 935.085 | 439 | 1240 | 1238.9381 | 0
2016-10-19 18:00 | 2101 | 917.624 | 524 | 1240 | 1238.9381 | 0
2016-10-19 19:00 | 2101 | 900.144 | 453 | 1240 | 1440 | 0
2016-10-19 20:00 | 2101 | 919.2 | 302 | 1240 | 1440 | 0
2016-10-19 21:00 | 2101 | 872.06 | 302 | 1240 | 1430.7692 | 0
2016-10-19 22:00 | 2421 | 802 | 302 | 1240 | 1430.7692 | 0
2016-10-19 23:00 | 2421 | 694.07 | 302 | 1240 | 1521.4286 | 0
2016-10-20 | 2421 | 640.04 | 677 | 1240 | 1521.4286 | 0
2016-10-20 01:00 | 2421 | 609.22 | 302 | 1240 | 1521.4286 | 0
2016-10-20 02:00 | 2595 | 529.164 | 391 | 1240 | 1521.4286 | 0
2016-10-20 03:00 | 2595 | 520.146 | 305 | 1240 | 1521.4286 | 0
2016-10-20 04:00 | 2595 | 523.422 | 302 | 1240 | 1521.4286 | 0
2016-10-20 05:00 | 2595 | 612.18 | 545 | 1240 | 1521.4286 | 0
2016-10-20 06:00 | 3002 | 645.278 | 695 | 1240 | 1521.4286 | 0
2016-10-20 07:00 | 3002 | 673.417 | 497 | 1240 | 1521.4286 | 0
2016-10-20 08:00 | 3002 | 670.263 | 333 | 1240 | 1521.4286 | 0
2016-10-20 09:00 | 3002 | 699.2 | 560 | 1240 | 1521.4286 | 0
2016-10-20 10:00 | 3145 | 772.16 | 595 | 1240 | 1430.7692 | 0
2016-10-20 11:00 | 3145 | 808.88 | 538 | 1240 | 1430.7692 | 0
2016-10-20 12:00 | 3145 | 845.18 | 497 | 1240 | 1440 | 0
2016-10-20 13:00 | 3145 | 840.123 | 473 | 1240 | 1440 | 0
2016-10-20 14:00 | 2424 | 867.35 | 534 | 1240 | 1238.9381 | 0
2016-10-20 15:00 | 2424 | 894.178 | 521 | 1240 | 1238.9381 | 0
2016-10-20 16:00 | 2424 | 905.521 | 394 | 1240 | 1238.9381 | 0
2016-10-20 17:00 | 2424 | 896.173 | 439 | 1240 | 1440 | 0
2016-10-20 18:00 | 2101 | 921.5 | 524 | 1240 | 1440 | 0
2016-10-20 19:00 | 2101 | 899.66 | 453 | 1240 | 1430.7692 | 0
2016-10-20 20:00 | 2101 | 828.742 | 302 | 1240 | 1430.7692 | 0
2016-10-20 21:00 | 2101 | 782.572 | 302 | 1240 | 1521.4286 | 0
2016-10-20 22:00 | 2421 | 758.78 | 302 | 1240 | 1673.3333 | 0
2016-10-20 23:00 | 2421 | 688.78 | 302 | 1240 | 1673.3333 | 0
2016-10-21 | 2421 | 592.812 | 677 | 1240 | 1673.3333 | 0
2016-10-21 01:00 | 2421 | 565.326 | 302 | 1240 | 1673.3333 | 0
2016-10-21 02:00 | 2595 | 546.588 | 391 | 1240 | 1673.3333 | 0
2016-10-21 03:00 | 2595 | 536.616 | 305 | 1240 | 1673.3333 | 0
2016-10-21 04:00 | 2595 | 539.73 | 302 | 1240 | 1730 | 0
2016-10-21 05:00 | 2595 | 632.66 | 545 | 1240 | 1730 | 0
2016-10-21 06:00 | 3002 | 700.48 | 695 | 1240 | 1673.3333 | 0
2016-10-21 07:00 | 3002 | 692.398 | 497 | 1240 | 1521.4286 | 0
2016-10-21 08:00 | 3002 | 728.14 | 333 | 1240 | 1521.4286 | 0
2016-10-21 09:00 | 3002 | 756.1 | 560 | 1240 | 1521.4286 | 0
2016-10-21 10:00 | 3145 | 754.87 | 595 | 1240 | 1430.7692 | 0
2016-10-21 11:00 | 3145 | 795.283 | 538 | 1240 | 1430.7692 | 0
2016-10-21 12:00 | 3145 | 829.141 | 497 | 1240 | 1430.7692 | 0
2016-10-21 13:00 | 3145 | 910.32 | 473 | 1240 | 1430.7692 | 0
2016-10-21 14:00 | 2424 | 942.22 | 534 | 1240 | 1430.7692 | 0
2016-10-21 15:00 | 2424 | 963.6 | 521 | 1240 | 1430.7692 | 0
2016-10-21 16:00 | 2424 | 971.6 | 394 | 1240 | 1430.7692 | 0
2016-10-21 17:00 | 2424 | 953.78 | 439 | 1240 | 1430.7692 | 0
2016-10-21 18:00 | 2101 | 890.986 | 524 | 1240 | 1430.7692 | 0
2016-10-21 19:00 | 2101 | 875.881 | 453 | 1240 | 1521.4286 | 0
2016-10-21 20:00 | 2101 | 899.34 | 302 | 1240 | 1521.4286 | 0
2016-10-21 21:00 | 2101 | 855.54 | 302 | 1240 | 1673.3333 | 0
2016-10-21 22:00 | 2421 | 794.92 | 302 | 1240 | 1673.3333 | 0
2016-10-21 23:00 | 2421 | 654.552 | 302 | 1240 | 1673.3333 | 0
2016-10-22 | 2421 | 636.822 | 677 | 1240 | 1673.3333 | 0
2016-10-22 01:00 | 2421 | 624.186 | 302 | 1240 | 1730 | 0
2016-10-22 02:00 | 2595 | 604.458 | 391 | 1240 | 1730 | 0
2016-10-22 03:00 | 2595 | 592.902 | 305 | 1240 | 1730 | 0
2016-10-22 04:00 | 2595 | 597.51 | 302 | 1240 | 1673.3333 | 0
2016-10-22 05:00 | 2595 | 699.22 | 545 | 1240 | 1673.3333 | 0
2016-10-22 06:00 | 3002 | 737.618 | 695 | 1240 | 1521.4286 | 0
2016-10-22 07:00 | 3002 | 772.635 | 497 | 1240 | 1521.4286 | 0
2016-10-22 08:00 | 3002 | 772.027 | 333 | 1240 | 1521.4286 | 0
2016-10-22 09:00 | 3002 | 796.499 | 560 | 1240 | 1521.4286 | 0
2016-10-22 10:00 | 3145 | 831.364 | 595 | 1240 | 1430.7692 | 0
2016-10-22 11:00 | 3145 | 858.363 | 538 | 1240 | 1430.7692 | 0
2016-10-22 12:00 | 3145 | 879.871 | 497 | 1240 | 1430.7692 | 0
2016-10-22 13:00 | 3145 | 905.787 | 473 | 1240 | 1430.7692 | 0
2016-10-22 14:00 | 2424 | 972.38 | 534 | 1240 | 1430.7692 | 0
2016-10-22 15:00 | 2424 | 980.04 | 521 | 1240 | 1440 | 0
2016-10-22 16:00 | 2424 | 979.68 | 394 | 1240 | 1440 | 0
2016-10-22 17:00 | 2424 | 959.92 | 439 | 1240 | 1440 | 0
2016-10-22 18:00 | 2101 | 949.68 | 524 | 1240 | 1440 | 0
2016-10-22 19:00 | 2101 | 892.468 | 453 | 1240 | 1430.7692 | 0
2016-10-22 20:00 | 2101 | 873.563 | 302 | 1240 | 1430.7692 | 0
2016-10-22 21:00 | 2101 | 839.306 | 302 | 1240 | 1521.4286 | 0
2016-10-22 22:00 | 2421 | 844.22 | 302 | 1240 | 1521.4286 | 0
2016-10-22 23:00 | 2421 | 794.26 | 302 | 1240 | 1673.3333 | 0
2016-10-23 | 2421 | 793.88 | 677 | 1240 | 1673.3333 | 0
2016-10-23 01:00 | 2421 | 755.38 | 302 | 1240 | 1673.3333 | 0
2016-10-23 02:00 | 2595 | 729.16 | 391 | 1240 | 1673.3333 | 0
2016-10-23 03:00 | 2595 | 639.576 | 305 | 1240 | 1673.3333 | 0
2016-10-23 04:00 | 2595 | 633.618 | 302 | 1240 | 1673.3333 | 0
2016-10-23 05:00 | 2595 | 640.404 | 545 | 1240 | 1673.3333 | 0
2016-10-23 06:00 | 3002 | 736.3 | 695 | 1240 | 1673.3333 | 0
2016-10-23 07:00 | 3002 | 761.6 | 497 | 1240 | 1673.3333 | 0
2016-10-23 08:00 | 3002 | 791.88 | 333 | 1240 | 1673.3333 | 0
2016-10-23 09:00 | 3002 | 798.57 | 560 | 1240 | 1521.4286 | 0
2016-10-23 10:00 | 3145 | 835.088 | 595 | 1240 | 1521.4286 | 0
2016-10-23 11:00 | 3145 | 858.648 | 538 | 1240 | 1521.4286 | 0
2016-10-23 12:00 | 3145 | 873.506 | 497 | 1240 | 1521.4286 | 0
2016-10-23 13:00 | 3145 | 875.71 | 473 | 1240 | 1521.4286 | 0
2016-10-23 14:00 | 2424 | 877.762 | 534 | 1240 | 1521.4286 | 0
2016-10-23 15:00 | 2424 | 879.054 | 521 | 1240 | 1521.4286 | 0
2016-10-23 16:00 | 2424 | 874.513 | 394 | 1240 | 1521.4286 | 0
2016-10-23 17:00 | 2424 | 904.3 | 439 | 1240 | 1521.4286 | 0
2016-10-23 18:00 | 2101 | 860.111 | 524 | 1240 | 1521.4286 | 0
2016-10-23 19:00 | 2101 | 861.118 | 453 | 1240 | 1521.4286 | 0
2016-10-23 20:00 | 2101 | 847.286 | 302 | 1240 | 1521.4286 | 0
2016-10-23 21:00 | 2101 | 863.34 | 302 | 1240 | 1673.3333 | 0
2016-10-23 22:00 | 2421 | 821.34 | 302 | 1240 | 1673.3333 | 0
2016-10-23 23:00 | 2421 | 772.38 | 302 | 1240 | 1730 | 0
2016-10-24 | 2421 | 659.88 | 677 | 1240 | 1730 | 0
2016-10-24 01:00 | 2421 | 633.942 | 302 | 1240 | 1730 | 0
2016-10-24 02:00 | 2595 | 613.53 | 391 | 1240 | 1730 | 0
2016-10-24 03:00 | 2595 | 600.12 | 305 | 1240 | 1730 | 0
2016-10-24 04:00 | 2595 | 593.064 | 302 | 1240 | 1730 | 0
2016-10-24 05:00 | 2595 | 595.764 | 545 | 1240 | 1730 | 0
2016-10-24 06:00 | 3002 | 609.48 | 695 | 1240 | 1730 | 0
2016-10-24 07:00 | 3002 | 623.61 | 497 | 1240 | 1730 | 0
2016-10-24 08:00 | 3002 | 651.6 | 333 | 1240 | 1730 | 0
2016-10-24 09:00 | 3002 | 779.54 | 560 | 1240 | 1673.3333 | 0
2016-10-24 10:00 | 3145 | 787.493 | 595 | 1240 | 1521.4286 | 0
2016-10-24 11:00 | 3145 | 832.39 | 538 | 1240 | 1521.4286 | 0
2016-10-24 12:00 | 3145 | 875.862 | 497 | 1240 | 1430.7692 | 0
2016-10-24 13:00 | 3145 | 963.22 | 473 | 1240 | 1430.7692 | 0
2016-10-24 14:00 | 2424 | 1000.64 | 534 | 1240 | 1430.7692 | 0
2016-10-24 15:00 | 2424 | 1027.38 | 521 | 1240 | 1440 | 0
2016-10-24 16:00 | 2424 | 1038.32 | 394 | 1240 | 1440 | 0
2016-10-24 17:00 | 2424 | 1028.12 | 439 | 1240 | 1440 | 0
2016-10-24 18:00 | 2101 | 1018.28 | 524 | 1240 | 1440 | 0
2016-10-24 19:00 | 2101 | 1008.42 | 453 | 1240 | 1440 | 0
2016-10-24 20:00 | 2101 | 982.46 | 302 | 1240 | 1430.7692 | 0
2016-10-24 21:00 | 2101 | 935.46 | 302 | 1240 | 1430.7692 | 0
2016-10-24 22:00 | 2421 | 828.229 | 302 | 1240 | 1521.4286 | 0
2016-10-24 23:00 | 2421 | 798.98 | 302 | 1240 | 1673.3333 | 0
2016-10-25 | 2421 | 619.812 | 677 | 1240 | 1730 | 0
2016-10-25 01:00 | 2421 | 593.784 | 302 | 1240 | 1730 | 0
2016-10-25 02:00 | 2595 | 578.61 | 391 | 1240 | 1730 | 0
2016-10-25 03:00 | 2595 | 573.858 | 305 | 1240 | 1730 | 0
2016-10-25 04:00 | 2595 | 582.858 | 302 | 1240 | 1730 | 0
2016-10-25 05:00 | 2595 | 619.002 | 545 | 1240 | 1730 | 0
2016-10-25 06:00 | 3002 | 688.23 | 695 | 1240 | 1730 | 0
2016-10-25 07:00 | 3002 | 801.92 | 497 | 1240 | 1730 | 0
2016-10-25 08:00 | 3002 | 722.052 | 333 | 1240 | 1730 | 0
2016-10-25 09:00 | 3002 | 834.38 | 560 | 1240 | 1673.3333 | 0
2016-10-25 10:00 | 3145 | 870.6 | 595 | 1240 | 1673.3333 | 0
2016-10-25 11:00 | 3145 | 911.2 | 538 | 1240 | 1673.3333 | 0
2016-10-25 12:00 | 3145 | 900.562 | 497 | 1240 | 1521.4286 | 0
2016-10-25 13:00 | 3145 | 943.939 | 473 | 1240 | 1430.7692 | 0
2016-10-25 14:00 | 2424 | 1025.34 | 534 | 1240 | 1430.7692 | 0
2016-10-25 15:00 | 2424 | 1048.34 | 521 | 1240 | 1430.7692 | 0
2016-10-25 16:00 | 2424 | 1057.28 | 394 | 1240 | 1430.7692 | 0
2016-10-25 17:00 | 2424 | 1037.94 | 439 | 1240 | 1430.7692 | 0
2016-10-25 18:00 | 2101 | 1032.54 | 524 | 1240 | 1430.7692 | 0
2016-10-25 19:00 | 2101 | 975.783 | 453 | 1240 | 1430.7692 | 0
2016-10-25 20:00 | 2101 | 954.237 | 302 | 1240 | 1521.4286 | 0
2016-10-25 21:00 | 2101 | 915.629 | 302 | 1240 | 1521.4286 | 0
2016-10-25 22:00 | 2421 | 898.76 | 302 | 1240 | 1673.3333 | 0
2016-10-25 23:00 | 2421 | 747.576 | 302 | 1240 | 1730 | 0
2016-10-26 | 2421 | 667.224 | 677 | 1240 | 1730 | 0
2016-10-26 01:00 | 2421 | 638.694 | 302 | 1240 | 1730 | 0
2016-10-26 02:00 | 2595 | 619.92 | 391 | 1240 | 1730 | 0
2016-10-26 03:00 | 2595 | 602.856 | 305 | 1240 | 1730 | 0
2016-10-26 04:00 | 2595 | 599.922 | 302 | 1240 | 1730 | 0
2016-10-26 05:00 | 2595 | 626.508 | 545 | 1240 | 1730 | 0
2016-10-26 06:00 | 3002 | 765.56 | 695 | 1240 | 1673.3333 | 0
2016-10-26 07:00 | 3002 | 748.866 | 497 | 1240 | 1521.4286 | 0
2016-10-26 08:00 | 3002 | 739.86 | 333 | 1240 | 1521.4286 | 0
2016-10-26 09:00 | 3002 | 758.898 | 560 | 1240 | 1521.4286 | 0
2016-10-26 10:00 | 3145 | 828.14 | 595 | 1240 | 1430.7692 | 0
2016-10-26 11:00 | 3145 | 856.86 | 538 | 1240 | 1440 | 0
2016-10-26 12:00 | 3145 | 883.72 | 497 | 1240 | 1440 | 0
2016-10-26 13:00 | 3145 | 916.54 | 473 | 1240 | 1440 | 0
2016-10-26 14:00 | 2424 | 941.22 | 534 | 1240 | 1440 | 0
2016-10-26 15:00 | 2424 | 959.24 | 521 | 1240 | 1440 | 0
2016-10-26 16:00 | 2424 | 969.06 | 394 | 1240 | 1440 | 0
2016-10-26 17:00 | 2424 | 952.68 | 439 | 1240 | 1440 | 0
2016-10-26 18:00 | 2101 | 935.58 | 524 | 1240 | 1440 | 0
2016-10-26 19:00 | 2101 | 918.46 | 453 | 1240 | 1440 | 0
2016-10-26 20:00 | 2101 | 891.28 | 302 | 1240 | 1440 | 0
2016-10-26 21:00 | 2101 | 842.98 | 302 | 1240 | 1430.7692 | 0
2016-10-26 22:00 | 2421 | 739.784 | 302 | 1240 | 1521.4286 | 0
2016-10-26 23:00 | 2421 | 710.9 | 302 | 1240 | 1730 | 0
2016-10-27 | 2421 | 564.768 | 677 | 1240 | 1730 | 0
2016-10-27 01:00 | 2421 | 541.098 | 302 | 1240 | 1730 | 0
2016-10-27 02:00 | 2595 | 527.418 | 391 | 1240 | 1730 | 0
2016-10-27 03:00 | 2595 | 521.622 | 305 | 1240 | 1730 | 0
2016-10-27 04:00 | 2595 | 527.868 | 302 | 1240 | 1730 | 0
2016-10-27 05:00 | 2595 | 557.622 | 545 | 1240 | 1730 | 0
2016-10-27 06:00 | 3002 | 689.64 | 695 | 1240 | 1673.3333 | 0
2016-10-27 07:00 | 3002 | 720.1 | 497 | 1240 | 1673.3333 | 0
2016-10-27 08:00 | 3002 | 715.72 | 333 | 1240 | 1673.3333 | 0
2016-10-27 09:00 | 3002 | 701.404 | 560 | 1240 | 1521.4286 | 0
2016-10-27 10:00 | 3145 | 730.303 | 595 | 1240 | 1521.4286 | 0
2016-10-27 11:00 | 3145 | 801.64 | 538 | 1240 | 1430.7692 | 0
2016-10-27 12:00 | 3145 | 840.52 | 497 | 1240 | 1440 | 0
2016-10-27 13:00 | 3145 | 877.24 | 473 | 1240 | 1440 | 0
2016-10-27 14:00 | 2424 | 909.42 | 534 | 1240 | 1440 | 0
2016-10-27 15:00 | 2424 | 890.378 | 521 | 1240 | 1440 | 0
2016-10-27 16:00 | 2424 | 901.208 | 394 | 1240 | 1440 | 0
2016-10-27 17:00 | 2424 | 934.72 | 439 | 1240 | 1440 | 0
2016-10-27 18:00 | 2101 | 921.4 | 524 | 1240 | 1430.7692 | 0
2016-10-27 19:00 | 2101 | 908.08 | 453 | 1240 | 1430.7692 | 0
2016-10-27 20:00 | 2101 | 879.74 | 302 | 1240 | 1430.7692 | 0
2016-10-27 21:00 | 2101 | 794.276 | 302 | 1240 | 1521.4286 | 0
2016-10-27 22:00 | 2421 | 764.86 | 302 | 1240 | 1673.3333 | 0
2016-10-27 23:00 | 2421 | 627.03 | 302 | 1240 | 1673.3333 | 0
2016-10-28 | 2421 | 693.74 | 677 | 1240 | 1673.3333 | 0
2016-10-28 01:00 | 2421 | 678.28 | 302 | 1240 | 1673.3333 | 0
2016-10-28 02:00 | 2595 | 591.084 | 391 | 1240 | 1730 | 0
2016-10-28 03:00 | 2595 | 576.558 | 305 | 1240 | 1730 | 0
2016-10-28 04:00 | 2595 | 573.21 | 302 | 1240 | 1730 | 0
2016-10-28 05:00 | 2595 | 598.536 | 545 | 1240 | 1673.3333 | 0
2016-10-28 06:00 | 3002 | 733.48 | 695 | 1240 | 1673.3333 | 0
2016-10-28 07:00 | 3002 | 758.52 | 497 | 1240 | 1673.3333 | 0
2016-10-28 08:00 | 3002 | 742.88 | 333 | 1240 | 1673.3333 | 0
2016-10-28 09:00 | 3002 | 755.56 | 560 | 1240 | 1673.3333 | 0
2016-10-28 10:00 | 3145 | 735.547 | 595 | 1240 | 1521.4286 | 0
2016-10-28 11:00 | 3145 | 754.756 | 538 | 1240 | 1521.4286 | 0
2016-10-28 12:00 | 3145 | 764.142 | 497 | 1240 | 1521.4286 | 0
2016-10-28 13:00 | 3145 | 815.62 | 473 | 1240 | 1521.4286 | 0
2016-10-28 14:00 | 2424 | 782.895 | 534 | 1240 | 1521.4286 | 0
2016-10-28 15:00 | 2424 | 786.657 | 521 | 1240 | 1521.4286 | 0
2016-10-28 16:00 | 2424 | 787.455 | 394 | 1240 | 1521.4286 | 0
2016-10-28 17:00 | 2424 | 773.186 | 439 | 1240 | 1521.4286 | 0
2016-10-28 18:00 | 2101 | 772.901 | 524 | 1240 | 1521.4286 | 0
2016-10-28 19:00 | 2101 | 772.616 | 453 | 1240 | 1521.4286 | 0
2016-10-28 20:00 | 2101 | 758.936 | 302 | 1240 | 1521.4286 | 0
2016-10-28 21:00 | 2101 | 722.817 | 302 | 1240 | 1521.4286 | 0
2016-10-28 22:00 | 2421 | 708.62 | 302 | 1240 | 1673.3333 | 0
2016-10-28 23:00 | 2421 | 585.666 | 302 | 1240 | 1673.3333 | 0
2016-10-29 | 2421 | 581.958 | 677 | 1240 | 1673.3333 | 0
2016-10-29 01:00 | 2421 | 578.358 | 302 | 1240 | 1673.3333 | 0
2016-10-29 02:00 | 2595 | 574.992 | 391 | 1240 | 1673.3333 | 0
2016-10-29 03:00 | 2595 | 572.112 | 305 | 1240 | 1673.3333 | 0
2016-10-29 04:00 | 2595 | 581.868 | 302 | 1240 | 1673.3333 | 0
2016-10-29 05:00 | 2595 | 688.06 | 545 | 1240 | 1673.3333 | 0
2016-10-29 06:00 | 3002 | 775.6 | 695 | 1240 | 1673.3333 | 0
2016-10-29 07:00 | 3002 | 775.504 | 497 | 1240 | 1521.4286 | 0
2016-10-29 08:00 | 3002 | 764.579 | 333 | 1240 | 1521.4286 | 0
2016-10-29 09:00 | 3002 | 773.167 | 560 | 1240 | 1521.4286 | 0
2016-10-29 10:00 | 3145 | 779.874 | 595 | 1240 | 1521.4286 | 0
2016-10-29 11:00 | 3145 | 783.332 | 538 | 1240 | 1430.7692 | 0
2016-10-29 12:00 | 3145 | 783.902 | 497 | 1240 | 1430.7692 | 0
2016-10-29 13:00 | 3145 | 791.483 | 473 | 1240 | 1430.7692 | 0
2016-10-29 14:00 | 2424 | 837.42 | 534 | 1240 | 1430.7692 | 0
2016-10-29 15:00 | 2424 | 844.32 | 521 | 1240 | 1430.7692 | 0
2016-10-29 16:00 | 2424 | 850.18 | 394 | 1240 | 1430.7692 | 0
2016-10-29 17:00 | 2424 | 841.78 | 439 | 1240 | 1430.7692 | 0
2016-10-29 18:00 | 2101 | 799.805 | 524 | 1240 | 1430.7692 | 0
2016-10-29 19:00 | 2101 | 799.9 | 453 | 1240 | 1521.4286 | 0
2016-10-29 20:00 | 2101 | 825.52 | 302 | 1240 | 1673.3333 | 0
2016-10-29 21:00 | 2101 | 798.3 | 302 | 1240 | 1730 | 0
2016-10-29 22:00 | 2421 | 683.046 | 302 | 1240 | 1730 | 0
2016-10-29 23:00 | 2421 | 644.292 | 302 | 1240 | 1730 | 0
2016-10-30 | 2421 | 639.558 | 677 | 1240 | 1730 | 0
2016-10-30 01:00 | 2421 | 639.144 | 302 | 1240 | 1730 | 0
2016-10-30 02:00 | 2595 | 627.012 | 391 | 1240 | 1730 | 0
2016-10-30 03:00 | 2595 | 621.324 | 305 | 1240 | 1730 | 0
2016-10-30 04:00 | 2595 | 623.502 | 302 | 1240 | 1730 | 0
2016-10-30 05:00 | 2595 | 639.738 | 545 | 1240 | 1730 | 0
2016-10-30 06:00 | 3002 | 744.16 | 695 | 1240 | 1730 | 0
2016-10-30 07:00 | 3002 | 780.38 | 497 | 1240 | 1673.3333 | 0
2016-10-30 08:00 | 3002 | 813.78 | 333 | 1240 | 1673.3333 | 0
2016-10-30 09:00 | 3002 | 832.8 | 560 | 1240 | 1521.4286 | 0
2016-10-30 10:00 | 3145 | 803.206 | 595 | 1240 | 1521.4286 | 0
2016-10-30 11:00 | 3145 | 808.089 | 538 | 1240 | 1430.7692 | 0
2016-10-30 12:00 | 3145 | 851.06 | 497 | 1240 | 1440 | 0
2016-10-30 13:00 | 3145 | 853.24 | 473 | 1240 | 1440 | 0
2016-10-30 14:00 | 2424 | 861.48 | 534 | 1240 | 1440 | 0
2016-10-30 15:00 | 2424 | 876.46 | 521 | 1240 | 1440 | 0
2016-10-30 16:00 | 2424 | 889.8 | 394 | 1240 | 1440 | 0
2016-10-30 17:00 | 2424 | 889.4 | 439 | 1240 | 1440 | 0
2016-10-30 18:00 | 2101 | 898.92 | 524 | 1240 | 1440 | 0
2016-10-30 19:00 | 2101 | 908.44 | 453 | 1240 | 1440 | 0
2016-10-30 20:00 | 2101 | 848.825 | 302 | 1240 | 1430.7692 | 0
2016-10-30 21:00 | 2101 | 820.857 | 302 | 1240 | 1521.4286 | 0
2016-10-30 22:00 | 2421 | 823.56 | 302 | 1240 | 1673.3333 | 0
2016-10-30 23:00 | 2421 | 776.6 | 302 | 1240 | 1673.3333 | 0
2016-10-31 | 2421 | 665.334 | 677 | 1240 | 1730 | 0
2016-10-31 01:00 | 2421 | 639.342 | 302 | 1240 | 1730 | 0
2016-10-31 02:00 | 2595 | 623.016 | 391 | 1240 | 1730 | 0
2016-10-31 03:00 | 2595 | 614.646 | 305 | 1240 | 1730 | 0
2016-10-31 04:00 | 2595 | 611.748 | 302 | 1240 | 1730 | 0
2016-10-31 05:00 | 2595 | 619.452 | 545 | 1240 | 1730 | 0
2016-10-31 06:00 | 3002 | 637.272 | 695 | 1240 | 1730 | 0
2016-10-31 07:00 | 3002 | 658.512 | 497 | 1240 | 1730 | 0
2016-10-31 08:00 | 3002 | 755.7 | 333 | 1240 | 1673.3333 | 0
2016-10-31 09:00 | 3002 | 789.12 | 560 | 1240 | 1673.3333 | 0
2016-10-31 10:00 | 3145 | 778.012 | 595 | 1240 | 1521.4286 | 0
2016-10-31 11:00 | 3145 | 847.44 | 538 | 1240 | 1430.7692 | 0
2016-10-31 12:00 | 3145 | 879.44 | 497 | 1240 | 1440 | 0
2016-10-31 13:00 | 3145 | 867.901 | 473 | 1240 | 1440 | 0
2016-10-31 14:00 | 2424 | 903.697 | 534 | 1240 | 1238.9381 | 0
2016-10-31 15:00 | 2424 | 941.621 | 521 | 1240 | 1238.9381 | 0
2016-10-31 16:00 | 2424 | 1071.462 | 394 | 1240 | 1238.9381 | 0
2016-10-31 17:00 | 2424 | 969.114 | 439 | 1240 | 1238.9381 | 0
2016-10-31 18:00 | 2101 | 956.631 | 524 | 1240 | 1238.9381 | 0
2016-10-31 19:00 | 2101 | 944.129 | 453 | 1240 | 1238.9381 | 0
2016-10-31 20:00 | 2101 | 926.592 | 302 | 1240 | 1238.9381 | 0
2016-10-31 21:00 | 2101 | 912.494 | 302 | 1240 | 1440 | 0
2016-10-31 22:00 | 2421 | 914.68 | 302 | 1240 | 1440 | 0
2016-10-31 23:00 | 2421 | 842.84 | 302 | 1240 | 1430.7692 | 0
2016-11-01 | 2662 | 703.06 | 624 | 1240 | 1673.3333 | 0
2016-11-01 01:00 | 2662 | 582.246 | 312 | 1240 | 1673.3333 | 0
2016-11-01 02:00 | 2610 | 571.824 | 401 | 1240 | 1673.3333 | 0
2016-11-01 03:00 | 2610 | 568.404 | 346 | 1240 | 1673.3333 | 0
2016-11-01 04:00 | 2610 | 578.934 | 389 | 1240 | 1673.3333 | 0
2016-11-01 05:00 | 2610 | 615.888 | 562 | 1240 | 1673.3333 | 0
2016-11-01 06:00 | 2535 | 759.78 | 726 | 1240 | 1673.3333 | 0
2016-11-01 07:00 | 2535 | 760.798 | 469 | 1240 | 1521.4286 | 0
2016-11-01 08:00 | 2535 | 762.109 | 442 | 1240 | 1521.4286 | 0
2016-11-01 09:00 | 2535 | 779.209 | 446 | 1240 | 1521.4286 | 0
2016-11-01 10:00 | 2687 | 847.56 | 528 | 1240 | 1430.7692 | 0
2016-11-01 11:00 | 2687 | 874.74 | 532 | 1240 | 1430.7692 | 0
2016-11-01 12:00 | 2687 | 899.88 | 379 | 1240 | 1430.7692 | 0
2016-11-01 13:00 | 2687 | 927.88 | 429 | 1240 | 1440 | 0
2016-11-01 14:00 | 2519 | 901.265 | 366 | 1240 | 1440 | 0
2016-11-01 15:00 | 2519 | 913.577 | 335 | 1240 | 1440 | 0
2016-11-01 16:00 | 2519 | 920.911 | 418 | 1240 | 1440 | 0
2016-11-01 17:00 | 2519 | 956.96 | 638 | 1240 | 1430.7692 | 0
2016-11-01 18:00 | 3598 | 959.96 | 524 | 1240 | 1430.7692 | 0
2016-11-01 19:00 | 3598 | 962.98 | 385 | 1240 | 1430.7692 | 0
2016-11-01 20:00 | 3598 | 888.991 | 429 | 1240 | 1430.7692 | 0
2016-11-01 21:00 | 3598 | 846.583 | 326 | 1240 | 1521.4286 | 0
2016-11-01 22:00 | 2662 | 823.66 | 312 | 1240 | 1673.3333 | 0
2016-11-01 23:00 | 2662 | 746.98 | 312 | 1240 | 1730 | 0
2016-11-02 | 2662 | 735.14 | 624 | 1240 | 1730 | 0
2016-11-02 01:00 | 2662 | 629.658 | 312 | 1240 | 1730 | 0
2016-11-02 02:00 | 2610 | 611.028 | 401 | 1240 | 1730 | 0
2016-11-02 03:00 | 2610 | 598.428 | 346 | 1240 | 1730 | 0
2016-11-02 04:00 | 2610 | 601.218 | 389 | 1240 | 1730 | 0
2016-11-02 05:00 | 2610 | 631.188 | 562 | 1240 | 1730 | 0
2016-11-02 06:00 | 2535 | 777.46 | 726 | 1240 | 1730 | 0
2016-11-02 07:00 | 2535 | 820.32 | 469 | 1240 | 1673.3333 | 0
2016-11-02 08:00 | 2535 | 810.52 | 442 | 1240 | 1673.3333 | 0
2016-11-02 09:00 | 2535 | 814.54 | 446 | 1240 | 1730 | 0
2016-11-02 10:00 | 2687 | 826.02 | 528 | 1240 | 1673.3333 | 0
2016-11-02 11:00 | 2687 | 833.24 | 532 | 1240 | 1673.3333 | 0
2016-11-02 12:00 | 2687 | 838.26 | 379 | 1240 | 1673.3333 | 0
2016-11-02 13:00 | 2687 | 845.88 | 429 | 1240 | 1673.3333 | 0
2016-11-02 14:00 | 2519 | 850.72 | 366 | 1240 | 1673.3333 | 0
2016-11-02 15:00 | 2519 | 850.26 | 335 | 1240 | 1673.3333 | 0
2016-11-02 16:00 | 2519 | 852.34 | 418 | 1240 | 1673.3333 | 0
2016-11-02 17:00 | 2519 | 852.5 | 638 | 1240 | 1673.3333 | 0
2016-11-02 18:00 | 3598 | 867.42 | 524 | 1240 | 1673.3333 | 0
2016-11-02 19:00 | 3598 | 882.36 | 385 | 1240 | 1673.3333 | 0
2016-11-02 20:00 | 3598 | 867.58 | 429 | 1240 | 1673.3333 | 0
2016-11-02 21:00 | 3598 | 828.72 | 326 | 1240 | 1673.3333 | 0
2016-11-02 22:00 | 2662 | 768.72 | 312 | 1240 | 1673.3333 | 0
2016-11-02 23:00 | 2662 | 710.1 | 312 | 1240 | 1673.3333 | 0
2016-11-03 | 2662 | 569.34 | 624 | 1240 | 1673.3333 | 0
2016-11-03 01:00 | 2662 | 551.34 | 312 | 1240 | 1673.3333 | 0
2016-11-03 02:00 | 2610 | 543.636 | 401 | 1240 | 1730 | 0
2016-11-03 03:00 | 2610 | 540.936 | 346 | 1240 | 1730 | 0
2016-11-03 04:00 | 2610 | 548.694 | 389 | 1240 | 1730 | 0
2016-11-03 05:00 | 2610 | 585.684 | 562 | 1240 | 1730 | 0
2016-11-03 06:00 | 2535 | 730.66 | 726 | 1240 | 1730 | 0
2016-11-03 07:00 | 2535 | 776.86 | 469 | 1240 | 1730 | 0
2016-11-03 08:00 | 2535 | 694.656 | 442 | 1240 | 1730 | 0
2016-11-03 09:00 | 2535 | 698.076 | 446 | 1240 | 1730 | 0
2016-11-03 10:00 | 2687 | 770.86 | 528 | 1240 | 1730 | 0
2016-11-03 11:00 | 2687 | 768.02 | 532 | 1240 | 1730 | 0
2016-11-03 12:00 | 2687 | 699.84 | 379 | 1240 | 1730 | 0
2016-11-03 13:00 | 2687 | 703.476 | 429 | 1240 | 1730 | 0
2016-11-03 14:00 | 2519 | 702.036 | 366 | 1240 | 1730 | 0
2016-11-03 15:00 | 2519 | 699.516 | 335 | 1240 | 1730 | 0
2016-11-03 16:00 | 2519 | 701.154 | 418 | 1240 | 1730 | 0
2016-11-03 17:00 | 2519 | 704.844 | 638 | 1240 | 1730 | 0
2016-11-03 18:00 | 3598 | 722.646 | 524 | 1240 | 1730 | 0
2016-11-03 19:00 | 3598 | 822.74 | 385 | 1240 | 1730 | 0
2016-11-03 20:00 | 3598 | 810.98 | 429 | 1240 | 1730 | 0
2016-11-03 21:00 | 3598 | 779.86 | 326 | 1240 | 1730 | 0
2016-11-03 22:00 | 2662 | 652.266 | 312 | 1240 | 1800 | 0
2016-11-03 23:00 | 2662 | 604.836 | 312 | 1240 | 1800 | 0
2016-11-04 | 2662 | 566.946 | 624 | 1240 | 1800 | 0
2016-11-04 01:00 | 2662 | 549.162 | 312 | 1240 | 1800 | 0
2016-11-04 02:00 | 2610 | 540.306 | 401 | 1240 | 1800 | 0
2016-11-04 03:00 | 2610 | 539.676 | 346 | 1240 | 1800 | 0
2016-11-04 04:00 | 2610 | 549.594 | 389 | 1240 | 1730 | 0
2016-11-04 05:00 | 2610 | 588.06 | 562 | 1240 | 1730 | 0
2016-11-04 06:00 | 2535 | 660.996 | 726 | 1240 | 1730 | 0
2016-11-04 07:00 | 2535 | 772.26 | 469 | 1240 | 1730 | 0
2016-11-04 08:00 | 2535 | 760.54 | 442 | 1240 | 1730 | 0
2016-11-04 09:00 | 2535 | 759.52 | 446 | 1240 | 1730 | 0
2016-11-04 10:00 | 2687 | 767.06 | 528 | 1240 | 1673.3333 | 0
2016-11-04 11:00 | 2687 | 768.68 | 532 | 1240 | 1673.3333 | 0
2016-11-04 12:00 | 2687 | 765.46 | 379 | 1240 | 1673.3333 | 0
2016-11-04 13:00 | 2687 | 763.58 | 429 | 1240 | 1673.3333 | 0
2016-11-04 14:00 | 2519 | 757.98 | 366 | 1240 | 1673.3333 | 0
2016-11-04 15:00 | 2519 | 754.38 | 335 | 1240 | 1673.3333 | 0
2016-11-04 16:00 | 2519 | 754.24 | 418 | 1240 | 1673.3333 | 0
2016-11-04 17:00 | 2519 | 748.4 | 638 | 1240 | 1673.3333 | 0
2016-11-04 18:00 | 3598 | 772.12 | 524 | 1240 | 1673.3333 | 0
2016-11-04 19:00 | 3598 | 756.029 | 385 | 1240 | 1521.4286 | 0
2016-11-04 20:00 | 3598 | 752.571 | 429 | 1240 | 1521.4286 | 0
2016-11-04 21:00 | 3598 | 726.978 | 326 | 1240 | 1521.4286 | 0
2016-11-04 22:00 | 2662 | 720.84 | 312 | 1240 | 1521.4286 | 0
2016-11-04 23:00 | 2662 | 671.56 | 312 | 1240 | 1521.4286 | 0
2016-11-05 | 2662 | 683.06 | 624 | 1240 | 1521.4286 | 0
2016-11-05 01:00 | 2662 | 684.42 | 312 | 1240 | 1521.4286 | 0
2016-11-05 02:00 | 2610 | 678.68 | 401 | 1240 | 1521.4286 | 0
2016-11-05 03:00 | 2610 | 680.96 | 346 | 1240 | 1521.4286 | 0
2016-11-05 04:00 | 2610 | 700.08 | 389 | 1240 | 1521.4286 | 0
2016-11-05 05:00 | 2610 | 717.668 | 562 | 1240 | 1430.7692 | 0
2016-11-05 06:00 | 2535 | 852.8 | 726 | 1240 | 1430.7692 | 0
2016-11-05 07:00 | 2535 | 900.96 | 469 | 1240 | 1440 | 0
2016-11-05 08:00 | 2535 | 882.9 | 442 | 1240 | 1430.7692 | 0
2016-11-05 09:00 | 2535 | 874.66 | 446 | 1240 | 1430.7692 | 0
2016-11-05 10:00 | 2687 | 867.32 | 528 | 1240 | 1430.7692 | 0
2016-11-05 11:00 | 2687 | 856.96 | 532 | 1240 | 1430.7692 | 0
2016-11-05 12:00 | 2687 | 841.62 | 379 | 1240 | 1430.7692 | 0
2016-11-05 13:00 | 2687 | 834.64 | 429 | 1240 | 1430.7692 | 0
2016-11-05 14:00 | 2519 | 827.44 | 366 | 1240 | 1430.7692 | 0
2016-11-05 15:00 | 2519 | 820.56 | 335 | 1240 | 1430.7692 | 0
2016-11-05 16:00 | 2519 | 816.12 | 418 | 1240 | 1430.7692 | 0
2016-11-05 17:00 | 2519 | 811.8 | 638 | 1240 | 1430.7692 | 0
2016-11-05 18:00 | 3598 | 830.88 | 524 | 1240 | 1430.7692 | 0
2016-11-05 19:00 | 3598 | 849.96 | 385 | 1240 | 1430.7692 | 0
2016-11-05 20:00 | 3598 | 797.563 | 429 | 1240 | 1521.4286 | 0
2016-11-05 21:00 | 3598 | 782.363 | 326 | 1240 | 1673.3333 | 0
2016-11-05 22:00 | 2662 | 795.56 | 312 | 1240 | 1730 | 0
2016-11-05 23:00 | 2662 | 685.134 | 312 | 1240 | 1730 | 0
2016-11-06 | 2662 | 757.18 | 624 | 1240 | 1730 | 0
2016-11-06 01:00 | 2662 | 663.822 | 312 | 1240 | 1730 | 0
2016-11-06 02:00 | 2610 | 655.29 | 401 | 1240 | 1730 | 0
2016-11-06 03:00 | 2610 | 655.29 | 346 | 1240 | 1730 | 0
2016-11-06 04:00 | 2610 | 663.39 | 389 | 1240 | 1730 | 0
2016-11-06 05:00 | 2610 | 761.26 | 562 | 1240 | 1730 | 0
2016-11-06 06:00 | 2535 | 805.16 | 726 | 1240 | 1673.3333 | 0
2016-11-06 07:00 | 2535 | 807.272 | 469 | 1240 | 1521.4286 | 0
2016-11-06 08:00 | 2535 | 829.198 | 442 | 1240 | 1521.4286 | 0
2016-11-06 09:00 | 2535 | 832.181 | 446 | 1240 | 1521.4286 | 0
2016-11-06 10:00 | 2687 | 821.218 | 528 | 1240 | 1521.4286 | 0
2016-11-06 11:00 | 2687 | 802.085 | 532 | 1240 | 1521.4286 | 0
2016-11-06 12:00 | 2687 | 782.287 | 379 | 1240 | 1521.4286 | 0
2016-11-06 13:00 | 2687 | 763.61 | 429 | 1240 | 1521.4286 | 0
2016-11-06 14:00 | 2519 | 790.04 | 366 | 1240 | 1521.4286 | 0
2016-11-06 15:00 | 2519 | 785.48 | 335 | 1240 | 1521.4286 | 0
2016-11-06 16:00 | 2519 | 785.44 | 418 | 1240 | 1521.4286 | 0
2016-11-06 17:00 | 2519 | 787.02 | 638 | 1240 | 1521.4286 | 0
2016-11-06 18:00 | 3598 | 814.74 | 524 | 1240 | 1673.3333 | 0
2016-11-06 19:00 | 3598 | 842.46 | 385 | 1240 | 1673.3333 | 0
2016-11-06 20:00 | 3598 | 836.74 | 429 | 1240 | 1673.3333 | 0
2016-11-06 21:00 | 3598 | 818.84 | 326 | 1240 | 1730 | 0
2016-11-06 22:00 | 2662 | 710.46 | 312 | 1240 | 1730 | 0
2016-11-06 23:00 | 2662 | 678.51 | 312 | 1240 | 1730 | 0
2016-11-07 | 2662 | 668.916 | 624 | 1240 | 1730 | 0
2016-11-07 01:00 | 2662 | 641.43 | 312 | 1240 | 1730 | 0
2016-11-07 02:00 | 2610 | 639.9 | 401 | 1240 | 1730 | 0
2016-11-07 03:00 | 2610 | 645.624 | 346 | 1240 | 1730 | 0
2016-11-07 04:00 | 2610 | 655.866 | 389 | 1240 | 1730 | 0
2016-11-07 05:00 | 2610 | 676.278 | 562 | 1240 | 1730 | 0
2016-11-07 06:00 | 2535 | 781.24 | 726 | 1240 | 1730 | 0
2016-11-07 07:00 | 2535 | 810.62 | 469 | 1240 | 1673.3333 | 0
2016-11-07 08:00 | 2535 | 834.84 | 442 | 1240 | 1673.3333 | 0
2016-11-07 09:00 | 2535 | 836.12 | 446 | 1240 | 1673.3333 | 0
2016-11-07 10:00 | 2687 | 824.98 | 528 | 1240 | 1673.3333 | 0
2016-11-07 11:00 | 2687 | 813.3 | 532 | 1240 | 1673.3333 | 0
2016-11-07 12:00 | 2687 | 813.18 | 379 | 1240 | 1673.3333 | 0
2016-11-07 13:00 | 2687 | 811.4 | 429 | 1240 | 1673.3333 | 0
2016-11-07 14:00 | 2519 | 811 | 366 | 1240 | 1673.3333 | 0
2016-11-07 15:00 | 2519 | 813.94 | 335 | 1240 | 1673.3333 | 0
2016-11-07 16:00 | 2519 | 821.42 | 418 | 1240 | 1673.3333 | 0
2016-11-07 17:00 | 2519 | 848.56 | 638 | 1240 | 1673.3333 | 0
2016-11-07 18:00 | 3598 | 870.62 | 524 | 1240 | 1673.3333 | 0
2016-11-07 19:00 | 3598 | 892.66 | 385 | 1240 | 1673.3333 | 0
2016-11-07 20:00 | 3598 | 872.66 | 429 | 1240 | 1673.3333 | 0
2016-11-07 21:00 | 3598 | 837.96 | 326 | 1240 | 1730 | 0
2016-11-07 22:00 | 2662 | 708.966 | 312 | 1240 | 1730 | 0
2016-11-07 23:00 | 2662 | 662.508 | 312 | 1240 | 1730 | 0
2016-11-08 | 2662 | 582.318 | 624 | 1240 | 1730 | 0
2016-11-08 01:00 | 2662 | 572.292 | 312 | 1240 | 1730 | 0
2016-11-08 02:00 | 2610 | 570.96 | 401 | 1240 | 1730 | 0
2016-11-08 03:00 | 2610 | 576.882 | 346 | 1240 | 1730 | 0
2016-11-08 04:00 | 2610 | 599.094 | 389 | 1240 | 1730 | 0
2016-11-08 05:00 | 2610 | 652.554 | 562 | 1240 | 1730 | 0
2016-11-08 06:00 | 2535 | 813.54 | 726 | 1240 | 1673.3333 | 0
2016-11-08 07:00 | 2535 | 828.98 | 469 | 1240 | 1673.3333 | 0
2016-11-08 08:00 | 2535 | 827.7 | 442 | 1240 | 1673.3333 | 0
2016-11-08 09:00 | 2535 | 832.52 | 446 | 1240 | 1673.3333 | 0
2016-11-08 10:00 | 2687 | 838.68 | 528 | 1240 | 1673.3333 | 0
2016-11-08 11:00 | 2687 | 842.78 | 532 | 1240 | 1521.4286 | 0
2016-11-08 12:00 | 2687 | 804.365 | 379 | 1240 | 1521.4286 | 0
2016-11-08 13:00 | 2687 | 814.017 | 429 | 1240 | 1521.4286 | 0
2016-11-08 14:00 | 2519 | 815.822 | 366 | 1240 | 1521.4286 | 0
2016-11-08 15:00 | 2519 | 816.734 | 335 | 1240 | 1521.4286 | 0
2016-11-08 16:00 | 2519 | 815.917 | 418 | 1240 | 1521.4286 | 0
2016-11-08 17:00 | 2519 | 826.139 | 638 | 1240 | 1521.4286 | 0
2016-11-08 18:00 | 3598 | 833.777 | 524 | 1240 | 1521.4286 | 0
2016-11-08 19:00 | 3598 | 885.7 | 385 | 1240 | 1673.3333 | 0
2016-11-08 20:00 | 3598 | 861.06 | 429 | 1240 | 1673.3333 | 0
2016-11-08 21:00 | 3598 | 739.026 | 326 | 1240 | 1730 | 0
2016-11-08 22:00 | 2662 | 681.732 | 312 | 1240 | 1730 | 0
2016-11-08 23:00 | 2662 | 633.96 | 312 | 1240 | 1730 | 0
2016-11-09 | 2662 | 594.414 | 624 | 1240 | 1730 | 0
2016-11-09 01:00 | 2662 | 578.952 | 312 | 1240 | 1730 | 0
2016-11-09 02:00 | 2610 | 569.304 | 401 | 1240 | 1730 | 0
2016-11-09 03:00 | 2610 | 568.404 | 346 | 1240 | 1730 | 0
2016-11-09 04:00 | 2610 | 582.642 | 389 | 1240 | 1730 | 0
2016-11-09 05:00 | 2610 | 626.04 | 562 | 1240 | 1730 | 0
2016-11-09 06:00 | 2535 | 699.228 | 726 | 1240 | 1730 | 0
2016-11-09 07:00 | 2535 | 793.52 | 469 | 1240 | 1730 | 0
2016-11-09 08:00 | 2535 | 719.154 | 442 | 1240 | 1730 | 0
2016-11-09 09:00 | 2535 | 813.86 | 446 | 1240 | 1673.3333 | 0
2016-11-09 10:00 | 2687 | 833.5 | 528 | 1240 | 1673.3333 | 0
2016-11-09 11:00 | 2687 | 844.34 | 532 | 1240 | 1673.3333 | 0
2016-11-09 12:00 | 2687 | 852.4 | 379 | 1240 | 1673.3333 | 0
2016-11-09 13:00 | 2687 | 862.86 | 429 | 1240 | 1673.3333 | 0
2016-11-09 14:00 | 2519 | 865.38 | 366 | 1240 | 1673.3333 | 0
2016-11-09 15:00 | 2519 | 863.66 | 335 | 1240 | 1673.3333 | 0
2016-11-09 16:00 | 2519 | 858.8 | 418 | 1240 | 1673.3333 | 0
2016-11-09 17:00 | 2519 | 869.04 | 638 | 1240 | 1673.3333 | 0
2016-11-09 18:00 | 3598 | 880.28 | 524 | 1240 | 1673.3333 | 0
2016-11-09 19:00 | 3598 | 891.54 | 385 | 1240 | 1673.3333 | 0
2016-11-09 20:00 | 3598 | 871.82 | 429 | 1240 | 1673.3333 | 0
2016-11-09 21:00 | 3598 | 828.78 | 326 | 1240 | 1673.3333 | 0
2016-11-09 22:00 | 2662 | 691.794 | 312 | 1240 | 1730 | 0
2016-11-09 23:00 | 2662 | 638.46 | 312 | 1240 | 1730 | 0
2016-11-10 | 2662 | 570.924 | 624 | 1240 | 1730 | 0
2016-11-10 01:00 | 2662 | 552.726 | 312 | 1240 | 1730 | 0
2016-11-10 02:00 | 2610 | 542.736 | 401 | 1240 | 1730 | 0
2016-11-10 03:00 | 2610 | 541.188 | 346 | 1240 | 1730 | 0
2016-11-10 04:00 | 2610 | 550.962 | 389 | 1240 | 1730 | 0
2016-11-10 05:00 | 2610 | 588.708 | 562 | 1240 | 1730 | 0
2016-11-10 06:00 | 2535 | 730.74 | 726 | 1240 | 1673.3333 | 0
2016-11-10 07:00 | 2535 | 748.68 | 469 | 1240 | 1673.3333 | 0
2016-11-10 08:00 | 2535 | 721.791 | 442 | 1240 | 1521.4286 | 0
2016-11-10 09:00 | 2535 | 741.95 | 446 | 1240 | 1521.4286 | 0
2016-11-10 10:00 | 2687 | 763.154 | 528 | 1240 | 1430.7692 | 0
2016-11-10 11:00 | 2687 | 821.12 | 532 | 1240 | 1430.7692 | 0
2016-11-10 12:00 | 2687 | 830.42 | 379 | 1240 | 1430.7692 | 0
2016-11-10 13:00 | 2687 | 840.1 | 429 | 1240 | 1430.7692 | 0
2016-11-10 14:00 | 2519 | 845.14 | 366 | 1240 | 1440 | 0
2016-11-10 15:00 | 2519 | 844.76 | 335 | 1240 | 1440 | 0
2016-11-10 16:00 | 2519 | 840.12 | 418 | 1240 | 1440 | 0
2016-11-10 17:00 | 2519 | 846.98 | 638 | 1240 | 1440 | 0
2016-11-10 18:00 | 3598 | 850.04 | 524 | 1240 | 1430.7692 | 0
2016-11-10 19:00 | 3598 | 853.12 | 385 | 1240 | 1430.7692 | 0
2016-11-10 20:00 | 3598 | 789.488 | 429 | 1240 | 1430.7692 | 0
2016-11-10 21:00 | 3598 | 753.787 | 326 | 1240 | 1521.4286 | 0
2016-11-10 22:00 | 2662 | 742.58 | 312 | 1240 | 1673.3333 | 0
2016-11-10 23:00 | 2662 | 619.164 | 312 | 1240 | 1730 | 0
2016-11-11 | 2662 | 579.492 | 624 | 1240 | 1730 | 0
2016-11-11 01:00 | 2662 | 560.988 | 312 | 1240 | 1730 | 0
2016-11-11 02:00 | 2610 | 551.772 | 401 | 1240 | 1730 | 0
2016-11-11 03:00 | 2610 | 548.082 | 346 | 1240 | 1730 | 0
2016-11-11 04:00 | 2610 | 556.434 | 389 | 1240 | 1730 | 0
2016-11-11 05:00 | 2610 | 590.238 | 562 | 1240 | 1730 | 0
2016-11-11 06:00 | 2535 | 730.6 | 726 | 1240 | 1730 | 0
2016-11-11 07:00 | 2535 | 756.92 | 469 | 1240 | 1730 | 0
2016-11-11 08:00 | 2535 | 767.8 | 442 | 1240 | 1730 | 0
2016-11-11 09:00 | 2535 | 787.98 | 446 | 1240 | 1673.3333 | 0
2016-11-11 10:00 | 2687 | 808.9 | 528 | 1240 | 1673.3333 | 0
2016-11-11 11:00 | 2687 | 821.02 | 532 | 1240 | 1673.3333 | 0
2016-11-11 12:00 | 2687 | 831.92 | 379 | 1240 | 1673.3333 | 0
2016-11-11 13:00 | 2687 | 845.34 | 429 | 1240 | 1673.3333 | 0
2016-11-11 14:00 | 2519 | 851.36 | 366 | 1240 | 1521.4286 | 0
2016-11-11 15:00 | 2519 | 850.48 | 335 | 1240 | 1521.4286 | 0
2016-11-11 16:00 | 2519 | 805.391 | 418 | 1240 | 1521.4286 | 0
2016-11-11 17:00 | 2519 | 812.668 | 638 | 1240 | 1521.4286 | 0
2016-11-11 18:00 | 3598 | 817.551 | 524 | 1240 | 1521.4286 | 0
2016-11-11 19:00 | 3598 | 822.453 | 385 | 1240 | 1521.4286 | 0
2016-11-11 20:00 | 3598 | 845.98 | 429 | 1240 | 1673.3333 | 0
2016-11-11 21:00 | 3598 | 808.14 | 326 | 1240 | 1673.3333 | 0
2016-11-11 22:00 | 2662 | 752.06 | 312 | 1240 | 1730 | 0
2016-11-11 23:00 | 2662 | 627.21 | 312 | 1240 | 1730 | 0
2016-11-12 | 2662 | 604.404 | 624 | 1240 | 1730 | 0
2016-11-12 01:00 | 2662 | 584.658 | 312 | 1240 | 1730 | 0
2016-11-12 02:00 | 2610 | 573.102 | 401 | 1240 | 1730 | 0
2016-11-12 03:00 | 2610 | 568.188 | 346 | 1240 | 1730 | 0
2016-11-12 04:00 | 2610 | 575.964 | 389 | 1240 | 1730 | 0
2016-11-12 05:00 | 2610 | 609.93 | 562 | 1240 | 1730 | 0
2016-11-12 06:00 | 2535 | 753.4 | 726 | 1240 | 1673.3333 | 0
2016-11-12 07:00 | 2535 | 780.2 | 469 | 1240 | 1673.3333 | 0
2016-11-12 08:00 | 2535 | 799.4 | 442 | 1240 | 1673.3333 | 0
2016-11-12 09:00 | 2535 | 825.28 | 446 | 1240 | 1673.3333 | 0
2016-11-12 10:00 | 2687 | 847.58 | 528 | 1240 | 1673.3333 | 0
2016-11-12 11:00 | 2687 | 863.3 | 532 | 1240 | 1673.3333 | 0
2016-11-12 12:00 | 2687 | 873.56 | 379 | 1240 | 1673.3333 | 0
2016-11-12 13:00 | 2687 | 884.24 | 429 | 1240 | 1673.3333 | 0
2016-11-12 14:00 | 2519 | 846.279 | 366 | 1240 | 1673.3333 | 0
2016-11-12 15:00 | 2519 | 835.145 | 335 | 1240 | 1673.3333 | 0
2016-11-12 16:00 | 2519 | 859.58 | 418 | 1240 | 1673.3333 | 0
2016-11-12 17:00 | 2519 | 815.442 | 638 | 1240 | 1521.4286 | 0
2016-11-12 18:00 | 3598 | 805.904 | 524 | 1240 | 1521.4286 | 0
2016-11-12 19:00 | 3598 | 796.385 | 385 | 1240 | 1521.4286 | 0
2016-11-12 20:00 | 3598 | 772.673 | 429 | 1240 | 1521.4286 | 0
2016-11-12 21:00 | 3598 | 741.513 | 326 | 1240 | 1521.4286 | 0
2016-11-12 22:00 | 2662 | 702.924 | 312 | 1240 | 1673.3333 | 0
2016-11-12 23:00 | 2662 | 695.08 | 312 | 1240 | 1673.3333 | 0
2016-11-13 | 2662 | 697.38 | 624 | 1240 | 1673.3333 | 0
2016-11-13 01:00 | 2662 | 708.84 | 312 | 1240 | 1673.3333 | 0
2016-11-13 02:00 | 2610 | 689.58 | 401 | 1240 | 1673.3333 | 0
2016-11-13 03:00 | 2610 | 682.1 | 346 | 1240 | 1673.3333 | 0
2016-11-13 04:00 | 2610 | 685.78 | 389 | 1240 | 1673.3333 | 0
2016-11-13 05:00 | 2610 | 703.08 | 562 | 1240 | 1673.3333 | 0
2016-11-13 06:00 | 2535 | 700.948 | 726 | 1240 | 1521.4286 | 0
2016-11-13 07:00 | 2535 | 731.443 | 469 | 1240 | 1521.4286 | 0
2016-11-13 08:00 | 2535 | 769.31 | 442 | 1240 | 1430.7692 | 0
2016-11-13 09:00 | 2535 | 835.32 | 446 | 1240 | 1430.7692 | 0
2016-11-13 10:00 | 2687 | 848.5 | 528 | 1240 | 1430.7692 | 0
2016-11-13 11:00 | 2687 | 836.02 | 532 | 1240 | 1430.7692 | 0
2016-11-13 12:00 | 2687 | 823.76 | 379 | 1240 | 1430.7692 | 0
2016-11-13 13:00 | 2687 | 809.62 | 429 | 1240 | 1430.7692 | 0
2016-11-13 14:00 | 2519 | 800.14 | 366 | 1240 | 1430.7692 | 0
2016-11-13 15:00 | 2519 | 795.38 | 335 | 1240 | 1440 | 0
2016-11-13 16:00 | 2519 | 797.42 | 418 | 1240 | 1440 | 0
2016-11-13 17:00 | 2519 | 824.26 | 638 | 1240 | 1440 | 0
2016-11-13 18:00 | 3598 | 840.32 | 524 | 1240 | 1440 | 0
2016-11-13 19:00 | 3598 | 856.38 | 385 | 1240 | 1440 | 0
2016-11-13 20:00 | 3598 | 845.34 | 429 | 1240 | 1440 | 0
2016-11-13 21:00 | 3598 | 825.9 | 326 | 1240 | 1430.7692 | 0
2016-11-13 22:00 | 2662 | 754.965 | 312 | 1240 | 1430.7692 | 0
2016-11-13 23:00 | 2662 | 721.316 | 312 | 1240 | 1521.4286 | 0
2016-11-14 | 2662 | 739.78 | 624 | 1240 | 1521.4286 | 0
2016-11-14 01:00 | 2662 | 721.98 | 312 | 1240 | 1521.4286 | 0
2016-11-14 02:00 | 2610 | 712.44 | 401 | 1240 | 1673.3333 | 0
2016-11-14 03:00 | 2610 | 709.12 | 346 | 1240 | 1673.3333 | 0
2016-11-14 04:00 | 2610 | 714.74 | 389 | 1240 | 1673.3333 | 0
2016-11-14 05:00 | 2610 | 731.32 | 562 | 1240 | 1673.3333 | 0
2016-11-14 06:00 | 2535 | 755.84 | 726 | 1240 | 1673.3333 | 0
2016-11-14 07:00 | 2535 | 780.04 | 469 | 1240 | 1673.3333 | 0
2016-11-14 08:00 | 2535 | 810.4 | 442 | 1240 | 1673.3333 | 0
2016-11-14 09:00 | 2535 | 823.8 | 446 | 1240 | 1673.3333 | 0
2016-11-14 10:00 | 2687 | 784.301 | 528 | 1240 | 1521.4286 | 0
2016-11-14 11:00 | 2687 | 779.589 | 532 | 1240 | 1521.4286 | 0
2016-11-14 12:00 | 2687 | 777.005 | 379 | 1240 | 1521.4286 | 0
2016-11-14 13:00 | 2687 | 770.944 | 429 | 1240 | 1521.4286 | 0
2016-11-14 14:00 | 2519 | 765.168 | 366 | 1240 | 1521.4286 | 0
2016-11-14 15:00 | 2519 | 764.142 | 335 | 1240 | 1430.7692 | 0
2016-11-14 16:00 | 2519 | 776.511 | 418 | 1240 | 1430.7692 | 0
2016-11-14 17:00 | 2519 | 865 | 638 | 1240 | 1430.7692 | 0
2016-11-14 18:00 | 3598 | 884.1 | 524 | 1240 | 1430.7692 | 0
2016-11-14 19:00 | 3598 | 903.18 | 385 | 1240 | 1430.7692 | 0
2016-11-14 20:00 | 3598 | 886.44 | 429 | 1240 | 1430.7692 | 0
2016-11-14 21:00 | 3598 | 854.5 | 326 | 1240 | 1430.7692 | 0
2016-11-14 22:00 | 2662 | 763.648 | 312 | 1240 | 1521.4286 | 0
2016-11-14 23:00 | 2662 | 752.46 | 312 | 1240 | 1673.3333 | 0
2016-11-15 | 2662 | 598.752 | 624 | 1240 | 1673.3333 | 0
2016-11-15 01:00 | 2662 | 584.478 | 312 | 1240 | 1673.3333 | 0
2016-11-15 02:00 | 2610 | 579.618 | 401 | 1240 | 1673.3333 | 0
2016-11-15 03:00 | 2610 | 584.01 | 346 | 1240 | 1673.3333 | 0
2016-11-15 04:00 | 2610 | 601.542 | 389 | 1240 | 1673.3333 | 0
2016-11-15 05:00 | 2610 | 722.04 | 562 | 1240 | 1673.3333 | 0
2016-11-15 06:00 | 2535 | 813.52 | 726 | 1240 | 1521.4286 | 0
2016-11-15 07:00 | 2535 | 794.808 | 469 | 1240 | 1521.4286 | 0
2016-11-15 08:00 | 2535 | 789.507 | 442 | 1240 | 1521.4286 | 0
2016-11-15 09:00 | 2535 | 790.913 | 446 | 1240 | 1521.4286 | 0
2016-11-15 10:00 | 2687 | 793.212 | 528 | 1240 | 1521.4286 | 0
2016-11-15 11:00 | 2687 | 791.16 | 532 | 1240 | 1521.4286 | 0
2016-11-15 12:00 | 2687 | 785.669 | 379 | 1240 | 1521.4286 | 0
2016-11-15 13:00 | 2687 | 828.84 | 429 | 1240 | 1521.4286 | 0
2016-11-15 14:00 | 2519 | 825.64 | 366 | 1240 | 1521.4286 | 0
2016-11-15 15:00 | 2519 | 826.74 | 335 | 1240 | 1521.4286 | 0
2016-11-15 16:00 | 2519 | 839.24 | 418 | 1240 | 1521.4286 | 0
2016-11-15 17:00 | 2519 | 825.227 | 638 | 1240 | 1521.4286 | 0
2016-11-15 18:00 | 3598 | 830.186 | 524 | 1240 | 1430.7692 | 0
2016-11-15 19:00 | 3598 | 835.164 | 385 | 1240 | 1430.7692 | 0
2016-11-15 20:00 | 3598 | 817.57 | 429 | 1240 | 1430.7692 | 0
2016-11-15 21:00 | 3598 | 783.712 | 326 | 1240 | 1430.7692 | 0
2016-11-15 22:00 | 2662 | 725.648 | 312 | 1240 | 1521.4286 | 0
2016-11-15 23:00 | 2662 | 711.42 | 312 | 1240 | 1521.4286 | 0
2016-11-16 | 2662 | 662.2 | 624 | 1240 | 1521.4286 | 0
2016-11-16 01:00 | 2662 | 579.636 | 312 | 1240 | 1673.3333 | 0
2016-11-16 02:00 | 2610 | 574.506 | 401 | 1240 | 1673.3333 | 0
2016-11-16 03:00 | 2610 | 576.864 | 346 | 1240 | 1673.3333 | 0
2016-11-16 04:00 | 2610 | 593.262 | 389 | 1240 | 1673.3333 | 0
2016-11-16 05:00 | 2610 | 642.258 | 562 | 1240 | 1521.4286 | 0
2016-11-16 06:00 | 2535 | 802 | 726 | 1240 | 1521.4286 | 0
2016-11-16 07:00 | 2535 | 779.266 | 469 | 1240 | 1521.4286 | 0
2016-11-16 08:00 | 2535 | 810.54 | 442 | 1240 | 1521.4286 | 0
2016-11-16 09:00 | 2535 | 769.367 | 446 | 1240 | 1521.4286 | 0
2016-11-16 10:00 | 2687 | 768.512 | 528 | 1240 | 1521.4286 | 0
2016-11-16 11:00 | 2687 | 763.857 | 532 | 1240 | 1521.4286 | 0
2016-11-16 12:00 | 2687 | 758.499 | 379 | 1240 | 1521.4286 | 0
2016-11-16 13:00 | 2687 | 757.872 | 429 | 1240 | 1521.4286 | 0
2016-11-16 14:00 | 2519 | 756.903 | 366 | 1240 | 1521.4286 | 0
2016-11-16 15:00 | 2519 | 796.52 | 335 | 1240 | 1521.4286 | 0
2016-11-16 16:00 | 2519 | 800 | 418 | 1240 | 1521.4286 | 0
2016-11-16 17:00 | 2519 | 780.957 | 638 | 1240 | 1521.4286 | 0
2016-11-16 18:00 | 3598 | 795.34 | 524 | 1240 | 1521.4286 | 0
2016-11-16 19:00 | 3598 | 852.34 | 385 | 1240 | 1673.3333 | 0
2016-11-16 20:00 | 3598 | 837.66 | 429 | 1240 | 1673.3333 | 0
2016-11-16 21:00 | 3598 | 726.462 | 326 | 1240 | 1730 | 0
2016-11-16 22:00 | 2662 | 683.514 | 312 | 1240 | 1730 | 0
2016-11-16 23:00 | 2662 | 636.66 | 312 | 1240 | 1730 | 0
2016-11-17 | 2662 | 572.22 | 624 | 1240 | 1730 | 0
2016-11-17 01:00 | 2662 | 559.8 | 312 | 1240 | 1730 | 0
2016-11-17 02:00 | 2610 | 555.912 | 401 | 1240 | 1730 | 0
2016-11-17 03:00 | 2610 | 557.514 | 346 | 1240 | 1730 | 0
2016-11-17 04:00 | 2610 | 572.346 | 389 | 1240 | 1730 | 0
2016-11-17 05:00 | 2610 | 614.7 | 562 | 1240 | 1730 | 0
2016-11-17 06:00 | 2535 | 689.022 | 726 | 1240 | 1730 | 0
2016-11-17 07:00 | 2535 | 697.77 | 469 | 1240 | 1730 | 0
2016-11-17 08:00 | 2535 | 686.466 | 442 | 1240 | 1730 | 0
2016-11-17 09:00 | 2535 | 683.748 | 446 | 1240 | 1730 | 0
2016-11-17 10:00 | 2687 | 684.27 | 528 | 1240 | 1730 | 0
2016-11-17 11:00 | 2687 | 686.538 | 532 | 1240 | 1730 | 0
2016-11-17 12:00 | 2687 | 687.006 | 379 | 1240 | 1730 | 0
2016-11-17 13:00 | 2687 | 697.914 | 429 | 1240 | 1730 | 0
2016-11-17 14:00 | 2519 | 699.714 | 366 | 1240 | 1730 | 0
2016-11-17 15:00 | 2519 | 701.046 | 335 | 1240 | 1730 | 0
2016-11-17 16:00 | 2519 | 701.154 | 418 | 1240 | 1730 | 0
2016-11-17 17:00 | 2519 | 795.6 | 638 | 1240 | 1730 | 0
2016-11-17 18:00 | 3598 | 802.16 | 524 | 1240 | 1730 | 0
2016-11-17 19:00 | 3598 | 808.72 | 385 | 1240 | 1730 | 0
2016-11-17 20:00 | 3598 | 794.08 | 429 | 1240 | 1730 | 0
2016-11-17 21:00 | 3598 | 765.88 | 326 | 1240 | 1730 | 0
2016-11-17 22:00 | 2662 | 715.26 | 312 | 1240 | 1730 | 0
2016-11-17 23:00 | 2662 | 663 | 312 | 1240 | 1730 | 0
2016-11-18 | 2662 | 579.636 | 624 | 1240 | 1730 | 0
2016-11-18 01:00 | 2662 | 565.668 | 312 | 1240 | 1730 | 0
2016-11-18 02:00 | 2610 | 561.186 | 401 | 1240 | 1730 | 0
2016-11-18 03:00 | 2610 | 564.624 | 346 | 1240 | 1730 | 0
2016-11-18 04:00 | 2610 | 583.344 | 389 | 1240 | 1730 | 0
2016-11-18 05:00 | 2610 | 705.82 | 562 | 1240 | 1673.3333 | 0
2016-11-18 06:00 | 2535 | 755.516 | 726 | 1240 | 1521.4286 | 0
2016-11-18 07:00 | 2535 | 773.604 | 469 | 1240 | 1521.4286 | 0
2016-11-18 08:00 | 2535 | 764.503 | 442 | 1240 | 1521.4286 | 0
2016-11-18 09:00 | 2535 | 763.287 | 446 | 1240 | 1521.4286 | 0
2016-11-18 10:00 | 2687 | 756.447 | 528 | 1240 | 1521.4286 | 0
2016-11-18 11:00 | 2687 | 743.793 | 532 | 1240 | 1521.4286 | 0
2016-11-18 12:00 | 2687 | 739.67 | 379 | 1240 | 1521.4286 | 0
2016-11-18 13:00 | 2687 | 736.041 | 429 | 1240 | 1521.4286 | 0
2016-11-18 14:00 | 2519 | 729.562 | 366 | 1240 | 1521.4286 | 0
2016-11-18 15:00 | 2519 | 726.446 | 335 | 1240 | 1521.4286 | 0
2016-11-18 16:00 | 2519 | 729.353 | 418 | 1240 | 1521.4286 | 0
2016-11-18 17:00 | 2519 | 755.326 | 638 | 1240 | 1521.4286 | 0
2016-11-18 18:00 | 3598 | 773.205 | 524 | 1240 | 1521.4286 | 0
2016-11-18 19:00 | 3598 | 791.084 | 385 | 1240 | 1521.4286 | 0
2016-11-18 20:00 | 3598 | 826.02 | 429 | 1240 | 1673.3333 | 0
2016-11-18 21:00 | 3598 | 802.74 | 326 | 1240 | 1730 | 0
2016-11-18 22:00 | 2662 | 679.374 | 312 | 1240 | 1730 | 0
2016-11-18 23:00 | 2662 | 639.756 | 312 | 1240 | 1730 | 0
2016-11-19 | 2662 | 635.958 | 624 | 1240 | 1730 | 0
2016-11-19 01:00 | 2662 | 632.43 | 312 | 1240 | 1730 | 0
2016-11-19 02:00 | 2610 | 631.458 | 401 | 1240 | 1730 | 0
2016-11-19 03:00 | 2610 | 636.822 | 346 | 1240 | 1730 | 0
2016-11-19 04:00 | 2610 | 656.46 | 389 | 1240 | 1730 | 0
2016-11-19 05:00 | 2610 | 710.478 | 562 | 1240 | 1730 | 0
2016-11-19 06:00 | 2535 | 882.86 | 726 | 1240 | 1673.3333 | 0
2016-11-19 07:00 | 2535 | 853.233 | 469 | 1240 | 1521.4286 | 0
2016-11-19 08:00 | 2535 | 872.42 | 442 | 1240 | 1521.4286 | 0
2016-11-19 09:00 | 2535 | 855.18 | 446 | 1240 | 1521.4286 | 0
2016-11-19 10:00 | 2687 | 846.32 | 528 | 1240 | 1521.4286 | 0
2016-11-19 11:00 | 2687 | 828.84 | 532 | 1240 | 1521.4286 | 0
2016-11-19 12:00 | 2687 | 814.12 | 379 | 1240 | 1521.4286 | 0
2016-11-19 13:00 | 2687 | 769.272 | 429 | 1240 | 1521.4286 | 0
2016-11-19 14:00 | 2519 | 763.078 | 366 | 1240 | 1521.4286 | 0
2016-11-19 15:00 | 2519 | 759.544 | 335 | 1240 | 1521.4286 | 0
2016-11-19 16:00 | 2519 | 796.64 | 418 | 1240 | 1673.3333 | 0
2016-11-19 17:00 | 2519 | 815.86 | 638 | 1240 | 1673.3333 | 0
2016-11-19 18:00 | 3598 | 819.9 | 524 | 1240 | 1673.3333 | 0
2016-11-19 19:00 | 3598 | 823.94 | 385 | 1240 | 1673.3333 | 0
2016-11-19 20:00 | 3598 | 810.98 | 429 | 1240 | 1673.3333 | 0
2016-11-19 21:00 | 3598 | 710.802 | 326 | 1240 | 1730 | 0
2016-11-19 22:00 | 2662 | 681.084 | 312 | 1240 | 1730 | 0
2016-11-19 23:00 | 2662 | 645.786 | 312 | 1240 | 1730 | 0
2016-11-20 | 2662 | 643.158 | 624 | 1240 | 1730 | 0
2016-11-20 01:00 | 2662 | 641.556 | 312 | 1240 | 1730 | 0
2016-11-20 02:00 | 2610 | 631.872 | 401 | 1240 | 1730 | 0
2016-11-20 03:00 | 2610 | 629.352 | 346 | 1240 | 1730 | 0
2016-11-20 04:00 | 2610 | 635.202 | 389 | 1240 | 1730 | 0
2016-11-20 05:00 | 2610 | 654.714 | 562 | 1240 | 1730 | 0
2016-11-20 06:00 | 2535 | 685.44 | 726 | 1240 | 1730 | 0
2016-11-20 07:00 | 2535 | 784.12 | 469 | 1240 | 1730 | 0
2016-11-20 08:00 | 2535 | 814.84 | 442 | 1240 | 1673.3333 | 0
2016-11-20 09:00 | 2535 | 833.26 | 446 | 1240 | 1673.3333 | 0
2016-11-20 10:00 | 2687 | 838.74 | 528 | 1240 | 1521.4286 | 0
2016-11-20 11:00 | 2687 | 796.176 | 532 | 1240 | 1521.4286 | 0
2016-11-20 12:00 | 2687 | 788.215 | 379 | 1240 | 1521.4286 | 0
2016-11-20 13:00 | 2687 | 781.223 | 429 | 1240 | 1521.4286 | 0
2016-11-20 14:00 | 2519 | 774.193 | 366 | 1240 | 1521.4286 | 0
2016-11-20 15:00 | 2519 | 772.122 | 335 | 1240 | 1521.4286 | 0
2016-11-20 16:00 | 2519 | 811.6 | 418 | 1240 | 1521.4286 | 0
2016-11-20 17:00 | 2519 | 800.052 | 638 | 1240 | 1521.4286 | 0
2016-11-20 18:00 | 3598 | 851.4 | 524 | 1240 | 1521.4286 | 0
2016-11-20 19:00 | 3598 | 860.66 | 385 | 1240 | 1673.3333 | 0
2016-11-20 20:00 | 3598 | 843.96 | 429 | 1240 | 1730 | 0
2016-11-20 21:00 | 3598 | 740.268 | 326 | 1240 | 1730 | 0
2016-11-20 22:00 | 2662 | 706.716 | 312 | 1240 | 1730 | 0
2016-11-20 23:00 | 2662 | 669.06 | 312 | 1240 | 1730 | 0
2016-11-21 | 2662 | 654.57 | 624 | 1240 | 1730 | 0
2016-11-21 01:00 | 2662 | 634.95 | 312 | 1240 | 1730 | 0
2016-11-21 02:00 | 2610 | 621.45 | 401 | 1240 | 1730 | 0
2016-11-21 03:00 | 2610 | 613.818 | 346 | 1240 | 1730 | 0
2016-11-21 04:00 | 2610 | 612.432 | 389 | 1240 | 1730 | 0
2016-11-21 05:00 | 2610 | 620.946 | 562 | 1240 | 1730 | 0
2016-11-21 06:00 | 2535 | 635.274 | 726 | 1240 | 1730 | 0
2016-11-21 07:00 | 2535 | 648.9 | 469 | 1240 | 1730 | 0
2016-11-21 08:00 | 2535 | 692.208 | 442 | 1240 | 1730 | 0
2016-11-21 09:00 | 2535 | 725.652 | 446 | 1240 | 1730 | 0
2016-11-21 10:00 | 2687 | 833.64 | 528 | 1240 | 1730 | 0
2016-11-21 11:00 | 2687 | 856.06 | 532 | 1240 | 1673.3333 | 0
2016-11-21 12:00 | 2687 | 870.68 | 379 | 1240 | 1673.3333 | 0
2016-11-21 13:00 | 2687 | 880.18 | 429 | 1240 | 1673.3333 | 0
2016-11-21 14:00 | 2519 | 887.6 | 366 | 1240 | 1521.4286 | 0
2016-11-21 15:00 | 2519 | 890.42 | 335 | 1240 | 1521.4286 | 0
2016-11-21 16:00 | 2519 | 887.2 | 418 | 1240 | 1521.4286 | 0
2016-11-21 17:00 | 2519 | 869.269 | 638 | 1240 | 1521.4286 | 0
2016-11-21 18:00 | 3598 | 882.474 | 524 | 1240 | 1521.4286 | 0
2016-11-21 19:00 | 3598 | 895.679 | 385 | 1240 | 1521.4286 | 0
2016-11-21 20:00 | 3598 | 876.109 | 429 | 1240 | 1521.4286 | 0
2016-11-21 21:00 | 3598 | 890.48 | 326 | 1240 | 1521.4286 | 0
2016-11-21 22:00 | 2662 | 839.86 | 312 | 1240 | 1673.3333 | 0
2016-11-21 23:00 | 2662 | 705.456 | 312 | 1240 | 1673.3333 | 0
2016-11-22 | 2662 | 575.046 | 624 | 1240 | 1730 | 0
2016-11-22 01:00 | 2662 | 555.336 | 312 | 1240 | 1730 | 0
2016-11-22 02:00 | 2610 | 543.114 | 401 | 1240 | 1730 | 0
2016-11-22 03:00 | 2610 | 540.81 | 346 | 1240 | 1730 | 0
2016-11-22 04:00 | 2610 | 549.27 | 389 | 1240 | 1730 | 0
2016-11-22 05:00 | 2610 | 582.498 | 562 | 1240 | 1730 | 0
2016-11-22 06:00 | 2535 | 640.224 | 726 | 1240 | 1730 | 0
2016-11-22 07:00 | 2535 | 742.82 | 469 | 1240 | 1730 | 0
2016-11-22 08:00 | 2535 | 764.12 | 442 | 1240 | 1730 | 0
2016-11-22 09:00 | 2535 | 793.56 | 446 | 1240 | 1673.3333 | 0
2016-11-22 10:00 | 2687 | 819 | 528 | 1240 | 1673.3333 | 0
2016-11-22 11:00 | 2687 | 797.924 | 532 | 1240 | 1521.4286 | 0
2016-11-22 12:00 | 2687 | 808.412 | 379 | 1240 | 1521.4286 | 0
2016-11-22 13:00 | 2687 | 824.79 | 429 | 1240 | 1521.4286 | 0
2016-11-22 14:00 | 2519 | 835.468 | 366 | 1240 | 1521.4286 | 0
2016-11-22 15:00 | 2519 | 835.715 | 335 | 1240 | 1521.4286 | 0
2016-11-22 16:00 | 2519 | 829.977 | 418 | 1240 | 1521.4286 | 0
2016-11-22 17:00 | 2519 | 834.195 | 638 | 1240 | 1521.4286 | 0
2016-11-22 18:00 | 3598 | 836.589 | 524 | 1240 | 1521.4286 | 0
2016-11-22 19:00 | 3598 | 838.983 | 385 | 1240 | 1521.4286 | 0
2016-11-22 20:00 | 3598 | 820.382 | 429 | 1240 | 1521.4286 | 0
2016-11-22 21:00 | 3598 | 787.911 | 326 | 1240 | 1521.4286 | 0
2016-11-22 22:00 | 2662 | 778.76 | 312 | 1240 | 1673.3333 | 0
2016-11-22 23:00 | 2662 | 646.668 | 312 | 1240 | 1730 | 0
2016-11-23 | 2662 | 578.268 | 624 | 1240 | 1730 | 0
2016-11-23 01:00 | 2662 | 554.562 | 312 | 1240 | 1730 | 0
2016-11-23 02:00 | 2610 | 541.278 | 401 | 1240 | 1730 | 0
2016-11-23 03:00 | 2610 | 536.454 | 346 | 1240 | 1730 | 0
2016-11-23 04:00 | 2610 | 542.808 | 389 | 1240 | 1730 | 0
2016-11-23 05:00 | 2610 | 571.248 | 562 | 1240 | 1730 | 0
2016-11-23 06:00 | 2535 | 694.52 | 726 | 1240 | 1673.3333 | 0
2016-11-23 07:00 | 2535 | 718.1 | 469 | 1240 | 1521.4286 | 0
2016-11-23 08:00 | 2535 | 697.319 | 442 | 1240 | 1521.4286 | 0
2016-11-23 09:00 | 2535 | 719.606 | 446 | 1240 | 1430.7692 | 0
2016-11-23 10:00 | 2687 | 783.84 | 528 | 1240 | 1430.7692 | 0
2016-11-23 11:00 | 2687 | 802.04 | 532 | 1240 | 1430.7692 | 0
2016-11-23 12:00 | 2687 | 816.06 | 379 | 1240 | 1430.7692 | 0
2016-11-23 13:00 | 2687 | 832.32 | 429 | 1240 | 1430.7692 | 0
2016-11-23 14:00 | 2519 | 841.34 | 366 | 1240 | 1430.7692 | 0
2016-11-23 15:00 | 2519 | 839.26 | 335 | 1240 | 1430.7692 | 0
2016-11-23 16:00 | 2519 | 784.909 | 418 | 1240 | 1430.7692 | 0
2016-11-23 17:00 | 2519 | 787.873 | 638 | 1240 | 1430.7692 | 0
2016-11-23 18:00 | 3598 | 788.272 | 524 | 1240 | 1430.7692 | 0
2016-11-23 19:00 | 3598 | 788.652 | 385 | 1240 | 1521.4286 | 0
2016-11-23 20:00 | 3598 | 769.348 | 429 | 1240 | 1521.4286 | 0
2016-11-23 21:00 | 3598 | 781.64 | 326 | 1240 | 1673.3333 | 0
2016-11-23 22:00 | 2662 | 744.56 | 312 | 1240 | 1730 | 0
2016-11-23 23:00 | 2662 | 624.816 | 312 | 1240 | 1730 | 0
2016-11-24 | 2662 | 606.654 | 624 | 1240 | 1730 | 0
2016-11-24 01:00 | 2662 | 585.144 | 312 | 1240 | 1730 | 0
2016-11-24 02:00 | 2610 | 573.93 | 401 | 1240 | 1730 | 0
2016-11-24 03:00 | 2610 | 567.81 | 346 | 1240 | 1730 | 0
2016-11-24 04:00 | 2610 | 572.76 | 389 | 1240 | 1730 | 0
2016-11-24 05:00 | 2610 | 598.896 | 562 | 1240 | 1730 | 0
2016-11-24 06:00 | 2535 | 640.53 | 726 | 1240 | 1730 | 0
2016-11-24 07:00 | 2535 | 665.802 | 469 | 1240 | 1730 | 0
2016-11-24 08:00 | 2535 | 693.522 | 442 | 1240 | 1730 | 0
2016-11-24 09:00 | 2535 | 810.1 | 446 | 1240 | 1730 | 0
2016-11-24 10:00 | 2687 | 845.1 | 528 | 1240 | 1673.3333 | 0
2016-11-24 11:00 | 2687 | 866.38 | 532 | 1240 | 1673.3333 | 0
2016-11-24 12:00 | 2687 | 877.08 | 379 | 1240 | 1673.3333 | 0
2016-11-24 13:00 | 2687 | 889.88 | 429 | 1240 | 1673.3333 | 0
2016-11-24 14:00 | 2519 | 847.78 | 366 | 1240 | 1521.4286 | 0
2016-11-24 15:00 | 2519 | 845.101 | 335 | 1240 | 1521.4286 | 0
2016-11-24 16:00 | 2519 | 829.711 | 418 | 1240 | 1521.4286 | 0
2016-11-24 17:00 | 2519 | 834.727 | 638 | 1240 | 1521.4286 | 0
2016-11-24 18:00 | 3598 | 832.409 | 524 | 1240 | 1521.4286 | 0
2016-11-24 19:00 | 3598 | 873.78 | 385 | 1240 | 1521.4286 | 0
2016-11-24 20:00 | 3598 | 851.72 | 429 | 1240 | 1673.3333 | 0
2016-11-24 21:00 | 3598 | 822.58 | 326 | 1240 | 1673.3333 | 0
2016-11-24 22:00 | 2662 | 781.68 | 312 | 1240 | 1730 | 0
2016-11-24 23:00 | 2662 | 657.936 | 312 | 1240 | 1730 | 0
2016-11-25 | 2662 | 657.558 | 624 | 1240 | 1730 | 0
2016-11-25 01:00 | 2662 | 657.216 | 312 | 1240 | 1730 | 0
2016-11-25 02:00 | 2610 | 635.958 | 401 | 1240 | 1730 | 0
2016-11-25 03:00 | 2610 | 624.186 | 346 | 1240 | 1730 | 0
2016-11-25 04:00 | 2610 | 621.738 | 389 | 1240 | 1730 | 0
2016-11-25 05:00 | 2610 | 632.088 | 562 | 1240 | 1730 | 0
2016-11-25 06:00 | 2535 | 647.982 | 726 | 1240 | 1730 | 0
2016-11-25 07:00 | 2535 | 663.642 | 469 | 1240 | 1730 | 0
2016-11-25 08:00 | 2535 | 711.072 | 442 | 1240 | 1730 | 0
2016-11-25 09:00 | 2535 | 852.96 | 446 | 1240 | 1673.3333 | 0
2016-11-25 10:00 | 2687 | 855.494 | 528 | 1240 | 1521.4286 | 0
2016-11-25 11:00 | 2687 | 876.926 | 532 | 1240 | 1521.4286 | 0
2016-11-25 12:00 | 2687 | 866.362 | 379 | 1240 | 1521.4286 | 0
2016-11-25 13:00 | 2687 | 885.78 | 429 | 1240 | 1521.4286 | 0
2016-11-25 14:00 | 2519 | 860 | 366 | 1240 | 1521.4286 | 0
2016-11-25 15:00 | 2519 | 838.52 | 335 | 1240 | 1521.4286 | 0
2016-11-25 16:00 | 2519 | 819.48 | 418 | 1240 | 1521.4286 | 0
2016-11-25 17:00 | 2519 | 785.726 | 638 | 1240 | 1521.4286 | 0
2016-11-25 18:00 | 3598 | 786.467 | 524 | 1240 | 1521.4286 | 0
2016-11-25 19:00 | 3598 | 787.189 | 385 | 1240 | 1521.4286 | 0
2016-11-25 20:00 | 3598 | 780.634 | 429 | 1240 | 1521.4286 | 0
2016-11-25 21:00 | 3598 | 770.792 | 326 | 1240 | 1521.4286 | 0
2016-11-25 22:00 | 2662 | 755.155 | 312 | 1240 | 1521.4286 | 0
2016-11-25 23:00 | 2662 | 734.027 | 312 | 1240 | 1521.4286 | 0
2016-11-26 | 2662 | 739.689 | 624 | 1240 | 1521.4286 | 0
2016-11-26 01:00 | 2662 | 750.937 | 312 | 1240 | 1521.4286 | 0
2016-11-26 02:00 | 2610 | 746.472 | 401 | 1240 | 1521.4286 | 0
2016-11-26 03:00 | 2610 | 750.253 | 346 | 1240 | 1521.4286 | 0
2016-11-26 04:00 | 2610 | 765.187 | 389 | 1240 | 1521.4286 | 0
2016-11-26 05:00 | 2610 | 794.428 | 562 | 1240 | 1430.7692 | 0
2016-11-26 06:00 | 2535 | 877.72 | 726 | 1240 | 1430.7692 | 0
2016-11-26 07:00 | 2535 | 904.98 | 469 | 1240 | 1440 | 0
2016-11-26 08:00 | 2535 | 923.48 | 442 | 1240 | 1440 | 0
2016-11-26 09:00 | 2535 | 932.06 | 446 | 1240 | 1440 | 0
2016-11-26 10:00 | 2687 | 926.26 | 528 | 1240 | 1440 | 0
2016-11-26 11:00 | 2687 | 906.68 | 532 | 1240 | 1440 | 0
2016-11-26 12:00 | 2687 | 879.32 | 379 | 1240 | 1440 | 0
2016-11-26 13:00 | 2687 | 852.98 | 429 | 1240 | 1440 | 0
2016-11-26 14:00 | 2519 | 831.78 | 366 | 1240 | 1440 | 0
2016-11-26 15:00 | 2519 | 822.26 | 335 | 1240 | 1440 | 0
2016-11-26 16:00 | 2519 | 828.52 | 418 | 1240 | 1440 | 0
2016-11-26 17:00 | 2519 | 882.66 | 638 | 1240 | 1440 | 0
2016-11-26 18:00 | 3598 | 870.428 | 524 | 1240 | 1238.9381 | 0
2016-11-26 19:00 | 3598 | 902.329 | 385 | 1240 | 1238.9381 | 0
2016-11-26 20:00 | 3598 | 905.559 | 429 | 1240 | 1238.9381 | 0
2016-11-26 21:00 | 3598 | 899.042 | 326 | 1240 | 1238.9381 | 0
2016-11-26 22:00 | 2662 | 879.529 | 312 | 1240 | 1440 | 0
2016-11-26 23:00 | 2662 | 896.3 | 312 | 1240 | 1440 | 0
2016-11-27 | 2662 | 797.126 | 624 | 1240 | 1440 | 0
2016-11-27 01:00 | 2662 | 787.056 | 312 | 1240 | 1430.7692 | 0
2016-11-27 02:00 | 2610 | 784.358 | 401 | 1240 | 1430.7692 | 0
2016-11-27 03:00 | 2610 | 789.45 | 346 | 1240 | 1430.7692 | 0
2016-11-27 04:00 | 2610 | 801.705 | 389 | 1240 | 1430.7692 | 0
2016-11-27 05:00 | 2610 | 826.709 | 562 | 1240 | 1430.7692 | 0
2016-11-27 06:00 | 2535 | 861.327 | 726 | 1240 | 1430.7692 | 0
2016-11-27 07:00 | 2535 | 928.52 | 469 | 1240 | 1430.7692 | 0
2016-11-27 08:00 | 2535 | 931.96 | 442 | 1240 | 1430.7692 | 0
2016-11-27 09:00 | 2535 | 913.18 | 446 | 1240 | 1430.7692 | 0
2016-11-27 10:00 | 2687 | 838.945 | 528 | 1240 | 1430.7692 | 0
2016-11-27 11:00 | 2687 | 848.26 | 532 | 1240 | 1430.7692 | 0
2016-11-27 12:00 | 2687 | 814.42 | 379 | 1240 | 1430.7692 | 0
2016-11-27 13:00 | 2687 | 746.016 | 429 | 1240 | 1430.7692 | 0
2016-11-27 14:00 | 2519 | 727.054 | 366 | 1240 | 1521.4286 | 0
2016-11-27 15:00 | 2519 | 758.98 | 335 | 1240 | 1521.4286 | 0
2016-11-27 16:00 | 2519 | 764.26 | 418 | 1240 | 1521.4286 | 0
2016-11-27 17:00 | 2519 | 774.782 | 638 | 1240 | 1521.4286 | 0
2016-11-27 18:00 | 3598 | 803.757 | 524 | 1240 | 1521.4286 | 0
2016-11-27 19:00 | 3598 | 832.732 | 385 | 1240 | 1521.4286 | 0
2016-11-27 20:00 | 3598 | 878.16 | 429 | 1240 | 1673.3333 | 0
2016-11-27 21:00 | 3598 | 869.06 | 326 | 1240 | 1673.3333 | 0
2016-11-27 22:00 | 2662 | 847.66 | 312 | 1240 | 1673.3333 | 0
2016-11-27 23:00 | 2662 | 733.86 | 312 | 1240 | 1730 | 0
2016-11-28 | 2662 | 704.574 | 624 | 1240 | 1730 | 0
2016-11-28 01:00 | 2662 | 688.338 | 312 | 1240 | 1730 | 0
2016-11-28 02:00 | 2610 | 681.768 | 401 | 1240 | 1730 | 0
2016-11-28 03:00 | 2610 | 681.588 | 346 | 1240 | 1730 | 0
2016-11-28 04:00 | 2610 | 689.634 | 389 | 1240 | 1730 | 0
2016-11-28 05:00 | 2610 | 705.366 | 562 | 1240 | 1730 | 0
2016-11-28 06:00 | 2535 | 727.938 | 726 | 1240 | 1730 | 0
2016-11-28 07:00 | 2535 | 743.112 | 469 | 1240 | 1730 | 0
2016-11-28 08:00 | 2535 | 754.974 | 442 | 1240 | 1730 | 0
2016-11-28 09:00 | 2535 | 753.498 | 446 | 1240 | 1730 | 0
2016-11-28 10:00 | 2687 | 738.36 | 528 | 1240 | 1730 | 0
2016-11-28 11:00 | 2687 | 723.762 | 532 | 1240 | 1730 | 0
2016-11-28 12:00 | 2687 | 715.374 | 379 | 1240 | 1730 | 0
2016-11-28 13:00 | 2687 | 706.608 | 429 | 1240 | 1730 | 0
2016-11-28 14:00 | 2519 | 699.57 | 366 | 1240 | 1730 | 0
2016-11-28 15:00 | 2519 | 698.616 | 335 | 1240 | 1730 | 0
2016-11-28 16:00 | 2519 | 710.244 | 418 | 1240 | 1730 | 0
2016-11-28 17:00 | 2519 | 841.28 | 638 | 1240 | 1673.3333 | 0
2016-11-28 18:00 | 3598 | 862.76 | 524 | 1240 | 1673.3333 | 0
2016-11-28 19:00 | 3598 | 884.26 | 385 | 1240 | 1673.3333 | 0
2016-11-28 20:00 | 3598 | 867.66 | 429 | 1240 | 1730 | 0
2016-11-28 21:00 | 3598 | 749.862 | 326 | 1240 | 1730 | 0
2016-11-28 22:00 | 2662 | 704.934 | 312 | 1240 | 1730 | 0
2016-11-28 23:00 | 2662 | 652.77 | 312 | 1240 | 1730 | 0
2016-11-29 | 2662 | 576.432 | 624 | 1240 | 1730 | 0
2016-11-29 01:00 | 2662 | 559.728 | 312 | 1240 | 1730 | 0
2016-11-29 02:00 | 2610 | 553.482 | 401 | 1240 | 1730 | 0
2016-11-29 03:00 | 2610 | 554.346 | 346 | 1240 | 1730 | 0
2016-11-29 04:00 | 2610 | 566.946 | 389 | 1240 | 1730 | 0
2016-11-29 05:00 | 2610 | 609.264 | 562 | 1240 | 1730 | 0
2016-11-29 06:00 | 2535 | 675.45 | 726 | 1240 | 1730 | 0
2016-11-29 07:00 | 2535 | 777.68 | 469 | 1240 | 1673.3333 | 0
2016-11-29 08:00 | 2535 | 781.24 | 442 | 1240 | 1673.3333 | 0
2016-11-29 09:00 | 2535 | 797.58 | 446 | 1240 | 1673.3333 | 0
2016-11-29 10:00 | 2687 | 772.027 | 528 | 1240 | 1521.4286 | 0
2016-11-29 11:00 | 2687 | 786.676 | 532 | 1240 | 1521.4286 | 0
2016-11-29 12:00 | 2687 | 793.744 | 379 | 1240 | 1521.4286 | 0
2016-11-29 13:00 | 2687 | 804.118 | 429 | 1240 | 1521.4286 | 0
2016-11-29 14:00 | 2519 | 849.62 | 366 | 1240 | 1521.4286 | 0
2016-11-29 15:00 | 2519 | 849.04 | 335 | 1240 | 1521.4286 | 0
2016-11-29 16:00 | 2519 | 839.82 | 418 | 1240 | 1521.4286 | 0
2016-11-29 17:00 | 2519 | 819.945 | 638 | 1240 | 1521.4286 | 0
2016-11-29 18:00 | 3598 | 833.207 | 524 | 1240 | 1521.4286 | 0
2016-11-29 19:00 | 3598 | 846.469 | 385 | 1240 | 1521.4286 | 0
2016-11-29 20:00 | 3598 | 827.222 | 429 | 1240 | 1521.4286 | 0
2016-11-29 21:00 | 3598 | 793.06 | 326 | 1240 | 1521.4286 | 0
2016-11-29 22:00 | 2662 | 776.7 | 312 | 1240 | 1673.3333 | 0
2016-11-29 23:00 | 2662 | 715.86 | 312 | 1240 | 1673.3333 | 0
2016-11-30 | 2662 | 605.412 | 624 | 1240 | 1730 | 0
2016-11-30 01:00 | 2662 | 586.764 | 312 | 1240 | 1730 | 0
2016-11-30 02:00 | 2610 | 578.844 | 401 | 1240 | 1730 | 0
2016-11-30 03:00 | 2610 | 580.896 | 346 | 1240 | 1730 | 0
2016-11-30 04:00 | 2610 | 598.482 | 389 | 1240 | 1730 | 0
2016-11-30 05:00 | 2610 | 650.358 | 562 | 1240 | 1730 | 0
2016-11-30 06:00 | 2535 | 819.88 | 726 | 1240 | 1673.3333 | 0
2016-11-30 07:00 | 2535 | 854.94 | 469 | 1240 | 1673.3333 | 0
2016-11-30 08:00 | 2535 | 846.56 | 442 | 1240 | 1673.3333 | 0
2016-11-30 09:00 | 2535 | 851.28 | 446 | 1240 | 1673.3333 | 0
2016-11-30 10:00 | 2687 | 806.987 | 528 | 1240 | 1521.4286 | 0
2016-11-30 11:00 | 2687 | 808.26 | 532 | 1240 | 1521.4286 | 0
2016-11-30 12:00 | 2687 | 797.335 | 379 | 1240 | 1521.4286 | 0
2016-11-30 13:00 | 2687 | 788.557 | 429 | 1240 | 1521.4286 | 0
2016-11-30 14:00 | 2519 | 776.511 | 366 | 1240 | 1521.4286 | 0
2016-11-30 15:00 | 2519 | 770.013 | 335 | 1240 | 1521.4286 | 0
2016-11-30 16:00 | 2519 | 779.057 | 418 | 1240 | 1521.4286 | 0
2016-11-30 17:00 | 2519 | 868.88 | 638 | 1240 | 1430.7692 | 0
2016-11-30 18:00 | 3598 | 905.86 | 524 | 1240 | 1440 | 0
2016-11-30 19:00 | 3598 | 895.679 | 385 | 1240 | 1440 | 0
2016-11-30 20:00 | 3598 | 897.503 | 429 | 1240 | 1440 | 0
2016-11-30 21:00 | 3598 | 923.04 | 326 | 1240 | 1440 | 0
2016-11-30 22:00 | 2662 | 877.02 | 312 | 1240 | 1430.7692 | 0
2016-11-30 23:00 | 2662 | 786.657 | 312 | 1240 | 1430.7692 | 0
2016-12-01 | 3150 | 758.46 | 350 | 1240 | 1430.7692 | 0
2016-12-01 01:00 | 3150 | 748.78 | 336 | 1240 | 1521.4286 | 0
2016-12-01 02:00 | 3840 | 748.64 | 336 | 1240 | 1521.4286 | 0
2016-12-01 03:00 | 3840 | 757.74 | 398 | 1240 | 1521.4286 | 0
2016-12-01 04:00 | 3840 | 782.16 | 651 | 1240 | 1521.4286 | 0
2016-12-01 05:00 | 3840 | 804.365 | 832 | 1240 | 1521.4286 | 0
2016-12-01 06:00 | 4090 | 940.92 | 523 | 1240 | 1430.7692 | 0
2016-12-01 07:00 | 4090 | 952.88 | 389 | 1240 | 1430.7692 | 77.3508
2016-12-01 08:00 | 4090 | 860.814 | 336 | 1240 | 1430.7692 | 222.4168
2016-12-01 09:00 | 4090 | 820.762 | 436 | 1240 | 1521.4286 | 71.8094
2016-12-01 10:00 | 3148 | 789.355 | 399 | 1240 | 1521.4286 | 0
2016-12-01 11:00 | 3148 | 760.95 | 348 | 1240 | 1521.4286 | 0
2016-12-01 12:00 | 3148 | 736.022 | 427 | 1240 | 1521.4286 | 0
2016-12-01 13:00 | 3148 | 718.846 | 336 | 1240 | 1521.4286 | 0
2016-12-01 14:00 | 4512 | 710.353 | 336 | 1240 | 1521.4286 | 704.2184
2016-12-01 15:00 | 4512 | 703.551 | 420 | 1240 | 1521.4286 | 627.0204
2016-12-01 16:00 | 4512 | 710.695 | 656 | 1240 | 1521.4286 | 383.8764
2016-12-01 17:00 | 4512 | 749.208 | 526 | 1240 | 1521.4286 | 475.3634
2016-12-01 18:00 | 3971 | 778.316 | 401 | 1240 | 1521.4286 | 30.2554
2016-12-01 19:00 | 3971 | 807.424 | 336 | 1240 | 1521.4286 | 66.1474
2016-12-01 20:00 | 3971 | 806.569 | 336 | 1240 | 1521.4286 | 67.0024
2016-12-01 21:00 | 3971 | 787.588 | 336 | 1240 | 1521.4286 | 85.9834
2016-12-01 22:00 | 3150 | 782.48 | 336 | 1240 | 1673.3333 | 0
2016-12-01 23:00 | 3150 | 732.52 | 472 | 1240 | 1673.3333 | 0
2016-12-02 | 3150 | 651.024 | 350 | 1240 | 1673.3333 | 0
2016-12-02 01:00 | 3150 | 639.72 | 336 | 1240 | 1673.3333 | 0
2016-12-02 02:00 | 3840 | 707.82 | 336 | 1240 | 1673.3333 | 0
2016-12-02 03:00 | 3840 | 715 | 398 | 1240 | 1673.3333 | 0
2016-12-02 04:00 | 3840 | 739.52 | 651 | 1240 | 1673.3333 | 0
2016-12-02 05:00 | 3840 | 799.32 | 832 | 1240 | 1521.4286 | 0
2016-12-02 06:00 | 4090 | 848.882 | 523 | 1240 | 1430.7692 | 47.3488
2016-12-02 07:00 | 4090 | 860.396 | 389 | 1240 | 1430.7692 | 169.8348
2016-12-02 08:00 | 4090 | 823.175 | 336 | 1240 | 1430.7692 | 260.0558
2016-12-02 09:00 | 4090 | 833.14 | 436 | 1240 | 1430.7692 | 150.0908
2016-12-02 10:00 | 3148 | 770.735 | 399 | 1240 | 1430.7692 | 0
2016-12-02 11:00 | 3148 | 749.702 | 348 | 1240 | 1430.7692 | 0
2016-12-02 12:00 | 3148 | 735.49 | 427 | 1240 | 1430.7692 | 0
2016-12-02 13:00 | 3148 | 727.947 | 336 | 1240 | 1430.7692 | 0
2016-12-02 14:00 | 4512 | 721.81 | 336 | 1240 | 1430.7692 | 783.4208
2016-12-02 15:00 | 4512 | 720.138 | 420 | 1240 | 1430.7692 | 701.0928
2016-12-02 16:00 | 4512 | 724.071 | 656 | 1240 | 1430.7692 | 461.1598
2016-12-02 17:00 | 4512 | 794.82 | 526 | 1240 | 1430.7692 | 520.4108
2016-12-02 18:00 | 3971 | 815.1 | 401 | 1240 | 1430.7692 | 84.1308
2016-12-02 19:00 | 3971 | 835.38 | 336 | 1240 | 1430.7692 | 128.8508
2016-12-02 20:00 | 3971 | 825.98 | 336 | 1240 | 1430.7692 | 138.2508
2016-12-02 21:00 | 3971 | 759.848 | 336 | 1240 | 1430.7692 | 204.3828
2016-12-02 22:00 | 3150 | 714.172 | 336 | 1240 | 1521.4286 | 0
2016-12-02 23:00 | 3150 | 698.62 | 472 | 1240 | 1521.4286 | 0
2016-12-03 | 3150 | 704.62 | 350 | 1240 | 1521.4286 | 0
2016-12-03 01:00 | 3150 | 710.76 | 336 | 1240 | 1521.4286 | 0
2016-12-03 02:00 | 3840 | 705.38 | 336 | 1240 | 1521.4286 | 37.1914
2016-12-03 03:00 | 3840 | 710.72 | 398 | 1240 | 1521.4286 | 0
2016-12-03 04:00 | 3840 | 732.06 | 651 | 1240 | 1521.4286 | 0
2016-12-03 05:00 | 3840 | 754.11 | 832 | 1240 | 1521.4286 | 0
2016-12-03 06:00 | 4090 | 848.939 | 523 | 1240 | 1430.7692 | 47.2918
2016-12-03 07:00 | 4090 | 914.04 | 389 | 1240 | 1430.7692 | 116.1908
2016-12-03 08:00 | 4090 | 846.222 | 336 | 1240 | 1430.7692 | 237.0088
2016-12-03 09:00 | 4090 | 830.813 | 436 | 1240 | 1521.4286 | 61.7584
2016-12-03 10:00 | 3148 | 820.572 | 399 | 1240 | 1521.4286 | 0
2016-12-03 11:00 | 3148 | 812.098 | 348 | 1240 | 1521.4286 | 0
2016-12-03 12:00 | 3148 | 806.056 | 427 | 1240 | 1521.4286 | 0
2016-12-03 13:00 | 3148 | 807.025 | 336 | 1240 | 1521.4286 | 0
2016-12-03 14:00 | 4512 | 806.512 | 336 | 1240 | 1521.4286 | 608.0594
2016-12-03 15:00 | 4512 | 802.142 | 420 | 1240 | 1521.4286 | 528.4294
2016-12-03 16:00 | 4512 | 799.672 | 656 | 1240 | 1521.4286 | 294.8994
2016-12-03 17:00 | 4512 | 823.992 | 526 | 1240 | 1521.4286 | 400.5794
2016-12-03 18:00 | 3971 | 830.091 | 401 | 1240 | 1673.3333 | 0
2016-12-03 19:00 | 3971 | 880.18 | 336 | 1240 | 1673.3333 | 0
2016-12-03 20:00 | 3971 | 860.48 | 336 | 1240 | 1673.3333 | 0
2016-12-03 21:00 | 3971 | 836.26 | 336 | 1240 | 1730 | 0
2016-12-03 22:00 | 3150 | 716.85 | 336 | 1240 | 1730 | 0
2016-12-03 23:00 | 3150 | 672.21 | 472 | 1240 | 1730 | 0
2016-12-04 | 3150 | 657.306 | 350 | 1240 | 1730 | 0
2016-12-04 01:00 | 3150 | 630.036 | 336 | 1240 | 1730 | 0
2016-12-04 02:00 | 3840 | 614.826 | 336 | 1240 | 1730 | 0
2016-12-04 03:00 | 3840 | 609.156 | 398 | 1240 | 1730 | 0
2016-12-04 04:00 | 3840 | 613.188 | 651 | 1240 | 1730 | 0
2016-12-04 05:00 | 3840 | 627.948 | 832 | 1240 | 1730 | 0
2016-12-04 06:00 | 4090 | 659.916 | 523 | 1240 | 1730 | 0
2016-12-04 07:00 | 4090 | 681.588 | 389 | 1240 | 1730 | 49.412
2016-12-04 08:00 | 4090 | 715.122 | 336 | 1240 | 1730 | 68.878
2016-12-04 09:00 | 4090 | 824.22 | 436 | 1240 | 1730 | 0
2016-12-04 10:00 | 3148 | 842.78 | 399 | 1240 | 1730 | 0
2016-12-04 11:00 | 3148 | 849.32 | 348 | 1240 | 1673.3333 | 0
2016-12-04 12:00 | 3148 | 851.38 | 427 | 1240 | 1673.3333 | 0
2016-12-04 13:00 | 3148 | 808.089 | 336 | 1240 | 1673.3333 | 0
2016-12-04 14:00 | 4512 | 808.393 | 336 | 1240 | 1673.3333 | 454.2737
2016-12-04 15:00 | 4512 | 805.163 | 420 | 1240 | 1673.3333 | 373.5037
2016-12-04 16:00 | 4512 | 804.593 | 656 | 1240 | 1521.4286 | 289.9784
2016-12-04 17:00 | 4512 | 835.335 | 526 | 1240 | 1521.4286 | 389.2364
2016-12-04 18:00 | 3971 | 849.338 | 401 | 1240 | 1521.4286 | 0
2016-12-04 19:00 | 3971 | 863.341 | 336 | 1240 | 1521.4286 | 10.2304
2016-12-04 20:00 | 3971 | 853.1 | 336 | 1240 | 1521.4286 | 20.4714
2016-12-04 21:00 | 3971 | 835.639 | 336 | 1240 | 1521.4286 | 37.9324
2016-12-04 22:00 | 3150 | 805.353 | 336 | 1240 | 1521.4286 | 0
2016-12-04 23:00 | 3150 | 765.833 | 472 | 1240 | 1521.4286 | 0
2016-12-05 | 3150 | 755.22 | 350 | 1240 | 1521.4286 | 0
2016-12-05 01:00 | 3150 | 735.04 | 336 | 1240 | 1521.4286 | 0
2016-12-05 02:00 | 3840 | 725.84 | 336 | 1240 | 1521.4286 | 16.7314
2016-12-05 03:00 | 3840 | 725.72 | 398 | 1240 | 1521.4286 | 0
2016-12-05 04:00 | 3840 | 735.5 | 651 | 1240 | 1521.4286 | 0
2016-12-05 05:00 | 3840 | 758.24 | 832 | 1240 | 1521.4286 | 0
2016-12-05 06:00 | 4090 | 753.255 | 523 | 1240 | 1521.4286 | 52.3164
2016-12-05 07:00 | 4090 | 780.387 | 389 | 1240 | 1521.4286 | 159.1844
2016-12-05 08:00 | 4090 | 817.665 | 336 | 1240 | 1430.7692 | 265.5658
2016-12-05 09:00 | 4090 | 879.5 | 436 | 1240 | 1430.7692 | 103.7308
2016-12-05 10:00 | 3148 | 876.72 | 399 | 1240 | 1430.7692 | 0
2016-12-05 11:00 | 3148 | 860.78 | 348 | 1240 | 1430.7692 | 0
2016-12-05 12:00 | 3148 | 846.04 | 427 | 1240 | 1430.7692 | 0
2016-12-05 13:00 | 3148 | 831.14 | 336 | 1240 | 1430.7692 | 0
2016-12-05 14:00 | 4512 | 815.76 | 336 | 1240 | 1430.7692 | 689.4708
2016-12-05 15:00 | 4512 | 812.46 | 420 | 1240 | 1430.7692 | 608.7708
2016-12-05 16:00 | 4512 | 828.92 | 656 | 1240 | 1430.7692 | 356.3108
2016-12-05 17:00 | 4512 | 850.782 | 526 | 1240 | 1440 | 455.218
2016-12-05 18:00 | 3971 | 891.442 | 401 | 1240 | 1238.9381 | 199.6199
2016-12-05 19:00 | 3971 | 932.102 | 336 | 1240 | 1238.9381 | 223.9599
2016-12-05 20:00 | 3971 | 932.558 | 336 | 1240 | 1440 | 22.442
2016-12-05 21:00 | 3971 | 961.98 | 336 | 1240 | 1440 | 0
2016-12-05 22:00 | 3150 | 914.9 | 336 | 1240 | 1430.7692 | 0
2016-12-05 23:00 | 3150 | 861.58 | 472 | 1240 | 1430.7692 | 0
2016-12-06 | 3150 | 732.013 | 350 | 1240 | 1440 | 0
2016-12-06 01:00 | 3150 | 724.128 | 336 | 1240 | 1440 | 0
2016-12-06 02:00 | 3840 | 726.902 | 336 | 1240 | 1440 | 97.098
2016-12-06 03:00 | 3840 | 739.062 | 398 | 1240 | 1440 | 22.938
2016-12-06 04:00 | 3840 | 768.588 | 651 | 1240 | 1440 | 0
2016-12-06 05:00 | 3840 | 878.58 | 832 | 1240 | 1440 | 0
2016-12-06 06:00 | 4090 | 936.32 | 523 | 1240 | 1238.9381 | 151.7419
2016-12-06 07:00 | 4090 | 960.431 | 389 | 1240 | 1238.9381 | 261.6309
2016-12-06 08:00 | 4090 | 931.266 | 336 | 1240 | 1440 | 142.734
2016-12-06 09:00 | 4090 | 900.771 | 436 | 1240 | 1440 | 73.229
2016-12-06 10:00 | 3148 | 874.171 | 399 | 1240 | 1440 | 0
2016-12-06 11:00 | 3148 | 846.013 | 348 | 1240 | 1440 | 0
2016-12-06 12:00 | 3148 | 863.12 | 427 | 1240 | 1440 | 0
2016-12-06 13:00 | 3148 | 844.74 | 336 | 1240 | 1440 | 0
2016-12-06 14:00 | 4512 | 824.44 | 336 | 1240 | 1440 | 671.56
2016-12-06 15:00 | 4512 | 816.74 | 420 | 1240 | 1440 | 595.26
2016-12-06 16:00 | 4512 | 832.34 | 656 | 1240 | 1440 | 343.66
2016-12-06 17:00 | 4512 | 857.679 | 526 | 1240 | 1440 | 448.321
2016-12-06 18:00 | 3971 | 897.503 | 401 | 1240 | 1440 | 0
2016-12-06 19:00 | 3971 | 937.346 | 336 | 1240 | 1440 | 17.654
2016-12-06 20:00 | 3971 | 937.916 | 336 | 1240 | 1440 | 17.084
2016-12-06 21:00 | 3971 | 963 | 336 | 1240 | 1440 | 0
2016-12-06 22:00 | 3150 | 907.18 | 336 | 1240 | 1430.7692 | 0
2016-12-06 23:00 | 3150 | 808.165 | 472 | 1240 | 1521.4286 | 0
2016-12-07 | 3150 | 807.24 | 350 | 1240 | 1521.4286 | 0
2016-12-07 01:00 | 3150 | 798.22 | 336 | 1240 | 1521.4286 | 0
2016-12-07 02:00 | 3840 | 795.46 | 336 | 1240 | 1521.4286 | 0
2016-12-07 03:00 | 3840 | 806.54 | 398 | 1240 | 1521.4286 | 0
2016-12-07 04:00 | 3840 | 790.077 | 651 | 1240 | 1521.4286 | 0
2016-12-07 05:00 | 3840 | 852.72 | 832 | 1240 | 1521.4286 | 0
2016-12-07 06:00 | 4090 | 990.1 | 523 | 1240 | 1430.7692 | 0
2016-12-07 07:00 | 4090 | 1001.52 | 389 | 1240 | 1430.7692 | 28.7108
2016-12-07 08:00 | 4090 | 914.451 | 336 | 1240 | 1521.4286 | 78.1204
2016-12-07 09:00 | 4090 | 878.332 | 436 | 1240 | 1521.4286 | 14.2394
2016-12-07 10:00 | 3148 | 853.119 | 399 | 1240 | 1521.4286 | 0
2016-12-07 11:00 | 3148 | 825.322 | 348 | 1240 | 1521.4286 | 0
2016-12-07 12:00 | 3148 | 801.154 | 427 | 1240 | 1521.4286 | 0
2016-12-07 13:00 | 3148 | 786.866 | 336 | 1240 | 1521.4286 | 0
2016-12-07 14:00 | 4512 | 775.162 | 336 | 1240 | 1521.4286 | 639.4094
2016-12-07 15:00 | 4512 | 777.119 | 420 | 1240 | 1521.4286 | 553.4524
2016-12-07 16:00 | 4512 | 798.399 | 656 | 1240 | 1521.4286 | 296.1724
2016-12-07 17:00 | 4512 | 850.193 | 526 | 1240 | 1521.4286 | 374.3784
2016-12-07 18:00 | 3971 | 867.73 | 401 | 1240 | 1521.4286 | 0
2016-12-07 19:00 | 3971 | 885.267 | 336 | 1240 | 1521.4286 | 0
2016-12-07 20:00 | 3971 | 876.299 | 336 | 1240 | 1521.4286 | 0
2016-12-07 21:00 | 3971 | 841.719 | 336 | 1240 | 1521.4286 | 31.8524
2016-12-07 22:00 | 3150 | 787.797 | 336 | 1240 | 1521.4286 | 0
2016-12-07 23:00 | 3150 | 771.56 | 472 | 1240 | 1521.4286 | 0
2016-12-08 | 3150 | 729.42 | 350 | 1240 | 1521.4286 | 0
2016-12-08 01:00 | 3150 | 714.54 | 336 | 1240 | 1521.4286 | 0
2016-12-08 02:00 | 3840 | 711.52 | 336 | 1240 | 1521.4286 | 31.0514
2016-12-08 03:00 | 3840 | 720.62 | 398 | 1240 | 1521.4286 | 0
2016-12-08 04:00 | 3840 | 709.764 | 651 | 1240 | 1521.4286 | 0
2016-12-08 05:00 | 3840 | 772.35 | 832 | 1240 | 1521.4286 | 0
2016-12-08 06:00 | 4090 | 911.24 | 523 | 1240 | 1430.7692 | 0
2016-12-08 07:00 | 4090 | 939.64 | 389 | 1240 | 1430.7692 | 90.5908
2016-12-08 08:00 | 4090 | 914.68 | 336 | 1240 | 1430.7692 | 168.5508
2016-12-08 09:00 | 4090 | 847.077 | 436 | 1240 | 1430.7692 | 136.1538
2016-12-08 10:00 | 3148 | 872.28 | 399 | 1240 | 1430.7692 | 0
2016-12-08 11:00 | 3148 | 852.62 | 348 | 1240 | 1430.7692 | 0
2016-12-08 12:00 | 3148 | 833.08 | 427 | 1240 | 1430.7692 | 0
2016-12-08 13:00 | 3148 | 819.02 | 336 | 1240 | 1430.7692 | 0
2016-12-08 14:00 | 4512 | 808.16 | 336 | 1240 | 1430.7692 | 697.0708
2016-12-08 15:00 | 4512 | 803.64 | 420 | 1240 | 1430.7692 | 617.5908
2016-12-08 16:00 | 4512 | 811.96 | 656 | 1240 | 1430.7692 | 373.2708
2016-12-08 17:00 | 4512 | 870.88 | 526 | 1240 | 1440 | 435.12
2016-12-08 18:00 | 3971 | 906.5 | 401 | 1240 | 1440 | 0
2016-12-08 19:00 | 3971 | 942.14 | 336 | 1240 | 1440 | 12.86
2016-12-08 20:00 | 3971 | 942.88 | 336 | 1240 | 1430.7692 | 21.3508
2016-12-08 21:00 | 3971 | 878.028 | 336 | 1240 | 1521.4286 | 0
2016-12-08 22:00 | 3150 | 831.725 | 336 | 1240 | 1521.4286 | 0
2016-12-08 23:00 | 3150 | 822.62 | 472 | 1240 | 1673.3333 | 0
2016-12-09 | 3150 | 675.81 | 350 | 1240 | 1673.3333 | 0
2016-12-09 01:00 | 3150 | 670.23 | 336 | 1240 | 1673.3333 | 0
2016-12-09 02:00 | 3840 | 671.724 | 336 | 1240 | 1673.3333 | 0
2016-12-09 03:00 | 3840 | 680.418 | 398 | 1240 | 1673.3333 | 0
2016-12-09 04:00 | 3840 | 704.646 | 651 | 1240 | 1673.3333 | 0
2016-12-09 05:00 | 3840 | 844.3 | 832 | 1240 | 1673.3333 | 0
2016-12-09 06:00 | 4090 | 894.083 | 523 | 1240 | 1521.4286 | 0
2016-12-09 07:00 | 4090 | 904.419 | 389 | 1240 | 1521.4286 | 35.1524
2016-12-09 08:00 | 4090 | 863.74 | 336 | 1240 | 1521.4286 | 128.8314
2016-12-09 09:00 | 4090 | 874.56 | 436 | 1240 | 1521.4286 | 18.0114
2016-12-09 10:00 | 3148 | 844.2 | 399 | 1240 | 1521.4286 | 0
2016-12-09 11:00 | 3148 | 812.78 | 348 | 1240 | 1521.4286 | 0
2016-12-09 12:00 | 3148 | 784.04 | 427 | 1240 | 1521.4286 | 0
2016-12-09 13:00 | 3148 | 765.9 | 336 | 1240 | 1521.4286 | 0
2016-12-09 14:00 | 4512 | 750.52 | 336 | 1240 | 1521.4286 | 664.0514
2016-12-09 15:00 | 4512 | 706.097 | 420 | 1240 | 1521.4286 | 624.4744
2016-12-09 16:00 | 4512 | 711.417 | 656 | 1240 | 1521.4286 | 383.1544
2016-12-09 17:00 | 4512 | 754.129 | 526 | 1240 | 1521.4286 | 470.4424
2016-12-09 18:00 | 3971 | 819.3 | 401 | 1240 | 1430.7692 | 79.9308
2016-12-09 19:00 | 3971 | 844.78 | 336 | 1240 | 1430.7692 | 119.4508
2016-12-09 20:00 | 3971 | 798.228 | 336 | 1240 | 1430.7692 | 166.0028
2016-12-09 21:00 | 3971 | 775.599 | 336 | 1240 | 1521.4286 | 97.9724
2016-12-09 22:00 | 3150 | 730.113 | 336 | 1240 | 1521.4286 | 0
2016-12-09 23:00 | 3150 | 715.84 | 472 | 1240 | 1521.4286 | 0
2016-12-10 | 3150 | 730.62 | 350 | 1240 | 1521.4286 | 0
2016-12-10 01:00 | 3150 | 738.66 | 336 | 1240 | 1521.4286 | 0
2016-12-10 02:00 | 3840 | 734.66 | 336 | 1240 | 1521.4286 | 7.9114
2016-12-10 03:00 | 3840 | 703.779 | 398 | 1240 | 1521.4286 | 0
2016-12-10 04:00 | 3840 | 727.415 | 651 | 1240 | 1521.4286 | 0
2016-12-10 05:00 | 3840 | 784.89 | 832 | 1240 | 1430.7692 | 0
2016-12-10 06:00 | 4090 | 875.786 | 523 | 1240 | 1440 | 11.214
2016-12-10 07:00 | 4090 | 895.451 | 389 | 1240 | 1440 | 125.549
2016-12-10 08:00 | 4090 | 913.76 | 336 | 1240 | 1440 | 160.24
2016-12-10 09:00 | 4090 | 889.62 | 436 | 1240 | 1430.7692 | 93.6108
2016-12-10 10:00 | 3148 | 868.1 | 399 | 1240 | 1430.7692 | 0
2016-12-10 11:00 | 3148 | 847.06 | 348 | 1240 | 1430.7692 | 0
2016-12-10 12:00 | 3148 | 787.037 | 427 | 1240 | 1430.7692 | 0
2016-12-10 13:00 | 3148 | 777.993 | 336 | 1240 | 1430.7692 | 0
2016-12-10 14:00 | 4512 | 769.956 | 336 | 1240 | 1430.7692 | 735.2748
2016-12-10 15:00 | 4512 | 764.465 | 420 | 1240 | 1430.7692 | 656.7658
2016-12-10 16:00 | 4512 | 767.695 | 656 | 1240 | 1430.7692 | 417.5358
2016-12-10 17:00 | 4512 | 846.46 | 526 | 1240 | 1430.7692 | 468.7708
2016-12-10 18:00 | 3971 | 813.618 | 401 | 1240 | 1521.4286 | 0
2016-12-10 19:00 | 3971 | 823.099 | 336 | 1240 | 1521.4286 | 50.4724
2016-12-10 20:00 | 3971 | 851.4 | 336 | 1240 | 1673.3333 | 0
2016-12-10 21:00 | 3971 | 829.92 | 336 | 1240 | 1673.3333 | 0
2016-12-10 22:00 | 3150 | 793.14 | 336 | 1240 | 1730 | 0
2016-12-10 23:00 | 3150 | 672.894 | 472 | 1240 | 1730 | 0
2016-12-11 | 3150 | 661.158 | 350 | 1240 | 1730 | 0
2016-12-11 01:00 | 3150 | 656.928 | 336 | 1240 | 1730 | 0
2016-12-11 02:00 | 3840 | 642.114 | 336 | 1240 | 1730 | 0
2016-12-11 03:00 | 3840 | 636.318 | 398 | 1240 | 1730 | 0
2016-12-11 04:00 | 3840 | 642.312 | 651 | 1240 | 1730 | 0
2016-12-11 05:00 | 3840 | 662.544 | 832 | 1240 | 1730 | 0
2016-12-11 06:00 | 4090 | 692.946 | 523 | 1240 | 1730 | 0
2016-12-11 07:00 | 4090 | 800.28 | 389 | 1240 | 1730 | 0
2016-12-11 08:00 | 4090 | 834.72 | 336 | 1240 | 1673.3333 | 5.9467
2016-12-11 09:00 | 4090 | 864.78 | 436 | 1240 | 1673.3333 | 0
2016-12-11 10:00 | 3148 | 868.04 | 399 | 1240 | 1521.4286 | 0
2016-12-11 11:00 | 3148 | 822.966 | 348 | 1240 | 1521.4286 | 0
2016-12-11 12:00 | 3148 | 812.003 | 427 | 1240 | 1521.4286 | 0
2016-12-11 13:00 | 3148 | 799.197 | 336 | 1240 | 1521.4286 | 0
2016-12-11 14:00 | 4512 | 788.386 | 336 | 1240 | 1430.7692 | 716.8448
2016-12-11 15:00 | 4512 | 783.75 | 420 | 1240 | 1430.7692 | 637.4808
2016-12-11 16:00 | 4512 | 789.222 | 656 | 1240 | 1430.7692 | 396.0088
2016-12-11 17:00 | 4512 | 833.625 | 526 | 1240 | 1430.7692 | 481.6058
2016-12-11 18:00 | 3971 | 899.84 | 401 | 1240 | 1430.7692 | 0
2016-12-11 19:00 | 3971 | 876.071 | 336 | 1240 | 1430.7692 | 88.1598
2016-12-11 20:00 | 3971 | 870.466 | 336 | 1240 | 1521.4286 | 3.1054
2016-12-11 21:00 | 3971 | 861.441 | 336 | 1240 | 1521.4286 | 12.1304
2016-12-11 22:00 | 3150 | 875.76 | 336 | 1240 | 1521.4286 | 0
2016-12-11 23:00 | 3150 | 843.1 | 472 | 1240 | 1521.4286 | 0
2016-12-12 | 3150 | 782.3 | 350 | 1240 | 1521.4286 | 0
2016-12-12 01:00 | 3150 | 769.08 | 336 | 1240 | 1521.4286 | 0
2016-12-12 02:00 | 3840 | 768.04 | 336 | 1240 | 1521.4286 | 0
2016-12-12 03:00 | 3840 | 777.42 | 398 | 1240 | 1521.4286 | 0
2016-12-12 04:00 | 3840 | 796.22 | 651 | 1240 | 1521.4286 | 0
2016-12-12 05:00 | 3840 | 785.023 | 832 | 1240 | 1521.4286 | 0
2016-12-12 06:00 | 4090 | 821.579 | 523 | 1240 | 1521.4286 | 0
2016-12-12 07:00 | 4090 | 853.385 | 389 | 1240 | 1521.4286 | 86.1864
2016-12-12 08:00 | 4090 | 929.74 | 336 | 1240 | 1430.7692 | 153.4908
2016-12-12 09:00 | 4090 | 937.52 | 436 | 1240 | 1430.7692 | 45.7108
2016-12-12 10:00 | 3148 | 923.54 | 399 | 1240 | 1430.7692 | 0
2016-12-12 11:00 | 3148 | 902.74 | 348 | 1240 | 1430.7692 | 0
2016-12-12 12:00 | 3148 | 882.36 | 427 | 1240 | 1430.7692 | 0
2016-12-12 13:00 | 3148 | 860.68 | 336 | 1240 | 1430.7692 | 0
2016-12-12 14:00 | 4512 | 841.76 | 336 | 1240 | 1430.7692 | 663.4708
2016-12-12 15:00 | 4512 | 835.02 | 420 | 1240 | 1430.7692 | 586.2108
2016-12-12 16:00 | 4512 | 851.7 | 656 | 1240 | 1440 | 324.3
2016-12-12 17:00 | 4512 | 878.18 | 526 | 1240 | 1238.9381 | 628.8819
2016-12-12 18:00 | 3971 | 927.998 | 401 | 1240 | 1238.9381 | 163.0639
2016-12-12 19:00 | 3971 | 1080.744 | 336 | 1240 | 1238.9381 | 75.3179
2016-12-12 20:00 | 3971 | 1086.897 | 336 | 1240 | 1238.9381 | 69.1649
2016-12-12 21:00 | 3971 | 1072.239 | 336 | 1240 | 1238.9381 | 83.8229
2016-12-12 22:00 | 3150 | 927.694 | 336 | 1240 | 1238.9381 | 0
2016-12-12 23:00 | 3150 | 926.62 | 472 | 1240 | 1440 | 0
2016-12-13 | 3150 | 782.8 | 350 | 1240 | 1440 | 0
2016-12-13 01:00 | 3150 | 775.238 | 336 | 1240 | 1430.7692 | 0
2016-12-13 02:00 | 3840 | 819.88 | 336 | 1240 | 1430.7692 | 13.3508
2016-12-13 03:00 | 3840 | 834.12 | 398 | 1240 | 1430.7692 | 0
2016-12-13 04:00 | 3840 | 822.871 | 651 | 1240 | 1430.7692 | 0
2016-12-13 05:00 | 3840 | 890.701 | 832 | 1240 | 1430.7692 | 0
2016-12-13 06:00 | 4090 | 1044.16 | 523 | 1240 | 1440 | 0
2016-12-13 07:00 | 4090 | 1015.873 | 389 | 1240 | 1440 | 5.127
2016-12-13 08:00 | 4090 | 1022.68 | 336 | 1240 | 1440 | 51.32
2016-12-13 09:00 | 4090 | 976.72 | 436 | 1240 | 1430.7692 | 6.5108
2016-12-13 10:00 | 3148 | 936.48 | 399 | 1240 | 1430.7692 | 0
2016-12-13 11:00 | 3148 | 847.704 | 348 | 1240 | 1430.7692 | 0
2016-12-13 12:00 | 3148 | 812.972 | 427 | 1240 | 1430.7692 | 0
2016-12-13 13:00 | 3148 | 786.999 | 336 | 1240 | 1430.7692 | 0
2016-12-13 14:00 | 4512 | 766.992 | 336 | 1240 | 1430.7692 | 738.2388
2016-12-13 15:00 | 4512 | 758.157 | 420 | 1240 | 1430.7692 | 663.0738
2016-12-13 16:00 | 4512 | 806.42 | 656 | 1240 | 1430.7692 | 378.8108
2016-12-13 17:00 | 4512 | 868.4 | 526 | 1240 | 1430.7692 | 446.8308
2016-12-13 18:00 | 3971 | 912.74 | 401 | 1240 | 1430.7692 | 0
2016-12-13 19:00 | 3971 | 957.08 | 336 | 1240 | 1430.7692 | 7.1508
2016-12-13 20:00 | 3971 | 957.74 | 336 | 1240 | 1430.7692 | 6.4908
2016-12-13 21:00 | 3971 | 889.371 | 336 | 1240 | 1521.4286 | 0
2016-12-13 22:00 | 3150 | 835.772 | 336 | 1240 | 1521.4286 | 0
2016-12-13 23:00 | 3150 | 824.78 | 472 | 1240 | 1521.4286 | 0
2016-12-14 | 3150 | 786.4 | 350 | 1240 | 1521.4286 | 0
2016-12-14 01:00 | 3150 | 773.64 | 336 | 1240 | 1673.3333 | 0
2016-12-14 02:00 | 3840 | 773.8 | 336 | 1240 | 1521.4286 | 0
2016-12-14 03:00 | 3840 | 781.48 | 398 | 1240 | 1521.4286 | 0
2016-12-14 04:00 | 3840 | 808.68 | 651 | 1240 | 1521.4286 | 0
2016-12-14 05:00 | 3840 | 826.823 | 832 | 1240 | 1521.4286 | 0
2016-12-14 06:00 | 4090 | 966.32 | 523 | 1240 | 1521.4286 | 0
2016-12-14 07:00 | 4090 | 930.411 | 389 | 1240 | 1521.4286 | 9.1604
2016-12-14 08:00 | 4090 | 884.013 | 336 | 1240 | 1521.4286 | 108.5584
2016-12-14 09:00 | 4090 | 889.7 | 436 | 1240 | 1673.3333 | 0
2016-12-14 10:00 | 3148 | 855.04 | 399 | 1240 | 1673.3333 | 0
2016-12-14 11:00 | 3148 | 827.24 | 348 | 1240 | 1673.3333 | 0
2016-12-14 12:00 | 3148 | 762.28 | 427 | 1240 | 1673.3333 | 0
2016-12-14 13:00 | 3148 | 749.968 | 336 | 1240 | 1673.3333 | 0
2016-12-14 14:00 | 4512 | 776.78 | 336 | 1240 | 1673.3333 | 485.8867
2016-12-14 15:00 | 4512 | 771.5 | 420 | 1240 | 1673.3333 | 407.1667
2016-12-14 16:00 | 4512 | 736.326 | 656 | 1240 | 1673.3333 | 206.3407
2016-12-14 17:00 | 4512 | 775.903 | 526 | 1240 | 1673.3333 | 296.7637
2016-12-14 18:00 | 3971 | 843.08 | 401 | 1240 | 1673.3333 | 0
2016-12-14 19:00 | 3971 | 869.44 | 336 | 1240 | 1673.3333 | 0
2016-12-14 20:00 | 3971 | 860.48 | 336 | 1240 | 1673.3333 | 0
2016-12-14 21:00 | 3971 | 834.38 | 336 | 1240 | 1730 | 0
2016-12-14 22:00 | 3150 | 699.696 | 336 | 1240 | 1730 | 0
2016-12-14 23:00 | 3150 | 644.958 | 472 | 1240 | 1730 | 0
2016-12-15 | 3150 | 616.032 | 350 | 1240 | 1730 | 0
2016-12-15 01:00 | 3150 | 600.12 | 336 | 1240 | 1730 | 0
2016-12-15 02:00 | 3840 | 593.496 | 336 | 1240 | 1730 | 0
2016-12-15 03:00 | 3840 | 595.08 | 398 | 1240 | 1730 | 0
2016-12-15 04:00 | 3840 | 611.964 | 651 | 1240 | 1730 | 0
2016-12-15 05:00 | 3840 | 658.926 | 832 | 1240 | 1730 | 0
2016-12-15 06:00 | 4090 | 735.192 | 523 | 1240 | 1730 | 0
2016-12-15 07:00 | 4090 | 753.786 | 389 | 1240 | 1730 | 0
2016-12-15 08:00 | 4090 | 732.204 | 336 | 1240 | 1730 | 51.796
2016-12-15 09:00 | 4090 | 726.768 | 436 | 1240 | 1730 | 0
2016-12-15 10:00 | 3148 | 721.458 | 399 | 1240 | 1730 | 0
2016-12-15 11:00 | 3148 | 717.102 | 348 | 1240 | 1730 | 0
2016-12-15 12:00 | 3148 | 713.592 | 427 | 1240 | 1730 | 0
2016-12-15 13:00 | 3148 | 716.076 | 336 | 1240 | 1730 | 0
2016-12-15 14:00 | 4512 | 718.506 | 336 | 1240 | 1730 | 487.494
2016-12-15 15:00 | 4512 | 716.922 | 420 | 1240 | 1730 | 405.078
2016-12-15 16:00 | 4512 | 715.698 | 656 | 1240 | 1730 | 170.302
2016-12-15 17:00 | 4512 | 824.52 | 526 | 1240 | 1730 | 191.48
2016-12-15 18:00 | 3971 | 845.78 | 401 | 1240 | 1730 | 0
2016-12-15 19:00 | 3971 | 867.02 | 336 | 1240 | 1730 | 0
2016-12-15 20:00 | 3971 | 852.1 | 336 | 1240 | 1730 | 0
2016-12-15 21:00 | 3971 | 741.402 | 336 | 1240 | 1730 | 0
2016-12-15 22:00 | 3150 | 689.418 | 336 | 1240 | 1730 | 0
2016-12-15 23:00 | 3150 | 630.432 | 472 | 1240 | 1730 | 0
2016-12-16 | 3150 | 574.416 | 350 | 1240 | 1730 | 0
2016-12-16 01:00 | 3150 | 556.56 | 336 | 1240 | 1730 | 0
2016-12-16 02:00 | 3840 | 546.876 | 336 | 1240 | 1730 | 0
2016-12-16 03:00 | 3840 | 548.55 | 398 | 1240 | 1730 | 0
2016-12-16 04:00 | 3840 | 564.966 | 651 | 1240 | 1730 | 0
2016-12-16 05:00 | 3840 | 612.396 | 832 | 1240 | 1730 | 0
2016-12-16 06:00 | 4090 | 772.4 | 523 | 1240 | 1730 | 0
2016-12-16 07:00 | 4090 | 806.46 | 389 | 1240 | 1673.3333 | 0
2016-12-16 08:00 | 4090 | 801.14 | 336 | 1240 | 1673.3333 | 39.5267
2016-12-16 09:00 | 4090 | 764.769 | 436 | 1240 | 1521.4286 | 127.8024
2016-12-16 10:00 | 3148 | 763.857 | 399 | 1240 | 1521.4286 | 0
2016-12-16 11:00 | 3148 | 760.247 | 348 | 1240 | 1521.4286 | 0
2016-12-16 12:00 | 3148 | 752.343 | 427 | 1240 | 1521.4286 | 0
2016-12-16 13:00 | 3148 | 747.555 | 336 | 1240 | 1521.4286 | 0
2016-12-16 14:00 | 4512 | 738.397 | 336 | 1240 | 1521.4286 | 676.1744
2016-12-16 15:00 | 4512 | 733.476 | 420 | 1240 | 1521.4286 | 597.0954
2016-12-16 16:00 | 4512 | 738.815 | 656 | 1240 | 1430.7692 | 446.4158
2016-12-16 17:00 | 4512 | 779.266 | 526 | 1240 | 1430.7692 | 535.9648
2016-12-16 18:00 | 3971 | 804.099 | 401 | 1240 | 1430.7692 | 95.1318
2016-12-16 19:00 | 3971 | 872.54 | 336 | 1240 | 1430.7692 | 91.6908
2016-12-16 20:00 | 3971 | 870.94 | 336 | 1240 | 1430.7692 | 93.2908
2016-12-16 21:00 | 3971 | 806.284 | 336 | 1240 | 1521.4286 | 67.2874
2016-12-16 22:00 | 3150 | 762.622 | 336 | 1240 | 1521.4286 | 0
2016-12-16 23:00 | 3150 | 749.68 | 472 | 1240 | 1521.4286 | 0
2016-12-17 | 3150 | 746.1 | 350 | 1240 | 1521.4286 | 0
2016-12-17 01:00 | 3150 | 730.98 | 336 | 1240 | 1521.4286 | 0
2016-12-17 02:00 | 3840 | 725.22 | 336 | 1240 | 1521.4286 | 17.3514
2016-12-17 03:00 | 3840 | 731.08 | 398 | 1240 | 1521.4286 | 0
2016-12-17 04:00 | 3840 | 716.376 | 651 | 1240 | 1521.4286 | 0
2016-12-17 05:00 | 3840 | 770.754 | 832 | 1240 | 1430.7692 | 0
2016-12-17 06:00 | 4090 | 905.12 | 523 | 1240 | 1440 | 0
2016-12-17 07:00 | 4090 | 885.552 | 389 | 1240 | 1440 | 135.448
2016-12-17 08:00 | 4090 | 914.74 | 336 | 1240 | 1440 | 159.26
2016-12-17 09:00 | 4090 | 906.8 | 436 | 1240 | 1440 | 67.2
2016-12-17 10:00 | 3148 | 895.8 | 399 | 1240 | 1440 | 0
2016-12-17 11:00 | 3148 | 879.86 | 348 | 1240 | 1440 | 0
2016-12-17 12:00 | 3148 | 861.4 | 427 | 1240 | 1440 | 0
2016-12-17 13:00 | 3148 | 847.22 | 336 | 1240 | 1440 | 0
2016-12-17 14:00 | 4512 | 836.4 | 336 | 1240 | 1440 | 659.6
2016-12-17 15:00 | 4512 | 838.34 | 420 | 1240 | 1440 | 573.66
2016-12-17 16:00 | 4512 | 853.44 | 656 | 1240 | 1440 | 322.56
2016-12-17 17:00 | 4512 | 862.353 | 526 | 1240 | 1440 | 443.647
2016-12-17 18:00 | 3971 | 879.13 | 401 | 1240 | 1440 | 10.87
2016-12-17 19:00 | 3971 | 895.907 | 336 | 1240 | 1440 | 59.093
2016-12-17 20:00 | 3971 | 887.737 | 336 | 1240 | 1440 | 67.263
2016-12-17 21:00 | 3971 | 915.76 | 336 | 1240 | 1440 | 39.24
2016-12-17 22:00 | 3150 | 880.42 | 336 | 1240 | 1430.7692 | 0
2016-12-17 23:00 | 3150 | 837.7 | 472 | 1240 | 1430.7692 | 0
2016-12-18 | 3150 | 841.8 | 350 | 1240 | 1430.7692 | 0
2016-12-18 01:00 | 3150 | 843.48 | 336 | 1240 | 1430.7692 | 0
2016-12-18 02:00 | 3840 | 836.64 | 336 | 1240 | 1430.7692 | 0
2016-12-18 03:00 | 3840 | 841.1 | 398 | 1240 | 1430.7692 | 0
2016-12-18 04:00 | 3840 | 856.74 | 651 | 1240 | 1430.7692 | 0
2016-12-18 05:00 | 3840 | 888.98 | 832 | 1240 | 1430.7692 | 0
2016-12-18 06:00 | 4090 | 891.727 | 523 | 1240 | 1440 | 0
2016-12-18 07:00 | 4090 | 930.601 | 389 | 1240 | 1440 | 90.399
2016-12-18 08:00 | 4090 | 945.782 | 336 | 1240 | 1440 | 128.218
2016-12-18 09:00 | 4090 | 931.418 | 436 | 1240 | 1440 | 42.582
2016-12-18 10:00 | 3148 | 896.382 | 399 | 1240 | 1440 | 0
2016-12-18 11:00 | 3148 | 901.58 | 348 | 1240 | 1440 | 0
2016-12-18 12:00 | 3148 | 861.96 | 427 | 1240 | 1440 | 0
2016-12-18 13:00 | 3148 | 829.1 | 336 | 1240 | 1440 | 0
2016-12-18 14:00 | 4512 | 805.44 | 336 | 1240 | 1440 | 690.56
2016-12-18 15:00 | 4512 | 794.12 | 420 | 1240 | 1440 | 617.88
2016-12-18 16:00 | 4512 | 801.66 | 656 | 1240 | 1440 | 374.34
2016-12-18 17:00 | 4512 | 861.36 | 526 | 1240 | 1440 | 444.64
2016-12-18 18:00 | 3971 | 856.577 | 401 | 1240 | 1440 | 33.423
2016-12-18 19:00 | 3971 | 941.94 | 336 | 1240 | 1440 | 13.06
2016-12-18 20:00 | 3971 | 947.56 | 336 | 1240 | 1430.7692 | 16.6708
2016-12-18 21:00 | 3971 | 894.349 | 336 | 1240 | 1430.7692 | 69.8818
2016-12-18 22:00 | 3150 | 872.309 | 336 | 1240 | 1430.7692 | 0
2016-12-18 23:00 | 3150 | 840.37 | 472 | 1240 | 1430.7692 | 0
2016-12-19 | 3150 | 824.866 | 350 | 1240 | 1430.7692 | 0
2016-12-19 01:00 | 3150 | 806.645 | 336 | 1240 | 1430.7692 | 0
2016-12-19 02:00 | 3840 | 800.831 | 336 | 1240 | 1430.7692 | 32.3998
2016-12-19 03:00 | 3840 | 801.268 | 398 | 1240 | 1430.7692 | 0
2016-12-19 04:00 | 3840 | 808.944 | 651 | 1240 | 1430.7692 | 0
2016-12-19 05:00 | 3840 | 829.578 | 832 | 1240 | 1430.7692 | 0
2016-12-19 06:00 | 4090 | 860.643 | 523 | 1240 | 1430.7692 | 35.5878
2016-12-19 07:00 | 4090 | 932.7 | 389 | 1240 | 1430.7692 | 97.5308
2016-12-19 08:00 | 4090 | 947.84 | 336 | 1240 | 1430.7692 | 135.3908
2016-12-19 09:00 | 4090 | 884.184 | 436 | 1240 | 1430.7692 | 99.0468
2016-12-19 10:00 | 3148 | 849.433 | 399 | 1240 | 1430.7692 | 0
2016-12-19 11:00 | 3148 | 859.14 | 348 | 1240 | 1430.7692 | 0
2016-12-19 12:00 | 3148 | 791.122 | 427 | 1240 | 1430.7692 | 0
2016-12-19 13:00 | 3148 | 770.754 | 336 | 1240 | 1430.7692 | 0
2016-12-19 14:00 | 4512 | 753.901 | 336 | 1240 | 1430.7692 | 751.3298
2016-12-19 15:00 | 4512 | 746.89 | 420 | 1240 | 1430.7692 | 674.3408
2016-12-19 16:00 | 4512 | 754.3 | 656 | 1240 | 1430.7692 | 430.9308
2016-12-19 17:00 | 4512 | 805.942 | 526 | 1240 | 1430.7692 | 509.2888
2016-12-19 18:00 | 3971 | 841.035 | 401 | 1240 | 1430.7692 | 58.1958
2016-12-19 19:00 | 3971 | 876.128 | 336 | 1240 | 1430.7692 | 88.1028
2016-12-19 20:00 | 3971 | 872.176 | 336 | 1240 | 1521.4286 | 1.3954
2016-12-19 21:00 | 3971 | 852.226 | 336 | 1240 | 1521.4286 | 21.3454
2016-12-19 22:00 | 3150 | 856.3 | 336 | 1240 | 1521.4286 | 0
2016-12-19 23:00 | 3150 | 802.16 | 472 | 1240 | 1673.3333 | 0
2016-12-20 | 3150 | 654.264 | 350 | 1240 | 1730 | 0
2016-12-20 01:00 | 3150 | 635.904 | 336 | 1240 | 1730 | 0
2016-12-20 02:00 | 3840 | 627.174 | 336 | 1240 | 1730 | 0
2016-12-20 03:00 | 3840 | 626.544 | 398 | 1240 | 1730 | 0
2016-12-20 04:00 | 3840 | 639.036 | 651 | 1240 | 1730 | 0
2016-12-20 05:00 | 3840 | 677.52 | 832 | 1240 | 1673.3333 | 0
2016-12-20 06:00 | 4090 | 813.02 | 523 | 1240 | 1673.3333 | 0
2016-12-20 07:00 | 4090 | 839.8 | 389 | 1240 | 1673.3333 | 0
2016-12-20 08:00 | 4090 | 846.5 | 336 | 1240 | 1673.3333 | 0
2016-12-20 09:00 | 4090 | 852.9 | 436 | 1240 | 1673.3333 | 0
2016-12-20 10:00 | 3148 | 853.4 | 399 | 1240 | 1673.3333 | 0
2016-12-20 11:00 | 3148 | 850.36 | 348 | 1240 | 1673.3333 | 0
2016-12-20 12:00 | 3148 | 846.8 | 427 | 1240 | 1673.3333 | 0
2016-12-20 13:00 | 3148 | 847.7 | 336 | 1240 | 1673.3333 | 0
2016-12-20 14:00 | 4512 | 847.56 | 336 | 1240 | 1673.3333 | 415.1067
2016-12-20 15:00 | 4512 | 845.78 | 420 | 1240 | 1673.3333 | 332.8867
2016-12-20 16:00 | 4512 | 843.2 | 656 | 1240 | 1673.3333 | 99.4667
2016-12-20 17:00 | 4512 | 828.191 | 526 | 1240 | 1673.3333 | 244.4757
2016-12-20 18:00 | 3971 | 848.73 | 401 | 1240 | 1673.3333 | 0
2016-12-20 19:00 | 3971 | 869.269 | 336 | 1240 | 1673.3333 | 0
2016-12-20 20:00 | 3971 | 895.62 | 336 | 1240 | 1673.3333 | 0
2016-12-20 21:00 | 3971 | 868.4 | 336 | 1240 | 1673.3333 | 0
2016-12-20 22:00 | 3150 | 736.776 | 336 | 1240 | 1673.3333 | 0
2016-12-20 23:00 | 3150 | 681.066 | 472 | 1240 | 1673.3333 | 0
2016-12-21 | 3150 | 625.896 | 350 | 1240 | 1730 | 0
2016-12-21 01:00 | 3150 | 601.686 | 336 | 1240 | 1730 | 0
2016-12-21 02:00 | 3840 | 588.942 | 336 | 1240 | 1730 | 0
2016-12-21 03:00 | 3840 | 581.976 | 398 | 1240 | 1730 | 0
2016-12-21 04:00 | 3840 | 591.372 | 651 | 1240 | 1730 | 0
2016-12-21 05:00 | 3840 | 621.414 | 832 | 1240 | 1730 | 0
2016-12-21 06:00 | 4090 | 746.58 | 523 | 1240 | 1730 | 0
2016-12-21 07:00 | 4090 | 779.26 | 389 | 1240 | 1730 | 0
2016-12-21 08:00 | 4090 | 796.8 | 336 | 1240 | 1730 | 0
2016-12-21 09:00 | 4090 | 819.5 | 436 | 1240 | 1730 | 0
2016-12-21 10:00 | 3148 | 836.58 | 399 | 1240 | 1673.3333 | 0
2016-12-21 11:00 | 3148 | 803.491 | 348 | 1240 | 1521.4286 | 0
2016-12-21 12:00 | 3148 | 811.281 | 427 | 1240 | 1521.4286 | 0
2016-12-21 13:00 | 3148 | 824.961 | 336 | 1240 | 1521.4286 | 0
2016-12-21 14:00 | 4512 | 877.14 | 336 | 1240 | 1430.7692 | 628.0908
2016-12-21 15:00 | 4512 | 881.86 | 420 | 1240 | 1430.7692 | 539.3708
2016-12-21 16:00 | 4512 | 876.6 | 656 | 1240 | 1430.7692 | 308.6308
2016-12-21 17:00 | 4512 | 890.06 | 526 | 1240 | 1430.7692 | 425.1708
2016-12-21 18:00 | 3971 | 901.24 | 401 | 1240 | 1430.7692 | 0
2016-12-21 19:00 | 3971 | 912.42 | 336 | 1240 | 1430.7692 | 51.8108
2016-12-21 20:00 | 3971 | 889.48 | 336 | 1240 | 1430.7692 | 74.7508
2016-12-21 21:00 | 3971 | 859.8 | 336 | 1240 | 1430.7692 | 104.4308
2016-12-21 22:00 | 3150 | 766.555 | 336 | 1240 | 1521.4286 | 0
2016-12-21 23:00 | 3150 | 708.358 | 472 | 1240 | 1673.3333 | 0
2016-12-22 | 3150 | 660.26 | 350 | 1240 | 1673.3333 | 0
2016-12-22 01:00 | 3150 | 635.66 | 336 | 1240 | 1673.3333 | 0
2016-12-22 02:00 | 3840 | 623.98 | 336 | 1240 | 1673.3333 | 0
2016-12-22 03:00 | 3840 | 559.242 | 398 | 1240 | 1673.3333 | 0
2016-12-22 04:00 | 3840 | 569.826 | 651 | 1240 | 1673.3333 | 0
2016-12-22 05:00 | 3840 | 669.2 | 832 | 1240 | 1673.3333 | 0
2016-12-22 06:00 | 4090 | 731.32 | 523 | 1240 | 1673.3333 | 0
2016-12-22 07:00 | 4090 | 731.196 | 389 | 1240 | 1673.3333 | 56.4707
2016-12-22 08:00 | 4090 | 748.334 | 336 | 1240 | 1521.4286 | 244.2374
2016-12-22 09:00 | 4090 | 765.206 | 436 | 1240 | 1521.4286 | 127.3654
2016-12-22 10:00 | 3148 | 774.06 | 399 | 1240 | 1521.4286 | 0
2016-12-22 11:00 | 3148 | 777.651 | 348 | 1240 | 1521.4286 | 0
2016-12-22 12:00 | 3148 | 772.673 | 427 | 1240 | 1521.4286 | 0
2016-12-22 13:00 | 3148 | 769.386 | 336 | 1240 | 1521.4286 | 0
2016-12-22 14:00 | 4512 | 765.681 | 336 | 1240 | 1521.4286 | 648.8904
2016-12-22 15:00 | 4512 | 764.104 | 420 | 1240 | 1521.4286 | 566.4674
2016-12-22 16:00 | 4512 | 767.22 | 656 | 1240 | 1521.4286 | 327.3514
2016-12-22 17:00 | 4512 | 842.46 | 526 | 1240 | 1430.7692 | 472.7708
2016-12-22 18:00 | 3971 | 855.74 | 401 | 1240 | 1430.7692 | 43.4908
2016-12-22 19:00 | 3971 | 825.55 | 336 | 1240 | 1521.4286 | 48.0214
2016-12-22 20:00 | 3971 | 812.554 | 336 | 1240 | 1521.4286 | 61.0174
2016-12-22 21:00 | 3971 | 792.167 | 336 | 1240 | 1521.4286 | 81.4044
2016-12-22 22:00 | 3150 | 751.108 | 336 | 1240 | 1521.4286 | 0
2016-12-22 23:00 | 3150 | 741.24 | 472 | 1240 | 1521.4286 | 0
2016-12-23 | 3150 | 709.18 | 350 | 1240 | 1521.4286 | 0
2016-12-23 01:00 | 3150 | 683.5 | 336 | 1240 | 1521.4286 | 0
2016-12-23 02:00 | 3840 | 668.62 | 336 | 1240 | 1521.4286 | 73.9514
2016-12-23 03:00 | 3840 | 663.8 | 398 | 1240 | 1521.4286 | 16.7714
2016-12-23 04:00 | 3840 | 674.9 | 651 | 1240 | 1521.4286 | 0
2016-12-23 05:00 | 3840 | 671.346 | 832 | 1240 | 1521.4286 | 0
2016-12-23 06:00 | 4090 | 714.818 | 523 | 1240 | 1521.4286 | 90.7534
2016-12-23 07:00 | 4090 | 743.128 | 389 | 1240 | 1430.7692 | 287.1028
2016-12-23 08:00 | 4090 | 801.72 | 336 | 1240 | 1430.7692 | 281.5108
2016-12-23 09:00 | 4090 | 823.88 | 436 | 1240 | 1430.7692 | 159.3508
2016-12-23 10:00 | 3148 | 832.32 | 399 | 1240 | 1430.7692 | 0
2016-12-23 11:00 | 3148 | 787.436 | 348 | 1240 | 1430.7692 | 0
2016-12-23 12:00 | 3148 | 774.725 | 427 | 1240 | 1521.4286 | 0
2016-12-23 13:00 | 3148 | 765.244 | 336 | 1240 | 1521.4286 | 0
2016-12-23 14:00 | 4512 | 795.98 | 336 | 1240 | 1521.4286 | 618.5914
2016-12-23 15:00 | 4512 | 789.28 | 420 | 1240 | 1521.4286 | 541.2914
2016-12-23 16:00 | 4512 | 751.906 | 656 | 1240 | 1521.4286 | 342.6654
2016-12-23 17:00 | 4512 | 790.875 | 526 | 1240 | 1521.4286 | 433.6964
2016-12-23 18:00 | 3971 | 802.446 | 401 | 1240 | 1521.4286 | 6.1254
2016-12-23 19:00 | 3971 | 813.998 | 336 | 1240 | 1521.4286 | 59.5734
2016-12-23 20:00 | 3971 | 802.142 | 336 | 1240 | 1521.4286 | 71.4294
2016-12-23 21:00 | 3971 | 781.983 | 336 | 1240 | 1521.4286 | 91.5884
2016-12-23 22:00 | 3150 | 748.505 | 336 | 1240 | 1521.4286 | 0
2016-12-23 23:00 | 3150 | 704.292 | 472 | 1240 | 1521.4286 | 0
2016-12-24 | 3150 | 694.469 | 350 | 1240 | 1521.4286 | 0
2016-12-24 01:00 | 3150 | 703.76 | 336 | 1240 | 1521.4286 | 0
2016-12-24 02:00 | 3840 | 687.32 | 336 | 1240 | 1521.4286 | 55.2514
2016-12-24 03:00 | 3840 | 680.88 | 398 | 1240 | 1521.4286 | 0
2016-12-24 04:00 | 3840 | 686.9 | 651 | 1240 | 1521.4286 | 0
2016-12-24 05:00 | 3840 | 706.28 | 832 | 1240 | 1521.4286 | 0
2016-12-24 06:00 | 4090 | 738.8 | 523 | 1240 | 1521.4286 | 66.7714
2016-12-24 07:00 | 4090 | 724.907 | 389 | 1240 | 1521.4286 | 214.6644
2016-12-24 08:00 | 4090 | 752.4 | 336 | 1240 | 1521.4286 | 240.1714
2016-12-24 09:00 | 4090 | 785.859 | 436 | 1240 | 1521.4286 | 106.7124
2016-12-24 10:00 | 3148 | 805.068 | 399 | 1240 | 1521.4286 | 0
2016-12-24 11:00 | 3148 | 813.808 | 348 | 1240 | 1521.4286 | 0
2016-12-24 12:00 | 3148 | 814.131 | 427 | 1240 | 1521.4286 | 0
2016-12-24 13:00 | 3148 | 812.858 | 336 | 1240 | 1521.4286 | 0
2016-12-24 14:00 | 4512 | 854.72 | 336 | 1240 | 1521.4286 | 559.8514
2016-12-24 15:00 | 4512 | 852.56 | 420 | 1240 | 1521.4286 | 478.0114
2016-12-24 16:00 | 4512 | 857.26 | 656 | 1240 | 1521.4286 | 237.3114
2016-12-24 17:00 | 4512 | 844.075 | 526 | 1240 | 1521.4286 | 380.4964
2016-12-24 18:00 | 3971 | 841.871 | 401 | 1240 | 1521.4286 | 0
2016-12-24 19:00 | 3971 | 839.686 | 336 | 1240 | 1521.4286 | 33.8854
2016-12-24 20:00 | 3971 | 868.72 | 336 | 1240 | 1430.7692 | 95.5108
2016-12-24 21:00 | 3971 | 852.52 | 336 | 1240 | 1430.7692 | 111.7108
2016-12-24 22:00 | 3150 | 790.476 | 336 | 1240 | 1521.4286 | 0
2016-12-24 23:00 | 3150 | 766.631 | 472 | 1240 | 1521.4286 | 0
2016-12-25 | 3150 | 754.623 | 350 | 1240 | 1521.4286 | 0
2016-12-25 01:00 | 3150 | 780.92 | 336 | 1240 | 1521.4286 | 0
2016-12-25 02:00 | 3840 | 774.82 | 336 | 1240 | 1521.4286 | 0
2016-12-25 03:00 | 3840 | 775 | 398 | 1240 | 1521.4286 | 0
2016-12-25 04:00 | 3840 | 784.42 | 651 | 1240 | 1521.4286 | 0
2016-12-25 05:00 | 3840 | 805.92 | 832 | 1240 | 1521.4286 | 0
2016-12-25 06:00 | 4090 | 795.834 | 523 | 1240 | 1521.4286 | 9.7374
2016-12-25 07:00 | 4090 | 829.179 | 389 | 1240 | 1521.4286 | 110.3924
2016-12-25 08:00 | 4090 | 907.32 | 336 | 1240 | 1521.4286 | 85.2514
2016-12-25 09:00 | 4090 | 932.24 | 436 | 1240 | 1521.4286 | 0
2016-12-25 10:00 | 3148 | 892.715 | 399 | 1240 | 1521.4286 | 0
2016-12-25 11:00 | 3148 | 933.44 | 348 | 1240 | 1521.4286 | 0
2016-12-25 12:00 | 3148 | 864.215 | 427 | 1240 | 1521.4286 | 0
2016-12-25 13:00 | 3148 | 832.428 | 336 | 1240 | 1521.4286 | 0
2016-12-25 14:00 | 4512 | 804.555 | 336 | 1240 | 1521.4286 | 610.0164
2016-12-25 15:00 | 4512 | 787.759 | 420 | 1240 | 1521.4286 | 542.8124
2016-12-25 16:00 | 4512 | 791.597 | 656 | 1240 | 1521.4286 | 302.9744
2016-12-25 17:00 | 4512 | 884.96 | 526 | 1240 | 1430.7692 | 430.2708
2016-12-25 18:00 | 3971 | 925.52 | 401 | 1240 | 1430.7692 | 0
2016-12-25 19:00 | 3971 | 917.776 | 336 | 1240 | 1440 | 37.224
2016-12-25 20:00 | 3971 | 926.782 | 336 | 1240 | 1440 | 28.218
2016-12-25 21:00 | 3971 | 927.01 | 336 | 1240 | 1440 | 27.99
2016-12-25 22:00 | 3150 | 915.515 | 336 | 1240 | 1440 | 0
2016-12-25 23:00 | 3150 | 890.321 | 472 | 1240 | 1440 | 0
2016-12-26 | 3150 | 896.743 | 350 | 1240 | 1440 | 0
2016-12-26 01:00 | 3150 | 904.362 | 336 | 1240 | 1440 | 0
2016-12-26 02:00 | 3840 | 901.417 | 336 | 1240 | 1440 | 0
2016-12-26 03:00 | 3840 | 910.347 | 398 | 1240 | 1440 | 0
2016-12-26 04:00 | 3840 | 926.364 | 651 | 1240 | 1238.9381 | 0
2016-12-26 05:00 | 3840 | 950.684 | 832 | 1240 | 1238.9381 | 0
2016-12-26 06:00 | 4090 | 1090.782 | 523 | 1240 | 1238.9381 | 0
2016-12-26 07:00 | 4090 | 1119.342 | 389 | 1240 | 1296.2963 | 45.3617
2016-12-26 08:00 | 4090 | 1126.923 | 336 | 1240 | 1296.2963 | 90.7807
2016-12-26 09:00 | 4090 | 1109.787 | 436 | 1240 | 1296.2963 | 7.9167
2016-12-26 10:00 | 3148 | 1071.378 | 399 | 1240 | 1238.9381 | 0
2016-12-26 11:00 | 3148 | 925.661 | 348 | 1240 | 1238.9381 | 0
2016-12-26 12:00 | 3148 | 885.419 | 427 | 1240 | 1238.9381 | 0
2016-12-26 13:00 | 3148 | 891.62 | 336 | 1240 | 1440 | 0
2016-12-26 14:00 | 4512 | 860.36 | 336 | 1240 | 1440 | 635.64
2016-12-26 15:00 | 4512 | 843.54 | 420 | 1240 | 1440 | 568.46
2016-12-26 16:00 | 4512 | 808.811 | 656 | 1240 | 1440 | 367.189
2016-12-26 17:00 | 4512 | 922.52 | 526 | 1240 | 1440 | 383.48
2016-12-26 18:00 | 3971 | 937.992 | 401 | 1240 | 1440 | 0
2016-12-26 19:00 | 3971 | 999.571 | 336 | 1240 | 1440 | 0
2016-12-26 20:00 | 3971 | 1069.04 | 336 | 1240 | 1440 | 0
2016-12-26 21:00 | 3971 | 1071.54 | 336 | 1240 | 1440 | 0
2016-12-26 22:00 | 3150 | 1044.56 | 336 | 1240 | 1440 | 0
2016-12-26 23:00 | 3150 | 1008.98 | 472 | 1240 | 1430.7692 | 0
2016-12-27 | 3150 | 859.997 | 350 | 1240 | 1430.7692 | 0
2016-12-27 01:00 | 3150 | 851.998 | 336 | 1240 | 1430.7692 | 0
2016-12-27 02:00 | 3840 | 852.777 | 336 | 1240 | 1430.7692 | 0
2016-12-27 03:00 | 3840 | 861.422 | 398 | 1240 | 1430.7692 | 0
2016-12-27 04:00 | 3840 | 884.146 | 651 | 1240 | 1430.7692 | 0
2016-12-27 05:00 | 3840 | 980.86 | 832 | 1240 | 1430.7692 | 0
2016-12-27 06:00 | 4090 | 1037.84 | 523 | 1240 | 1430.7692 | 0
2016-12-27 07:00 | 4090 | 1014.771 | 389 | 1240 | 1440 | 6.229
2016-12-27 08:00 | 4090 | 1061.08 | 336 | 1240 | 1430.7692 | 22.1508
2016-12-27 09:00 | 4090 | 1034.46 | 436 | 1240 | 1430.7692 | 0
2016-12-27 10:00 | 3148 | 1001.62 | 399 | 1240 | 1430.7692 | 0
2016-12-27 11:00 | 3148 | 961.26 | 348 | 1240 | 1430.7692 | 0
2016-12-27 12:00 | 3148 | 919.4 | 427 | 1240 | 1430.7692 | 0
2016-12-27 13:00 | 3148 | 887.06 | 336 | 1240 | 1430.7692 | 0
2016-12-27 14:00 | 4512 | 858.64 | 336 | 1240 | 1430.7692 | 646.5908
2016-12-27 15:00 | 4512 | 805.562 | 420 | 1240 | 1430.7692 | 615.6688
2016-12-27 16:00 | 4512 | 861.12 | 656 | 1240 | 1430.7692 | 324.1108
2016-12-27 17:00 | 4512 | 918.42 | 526 | 1240 | 1440 | 387.58
2016-12-27 18:00 | 3971 | 942.48 | 401 | 1240 | 1440 | 0
2016-12-27 19:00 | 3971 | 966.56 | 336 | 1240 | 1430.7692 | 0
2016-12-27 20:00 | 3971 | 950.62 | 336 | 1240 | 1430.7692 | 13.6108
2016-12-27 21:00 | 3971 | 878.522 | 336 | 1240 | 1521.4286 | 0
2016-12-27 22:00 | 3150 | 830.642 | 336 | 1240 | 1521.4286 | 0
2016-12-27 23:00 | 3150 | 778.943 | 472 | 1240 | 1521.4286 | 0
2016-12-28 | 3150 | 758.651 | 350 | 1240 | 1521.4286 | 0
2016-12-28 01:00 | 3150 | 773.36 | 336 | 1240 | 1521.4286 | 0
2016-12-28 02:00 | 3840 | 759.44 | 336 | 1240 | 1521.4286 | 0
2016-12-28 03:00 | 3840 | 755.6 | 398 | 1240 | 1521.4286 | 0
2016-12-28 04:00 | 3840 | 728.84 | 651 | 1240 | 1521.4286 | 0
2016-12-28 05:00 | 3840 | 764.351 | 832 | 1240 | 1521.4286 | 0
2016-12-28 06:00 | 4090 | 854.66 | 523 | 1240 | 1430.7692 | 41.5708
2016-12-28 07:00 | 4090 | 884.46 | 389 | 1240 | 1430.7692 | 145.7708
2016-12-28 08:00 | 4090 | 899.36 | 336 | 1240 | 1430.7692 | 183.8708
2016-12-28 09:00 | 4090 | 914.28 | 436 | 1240 | 1440 | 59.72
2016-12-28 10:00 | 3148 | 923.74 | 399 | 1240 | 1440 | 0
2016-12-28 11:00 | 3148 | 924.58 | 348 | 1240 | 1440 | 0
2016-12-28 12:00 | 3148 | 910.52 | 427 | 1240 | 1440 | 0
2016-12-28 13:00 | 3148 | 899.5 | 336 | 1240 | 1440 | 0
2016-12-28 14:00 | 4512 | 886.04 | 336 | 1240 | 1440 | 609.96
2016-12-28 15:00 | 4512 | 880.24 | 420 | 1240 | 1440 | 531.76
2016-12-28 16:00 | 4512 | 886.52 | 656 | 1240 | 1440 | 289.48
2016-12-28 17:00 | 4512 | 928.84 | 526 | 1240 | 1440 | 377.16
2016-12-28 18:00 | 3971 | 938.36 | 401 | 1240 | 1440 | 0
2016-12-28 19:00 | 3971 | 947.88 | 336 | 1240 | 1440 | 7.12
2016-12-28 20:00 | 3971 | 926.44 | 336 | 1240 | 1430.7692 | 37.7908
2016-12-28 21:00 | 3971 | 888.6 | 336 | 1240 | 1430.7692 | 75.6308
2016-12-28 22:00 | 3150 | 792.224 | 336 | 1240 | 1521.4286 | 0
2016-12-28 23:00 | 3150 | 778.68 | 472 | 1240 | 1673.3333 | 0
2016-12-29 | 3150 | 705.48 | 350 | 1240 | 1673.3333 | 0
2016-12-29 01:00 | 3150 | 610.794 | 336 | 1240 | 1730 | 0
2016-12-29 02:00 | 3840 | 598.032 | 336 | 1240 | 1730 | 0
2016-12-29 03:00 | 3840 | 592.704 | 398 | 1240 | 1730 | 0
2016-12-29 04:00 | 3840 | 598.212 | 651 | 1240 | 1730 | 0
2016-12-29 05:00 | 3840 | 625.176 | 832 | 1240 | 1730 | 0
2016-12-29 06:00 | 4090 | 739.64 | 523 | 1240 | 1730 | 0
2016-12-29 07:00 | 4090 | 768.88 | 389 | 1240 | 1730 | 0
2016-12-29 08:00 | 4090 | 779.66 | 336 | 1240 | 1730 | 4.34
2016-12-29 09:00 | 4090 | 797.36 | 436 | 1240 | 1730 | 0
2016-12-29 10:00 | 3148 | 808.08 | 399 | 1240 | 1730 | 0
2016-12-29 11:00 | 3148 | 811.94 | 348 | 1240 | 1730 | 0
2016-12-29 12:00 | 3148 | 807.4 | 427 | 1240 | 1730 | 0
2016-12-29 13:00 | 3148 | 800.46 | 336 | 1240 | 1730 | 0
2016-12-29 14:00 | 4512 | 716.598 | 336 | 1240 | 1730 | 489.402
2016-12-29 15:00 | 4512 | 712.35 | 420 | 1240 | 1730 | 409.65
2016-12-29 16:00 | 4512 | 792.1 | 656 | 1240 | 1730 | 93.9
2016-12-29 17:00 | 4512 | 815.02 | 526 | 1240 | 1730 | 200.98
2016-12-29 18:00 | 3971 | 829.02 | 401 | 1240 | 1730 | 0
2016-12-29 19:00 | 3971 | 843.02 | 336 | 1240 | 1730 | 0
2016-12-29 20:00 | 3971 | 825.7 | 336 | 1240 | 1730 | 0
2016-12-29 21:00 | 3971 | 717.516 | 336 | 1240 | 1730 | 0
2016-12-29 22:00 | 3150 | 680.67 | 336 | 1240 | 1730 | 0
2016-12-29 23:00 | 3150 | 637.776 | 472 | 1240 | 1730 | 0
2016-12-30 | 3150 | 601.344 | 350 | 1240 | 1800 | 0
2016-12-30 01:00 | 3150 | 579.852 | 336 | 1240 | 1800 | 0
2016-12-30 02:00 | 3840 | 567.864 | 336 | 1240 | 1800 | 0
2016-12-30 03:00 | 3840 | 563.76 | 398 | 1240 | 1730 | 0
2016-12-30 04:00 | 3840 | 571.032 | 651 | 1240 | 1730 | 0
2016-12-30 05:00 | 3840 | 597.114 | 832 | 1240 | 1730 | 0
2016-12-30 06:00 | 4090 | 636.534 | 523 | 1240 | 1730 | 0
2016-12-30 07:00 | 4090 | 660.222 | 389 | 1240 | 1730 | 70.778
2016-12-30 08:00 | 4090 | 672.984 | 336 | 1240 | 1730 | 111.016
2016-12-30 09:00 | 4090 | 689.382 | 436 | 1240 | 1730 | 0
2016-12-30 10:00 | 3148 | 702.36 | 399 | 1240 | 1730 | 0
2016-12-30 11:00 | 3148 | 706.32 | 348 | 1240 | 1730 | 0
2016-12-30 12:00 | 3148 | 704.808 | 427 | 1240 | 1730 | 0
2016-12-30 13:00 | 3148 | 703.746 | 336 | 1240 | 1730 | 0
2016-12-30 14:00 | 4512 | 699.714 | 336 | 1240 | 1730 | 506.286
2016-12-30 15:00 | 4512 | 695.196 | 420 | 1240 | 1730 | 426.804
2016-12-30 16:00 | 4512 | 692.604 | 656 | 1240 | 1730 | 193.396
2016-12-30 17:00 | 4512 | 795.04 | 526 | 1240 | 1730 | 220.96
2016-12-30 18:00 | 3971 | 812.58 | 401 | 1240 | 1730 | 0
2016-12-30 19:00 | 3971 | 830.14 | 336 | 1240 | 1730 | 0
2016-12-30 20:00 | 3971 | 733.86 | 336 | 1240 | 1730 | 0
2016-12-30 21:00 | 3971 | 712.188 | 336 | 1240 | 1730 | 0
2016-12-30 22:00 | 3150 | 680.886 | 336 | 1240 | 1730 | 0
2016-12-30 23:00 | 3150 | 639.864 | 472 | 1240 | 1730 | 0

## FFR_PFR_RRS_Reference Table
Reference Table
| Case 0 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
Inertia, GWs | 100 | 119.5 | 135.5 | 152 | 177 | 201.5 | 229.5 | 255.5 | 278 | 296.5 | 315.5 | 332 | 350
FFR/PFR | 2.35:1 | 2.2:1 | 2.0:1 | 1.5:1 | 1.4:1 | 1.3:1 | 1.25:1 | 1.13 :1 | 1.08:1 | 1.0:1 | 1.0:1 | 1.0:1 | 1.0:1
PFR Requirement (no FFR), MW | 7358 | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
Min PFR Requirement, MW | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | Based on BAL-003 IFRO
FFR Requirement | 2600 | 1800 | 1696 | 1641 | 1511 | 1431 | 1440 | 1239 | 1296 | 1000 | 1040 | 900 | 900
Combined Total PFR/FFR | 3840 | 3040 | 2936 | 2881 | 2751 | 2671 | 2680 | 2479 | 2536 | 2240 | 2280 | 2140 | 2140
B point frequency for CRS req., Hz | 59.8 | 59.8 | 59.79 | 59.79 | 59.79 | 59.77 | 59.78 | 59.77 | 59.78 | 59.76 | 59.75 | 59.75 | 59.76 | Based on single largest unit outage that doesn't cause UFR Load trip (system frequency above 59.7 Hz).