## Slide 1
Minimum Inertia Discussion
September 21, 2015
ERCOT FAS/SIRS Meeting

## Slide 2: Current Practice
Target:
  Frequency nadir >= 59.4 Hz in the event of the loss of two STPs.
  The first stage of firm under frequency load shedding is 59.3 Hz.
  A 0.1 Hz margin is considered to accommodate the potential variation of the system condition and modeling.
Study Assumptions:
  Only Resources providing Responsive Reserve Service provide primary frequency response. This includes Load Resources that provide RRS (trip load at 59.7 Hz).

## Slide 3: Example:
Disconnect two STPs
High Inertia ---: PFR=1,300MW
Mid Inertia ---: PFR=2,500MW
Low Inertia ---: PFR=4,700MW
60.1
59.3
System inertia and available frequency response determine the rate of frequency decay, frequency nadir, and settle frequency.

## Slide 4: Discussion
Impact of low system inertia
  Higher Rate of Change of Frequency (RoCoF)
    Faster frequency decay
    Higher chance to reach 59.7 Hz (Triggering of Load Resources)
    Less time for primary frequency response prior reaching to frequency nadir
    Lower frequency nadir
Rate of Change of Frequency (RoCoF)
  The general feedback from ERCOT Generation Resources indicate no specific RoCoF protection relay that can disconnect generators due to high RoCoF

## Slide 5: Low System Inertia Impact
 | System Inertia | PFR Needs | LRs Deployments (at 59.7 Hz)
Existing AS | ↓ | ↑ | ↑
FAST | ↓ | ↑ (if no or limited FFRS) | ↑ (if no FFRS1)
FAST | ↓ | ↗(with FFRS1,FFRS2) | ≈ (with FFRS1)

## Slide 6: Benefits of Having SIRS
Procuring SIRS in order to maintain a minimum amount of SIR on the system provides the ability to:
  Better limit firm under frequency load shedding.
  Determine (in advance) minimum amounts of RRS (CAS) and minimum amounts of PFRS, FFRS1/FFRS2 (FAS)
  “Target” how often FFRS1/FFRS2 are deployed