| NPRR Number | 713 | NPRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | January 28, 2016 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation of Nodal Operating Guide Revision Request (NOGRR) 147, Reactive Power Testing Requirements |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 8.1.1.2.1.4, Voltage Support Service Qualification |  |
| Related Documents Requiring Revision/Revision Requests |  | NOGRR147 |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) revises the language in Section 8.1.1.2.1.4 to reference the Reactive Power testing requirements in the Nodal Operating Guides and to harmonize the Nodal Protocol requirements with recently approved North American Electric Reliability Corporation (NERC) Reliability Standards. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Implementation of these changes will eliminate the need to have duplicative reactive test procedures for satisfying the regulatory requirements of the ERCOT Protocols, Nodal Operating Guides, and the NERC Reliability Standards. These duplicative procedures would cause confusion in training and operating procedures for the plant personnel who perform the testing in the field. The change of the periodicity of testing from two to five years will decrease the probable number of hours when Generation Resources may be required to run uneconomically to comply with testing requirements. |  |
| Credit Work Group Review |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR713 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |
| PRS Decision |  | On 7/16/15, PRS unanimously voted to table NPRR713 for one month and refer the issue to ROS. All Market Segments were present for the vote. On 8/13/15, PRS unanimously voted to table NPRR713. All Market Segments were present for the vote. On 10/15/15, PRS unanimously voted to recommend approval of NPRR713 as amended by the 9/14/15 NRG comments. All Market Segments were present for the vote. On 11/12/15, PRS unanimously voted to table NPRR713. All Market Segments were present for the vote. On 12/10/15, PRS unanimously voted to endorse and forward to TAC the 11/12/15 PRS Report and the Impact Analysis for NPRR713. The Consumer Market Segment was not present for the vote. |  |
| Summary of PRS Discussion |  | On 7/16/15, participants agreed that additional review at ROS could be beneficial and requested that ROS have a recommendation for review at next month’s PRS meeting. On 8/13/15, there was no discussion. On 10/15/15, there was no discussion. On 11/12/15, participants noted a need to table NPRR713 this month for review alongside NOGRR147. On 12/10/15, participants requested a preview of the data requirements if the language were to be approved and implemented. |  |
| TAC Decision |  | On 1/28/16, TAC unanimously voted to recommend approval of NPRR713 as recommended by PRS in the 12/10/15 PRS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 1/28/16, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of NPRR713 as it aligns language and requirements related to generator reactive testing in the Protocols with recently approved NERC Reliability Standards. |  |

| Sponsor |  |
| --- | --- |
| Name | Sherry K. Looney |
| E-mail Address | Sherry.looney@luminant.com |
| Company | Luminant Energy Company, LLC |
| Phone Number | 214-875-9278 |
| Cell Number | 469-688-7607 |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 080715 | Recommended PRS table NPRR713 to allow for further review by the Operations Working Group (OWG) along with related NOGRR147. |
| Oncor 081315 | Suggested additional revisions to better align with current ERCOT practices. |
| CenterPoint Energy 081915 | Provided additional clarifying edits. |
| Reactive Power Testing Workshop 090315 | Proposed additional clarifications to the 8/13/15 Oncor comments. |
| Reactive Power Testing Workshop 090815 | Corrected issues with the 9/3/15 Reactive Power Testing Workshop comments to align with the intent of the discussions at the 8/31/15 Reactive Power Testing Workshop. |
| NRG 091415 | Provided additional clarifying edits. |
| OWG 100815 | Endorsed NPRR713 as amended by the 9/14/15 NRG comments. |

Market Rules Notes

None

Revised Proposed Protocol Language

8.1.1.2.1.4	Voltage Support Service Qualification

(1)	The Resource Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources providing Voltage Support Service (VSS), as required by the Operating Guides.  Generation Resources providing VSS reactive capability limits shall be specified as follows:  lagging reactive capability should be specified using the Summer/Fall voltage profile, and leading capability specified using the Winter/Spring voltage profile.

(2)	The Resource Entity shall conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests are performed during the resource commissioning process and at a minimum of once every five years or within 12 months following the discovery of a change that affects its Real Power or Reactive Power capability by more than 10 percent of the last RARF submittal and is expected to last more than 6 months.  Mothballed Generation Resources that have not been tested within the last five years shall be verified within 12 calendar months upon return to service.  ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Resource Entity is not obligated to place Generation Resources On-Line solely for the purposes of testing.  The reactive capability tests must be conducted at a time agreed to in advance by the Resource Entity, its QSE, the applicable TSP, and ERCOT.

(3)	Leading and lagging reactive operating limits must be demonstrated following  the reactive power verification test procedure as more fully described in Nodal Operating Guides Section 3.3.2, Unit Reactive Capability Requirements.

(4)	The Resource Entity shall perform the Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests must be performed on initial qualification.  The AVR tests must be conducted at a time agreed on in advance by the Resource Entity, its QSE, the applicable TSP and ERCOT.