## Limit Data
John's List | Network Model Management System - (NMMS) | Resource Intergration | Independent Market Monitor | Registration - (Siebel) | Data Aggregation - (Lodestar) | Settlements & Billing - (Lodestar) | Meter Engineering | Market Management System - (MMS) | Outage Coordination | Operations Support Engineering | Operations Analysis | Advanced Network | Planning --SSWG | Planning --SPWG | Planning - Dynamic Studies | Energy Management System (EMS) | Resource Adequacy | CRR | Demand Integration (Steve Krein) | TRE | Comments
RARF-
Nameplate MVA | Used to convert RARF pu values to actual unit - check with Joe W. | Used to validate other resource data provided on RARF | [8 empty] | Used for checking other data elements submitted |  | Used for checking other data elements submitted, used for planning studies | Used for checking other data elements submitted, used for planning studies (Should match the base MVA for machine dynamic models) | Used for checking other data elements submitted
Real Power Rating |  | Used to validate other resource data provided on RARF |  |  | Used to populate settlement database - informational & reporting |  | Used to verify inputs on Meter Design Proposals |  |  |  | Used in Operations and Planning studies |  | Used for checking other data elements submitted, used for planning studies | Used for checking other data elements submitted, used for planning studies |  | Used in EMS Network Applications as Base MW.
Turbine Rating |  | Used to validate other resource data provided on RARF |  |  |  | Used in VC analysis Data validation point | [6 empty] | Used for checking other data elements submitted | Used for checking other data elements submitted, (Should match "turbine rating" parameter of governor model where model includes such parameter) | Used for checking other data elements submitted
High/Low Reasonability limits |  | Used to validate other resource data provided on RARF |  | Entry Point for value that migrates to MMS |  |  |  | COP submitted LSL/HSL outside LRL-HRL range are rejected; Inc/Dec curves with start/end points not at LRL and HRL are rejected; Resource Parameter submissions with ramp rate break points outside of LRL-HRL range are rejected. Also used to determine MW offer quantity for a combined cycle resource's Three Part Offer. | Used in Operations studies-EMS imports | Required for determining capability in emergency conditions | Used in Operations studies-EMS imports | Used in Operations studies-EMS imports |  | Sometimes used to check or refine governor model Pmax/Pmin limits when "out of limit" or other initialization errors occur. |  | Used in EMS SCADA for Validating the HSL and MW Telemetry. |  |  | Reasonability limits are used by MMS as part of COP and Offer validation |  | Also used to de-aggregate LMPs at a logical resource node
High/Low reasonability Ramp Rates (added-AD) | [7 empty] | Resource Parameter submissions with ramp rates outside of LRRRL-HRRRL range are rejected |  | Used in Operations studies-EMS imports | Used in Operations studies-EMS imports | Used in Operations studies-EMS imports |  |  |  | Used in EMS SCADA for Validating the Telemetered Ramp Rates |  |  | See response for MMS as it pertains to CLRs
Seasonal Net Sustainable |  |  |  |  | Used to populate settlement database for the Generation Resource Capacity Factor (GRCF) calculation - The GRCF is used in determining the Mitigated Offer Cap Multiplier | Used in VC analysis |  |  | Used to determine the outaged capacity during the outage. | Used in Operations studies-EMS imports | Used in Operations studies-EMS imports | Used in Operations studies-EMS imports | Used to determine max output of resource (Summer Max and Min only) | Used to determine max output of resource (Summer Max and Min only) | Used to determine max output of resource (Summer Max and Min only) |  | Used for CDR, SARA, NERC reliability assessments | Use the “Seasonal Net Max Sustainable Rating” from the “Parameters – GEN” tab for each of the four seasons to determine monthly PCRR eligibility amounts. These values are checked during the annual PCRR process to see if any of the PCRR-eligible Generation Resources have had a ratings change |  |  | One of the four values is used to validate the Reactive Capability Curve in the RARF. Which one?
Seasonal Net Emergency | [10 empty] | Used in Operations studies-EMS imports | [9 empty] | Data point used in Real Time Operations
Unit Derating per 5 degrees | [19 empty] | Requested by Brad Woods -Didn't we delete this as part of RRGRR-003?
NDCRC –
Seasonal HSL | [9 empty] | Required for verification of unnanounced unit testing and resource adequacy analyses - Evaluate for elimination from Protocols | Was used in Zonal systems | [9 empty] | Is this truly needed anymore?
COP | [9 empty] | Required per protocols
HEL/LEL | [9 empty] | Required for determining capability in emergency conditions | Not used-Info only
HSL/LSL | [5 empty] | Used to limit award range for TPOs and AS Offers in DAM and SASM; Used to determine resource capacity in RUCs; Used to validate AS capacity submitted in COP; Used to create Short-Term System Adequacy Report; Used to create "Load Forecast vs Actual" dashboard; Used in "Forecasted and Actual Wind Power Production: Current Day" dashboard |  | Used to limit award range for TPOs and AS Offers in DAM and SASM; Used to determine resource capacity in RUCs; Used to validate AS capacity submitted in COP; Used to create Short-Term System Adequacy Report; Used to create "Load Forecast vs Actual" dashboard; Used in "Forecasted and Actual Wind Power Production: Current Day" dashboard |  |  | Used in near term studies
Telemetry-
HSL/LSL | [5 empty] | Used for settlement calculations |  | SCED uses LDL-HDL range of each resource as dispatch range constraint (LDL,HDL is sent from EMMS and is based on LSL/HSL, ramp rates, and current resource output); SCED uses LSL/HDL in proxy energy offer curve generation process; HASL/LASL (based on HSL/LSL telemetry) used to make "Capacity available to SCED" dashboard; Used in "System Ancillyary Service Capacity Monitor" dashboard |  |  | SCED uses LDL-HDL range of each resource as dispatch range constraint (LDL,HDL is sent from EMMS and is based on LSL/HSL, ramp rates, and current resource output); SCED uses LSL/HDL in proxy energy offer curve generation process; HASL/LASL (based on HSL/LSL telemetry) used to make "Capacity available to SCED" dashboard; Used in "System Ancillyary Service Capacity Monitor" dashboard |  |  |  |  | Used to calculate HDL/LDL in Resource Limit Calculator. | Use telemetered HSL/LSL when determining capacity for WGRs, hydro resources, and DC Ties. |  | Load Equivalents are MPC and LPC and are used to determine dispatch amounts for NCLRs and the BP Instructions for CLRs
Scheduled Power Consumption (SPC) | [18 empty] | Used to calculate CLREDP for monthly and EEA Metrics for CLRs
Scheduled Power Consumption plus 2 (SPC+2) | [18 empty] | Used to validate the SPC value in telemetry for CLRs