## Summary
Release Date: March 1, 2017
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Summer 2017
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands given expected average weather conditions for the upcoming summer season (June - September 2017). This capacity is also sufficient given expected weather combined with either extremely low wind output or extreme outages.
This preliminary SARA report includes a 72,934 MW summer peak load forecast based on normal weather for 2002-2015. This forecast is 2.6% higher than last year's actual summer peak load of 71,110 MW. (Details on the load forecast methodology are available at: http://www.ercot.com/content/wcm/lists/114580/2017_Long-Term_Hourly_Peak_Demand_and_Energy_Forecast.pdf.) The peak load forecast for the final SARA report, to be released in May, will reflect the weather conditions expected at that time.
Expected new installed capacity additions include 2,481 MW of gas-fired generation (based on summer ratings), 1,169 MW of wind with a summer peak capacity contribution of 274 MW, and 439 MW of solar with a summer peak capacity contribution of 338 MW.
The capacity scenarios for this report include a unit outage forecast of 3,498 MW based on average seasonal historical outages beginning in February 2012. ERCOT also includes a scenario combining the peak load forecast with extremely low wind output. The low wind output amount, in MW, reflects the 10th percentile of wind output associated with the highest 100 net load hours (load minus wind output) over the last four summer seasons. Using net load for the calculations captures the combined variation of load and wind, and represents the demand that ERCOT must meet with other resources. The low wind output level translates into a summer peak capacity contribution of 3.8%, whereas the expected contribution based on historical wind output levels is 19.4%.
Although ERCOT has not been notified of changes to available generation capacity for the summer season associated with regulatory requirements, it continues to monitor and consult with generation resource owners regarding their regulatory compliance plans.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2017 - Preliminary
Release Date: March 1, 2017
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 67138.9 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3705.8 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -843.8 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 4154.7 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2012-2014)
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 2269.75 | Based on 14% of installed capacity for non-coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 1242.012 | Based on 58% of installed capacity for coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 426.58 | Based on 77% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0 | Gas-fired unit (371 MW) placed under RMR contract on June 2, 2016; notice of contract termination issued 2/27/17
|  | Non-Synchronous Ties Capacity Contribution, MW | 425.2 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2014-2016)
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 2481 | Based on in-service dates provided by developers of generation resources
|  | Planned Non-Coastal Wind with signed IA , MW | 128.688 | Based on in-service dates provided by developers of generation resources and 14% of installed capacity for non-coastal wind resources
|  | Planned Coastal Wind with signed IA , MW | 145 | Based on in-service dates provided by developers of generation resources and 58% of installed capacity for coastal wind resources
|  | Planned Solar Utility-Scale with signed IA, MW | 338.03 | Based on 77% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
| [a] Total Resources, MW |  | 81611.86
| [b] Peak Demand, MW |  | 72934 | Based on average peak weather conditions for the past 14 years (2002 – 2015)
| [c] Reserve Capacity [a - b], MW |  | 8677.86
Range of Potential Risks
|  |  | Forecasted Season Peak Load | Forecasted Season Peak Load / Extreme Generation Outages | Forecasted Season Peak Load / Low Wind Output | Extreme Peak Load / Typical Generation Outages
|  | Seasonal Load Adjustment | 0 | 0 | 0 | 3693 | Based on extreme weather conditions using 2011's weather
|  | Typical Maintenance Outages | 422 | 422 | 422 | 422 | Based on historical average of planned outages for June through September weekdays (starting in February 2012)
|  | Typical Forced Outages, Thermal | 3076 | 3076 | 3076 | 3076 | Based on historical average of forced outages for June through September weekdays (starting in February 2012)
|  | 90th Percentile Forced Outages, Thermal | 0 | 2019 | 0 | 0 | Based on historical forced outages assuming a 90% confidence interval
|  | Low Wind Output Adjustment | 0 | 0 | 3035 | 0 | Based on the 10th percentile of wind output associated with the 100 highest Net Load hours (Load minus wind output) for the 2013-2016 summer Peak Load seasons; this wind output level is 751 MW
| [d] Total Uses of Reserve Capacity |  | 3498 | 5517 | 6533 | 7191
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 5179.86 | 3160.86 | 2144.86 | 1486.86
Less than 2,300 MW indicates risk of EEA1

## Summer_Capacities
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1286
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1295
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
16 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800
22 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805
23 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805
24 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 535
25 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 535
26 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
27 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
28 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
29 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
30 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
31 | SANDOW U5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
32 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
33 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 156
34 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 156
35 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
36 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
37 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
38 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
39 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 149
40 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 149
41 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
42 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 157
43 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 157
44 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 319
45 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150
46 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150
47 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233
48 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 148.9
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 81.4
50 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 148.9
51 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 150.2
52 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 214.9
53 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 166
54 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 166
55 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
56 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75
57 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75
58 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70
59 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163
60 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163
61 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178
62 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 70
63 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 62
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 101
65 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 69
66 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 63
67 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 103
68 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 172
69 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 164
70 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 164
71 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
72 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 181
73 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 193
74 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 181
75 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 193
76 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
77 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 165
78 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 196
79 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116
80 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 169
81 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 169
82 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 182
83 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 169
84 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 161
85 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 161
86 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 169
87 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 161
88 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 161
89 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 420
90 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 420
91 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 151.6
92 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 151.6
93 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 176.2
94 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 151.7
95 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 151.7
96 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 174.5
97 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 148
98 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 148
99 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 148
100 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 148
101 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 197
102 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 197
103 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 216
104 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 216
105 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225
106 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225
107 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143
108 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143
109 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172
110 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 150
111 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 150
112 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 295
113 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
114 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
115 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295
116 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
117 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
118 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 163
119 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153
120 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153
121 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 163
122 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
123 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
124 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170
125 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170
126 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
127 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 208.6
128 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 208.6
129 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 253
130 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 235
131 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 235
132 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 235
133 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 235
134 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 252
135 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 252
136 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 157
137 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 157
138 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 319
139 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 149
140 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 143
141 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 145.3
142 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 143.7
143 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 204.9
144 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 204.9
145 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196
146 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195
147 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326
148 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195
149 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195
150 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312
151 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 191.2
152 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 191.2
153 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 334.7
154 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76
155 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76
156 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
157 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164
158 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164
159 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167
160 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74
161 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74
162 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
163 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72
164 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72
165 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
166 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 154
167 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 154
168 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 154
169 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
170 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
171 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50
172 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
173 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
174 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150
175 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145
176 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
177 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
178 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
180 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
181 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
182 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
183 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
184 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
185 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
186 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
187 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
188 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 96.6
189 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 96.6
190 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 96.6
191 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.6
192 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160
193 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125
194 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
197 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
198 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 212
199 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 212
200 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 241
201 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5
202 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5
203 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280
204 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 18
205 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 45
206 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 47
207 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48
208 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48
209 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48
210 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48
211 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 71
212 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 70
213 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 69
214 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 68
215 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 147
216 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 147
217 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 38
218 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 38
219 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 38
220 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 38
221 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 56
222 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 56
223 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 56
224 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
225 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56
226 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 56
227 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
228 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
229 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
230 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 90.1
231 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 87.3
232 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 45
233 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
234 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
235 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
236 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 68
237 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 68
238 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 68
239 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 68
240 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68
241 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67
242 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
243 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
244 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
245 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
246 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 68
247 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 65
248 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 68
249 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 69
250 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 70
251 | RED GATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
252 | RED GATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
253 | RED GATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
254 | RED GATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
255 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 104
256 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 104
257 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
258 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11
259 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11
260 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
261 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
262 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
263 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
264 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
265 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
266 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
267 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
268 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
269 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
270 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
271 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
272 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
273 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
274 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
275 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
276 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
277 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
278 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 79
279 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
280 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
281 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
282 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
283 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
284 | W A PARISH - PETRA NOVA CTG |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 74
285 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
286 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
287 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
288 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
289 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
290 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
291 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
292 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 107
293 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315
294 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
295 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
296 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
297 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
298 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
299 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
300 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
301 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
302 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
303 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
304 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
305 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
306 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
307 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 19
308 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 22
309 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 20
310 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
311 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 24
312 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
313 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
314 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
315 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
316 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
317 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
318 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
319 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
320 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
321 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
322 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
323 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
324 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
325 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
326 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
327 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
328 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
329 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
330 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
331 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
332 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
333 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
334 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
335 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
336 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
337 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
338 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
339 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
340 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
341 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
342 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
343 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
344 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
345 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
346 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
347 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
348 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
349 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
350 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
351 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
352 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
353 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 66852.6
354
355 | Operational Resources (Hydro)
356 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
357 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
358 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
359 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
360 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
361 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
362 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
363 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
364 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
365 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
366 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
367 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
368 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
369 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
370 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
371 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
372 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
373 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
374 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
375 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
376 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
377 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
378 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
379 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
380 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
381 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
382 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
383 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
384 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
385 | Operational Capacity Total (Hydro) | [6 empty] | 555.1
386 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 461.3
387
388 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -175
389 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 67138.9
390
391 | Operational Resources (Switchable)
392 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | WEST | 2016 | 54.6
393 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | WEST | 2016 | 54.6
394 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | WEST | 2016 | 54.6
395 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190
396 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190
397 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | WEST | 2016 | 190
398 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 153
399 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 155
400 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 315
401 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 153
402 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 155
403 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 315
404 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160
405 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160
406 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 160
407 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
408 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156
409 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135
410 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153
411 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402
412 | Switchable Capacity Total | [6 empty] | 3705.8
413
414 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -843.8
415
416 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0
417
418 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4150
419 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 4.7
420
421 | Operational Resources (Wind)
422 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
423 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
424 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
425 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
426 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
427 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
428 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
429 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
430 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
431 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
432 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
433 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
434 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
435 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
436 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
437 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
438 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
439 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
440 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
441 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
442 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
443 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
444 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
445 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
446 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2
447 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2
448 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
449 | ELECTRA WIND 1 |  | ELECTRAW_UNIT1 | WILBARGER | WIND | WEST | 2016 | 98.9
450 | ELECTRA WIND 2 |  | ELECTRAW_UNIT2 | WILBARGER | WIND | WEST | 2016 | 131.1
451 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
452 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
453 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
454 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
455 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
456 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
457 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
458 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
459 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
460 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2016 | 150
461 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9
462 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
463 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
464 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
465 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 50
466 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 100
467 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100
468 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2016 | 131.1
469 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2016 | 98.9
470 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
471 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
472 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
473 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115
474 | INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
475 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
476 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
477 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
478 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2016 | 96
479 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2016 | 74
480 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2016 | 30
481 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
482 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
483 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
484 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
485 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
486 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
487 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
488 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
489 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 103.8
490 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 106.3
491 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
492 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
493 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
494 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
495 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
496 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
497 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
498 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
499 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
500 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
501 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200
502 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110
503 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
504 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
505 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
506 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
507 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
508 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
509 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
510 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
511 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
512 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
513 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
514 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
515 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
516 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
517 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
518 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
519 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
520 | PYRON WIND |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
521 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
522 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
523 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
524 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
525 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
526 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
527 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
528 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
529 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
530 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
531 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145
532 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
533 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
534 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102
535 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98
536 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5
537 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8
538 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
539 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
540 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
541 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
542 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
543 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
544 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
545 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
546 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 18.1
547 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 105
548 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
549 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
550 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
551 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
552 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
553 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
554 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
555 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
556 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
557 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
558 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
559 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9
560 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3
561 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
562 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
563 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
564 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
565 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
566 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
567 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
568 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
569 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 16212.5
570 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 14
571
572 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
573 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
574 | CAMERON COUNTY WIND [CAMWIND_UNIT1] |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
575 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
576 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
577 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
578 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
579 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
580 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
581 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
582 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
583 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
584 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
585 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
586 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
587 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 94
588 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2141.4
589 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 58
590
591 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 18353.9
592
593 | Operational Resources (Solar)
594 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
595 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 22
596 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
597 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
598 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
599 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
600 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
601 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
602 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
603 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
604 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 104.5
605 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
606 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
607 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
608 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
609 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
610 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
611 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
612 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
613 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
614 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
615 | Operational Capacity Total (Solar) | [6 empty] | 554
616 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 77
617
618 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  | 2016 | 0
619
620 | Non-Synchronous Tie Resources
621 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
622 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
623 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
624 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
625 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
626 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
627 | Non-Synchronous Ties Total | [6 empty] | 1250
628 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 425.2
629
630 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
631 | BLUE SUMMIT BATTERY | 16INR0122 |  | WILBARGER | STORAGE | WEST | 2017 | 0
632 | COLORADO BEND II | 17INR0007 |  | WHARTON | GAS | SOUTH | 2017 | 1088
633 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0
634 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2019 | 0
635 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2017 | 324
636 | INDECK WHARTON ENERGY CENTER | 15INR0023 |  | WHARTON | GAS | SOUTH | 2019 | 0
637 | PINECREST ENERGY CENTER PROJECT | 16INR0006 |  | ANGELINA | GAS | NORTH | 2020 | 0
638 | WOLF HOLLOW 2 | 17INR0009 |  | HOOD | GAS | NORTH | 2017 | 1069
639 | FRIENDSWOOD G | 13INR0049 |  | HARRIS | GAS | HOUSTON | 2017 | 0
640 | BETHEL CAES PROJECT | 15INR0013 |  | ANDERSON | STORAGE | NORTH | 2020 | 0
641 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2018 | 0
642 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2018 | 0
643 | NASA-JSC CHP [PRIVATE USE NETWORK UNIT] | 16INR0054 |  | HARRIS | GAS | HOUSTON | 2017 | 0
644 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 2481
645
646 | Planned Wind Resources with Executed SGIA
647 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2017 | 0
648 | LONGHORN WIND SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
649 | MARIAH WIND A | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 0
650 | MARIAH WIND B | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2017 | 230.4
651 | MARIAH DEL SUR | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2018 | 0
652 | RATTLESNAKE DEN WIND 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2020 | 0
653 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2017 | 0
654 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2018 | 0
655 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2018 | 0
656 | GRANDVIEW WIND 3 (CONWAY) | 13INR0005c |  | CARSON | WIND | PANHANDLE | 2017 | 0
657 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2018 | 0
658 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2018 | 0
659 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2017 | 0
660 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2017 | 200
661 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2018 | 0
662 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2018 | 0
663 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2017 | 0
664 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2017 | 0
665 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2018 | 0
666 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2017 | 0
667 | WILLOW SPRINGS WIND | 14INR0060b |  | HASKELL | WIND | WEST | 2017 | 0
668 | MUENSTER WIND | 15INR0085 |  | COOKE | WIND | NORTH | 2017 | 125.6
669 | FALVEZ ASTRA W | 15INR0074 |  | DEAF SMITH | WIND | PANHANDLE | 2017 | 163.2
670 | CHAPMAN RANCH WIND I | 16INR0055 |  | NUECES | WIND-C | COASTAL | 2017 | 250
671 | BLANCO CANYON WIND (COTTON PLAINS) | 16INR0037 |  | FLOYD | WIND | PANHANDLE | 2017 | 50
672 | BLANCO CANYON WIND (OLD SETTLER) | 16INR0037b |  | FLOYD | WIND | PANHANDLE | 2017 | 150
673 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2019 | 0
674 | ROCK SPRINGS VAL VERDE WIND | 11INR0082a |  | VAL VERDE | WIND | WEST | 2017 | 0
675 | MAGIC VALLEY WIND II (REDFISH 2A and 2B) | 14INR0041a |  | WILLACY | WIND-C | COASTAL | 2017 | 0
676 | SALT FORK WIND 2 | 16INR0082 |  | CARSON | WIND | PANHANDLE | 2017 | 0
677 | SANTA RITA WIND | 16INR0091 |  | REAGAN | WIND | WEST | 2017 | 0
678 | SWISHER WIND | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2017 | 0
679 | BUCKTHORN WIND 1 | 14INR0057 |  | ERATH | WIND | NORTH | 2017 | 0
680 | FLUVANNA RENEWABLE 1 | 13INR0056 |  | SCURRY | WIND | WEST | 2017 | 0
681 | RTS WIND | 16INR0087 |  | MCCULLOCH | WIND | SOUTH | 2017 | 0
682 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
683 | LOGAN'S GAP WIND II | 15INR0082 |  | COMANCHE | WIND | NORTH | 2017 | 0
684 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2018 | 0
685 | SALT FORK WIND EXPANSION | 16INR0121 |  | CARSON | WIND | PANHANDLE | 2017 | 0
686 | CHOCOLATE BAYOU | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2018 | 0
687 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2018 | 0
688 | DERMOTT WIND 1 | 17INR0027 |  | SCURRY | WIND | WEST | 2017 | 0
689 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2018 | 0
690 | BEARKAT WIND A | 15INR0064 |  | GLASSCOCK | WIND | WEST | 2017 | 0
691 | BEARKAT WIND B | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2018 | 0
692 | INFINITY LIVE OAK WIND | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2017 | 0
693 | Planned Capacity Total (Wind) | [6 empty] | 1169.2
694
695 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 919.2
696 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 14
697
698 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 250
699 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 58
700
701 | Planned Solar Resources with Executed SGIA
702 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2017 | 7.4
703 | FS BARILLA SOLAR 2 | 12INR0059c |  | PECOS | SOLAR | WEST | 2017 | 0
704 | OCI ALAMO 6 (WEST TEXAS) | 15INR0070_1 |  | PECOS | SOLAR | WEST | 2017 | 110
705 | OCI ALAMO 6 (WEST TEXAS PHASE II) | 15INR0070_1b |  | PECOS | SOLAR | WEST | 2017 | 50
706 | SE BUCKTHORN WESTEX SOLAR (RIGGINS SOLAR) | 15INR0045 |  | PECOS | SOLAR | WEST | 2017 | 0
707 | FS EAST PECOS SOLAR | 16INR0073 |  | PECOS | SOLAR | WEST | 2017 | 120
708 | LC NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2017 | 0
709 | PECOS SOLAR POWER I | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0
710 | BNB LAMESA SOLAR | 16INR0023 |  | DAWSON | SOLAR | WEST | 2017 | 101.6
711 | BNB LAMESA SOLAR B | 16INR0023b |  | DAWSON | SOLAR | WEST | 2018 | 0
712 | CAPRICORN RIDGE SOLAR | 16INR0019 |  | COKE | SOLAR | WEST | 2017 | 0
713 | UPCO POWER 1 (SP-TX-12) | 16INR0065 |  | UPTON | SOLAR | WEST | 2019 | 0
714 | CASTLE GAP SOLAR 2 | 16INR0065a |  | UPTON | SOLAR | WEST | 2020 | 0
715 | SP-TX-12-PHASE B | 16INR0065b |  | UPTON | SOLAR | WEST | 2017 | 0
716 | SOLAIREHOLMAN 1 | 15INR0061 |  | BREWSTER | SOLAR | WEST | 2017 | 50
717 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2018 | 0
718 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0
719 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2020 | 0
720 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0
721 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2018 | 0
722 | Planned Capacity Total (Solar) | [6 empty] | 439
723 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 77
724
725 | RMR Resources
726 | GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 2016 | 371
727 | Total RMR Capacity | [6 empty] | 371
728
729 | Mothballed Resources
730 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420
731 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
732 | S R BERTRON CTG 2 (SINCE 5/15/2013) |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
733 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
734 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
735 | S R BERTRON U3 (SINCE 5/22/2013) |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
736 | S R BERTRON U4 (SINCE 5/22/2013) |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
737 | Total Mothballed Capacity | [6 empty] | 1567
738
739 | Retiring Resources Unavailable to ERCOT (since last SARA report)
740 | LUFKIN BIOMASS |  | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
741 | Total Retiring Capacity | [6 empty] | 45
Note on B631: 30 MW capacity; 0 MW assumed to be available for the peak load hour.
Note on B643: Iincorporated in aggregate PUN capacity, line items 424-425

## Background
Release Date: March 1, 2017
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.