## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE.
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2018)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items
AEN | Hamilton Aen CB HM_950 | CB | 138 | 15/4 | DCKT Burleson to Carson Creek 138 kV & Pedernales to Advanced Micro Devices Aen 138 kV | Manesium Plant - Northlan 138 kV | RT | Forced
AEN | Howard Lane Aen - Techridge | LN | 138 | 17/1 | DCKT Austrop to Daffin Gin & Aen Dunlap to Decker 138 kV | Howard Lane Tap - Howard Lane Aen 138 kV | ST | Planned
AEN | Slaughter Lane - Lytton Springs | LN | 138 | 17/11 | DCKT Stoney Ridge to Garfield Aen & Hicross Aen to Garfield Aen 138 kV | Lytton Springs - Pilot Knob 138 kV | RT | Planned
AEN, LCRA | Holman Aen - Fayette Plant 2 | LN | 345 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
AEP | Agave - Lon Hill | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Air Liquide Ingleside - … - Dupont Sw - Ingleside & Oxychem Ingleside | LN | 138 | 16/4, 17/8, 18/1 | Dupont Pp1 Ingleside to Ingleside Cogen Sw 138 kV (3A), Lon Hill to Coleto Creek 345 kV, Dupont Sw - Ingleside to Ingleside Cogen Sw 138 Kv | Duppont Pp1 Ingleside - Duppont Sw Ingleside 138 kV, Lon Hill - Pawnee Switching Station 345 kV, Dupont Pp1 - Ingleside to Dupont Sw - Ingleside 138 kV | ST, RT | Planned, Forced
AEP | Airco Aep - Rincon | LN | 138 | 17/5, 17/9, 17/10 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV, Coleto Creek to Victoria 138 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, Coleto Creek to Victoria 138 kV | Blessing - Lolita 138 kV, Lon Hill to Pawnee Switching Station 345 kV, Formosa - Lolita 138 kV, Coleto Creek - Victoria 138 kV | RT | Forced
AEP | Airline Aep - … - Westside Aep | LN | 138 | 18/1 | Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Rodd Field - Holly 138 kV | RT | Planned
AEP | Airline Aep - Holly | LN | 138 | 18/1 | Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Rodd Field - Holly 138 kV | RT | Planned
AEP | Ajo - Rio Hondo | LN | 345 | 16/2, 17/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV | Celanese Bishop - Nelson Sharpe 138 kV, Lon Hill - Bessel 138 kV | ST | Planned
AEP | Alpine - … - Barrilla | LN | 69 | 17/9 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
AEP | Armstrong Aep - … - Raymondville 2 | LN | 138 | 16/3 | Valley Import | N/A | RT | Forced
AEP | Aspermont Aep - Paint Creek | LN | 138 | 16/4 | Scurry Sw to Sun Sw 138 kV | Paint Creek Auto 69-2 138/69 kV | RT | Forced
AEP | Barney Davis Bus #1 (CB 6755, etc.) | BUS | 138 | 16/10 | DCKT Barney Davis to Airline Aep 138 kV | Barney Davis - Rodd Field 138 kV | ST | Planned | Y
AEP | Barney Davis Bus #2 (CB 5200, etc.) | BUS | 138 | 16/10, 17/2, 17/3 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned, Forced | Y
AEP | Barrilla - Fort Stockton Sw | LN | 69 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Bates - … - North Edinburg & Palmhurst | LN | 138 | 17/11 | DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Planned
AEP | Beeville - … - Victoria | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Bevo - Asherton | LN | 138 | 15/11 | Basecase | Low Voltage from Dimmit to DC Eagle Pass | ST | Forced
AEP | Big Three - … - Bp Chem Vistron4 | LN | 138 | 17/6 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned, Forced
AEP | Blessing - Stp Sw | LN | 138 | 18/1 | Lane City to Blessing 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced
AEP | Blessing Auto 1382 138/69 kV | XF | 138 | 17/10, 17/12 | Coleto Creek to Victoria 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 | Coleto Creek - Victoria 138 kV, Pawnee Switching Station - Calaveras 345 kV, San Miguel Auto ATAH 345/138 KV | RT | Planned
AEP | Bruni - Crestonio | LN | 138 | 15/5, 15/6 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP | Celanese Bishop Bus #1 (CB 6305, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Celanese Bishop Bus #2 (CB 6075, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Coleto - Lon Hill | LN | 345 | 17/3, 15/3, 16/1, 16/12 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV | RT, ST | Planned, Forced | Y, N
AEP | Coleto - Victoria (COLETO_VICTOR1) | LN | 138 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Del Sol - … - North Edinburg | LN | 345 | 16/10, 17/1 | Valley GTC | N/A | ST | Planned | Y
AEP | Dupont Sw Ingleside - ... - Portland | LN | 138 | 15/1 | DCKT Dupont Sw Ingleside to Whitepoint & Hecker 138 kV | Rincon - Whitepoint 138 kV | ST | Planned
AEP | Eagle Hydro Tap - … - Hamilton Road | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP | Fannin Sub - Victoria | LN | 69 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Fort Stockton Plant - … - Fort Stockton Sw | LN | 69 | 18/3, 18/4 | Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV, Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Yucca Drive Sw - Gas Pad 138 kV, 16Th Street Tnp - Woodward 2 138 kV, Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned
AEP | Fort Stockton Plant - Conoco Comp Station | LN | 69 | 18/3, 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Fort Stockton Plant - Solstice | LN | 138 | 17/12 | Basecase, Barrilla Auto Trx Fmr1 138/69 kV | Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Fort Stockton Plant Auto 69T1 138/69 kV | XF | 138 | 17/12, 18/3, 18/4 | Basecase, Barrilla Auto Trx Fmr1 138/69 Kv, Barilla to Solstice 138 kV, Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV | Yucca Drive Sw - Gas Pad 138 Kv, Alamito Creek - Paisano 69 kV, 16Th Street Tnp - Woodward 2 138 kV, Pig Creek - Solstice 138 kV | RT | Planned
AEP | Fort Stockton Sw - … - Rio Pecos | LN | 69 | 17/12, 18/1 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV, Barilla to Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Alamito Creek - Paisano 69 kV | RT | Forced
AEP | Frontera - … - Key Sw & Palmhurst | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Frontera - Bates | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Planned
AEP | Fulton - … - Rockport | LN | 69 | 17/9, 17/11 | DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Gateway - … - North Laredo Sw & Wormser Road | LN | 138 | 18/4 | Kendall to Cagnon 345 kV | CICO - Comfort 138 kV | RT | Forced
AEP | Gila - … - Whitepoint | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Hamilton Road - Brackettville | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned
AEP | Harlingen #1 - … - La Palma | LN | 69 | 18/1 | Lon Hill to Coleto Creek 345 kV, Dyann to Wharton 138 kV, La Palma to East Harrison 69 kV, North Edinburg Auto Trx 1382 345/138 kV | Warburton Road Switching Station - Victoria 138 kV, El_Campo - Lane City Pump 138 kV, North Edinburg Auto 138H 345/138 kV | RT | Forced
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS0) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS2) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Whitepoint (HECKER_WHITE_1) | LN | 138 | 17/3, 18/1 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Lon Hill to Coleto Creek 345 kV | Whitepoint - Rincon 138 kV, Warburton Road Switching Station - Victoria 138 kV | RT | Planned, Forced
AEP | Hecker - Whitepoint (HECKER_WHITE_2) | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV | Warburton Road Switching Station - Victoria 138 kV | RT | Forced
AEP | Hiway 9 Auto 69A2 138/69 kV | XF | 138 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Industrial Aep - Nueces Bay | LN | 69 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Ingleside - Aransas Pass | LN | 138 | 17/8 | Lon Hill to Coleto Creek 345 Kv | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | Ingleside - Dupont Sw | LN | 138 | 17/4 | Rockport to Rincon 138 kV | Gregory - Rincon 69 kV | ST | Forced
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned
AEP | Jim Treece - Tesla | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned | Y
AEP | Joslin Bus #1 (CB 8315, etc.) | BUS | 138 | 17/3 | Formosa Unit FORMOSG12, Formosa Unit FORMOSG3 | Formosa - Lolita 138 kV | RT | Planned
AEP | La Palma - … - Stewart Road | LN | 69 | 18/1 | North Edinburg Auto Trx 1382 345/138 kV | North Edinburg Auto 138H 345/138 kV | RT | Forced
AEP | La Palma Bus #2 (CB 5875, etc.) | BUS | 138 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Laredo Vft North - … - Mines Road | LN | 138 | 18/4 | Molina to Wormser Road 138 kV, Lobo to Molina 138 kV | Del_Mar - Laredo Plant 138 kV | RT | Planned
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Las Pulgas - Rio Hondo | LN | 138 | 17/4 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Liston - Garza | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned
AEP | Lobo - Laquinta | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y
AEP | Lobo - Laredo Vft North | LN | 138 | 15/4 | Laredo VFT North to Lobo 138 kV | Asherton - Catarina 138 kV | ST | Planned
AEP | Lobo Auto A1 345/138 kV | XF | 345 | 17/6 | Lobo Auto Trx A2 345/138 kV | Asherton - Catarina 138 kV | RT | Forced
AEP | Lolita - Victoria | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Blessing - Lolita 138 kV, Formosa - Lolita 138 kV | RT | Planned
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 15/2, 15/10, 16/3, 16/4 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Ajo to Rio Hondo 345 kV | Bunsen - Lon Hill 138 kV, Celanese Bishop - Kleberg 138 kV | ST | Planned | Y
AEP | Lon Hill - Whitepoint | LN | 345 | 17/8, 18/2 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Marion Auto AT2H 345/138 kV | RT | Forced
AEP | Lon Hill Auto 69A2 138/69 kV | XF | 138 | 17/4 | Hecker to WhitePoint 138 kV, Lon Hill Auto 69A1 138/69 kV | Whitepoint - Rincon 138 kV, Koch Up River Auto 69A1 138/69 kV | RT | Planned
AEP | Lon Hill Bus #1 (CB 6005, etc.) | BUS | 138 | 15/5 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned
AEP | Mvec (Rangerville) - … - Wesmer | LN | 138 | 18/2 | Polk Avenue to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Naval Base - … - Port Aransas | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 15/3, 16/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Valley GTC | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, N/A | RT, ST | Planned, Forced
AEP | North Edinburg - Rio Hondo | LN | 345 | 16/3 | North Edinburg to Lon Hill 345 kV | Burns Sub - Rio Hondo 138 kV | ST | Planned
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | North Edinburg Bus #1 (CB 5010, etc.) | BUS | 138 | 16/9 | North McAllen to North Edinburg 138 kV | North Edinburg - McColl Road 138 kV | ST | Planned
AEP | North McAllen - North Pharr | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 16/5, 16/6, 17/1 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned
AEP | Pig Creek - Musquiz | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned
AEP | Pig Creek - Solstice | LN | 138 | 17/9 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
AEP | Port Aransas - Seawall Aep | LN | 69 | 17/3, 18/1 | DCKT Whitepoint to McCambell & Dupons Sw Ingleside 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 Kv, Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Whitepoint - Rincon 138 kV, Rodd Field - Holly 138 kV | RT | Planned, Forced
AEP | Raymondville 2 - … - Rio Hondo | LN | 138 | 16/12 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Rio Hondo - La Palma | LN | 345 | 17/12 | Danevang Switching Station to Blessing 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV | Blessing Auto 69A1 138/69 kV, Pawnee Switching Station - Calaveras 345 kV | RT | Planned
AEP | Rockport Auto 69A1 138/69 kV | XF | 138 | 17/9 | Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | Rockport Auto T2 138/69 kV | XF | 138 | 17/9 | Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | San Angelo Concho - Rusthill | LN | 138 | 15/6 | San Angelo College Hills Auto 69T1 138/69 kV | San Angelo Power Station Auto 69T1 138/69 kV | RT | Forced
AEP | San Angelo Concho Auto 69T1 | XF | 138 | 15/2, 15/6, 15/7 | San Angelo North Auto 69T1 138/69 kV, San Angelo College Hills Auto 69T1 138/69 kV | San Angelo College Hills Auto 69T1 138/69 kV, San Angelo Power Station Auto 69T1 138/69 kV | RT | Planned, Forced
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned
AEP | Solstice to Alamito Creek | LN | 138 | 18/2 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Forced
AEP | Sonora Auto 69-1 138/69 kV | XF | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP | South Carbide - Hwy 511 Sub | LN | 138 | 16/6 | South Carbide to Loma Alta Sub 138 kV | La Palma - Villa Cavazos 138 kV | ST | Planned
AEP | Tesla - Jim Treec | LN | 345 | 17/2 | Panhandle GTC | N/A | ST | Planned
AEP | West Batesville Bus #1 (CB 1005, etc.) | BUS | 138 | 15/4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | ST | Planned
AEP | Whitepoint Auto 345A 345/138 kV | XF | 345 | 18/3 | Lon Hill Auto Trx Lon_Hill_3_2 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Forced
AEP | Whitepoint Bus #0010 (CB 3900, etc.) | BUS | 345 | 18/3 | DCKT Menger Creek to Cico 138 kV & Kendall to Cagnon 345 kV | Medina Lake - Tally Rd 138 kV | RT | Forced
AEP | Whitepoint Bus #0014 (CB 3930, etc.) | BUS | 345 | 18/3 | DCKT Menger Creek to Cico 138 kV & Kendall to Cagnon 345 kV | Medina Lake - Tally Rd 138 kV | RT | Forced
AEP, BRAZOS | Salt Creek Bepc - … - Spur | LN | 138 | 16/3, 16/10 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP, CNP | Whitepoint - South Texas Project | LN | 345 | 17/9, 17/11, 17/12, 18/1, 18/3 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | RT | Forced
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (1) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (2) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, ETT | Clear Crossing - … - Edith Clarke (EDITHC_GAUSS2) | LN | 345 | 17/7, 17/8, 17/9 | Basecase | Panhandle GTC | RT | Planned
AEP, ETT | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned
AEP, ETT | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned
AEP, LCRA | Mesa View Sw - … - Tunas Creek | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH1) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH2) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
AEP, ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6427, 6332_A) | LN | 138 | 18/3, 18/4 | Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV, Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | 16Th Street Tnp - Woodward 2 138 kV, Yucca Drive Sw - Gas Pad 138 kV | RT | Planned, Forced
AEP, SHARYLAND | Frontera - … - Railroad | LN | 138 | 18/3 | Polk Avenue to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP, SHARYLAND | North Edinburg - Palmito | LN | 345 | 18/1 | Basecase | Valley Import | RT | Forced
AEP, STEC | Calallen Sub - … - Stadium Aep | LN | 69 | 18/3 | Lon Hill Auto 382H 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Planned
AEP, STEC | Danevang Switching Station - Blessing | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned
AEP, STEC | George West Switching Station - … - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
AEP, STEC | La Sara Sub - … - Raymondville 2 | LN | 138 | 18/4 | San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP, STEC | Lobo - San Miguel | LN | 345 | 15/11, 16/4 | Rio Bravo to Zapata 138 kV, Javalina Tap to Rio Bravo 138 kV | Freer - San Diego 69 kV, Voltage Collapse | ST | Planned
AEP, STEC | Loop 463 - Victoria | LN | 138 | 16/3 | Four Corners to Sam Rayburn Sw 138 kV | Sam Rayburn Switching Station Auto 69_2 138/69 kV | ST | Planned
AEP, STEC | Moore Sw - Downie Sw | LN | 138 | 16/10, 17/4 | Downie Switching Station to Uvalde Aep 138 kV | Downie Switching Station Auto AX1 138/69 kV | ST | Planned | Y
AEP, STEC | Orange Grove Switching Station - Lon Hill | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced
BPUB | Loma Alta Substation - Waterport Substation | LN | 138 | 18/1 | La Palma to East Harrison 69 kV | Haine Drive - La Palma 138 kV | RT | Forced
BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB | Power Plant Substation - Sixth Street Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned
BPUB | South Plant Substation - Sixth Street Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned
BPUB | Waterport Sub - Loma Alta Sub 138 kV | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB | Waterport Sub - Southmost Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced
BPUB, TMPA | Gibbons Creek - Btu_Jack_Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y
BRAZOS | Hasse Auto Xfm1 138/69 kV | XF | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Forced
BRAZOS | Hilltop Lakes - Watson Chapel | LN | 138 | 17/8 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Lewisville Sw Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
BRAZOS | Navo - Krugerville | LN | 138 | 15/10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Forced
BRAZOS | Rw Miller - Jaybird | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Stephenville Bepc Auto FMR1 | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Whitney Bus 1525 (CB 5075, etc.) | BUS | 138 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS | Whitney Bus BB1 (CB 210, etc.) | BUS | 69 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS, DME, ONCOR | Arco - Navo - Collin Ses | LN | 138 | 16/6, 16/7, 16/8, 16/9, 17/3 | Fort Worth Sub to West Denton 138 kV, Jim Christal Sub to West Denton 138 kV, DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV, Fort Worth Sub - West Denton 138 kV, Corinth (Oncor) - Pockrus Sub 138 kV | RT | Planned
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Sw | LN | 345 | 17/3 | Jones Street Tnp to Lewisville | Ti Tnp - West Tnp 138 kV | RT | Planned
BRAZOS, ONCOR | Keller - … - Roanoke Sw | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
BRAZOS, ONCOR | Navarro - … - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
BRAZOS, ONCOR | Plano Communication Parkway - Spring Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Wagley Robertson - Summerfield 138 kV | RT | Planned
BRAZOS, ONCOR | Rhome Bepc - … - Roanoke Sw (RNKSW_ELZBTHCK) | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
BRAZOS, TMPA | Gibbons Creek - Keith Sw 138 kV | LN | 138 | 16/10 | Gibbons Creek to Btu_East 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | RT | Planned
BTU | Btu_Dansby - Btu_Atkins | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_Dowling - Btu_Enterprise | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced
BTU | Btu_Dowling - Btu_Texas_Am | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_East - Btu_Shady_Lane 69 | LN | 69 | 16/6 | Btu_Atkins Auto FMR1 138/69 kV | Btu_Briarcrest - Btu_Nall_Lane 69 kV | RT | Forced
CNP | Airpro - Quanum | LN | 138 | 17/5 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Channelview - Lynch 138 kV | RT | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018
CNP | Airpro - Shell | LN | 138 | 16/8, 18/1 | DCKT Chambers to King & Cedar Bayou to Jordan 345 kV, Ph Robinson to Center 345 kV | Aritek - Chorin 138 kV, Cedar Bayou Plant - Strang 138 kV | RT | Planned, Forced |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018
CNP | Arcola - … - Wa Parish (TM_WAP82) | LN | 138 | 17/10 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Bellaire - … - Britmoore (BI_UL_24) | LN | 138 | 17/11 | Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Planned |  | CenterPoint Energy | Identified Outage is remotely located from Overload (CNP outage and ONCOR overload)
CNP | Bellaire - … - Jeanetta | LN | 138 | 17/10 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Bellaire - Wa Parish | LN | 345 | 16/10 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Smithers 345 kV | ST | Planned
CNP | Bigvue - Power Systems Arco Cogen | LN | 138 | 17/4 | DCKT Cedar Bayou Plant to Quanum & Strang 138 kV | Channelview - Lynch 138 kV | RT | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018
CNP | Biport - … - Riwood | LN | 138 | 17/6 | DCKT Dow Chemical to Oasis 345 kV | Sintek to Stratt 138 kV | RT | Planned |  | CenterPoint Energy | Jones Creeek project completed in 2017
CNP | Bunker - … - Stadium | LN | 138 | 18/4 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Cedar Bayou Plant - Strang | LN | 138 | 17/10 | Ph Robinson to Center 345 kV | Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018. EXN-Lynch upgrades will be completed by YE 2018.
CNP | Center - Ph Robinson | LN | 345 | 16/5, 15/3, 16/3 | Meadow to Ph Robinson 345 kV, Ph Robinson Auto AT4 345/138 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV, DCKT Cedar Bayou Plant to Chambers & Jordan 345 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Meadow Auto AT1 345/138 kV, Cedar Bayou Plant Auto AT3 345/138 kV, Brine - Langston 138 kV, Cedar Bayou Plant - Strang 138 kV, Chorin - Strang 138 kV | RT, ST | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018. Second Auto at Meadow added in 2017. Have taken outages since with no observed congestion.
CNP | Chorin - Aritek | LN | 138 | 17/5 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Channelview - Lynch 138 kV | RT | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018
CNP | Copper - … - Seaway & Velasco | LN | 138 | 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Fairbanks To - Th Wharton | LN | 138 | 17/11 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Fairmont - … - Garden Villas (DR_GV_94) | LN | 138 | 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Garrott - Kirby (GT_KB_37) | LN | 138 | 17/9 | Meadow to Oasis 345 kV | Angleton - Liverpool 138 kV | RT | Planned
CNP | Goodyear - Lydell | LN | 138 | 17/4 | DCKT Greens Bayou to Gable & Hardy to Crockett 138 kV | Midtown - Garrott 138 kV | RT | Planned |  | CenterPoint Energy | Goodyear - Lydell line no longer exists under current system configuration. Additionally Midwtown-Garrott overload was temporarily derated during observed congestion. Line was uprated in early 2018.
CNP | Greens Bayou - … - Humble (GBYPW_94) | LN | 138 | 17/11 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | ST | Planned
CNP | Greens Bayou Bus #138A (CB G480, etc.) | BUS | 138 | 17/9 | Addicks to Th Wharton 345 Kv | Lauder - North Belt 138 kV | RT | Forced |  | CenterPoint Energy | Congestion due to temporary reconfigured GBY substation during Harvey
CNP | Greens Bayou Bus #138B (CB G500, etc.) | BUS | 138 | 17/9 | Addicks to Th Wharton 345 Kv | Lauder - North Belt 138 kV | RT | Forced |  | CenterPoint Energy | Congestion due to temporary reconfigured GBY substation during Harvey
CNP | Greens Bayou Bus #345A (CB A980, etc.) | BUS | 345 | 17/8, 17/9 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV, Addicks to Th Wharton 345 kV | Genral - University 69 kV, Lauder - North Belt 138 kV | RT | Forced |  | CenterPoint Energy | Congestion due to temporary reconfigured GBY substation during Harvey
CNP | Greens Bayou Bus #345D (CB A990, etc.) | BUS | 345 | 17/8, 17/9 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV, Addicks to Th Wharton 345 kV | Genral - University 69 kV, Lauder - North Belt 138 kV | RT | Forced |  | CenterPoint Energy | Congestion due to temporary reconfigured GBY substation during Harvey
CNP | H O Clarke - … - Southwyck | LN | 138 | 18/3 | DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 16/3 | DCKT South Texas Project to Dow Chemial & Jones Creek 345 kV | South Texas Project - Wa Parish 345 kV | RT | Planned
CNP | Jewett - Limestone (225) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned
CNP | Jewett - Limestone (226) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Jones Creek - Cortez | LN | 138 | 17/9 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV | RT | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Jordan - North Belt | LN | 345 | 17/9, 17/10 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Forced
CNP | Marine - Cortez | LN | 138 | 17/11, 18/1 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned, Forced |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Moody - … - Stewart | LN | 138 | 18/1 | Ph Robinson to Center 345 kV | Cedar Bayou Plant - Strang 138 kV | RT | Forced |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | North Belt - … - Scenic Woods | LN | 138 | 17/10 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Oasis - Dow Chemical (DOWOAS27) | LN | 345 | 16/9 | DCKT WA Parish to Bailey & Hillje 345 kV | Oasis - Dow Chemical 345 kV (18) | RT | Planned, Forced |  | CenterPoint Energy | Jones Creeek project completed in 2017 and second Auto Transformer added a Meadow allieviates congestion.
CNP | Petson - Monsan | LN | 138 | 17/10 | Petson to Monsan 138 kV | Intermediate - Southwyck 138 kV; | RT | Planned |  | CenterPoint Energy | Southwyck was reconfigured and Intermediate-Southwyck is now a radial line.
CNP | Richmond Tank Switchrack - Chamon Power | LN | 138 | 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 Kv | Singleton - Zenith 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Roans Prairie - Singleton | LN | 345 | 16/1 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Singleton - Zenith (SNGZEN98) | LN | 345 | 15/12, 17/1, 17/2, 17/3, 17/4, 15/7, 17/5, 17/10, 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV | Singleton - Zenith 345 kV (99), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (99), Singleton - Tomball 345 kV (74) | RT, ST | Planned, Forced |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | Singleton - Zenith (SNGZEN99) | LN | 345 | 15/12, 17/2, 17/3, 17/4, 17/1, 17/5, 17/10, 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV | Singleton - Zenith 345 kV (98), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (98), Singleton - Tomball 345 kV (74) | RT, ST | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP | South Channel - Sr Bertron | LN | 69 | 17/8 | DCKT Cedar Bayou Plant to Strang & Cedar Bayou Plant to Quanum 138 kV, Meadow to Oasis 345 kV, Meadow to Ph Robinson 345 kV | Exxon to Lynch 138 kV, Angleton - Liverpool 138 kV, Seminole Tnp - Friendswood Tnp 138 kV | RT | Planned |  | CenterPoint Energy | Topology changed due to PHR A3 reconfiguration and CKT 87 & 88 swap completed in 2018. EXN-Lynch upgrades will be completed by YE 2018.
CNP | South Lane City - New Gulf | LN | 138 | 15/12 | DCKT Wharton to East Bernard & Dyann 138 kV (UNSOLVED) | N/A | ST | Planned
CNP | Texwal Switchrack - Wallisville | LN | 69 | 17/8 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV | Genral - University 69 kV | RT | Forced |  | CenterPoint Energy | Conversion of Channel load to 138 kV solved loading issues on 69 kV.
CNP | Village Creek - Zenith | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Wa Parish - … - Telview & Dewalt (SIEWAP02) | LN | 138 | 18/4 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | Webster - Friendswood (FW_WEB05) | LN | 138 | 18/2 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP | White Oak Auto AT3 345/138 kV | XF | 345 | 16/6 | DCKT Britmoore to Sauer 138 kV | Bellaire - San Felipe 138 kV | RT | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM18) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM27) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, STEC | Franklins Camp Sub - … - Jones Creek | LN | 138 | 18/1 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
CNP, TMPA | Gibbons Creek - Limestone (Gib_Lime18) | LN | 345 | 18/2, 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP, TMPA | Gibbons Creek - Limestone (Gib_Lime50) | LN | 345 | 18/2, 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP, TMPA | Gibbons Creek - Singleton (SNGXGC99) | LN | 345 | 15/12, 17/4, 17/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Jewett to Singleton 345 kV | Singleton - Zenith 345 kV (98), Singleton - Zenith 345 kV (99), Singleton - Gibbons Creek 345 kV (75), Singleton - Gibbons Creek 345 kV (75), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned | Y | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP, TMPA | Gibbons Creek Bus 5200 (CB 5030, etc.) | BUS | 345 | 17/3 | DCKT Jewett to Singleton 345 kV | Singleton - Gibbons Creek 345 kV (75) | ST | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP, TMPA | Singleton - Gibbons Creek (SNGXGC75) | LN | 345 | 17/1, 17/4, 17/11 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV, Singleton - Gibbons Creek 345 kV (99), Singleton - Gibbons Creek 345 kV (99), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned |  | CenterPoint Energy | Houston Import Project system upgrades completed in 2018 allievates congenstion
CNP, TNMP | Ph Robinson - Gaf Tnp | LN | 138 | 18/1 | Caddo Sw Sta Tnp to Greenbelt Tnp 138 kV | Tejas Tnp - Comanche Sw Tnp 138 kV | RT | Planned |  |  | TNMP
CPS | Ballpark - … - Olmos | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Cagnon Auto MR3 | XF | 345 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Calaveras - Cagnon | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced
CPS | Calaveras - Pawnee Switching Station | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced
CPS | Calaveras - Skyline (N5_P4) | LN | 345 | 17/5, 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV | RT | Planned, Forced
CPS | Calaveras - Skyline (N5_P4_2) | LN | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV | RT | Planned
CPS | Cibolocr - ... - Green_Mt | LN | 138 | 15/2 | DCKT Hill Country to Marion & Elmcreek 345 kV | Marion - Skyline 345 kV | RT | Planned
CPS | Elmcreek - Hill Country | LN | 345 | 15/10 | DCKT Marion to Hill Country & Skyline 345 kV | EC Mornhinweg - Parkway Lcra 138 kV | ST | Planned
CPS | Hill Country Bus #1 (CB 11T4, etc.) | BUS | 138 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Holbrook - Kirby 138 kV | LN | 138 | 16/10 | DCKT Calaveras to Hotwells & Laredo1 138 kV | Kirby - St_Hedwg 138 kV | RT | Planned
CPS | Howard - Somerset | LN | 138 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV | RT | Planned
CPS | Laredo 1 - Five Pts | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Nacdches - Wb Tuttle | LN | 138 | 17/1 | DCKT Cagnon to Tcc & Pinn_Rd 138 kV | Medinabs - 36Th Street 138 kV | ST | Planned
CPS | Skyline - Elmcreek (P4_E5_1) | LN | 345 | 16/11 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV | RT | Planned
CPS | Skyline - Elmcreek (P4_E5_2) | LN | 345 | 16/11, 17/12 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV, Skyline - Elmcreek 345 kV | RT | Planned
CPS | Txresrch (V3) - Castrvll (D1) | LN | 138 | 16/8, 16/10 | Somerset to Howard 138 kV | Pleasanton Sub - Tordillo 69 kV | ST | Planned | Y
CPS | Weiderstein - Randolph | LN | 138 | 15/9 | DCKT Skyline to Harmony & Nachches 138 kV | Fratt - Parkway Lcra 138 kV | ST | Planned | Y
CROSS | Gray South Bus (CB G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y
CROSS | Railhead - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, N/A, Low Voltage in Panhandle area | RT, ST | Planned | Y
CROSS, SHARYLAND | Alibates - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, Low Voltage in Panhandle area | ST | Planned | Y
DME | Cooper Creek Sub - Industrial Sub | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME | Denton Steam - … - Woodrow Substation | LN | 138 | 18/3, 18/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Jones Street Tnp to Lewisville Sw 138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Ti Tnp - West Tnp 138 kV | RT | Planned
DME | Teasley - Forth Worth | LN | 138 | 15/10 | Denton Arco to North Denton Interchange 138 kV | Hickory - Locust 69 kV | ST | Planned
DME, GAR | Denton Steam Auto AT1 138/69 kV | XF | 138 | 18/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
DME, ONCOR, TNMP | Arco - Krugerville | LN | 138 | 17/5 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
DME, TMPA | Arco To - Cooper Creek Sub | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
DME, TMPA | Cooper Creek Sub - … - Denton Arco | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME, TMPA | Fort Worth Sub - West Denton | LN | 138 | 16/10 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV | ST | Planned | Y
DME, TMPA | North Denton - Arco - Denton Arco | LN | 138 | 15/7, 16/4, 16/5 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV, DCKT Roanoke Sw to West Denton & Lewisville Sw to Krum West Sw 345 kV | Teasley Sub - Pockrus Sub 138 k, Fort Worth Sub - West Denton 138 kV | RT | Planned, Forced
DME, TMPA | West Denton - Jimchristal | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest to Lakepointe Tnp 138 kV | RT | Planned
ETT, ONCOR | Riley - Krum West Sw (SKRWRI15) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ETT, ONCOR | Riley - Krum West Sw (SKRWRI25) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
GAR | Elmgrove - … - Olinger | LN | 138 | 15/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Elmgrove - Wylie Sw | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced
GAR | Wylie Sw - Olinger (WYL_OLI2) | LN | 138 | 15/9, 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned
LCRA | Bevo Auto BEVO | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned
LCRA | Clear Springs - Marion | LN | 345 | 18/2, 18/4 | DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | CICO - Comfort 138 kV, Marion Auto AT2H 345/138 kV | RT | Planned
LCRA | Coronado - … - Sherwood Shores | LN | 138 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Ctec Buchanan - … - Kingsland 1 | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Fayette Plant 1 - Fayette Plant 2 | LN | 345 | 15/3, 16/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Fayette Plant 1 - Fayetteville | LN | 345 | 15/2, 15/3 | DCKT Lost Pines to Austrop & Dunlop 345 kV | Fayette Plant 1 - Fayette Plant 2 345 kV | RT | Planned
LCRA | Fayette Plant 1 - Salem Lcra | LN | 345 | 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Lampasas - … - San Saba | LN | 138 | 17/5 | Comanche Sw (Oncor) to Mercers Gap Sw | Holder Auto FMR1 138/69 kV | RT | Planned
LCRA | Marion - Zorn | LN | 345 | 16/3, 18/2, 18/4 | DCKT South Texas Project Unit 1 & 2, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | Marion - Clear Springs 345 kV, Marion Auto AT2H 345/138 kV, CICO to Comfort 138 kV | RT | Planned
LCRA | Marion Bus #5201 (CB GCB_7010_CB, etc.) | BUS | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, Clear Springs Auto Trx Cleasp_At1 345/138 kV, DCKT Schertz to Cibolo 138 kV, DCKT Jewett to Singleton 345 kV, Clear Springs to Freiheit 138 kV | Skyline - Elmcreek 345 kV, Clear Springs Auto AT2H 345/138 kV, E C Mornhinweg to Parkway 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Henne - Zorn 138 kV | RT | Forced
LCRA | Marion Bus #5202 (CB GCB_7030_CB, etc.) | BUS | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, Clear Springs Auto Trx Cleasp_At1 345/138 kV, DCKT Schertz to Cibolo 138 kV, DCKT Jewett to Singleton 345 kV, Clear Springs to Freiheit 138 kV | Skyline - Elmcreek 345 kV, Clear Springs Auto AT2H 345/138 kV, E C Mornhinweg - Parkway 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Henne - Zorn 138 kV | RT | Forced
LCRA | McElmurray Tap Sw DSC MOS_19119 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Moore Lcra DSC MOS_13021 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Pitsburg - … - Ctec Buchanan | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Smithville - Winchester | LN | 138 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
LCRA | Turnersville - Lytton Springs | LN | 138 | 17/11 | DCKT Stoney Ridge to Garfield Aen & Hicross Aen to Garfield Aen 138 kV | Lytton Springs - Pilot Knob 138 kV | RT | Planned
LCRA | Winchester - Paige | LN | 138 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
LCRA | York Creek - Seguin | LN | 138 | 15/9 | DCKT Zorn to Marion & Clear Springs 345 kV | Comal - Henne 138 kV | ST | Forced
LCRA, STEC | Ricebird - Nada | LN | 138 | 18/1 | Dyann to Wharton 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced
LST, ONCOR | Big Brown Ses - Navarro (10) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT | Planned
LST, ONCOR | Big Brown Ses - Navarro (60) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV, DCKT Limestone to Navarro 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT, ST | Planned
ONCOR | Alcon Tap - Everman Sw | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned
ONCOR | Allen Sw - Renner Sw | LN | 345 | 18/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Andrews County South - … - Andrews North | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | No Trees Sw - Cheyenne Tap 138 kV | RT | Forced
ONCOR | Andrews North - Andrews County South | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned
ONCOR | Audelia Termination - … - Judd Court & Kirkland Park (3250_C) | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Benbrook Sw - Parker Sw (6005) | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Benbrook Sw - Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced
ONCOR | Big Brown Ses - Jewett (50) | LN | 345 | 17/4 | DCKT Trinidad Ses to Richland Chambers 345 kV | Big Brown Ses - Jewett 345 kV | RT | Forced
ONCOR | Bowen - … - Bowen Tate Tap & Village Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Brownwood - … - Brownwood Sw | LN | 138 | 17/2, 17/3, 17/4, 17/5 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6185) | LN | 138 | 17/4, 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265), Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6190) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced
ONCOR | Carrollton Northwest - … - Plano Tennyson (840) | LN | 138 | 16/1, 16/6 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Lewisville Sw Auto FMR2 345/138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Fort Worth Sub - West Denton 138 kV | RT | Planned
ONCOR | Carrollton Northwest Bus #1 | BUS | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Carrollton Tarpley Road - … - Renner Sw | LN | 138 | 17/9 | DCKT Liggett Sw to Venus Sw 345 Kv | Sargent Road - Watermill Sw 345 kV | RT | Planned
ONCOR | Cedar Crest Sw - … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Centerville Road Sw - … - Parkdale Sw (3680_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Centerville Road Sw - Forney Sw | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | ADD
CNP | Chambers - King | LN | 345 | 17/9, 17/10, 18/3 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV, DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV, Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned, Forced
ONCOR | Champion Paper Mill Tap - … - Lufkin Sw | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 kV | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Planned
CNP | Chocolate Bayou - … - H O Clarke & Karsten & Quail Valley (QV_TV_26) | LN | 138 | 17/10 | Coleto Creek to Victoria 138 kV, DCKT Jewett to Singleton 345 kV, Meadow to Oasis 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Coleto Creek - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Intermediate - Southwyck 138 kV, Singleton - Zenith 345 kV | RT | Planned |  | CenterPoint Energy | It is not likely that a 138 kV line outage would significantly impact a 345 kV that is remotely located. Also Houston Import Project related which now completed.
ONCOR | Collville - … - Norwood Sw | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Comanche Peak Ses - Everman Sw | LN | 345 | 2017 | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6016) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6062) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Sw (Oncor) - Brownwood | LN | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Planned
ONCOR | Crowley - … - Forest Hill Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Culberson Sw - … - Riverton Sw | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced
ONCOR | Cushing Southest Tap - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Forced
ONCOR | Denton Tap - … - Saginaw Sw (6402) | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Desoto Sw - Watermill Sw | LN | 345 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
ONCOR | Diboll Southern Pine - … - Lufkin Pershing Tap & Lufkin Hill Street Tap | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 Kv | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Forced
ONCOR | Duval - North Main Sw | LN | 138 | 18/1 | Forest Hill Sw Auto TRX FMR1 138/69 kV | Handley Ses Auto MR1H 138/69 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6260) | LN | 138 | 17/4 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6265) | LN | 138 | 17/4, 17/11, 18/2 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, DCKT Eagle Mountain to Saginaw Sw 138 kV | Blue Mound - Wagley Robertson 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | East Levee Sw - … - Record Crossing (3415_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | East Levee Sw - West Netowrk | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned
ONCOR | Edgemere Term - … - Kirkland Park (3630_B) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Elkton - Forney Sw | LN | 345 | 2017, 17/11 | Trinidad - Enterprise and - Stryker DCKT | Elkton 345/138 kV auto | ADD, RT | Planned
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD
ONCOR | Euless - … - Grapevine Ball Street (1065) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Grapevine Ball Street (745) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned, Forced
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Kimball Ave & McKamy Tap | LN | 138 | 17/5, 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Euless - … - Liggett Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Euless - … - Roanoke Sw (1065) | LN | 138 | 16/12, 17/1, 17/2, 17/3, 16/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned
ONCOR | Everman Sw - Oakhill Tap 1 | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned
ONCOR | Forney Sw - Royse Sw (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Forney Sw - Royse Sw (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Greenville Ave Sw - … - Kirkland Park (3490_B) | LN | 138 | 17/11, 17/12 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Hackberry - … - Norwood Sw (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Handley Ses - Tate Springs (6310_E) | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Handley Ses - White Tap 1 | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ONCOR | Hicks Sw - … - Roanoke Sw (6273_A, 6273_B, 6273_C) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Hicks Sw - … - Roanoke Sw (6274_C, 6274_A) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Hicks Sw - … - Saginaw Sw | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Hicks Sw - … - Saginaw Sw (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - … - Saginaw Sw (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Poi - Eagle Mountain Ses 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - Alliance (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6276) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6277) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hicks Sw Bus West (CB 13580, etc.) | BUS | 138 | 16/12, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw CB 11615 | LN | 345 | 16/12 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hutto - … - Round Rock (1660) - … - Georgetown South (1680) 138 kV | LN | 138 | 16/9 | DCKT Temple Sw to Knob Creek Sw 345 kV & Bell County 138 kV | Round Rock - Chief Brady 138 kV | RT | Planned
ONCOR | Jewett Bus #1 (CB 3900, etc.) | BUS | 345 | 16/11 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT, ST | Planned, Forced
ONCOR | Johnson Sw (Oncor) - Comanche Peak Ses | LN | 345 | 17/5, 17/9, 18/4 | Comanche Peak Ses to Mitchell Bend Sw 345 kV | Wolf Hollow 345 Sw - Comanche Peak Ses 345 kV | RT | Planned
ONCOR | Keller Tap - … - Roanoke Sw | LN | 138 | 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Kennedale - Century | LN | 345 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned, Forced
ONCOR | Kirkland Park - … - Greenville Ave Sw (3500_C) | LN | 138 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned
ONCOR | Lufkin South - … - Lufkin Sw (1370) | LN | 138 | 16/7 | Nacogdoches Se to Mt Enterprise 345 kV | Lufkin - Lufkin Sw 138 kV | RT | Planned
ONCOR | Lufkin Sw - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned
ONCOR | Lufkin Sw - Stryker Creek Ses | LN | 345 | 15/9, 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Planned, Forced
ONCOR | Lufkin Sw Auto MR1 | XF | 345 | 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Forced
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Midland County Northwest Sw - High Sky (6463_A) | LN | 138 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
ONCOR | Mitchell Bend Sw - Decordova Ses | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Montfort Sw - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
ONCOR | Monticello Ses - Sulphur Springs Sw | LN | 345 | 16/3 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Monticello Ses - Sulphur Springs Sw 345 kV | RT | Planned
ONCOR | Moss Sw - Yukon Sw | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Mountain Creek Ses - … - West Levee Sw (3380) | LN | 138 | 16/10 | Mountain Creek Ses Auto MR1 138/69 kV | Cedar Crest Sw - Oak Cliff South 138 kV | RT | Planned
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Northaven Sw - Edgemere Term (3630_C) | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Norwood Sw - Cedar Hill Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV | Sargent Road - Watermill Sw 345 kV | RT | Planned
ONCOR | Norwood Sw Auto Mrh1 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Norwood Sw Auto Mrh2 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Odessa Basin Sw - … - Wink Sub | LN | 69 | 17/3, 17/4, 17/6 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV, Wink Sub to Wink Tnp 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned, Forced
ONCOR | Paris Sw – Monticello Ses | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley Ses | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley South | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw Bus BB2 (CB 6790, etc.) | BUS | 345 | 2017 | Paris switch – Valley and Valley south 345 kV Dckt | Paris 345/138 kV auto | ADD
ONCOR | Paris Sw CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Parkdale Sw - … - Prairie Creek Sw | LN | 138 | 18/2, 18/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6720_G, 6720_I) | LN | 69 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto FMR1 138/69 kV | RT | Forced
ONCOR | Permian Basin Ses - Wink Sub | LN | 138 | 15/6 | Chevron Has to Wickett Whiting Oil 138 kV | Northward - Wink Sub 69 kV | RT | Planned
ONCOR | Permian Basin Ses Auto Fmr2 138/69 kV | XF | 138 | 17/6 | Winks to Permian Basin Ses, Wink Sub to Wink Tnp 138 kV | Permian Basin Ses Auto MR1H 138/69 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned
ONCOR | Permian Basin Ses Bus #2 (CB 2460, etc.) | BUS | 138 | 17/4 | Ward Gulf Tap to Wink Sub 138 kV, Chevron Has to Ward Gulf Tap South 138 kV | Permian Basin Ses Auto MR1 138/69 kV | RT, ST | Planned
ONCOR | Roanoke Sw - Hicks Sw | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT, ST | Planned | Y
ONCOR | Rocky Creek - Mitchell Bend Sw | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Royse Sw Auto #1 | XF | 345 | 15/9 | Royse Sw Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned
ONCOR | Sandow 5 Ses - Sandow Sw (1726) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow 5 Ses CB_S5360 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow Ses - Sandow Sw (1725) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5300 | CB | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5320 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Sw - Austrop (440) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Austrop (450) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Bell County East Sw (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced
ONCOR | Sandow Sw - Bell County East Sw (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced
ONCOR | Sandow Sw - Sandow Ses (1728) | LN | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sargent Road - West Levee Sw 345 kV | LN | 345 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Temple Sw - Bell County East Sw | LN | 345 | 15/3 | Navarro to Watermill Sw 345 kV | Big Brown Ses - Richland Chambers 345 kV | RT | Planned
ONCOR | Three Mile Draw Sw - Orla Southwest Poi | LN | 138 | 18/1 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Trinidad Ses - Watermill Sw | LN | 345 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned
ONCOR | Trinidad Ses Bus #1 (CB 4020, etc.) | BUS | 345 | 17/2 | DCKT Big Brown Ses to Jewett 345 kV | Trinidad Ses - Richland Chambers 345 kV | RT | Forced
ONCOR | Tyler East - … - Tyler Grande (1770) | LN | 138 | 16/10, 16/7 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned | Y
ONCOR | Watermill Sw - West Levee Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV, West Levee Sw Auto Trx Wlvee_3_1 345/138 kV | Sargent Road - Watermill Sw 345 kV, Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | White Tap 1 - Trinity | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ONCOR | Wink Sub - Orbison Tap | LN | 138 | 18/2 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
ONCOR | Wink Sub - Yucca Drive Sw | LN | 138 | 18/3 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV | RT | Planned
ONCOR | Wink Sub Auto Fmr1 138/69 kV | XF | 138 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto MR2L 138/69 kV | RT | Planned
ONCOR | Wink Sub Bus BBN (CB 12800, etc.) | BUS | 138 | 17/6 | Winks to Permian Basin Ses | Permian Basin Ses Auto MR1H 138/69 kV | RT | Planned
ONCOR | Wolf Switching Station - Ward Gulf Tap | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Yucca Drive Sw - … - Holt Sw | LN | 138 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned
ONCOR, TNMP | Permian Basin Ses - … - Yucca Drive Sw (6920_A, 6710) | LN | 69 | 18/3 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
SHARYLAND | Alibates - Aj Swope Sharyland Utilities | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Alibates - Tule Canyon (ALIB_TULE_2) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
SHARYLAND | Elbow - Bulldog Su | LN | 138 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Trigas Odessa Tap - Odessa Ehv Sw | ST | Planned | Y
SHARYLAND | Grandview Wind Farm - Alibates | LN | 345 | 15/5 | Isolates Generation | N/A | ST | Planned
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R1) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R2) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon Bus #1 (CB TCN7100, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Tule Canyon Bus #2 (CB TCN7102, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW1) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW2) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | Windmill Entire Station | ST | 345 | 16/8 | Basecase | Resource Isolation | ST | Planned | Y
STEC | Calliham Sw - … - San Miguel Sw & San Miguel 69 kV Switchyard | LN | 69 | 17/6, 18/4 | Zorn to Marion 345 kV, DCKT Big Hill to Kendall 345 kV | Marion - Clear Springs 345 kV, Hamilton Road - Maverick 138 kV | RT | Planned
STEC | Fowlerton - Tilden 138 Sub | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
STEC | Poteet Sub - Oaks Sub | LN | 69 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned
STEC | Sam Rayburn - Vanderbilt | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned
STEC | San Miguel Auto ATA | XF | 345 | 15/3, 16/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Pawnee Sw to San Miguel 345 kV | Fannin Sub - Victoria 69 kV, San Miguel Auto ATB 345/138 kV | ST | Planned | Y
STEC | San Miguel Auto ATB | XF | 345 | 15/10 | Lobo Auto AT2 345/138 kV | San Miguel Auto ATA 345/138 kV | ST | Planned
STEC | Vanderbilt Sw - Sam Rayburn Sw 138 kV | LN | 138 | 16/1 | Pawnee Sw to Coleto Creek 345 kV | Magruder - Victoria 138 kV | ST | Planned | Y
TMPA | Olinger - … - Pruitt | LN | 138 | 15/7 | Basecase | Low Voltage at Pruitt 138 kV | ST | Planned | Y
TNMP | Choctaw Tnp - … - Terminal Tnp | LN | 69 | 17/11 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
TNMP | Dickinson - Freeway Park | LN | 138 | 15/8 | North Alvin Tnp to Meadow 138 KV | PH Robinson - Southshore TNP 138 kV | RT | Forced
TNMP | Freeway Park Tnp - Alvin Tnp | LN | 138 | 16/6, 16/8 | Ph Robinson Auto AT1 345/138 kV, Ph Robinson Auto AT1 345/138 kV, North Alvin Tnp to Meadow 138 kV | Seminole Tnp - Friendswood Tnp 138 kV, Seminole Tnp - Friendswood Tnp 138 kV, Southshore Tnp - Ph Robinson 138 kV | RT, ST | Planned | Y, N
TNMP | Gaf - Greenbelt | LN | 138 | 16/2 | Freeway Park Tnp to Heights Tnp 138 kV | Heights Tnp - Ph Robinson 138 kV | ST | Planned
TNMP | Grant Avenue Tnp - Amoco Tnp | LN | 69 | 17/10, 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Caddo Sw Sta Tnp to Apache Tnp 138 kV | Singleton - Zenith 345 kV, Choctaw Tap Tnp - Choctaw Tnp | RT | Planned, Forced
TNMP | Greenbelt - Amoco Oil Cogen (G138_23) | LN | 138 | 16/2 | Greenbelt to Caddo Sw 138 kV | Greenbelt - Tejas 138 kV | ST | Planned
TNMP | Ih 20 Tnp Auto Iht1 138/69 kV | XF | 138 | 18/3, 18/4 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced
TNMP | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 17/11, 17/12 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
TNMP | Mainland Tnp - Freeway Park Tnp | LN | 138 | 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
TNMP | Praxair Tap Tnp - Grant Avenue Tnp | LN | 69 | 17/10 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
TNMP | Tejas Tnp - Greenbelt Tnp | LN | 138 | 17/11 | Caddo Sw Sta Tnp to Apache Tnp 138 kV | Choctaw Tap Tnp to Choctaw Tnp | RT | Planned
LCRA, ONCOR | North McCamey - Odessa Ehv Sw | LN | 345 | 2018 | McCamey GTC |  | ADD
LCRA, STEC | Schneeman Draw - Big Hill | LN | 345 | 2018 | McCamey GTC |  | ADD

## Form - Request for Addition
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Contingency | Overload | Addition Requestor | Reason for Addition