## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE.
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## Oncor Comments
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items
ONCOR | Big Brown Ses - Jewett (50) | LN | 345 | 17/4 | DCKT Trinidad Ses to Richland Chambers 345 kV | Big Brown Ses - Jewett 345 kV | RT | Forced |  | Oncor (Generation Retirement) | Big Brown generation was the driver of this congestion. Big Brown was retired on 2/12/2018 and this MTE should be removed.
LST, ONCOR | Big Brown Ses - Navarro (10) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT | Planned |  | Oncor (Generation Retirement) | Big Brown generation was the driver of this congestion. Big Brown was retired on 2/12/2018 and this MTE should be removed.
LST, ONCOR | Big Brown Ses - Navarro (60) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV, DCKT Limestone to Navarro 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT, ST | Planned |  | Oncor (Generation Retirement) | Big Brown generation was the driver of this congestion. Big Brown was retired on 2/12/2018 and this MTE should be removed.
ONCOR | Monticello Ses - Sulphur Springs Sw | LN | 345 | 16/3 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Monticello Ses - Sulphur Springs Sw 345 kV | RT | Planned |  | Oncor (Generation Retirement) | This should no longer be an issue with Monticello's retirement (1/4/2018).
ONCOR | Sandow 5 Ses - Sandow Sw (1726) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Sandow 5 Ses CB_S5360 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Sandow Ses - Sandow Sw (1725) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Sandow Ses CB_5300 | CB | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Sandow Ses CB_5320 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Sandow Sw - Sandow Ses (1728) | LN | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD |  |  | Oncor (Generation Retirement) | Sandow generation was the driver of this congestion. Sandow was retired on 1/11/2018 and this MTE should be removed.
ONCOR | Temple Sw - Bell County East Sw | LN | 345 | 15/3 | Navarro to Watermill Sw 345 kV | Big Brown Ses - Richland Chambers 345 kV | RT | Planned |  | Oncor (Generation Retirement) | Big Brown generation was the driver of this congestion. Big Brown was retired on 2/12/2018 and this MTE should be removed.
ONCOR | Trinidad Ses Bus #1 (CB 4020, etc.) | BUS | 345 | 17/2 | DCKT Big Brown Ses to Jewett 345 kV | Trinidad Ses - Richland Chambers 345 kV | RT | Forced |  | Oncor (Generation Retirement) | Big Brown generation was the driver of this congestion. Big Brown was retired on 2/12/2018 and this MTE should be removed.
ONCOR | Culberson Sw - … - Riverton Sw | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. Outaged line was part of Culberson loop construction. This part of construction is now completed, network topology has been changed. Besides, Culberson loop is a relativelly radial network, construction will not have significant impact on system congestion.
ONCOR | Duval - North Main Sw | LN | 138 | 18/1 | Forest Hill Sw Auto TRX FMR1 138/69 kV | Handley Ses Auto MR1H 138/69 kV | RT | Planned |  | Oncor (Invalid Entry) | This MTE no longer exists. Numerous lines in this area are being converted from 69kV to 138kV and the congestion observed may have been due to a temporary configuration during this work.
ONCOR | Greenville Ave Sw - … - Kirkland Park (3490_B) | LN | 138 | 17/11, 17/12 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. The Ti Tnp - West Tnp 138kV line is a 'frequent offender' from the standpoint of congestion. It makes sense that loss of the double circuit 345kV lines between Carrollton Northwest and Lewisville Switch would aggravate this constraint. It does not make sense that the Greenville Avenue - Kirkland Park 138kV line would significantly worsen this contingency because it is electrically and geographically isolated. It is possible that there were numerous outages at the time this congestion was observed in 2017 that contributed to the actual congestion. Since future congestion cannot be tied to the outage of this particular element, it should be removed from the MTE list. This constraint is a usually a high wind high north central weather zone load issue. Greenville Avenue - Kirkland Park 138kV has very small line outage distribution factor from the study case. It should not be identified as a major contributor to this constraint.
ONCOR | Hicks Sw CB 11615 | LN | 345 | 16/12 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Forced |  | Oncor (Invalid Entry) | With the current system configuration, keeping this breaker open reduces congestion. Loss of the Hicks - Roanoke 345kV line also trips the Hicks - Parker 345kV line, which routes power away from Hicks Switch to reduce overloads on the 138kV lines between Eagle Mountain and Saginaw.
ONCOR | Lufkin Sw - Stryker Creek Ses | LN | 345 | 15/9, 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Planned, Forced |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. The Centerville I45 - Pleasant Springs (Hcec) 138 kV line is not expected to overload (cause congestion) as it is operated as a radial 138kV feed into a 69kV network (served by autotransformers at Crockett, Palestine and Trinidad. Per studies performed on the SSWG cases posted in June 2018, the line outage distribution factor for this MTE is insignificant.
ONCOR | Lufkin Sw Auto MR1 | XF | 345 | 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Forced |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. The Centerville I45 - Pleasant Springs (Hcec) 138 kV line is not expected to overload (cause congestion) as it is operated as a radial 138kV feed into a 69kV network (served by autotransformers at Crockett, Palestine and Trinidad. Per studies performed on the SSWG cases posted in June 2018, the line outage distribution factor for this MTE is insignificant.
ONCOR | Midland County Northwest Sw - High Sky (6463_A) | LN | 138 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. With high wind, high loading on the Dermott - Bluff Creek 138kV line (Knapp - Scurry Chevron) is expected for a prior double circuit outage of the Clear Crossing - Dermott Switch lines followed by a fault on the double circuit Dermott - Scurry County South lines. These should remain on the MTE list. However, the Midland County Northwest - High Sky outage is electrically and geographically isolated and should be remoted from the MTE list. It does not significantly contribute to this congestion when out of service on its own.
ONCOR | Mountain Creek Ses - … - West Levee Sw (3380) | LN | 138 | 16/10 | Mountain Creek Ses Auto MR1 138/69 kV | Cedar Crest Sw - Oak Cliff South 138 kV | RT | Planned |  | Oncor (Invalid Entry) | This MTE is a radial line. An outage on this element will not cause congestion.
ONCOR | Odessa Basin Sw - … - Wink Sub | LN | 69 | 17/3, 17/4, 17/6 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV, Wink Sub to Wink Tnp 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned, Forced |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR | Paris Sw - Valley Ses | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD |  |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. With the listed outage and contingency applied, 1072 MVA rated Paris Sw - Valley South 345 kV line and 750 MVA rated Paris Sw 345/138 kV Auto will provide sufficient line capacity for Lamar Power Partners
ONCOR | Paris Sw - Valley South | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD |  |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. With the listed outage and contingency applied, 1072 MVA rated Paris Sw - Valley 345 kV line and 750 MVA rated Paris Sw 345/138 kV Auto will provide sufficient line capacity for Lamar Power Partners.
AEP, ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6427, 6332_A) | LN | 138 | 18/3, 18/4 | Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV, Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | 16Th Street Tnp - Woodward 2 138 kV, Yucca Drive Sw - Gas Pad 138 kV | RT | Planned, Forced |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6720_G, 6720_I) | LN | 69 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto FMR1 138/69 kV | RT | Forced |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR, TNMP | Permian Basin Ses - … - Yucca Drive Sw (6920_A, 6710) | LN | 69 | 18/3 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR | Permian Basin Ses - Wink Sub | LN | 138 | 15/6 | Chevron Has to Wickett Whiting Oil 138 kV | Northward - Wink Sub 69 kV | RT | Planned |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR | Permian Basin Ses Auto Fmr2 138/69 kV | XF | 138 | 17/6 | Winks to Permian Basin Ses, Wink Sub to Wink Tnp 138 kV | Permian Basin Ses Auto MR1H 138/69 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned |  | Oncor (Invalid Entry) | The MTE no longer exists and should be removed. The local area has been significantly reconfigured.
ONCOR | Permian Basin Ses Bus #2 (CB 2460, etc.) | BUS | 138 | 17/4 | Ward Gulf Tap to Wink Sub 138 kV, Chevron Has to Ward Gulf Tap South 138 kV | Permian Basin Ses Auto MR1 138/69 kV | RT, ST | Planned |  | Oncor (Invalid Entry) | The overloaded element no longer exists. The local area has been significantly reconfigured. This MTE should be removed from the list.
ONCOR | Three Mile Draw Sw - Orla Southwest Poi | LN | 138 | 18/1 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. Outaged line was part of Culberson loop construction. This part of construction is now completed, network topology has been changed. Besides, Culberson loop is a relativelly radial network, construction will not have significant impact on system congestion.
ONCOR | Trinidad Ses - Watermill Sw | LN | 345 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. The congestion on Herty North Sw - Nacogdoches Se 138 kV experienced in December of 2017 was primarily driven by the following MTEs: * Cushing Southest Tap - … - Nacogdoches Se * Lufkin Sw - … - Nacogdoches Se With either of these lines out of service, loss of the contingency (DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV) forces generation from Martin Lake and Mount Enterprise into the 138kV Lufkin system via the autotransformer at Nacogdoches Southeast. The prior outage of the Trinidad Ses - Watermill Sw 345kV line does not significantly impact this constraint and should be removed from the MTE list.
ONCOR | Wink Sub - Orbison Tap | LN | 138 | 18/2 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned |  | Oncor (Invalid Entry) | Studies do not support MTE for Contingency/Overload combination. Outaged line was part of Culberson loop construction. This part of construction is now completed, network topology has been changed. Besides, Culberson loop is a relativelly radial network, construction will not have significant impact on system congestion.
ONCOR | Wink Sub Bus BBN (CB 12800, etc.) | BUS | 138 | 17/6 | Winks to Permian Basin Ses | Permian Basin Ses Auto MR1H 138/69 kV | RT | Planned |  | Oncor (Invalid Entry) | The overloaded element no longer exists. The local area has been significantly reconfigured. This MTE should be removed from the list.
ONCOR | Alcon Tap - Everman Sw | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned |  | Oncor (Multiple Outages) | The congestion experienced in April 2018 was due to numerous overlapping outages that spanned most of April. Specifically, there was a line rebuild on the lines between Wedgewood Switch and Forest Hill Switch/Everman Switch. Also, the Everman Switch - Mansfield 138kV line was being rebuilt. The rebuild work included moving line terminations at Everman Switch, which ultimately required a bus outage (and the Everman Switch - Oak Hill line outage). Performing the work concurrently ultimately reduced the duration needed for the more impactful bus outages. Future congestion of this magnitude is not expected.
ONCOR | Benbrook Sw - Parker Sw (6005) | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | Various circumstances contributed to a significant number of outages, of a significant duration in March of 2018. The following outages overlapped to create the congestion experience. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * Parket Sw - Benbrook Sw 345kV line * Rocky Creek - Mitchell Bend Sw 345kV line * Mitchell Bend Sw - Decordova Ses 345kV line * Benbrook - Decordova Ses 345kV line * Everman - Courtland 345kV line * Everman - Kennedale 345kV line
ONCOR | Carrollton Tarpley Road - … - Renner Sw | LN | 138 | 17/9 | DCKT Liggett Sw to Venus Sw 345 Kv | Sargent Road - Watermill Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | It was the overlapping outages scheduled in September of 2017 on the two 138kV lines (Watermill - West Levee and Norwood - Cedar Hill) that contributed to the overloads on the Sargent Road - Watermill 345kV line for loss of the double circuit between Liggett and Venus Switch. The Carrollton Tarpley Road - Renner Switch 138kV double circuit line outage overlapped for a period with the 345kV lines; however, the impact was significantly less. A single 345kV line outage is not expected to cause significant congestion.
ONCOR | Comanche Sw (Oncor) - Brownwood | LN | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Planned |  | Oncor (Multiple Outages) | This issue was observed because one of the BEPC Hasse autos (in parallel) was forced out of service 8/23/17 - 2/28/18). Now that it is back in service, this congestion should not continue to occur for an outage of the Comanche Switch - Brownwood 138kV line.
ONCOR | Desoto Sw - Watermill Sw | LN | 345 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned |  | Oncor (Multiple Outages) | The congestion experienced in December of 2017 was due to multiple simultaneous outages in the area. Specifically, in addition to the 345kV Desoto Sw - Watermill Sw and the 138kV Navarro - Trinidad SES and Montfort Sw - Trinidad SES lines, the following equipment was out of service: 345/138kV Auto at Watermill and the 345kV Watermill - Trinidad line. These outages all overlapped 12/5 - 12/9. Prior outage cancellations and projects deferred from 2016 into 2017 contributed to the need to take these outages simultaneously. Given the large number of elements required to be out simultaneously, these elements should be removed from the MTE list.
ONCOR | Everman Sw - Oakhill Tap 1 | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned |  | Oncor (Multiple Outages) | The congestion experienced in April 2018 was due to numerous overlapping outages that spanned most of April. Specifically, there was a line rebuild on the lines between Wedgewood Switch and Forest Hill Switch/Everman Switch. Also, the Everman Switch - Mansfield 138kV line was being rebuilt. The rebuild work included moving line terminations at Everman Switch, which ultimately required a bus outage (and the Everman Switch - Oak Hill line outage). Performing the work concurrently ultimately reduced the duration needed for the more impactful bus outages. Future congestion of this magnitude is not expected.
ONCOR | Kennedale - Century | LN | 345 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned, Forced |  | Oncor (Multiple Outages) | The congestion experienced in April 2018 was due to numerous overlapping outages that spanned most of April. Specifically, there was a line rebuild on the lines between Wedgewood Switch and Forest Hill Switch/Everman Switch. Also, the Everman Switch - Mansfield 138kV line was being rebuilt. The rebuild work included moving line terminations at Everman Switch, which ultimately required a bus outage (and the Everman Switch - Oak Hill line outage). Performing the work concurrently ultimately reduced the duration needed for the more impactful bus outages. Future congestion of this magnitude is not expected.
ONCOR | Kirkland Park - … - Greenville Ave Sw (3500_C) | LN | 138 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | Various circumstances contributed to a significant number of outages, of a significant duration in March of 2018. The following outages overlapped to create the congestion experience. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * Parket Sw - Benbrook Sw 345kV line * Rocky Creek - Mitchell Bend Sw 345kV line * Mitchell Bend Sw - Decordova Ses 345kV line * Benbrook - Decordova Ses 345kV line * Everman - Courtland 345kV line * Everman - Kennedale 345kV line
ONCOR | Mitchell Bend Sw - Decordova Ses | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | Various circumstances contributed to a significant number of outages, of a significant duration in March of 2018. The following outages overlapped to create the congestion experience. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * Parket Sw - Benbrook Sw 345kV line * Rocky Creek - Mitchell Bend Sw 345kV line * Mitchell Bend Sw - Decordova Ses 345kV line * Benbrook - Decordova Ses 345kV line * Everman - Courtland 345kV line * Everman - Kennedale 345kV line
ONCOR | Montfort Sw - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned |  | Oncor (Multiple Outages) | The congestion experienced in December of 2017 was due to multiple simultaneous outages in the area. Specifically, in addition to the 345kV Desoto Sw - Watermill Sw and the 138kV Navarro - Trinidad SES and Montfort Sw - Trinidad SES lines, the following equipment was out of service: 345/138kV Auto at Watermill and the 345kV Watermill - Trinidad line. These outages all overlapped 12/5 - 12/9. Prior outage cancellations and projects deferred from 2016 into 2017 contributed to the need to take these outages simultaneously. Given the large number of elements required to be out simultaneously, these elements should be removed from the MTE list.
BRAZOS, ONCOR | Navarro - … - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned |  | Oncor (Multiple Outages) | The congestion experienced in December of 2017 was due to multiple simultaneous outages in the area. Specifically, in addition to the 345kV Desoto Sw - Watermill Sw and the 138kV Navarro - Trinidad SES and Montfort Sw - Trinidad SES lines, the following equipment was out of service: 345/138kV Auto at Watermill and the 345kV Watermill - Trinidad line. These outages all overlapped 12/5 - 12/9. Prior outage cancellations and projects deferred from 2016 into 2017 contributed to the need to take these outages simultaneously. Given the large number of elements required to be out simultaneously, these elements should be removed from the MTE list.
ONCOR | Norwood Sw - Cedar Hill Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV | Sargent Road - Watermill Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | It was the overlapping outages scheduled in September of 2017 on the two 138kV lines (Watermill - West Levee and Norwood - Cedar Hill) that contributed to the overloads on the Sargent Road - Watermill 345kV line for loss of the double circuit between Liggett and Venus Switch. The Carrollton Tarpley Road - Renner Switch 138kV double circuit line outage overlapped for a period with the 345kV lines; however, the impact was significantly less. A single 345kV line outage is not expected to cause significant congestion.
ONCOR | Rocky Creek - Mitchell Bend Sw | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned |  | Oncor (Multiple Outages) | Various circumstances contributed to a significant number of outages, of a significant duration in March of 2018. The following outages overlapped to create the congestion experience. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * Parket Sw - Benbrook Sw 345kV line * Rocky Creek - Mitchell Bend Sw 345kV line * Mitchell Bend Sw - Decordova Ses 345kV line * Benbrook - Decordova Ses 345kV line * Everman - Courtland 345kV line * Everman - Kennedale 345kV line
ONCOR | Watermill Sw - West Levee Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV, West Levee Sw Auto Trx Wlvee_3_1 345/138 kV | Sargent Road - Watermill Sw 345 kV, Industrial Blvd - Compton Street 138 kV | RT | Planned |  | Oncor (Multiple Outages) | Remove overloaded element: Industrial Blvd - Compton Street 138kV (and corresponding contingency: West Levee Sw Auto Trx Wlvee_3_1 345/138 kV) due to upgrade of the overloaded element. PETE ID: 2638 (TPIT 13TPIT0059). Upgrade the 3.2-mile Cedar Crest Sw. Sta. - Industrial Blvd Sw. Sta. 138kV line using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. It was the overlapping outages scheduled in September of 2017 on the two 138kV lines (Watermill - West Levee and Norwood - Cedar Hill) that contributed to the overloads on the Sargent Road - Watermill 345kV line for loss of the double circuit between Liggett and Venus Switch. The Carrollton Tarpley Road - Renner Switch 138kV double circuit line outage overlapped for a period with the 345kV lines; however, the impact was significantly less. A single 345kV line outage is not expected to cause significant congestion.
ONCOR | Andrews County South - … - Andrews North | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | No Trees Sw - Cheyenne Tap 138 kV | RT | Forced |  | Oncor (Project Complete) | PETE ID: 909. Rebuild the 18.0-mile Andrews County South Sw. Sta. - Andrews North Sw. Sta. 138 kV line on double-circuit structures with both circuits in place using a conductor rated 1649 A or greater. Actual in-service date 12/20/2017. Prior to completion of this project, there was only a single line between Andrews County South and Andrews North.
ONCOR | Andrews North - Andrews County South | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 909. Rebuild the 18.0-mile Andrews County South Sw. Sta. - Andrews North Sw. Sta. 138 kV line on double-circuit structures with both circuits in place using a conductor rated 1649 A or greater. Actual in-service date 12/20/2017. Prior to completion of this project, there was only a single line between Andrews County South and Andrews North.
BRAZOS, DME, ONCOR | Arco - Navo - Collin Ses | LN | 138 | 16/6, 16/7, 16/8, 16/9, 17/3 | Fort Worth Sub to West Denton 138 kV, Jim Christal Sub to West Denton 138 kV, DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV, Fort Worth Sub - West Denton 138 kV, Corinth (Oncor) - Pockrus Sub 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 725. Construct the 5/65-mile second circuit on the 138kV line from Krugerville - Arco with a conductor rated for 2071 A. Actual in-service date 6/12/2018.
ONCOR | Champion Paper Mill Tap - … - Lufkin Sw | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 kV | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 2548. Rebuild the Stryker Creek - Gresham Road Sw. Sta. 138kV line using conductor designed to operate at 2569 A. Actual in-service date 6/27/2018.
ONCOR | Denton Tap - … - Saginaw Sw (6402) | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Diboll Southern Pine - … - Lufkin Pershing Tap & Lufkin Hill Street Tap | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 Kv | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Forced |  | Oncor (Project Complete) | PETE ID: 2548. Rebuild the Stryker Creek - Gresham Road Sw. Sta. 138kV line using conductor designed to operate at 2569 A. Actual in-service date 6/27/2018.
BRAZOS, ONCOR | Keller - … - Roanoke Sw | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Keller Tap - … - Roanoke Sw | LN | 138 | 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Lufkin South - … - Lufkin Sw (1370) | LN | 138 | 16/7 | Nacogdoches Se to Mt Enterprise 345 kV | Lufkin - Lufkin Sw 138 kV | RT | Planned |  | Oncor (Project Complete) | PETE ID: 1756. Construct the 2.1-mile line along Lufkin Sw. Sta. - Lufkin 138kV corridor using two rows double-circuit structures with a conductor rated 2071 A or greater. Reconfigure Lufkin Sw. Sta. - Lufkin and Lufkin Sw. Sta. - Lufkin Biomass 138kV lines. Actual in-service date 12/28/2017.
ONCOR | Tyler East - … - Tyler Grande (1770) | LN | 138 | 16/10, 16/7 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned | Y | Oncor (Project Complete) | The overloaded line no longer exists due to construction of Black Fork Switch (ring bus configuration). PETE ID: 1737. Rebuild the existing Tyler Northwest 138kV Sw. Sta by establishing Black Fork Switch. Actual in-service date 12/29/2017.
ONCOR | Allen Sw - Renner Sw | LN | 345 | 18/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
DME, ONCOR, TNMP | Arco - Krugerville | LN | 138 | 17/5 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Audelia Termination - … - Judd Court & Kirkland Park (3250_C) | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Bowen - … - Bowen Tate Tap & Village Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Centerville Road Sw - … - Parkdale Sw (3680_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Collville - … - Norwood Sw | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Crowley - … - Forest Hill Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6260) | LN | 138 | 17/4 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6265) | LN | 138 | 17/4, 17/11, 18/2 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, DCKT Eagle Mountain to Saginaw Sw 138 kV | Blue Mound - Wagley Robertson 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements. PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | East Levee Sw - … - Record Crossing (3415_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Edgemere Term - … - Kirkland Park (3630_B) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Euless - … - Grapevine Ball Street (1065) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Euless - … - Grapevine Ball Street (745) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned, Forced |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Euless - … - Kimball Ave & McKamy Tap | LN | 138 | 17/5, 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Euless - … - Liggett Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Handley Ses - Tate Springs (6310_E) | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Handley Ses - White Tap 1 | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Forced |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - … - Roanoke Sw (6273_A, 6273_B, 6273_C) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - … - Roanoke Sw (6274_C, 6274_A) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - … - Saginaw Sw | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6276) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6277) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Forced |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw Bus West (CB 13580, etc.) | BUS | 138 | 16/12, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | This congestion was observed prior to complete energization of the 138kV breaker-and-a-half configuration at Hicks Switch. With the current configuration, the bus can be removed from service without causing congestion.
ONCOR | Northaven Sw - Edgemere Term (3630_C) | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Norwood Sw Auto Mrh1 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Norwood Sw Auto Mrh2 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Parkdale Sw - … - Prairie Creek Sw | LN | 138 | 18/2, 18/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
BRAZOS, ONCOR | Plano Communication Parkway - Spring Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Wagley Robertson - Summerfield 138 kV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
BRAZOS, ONCOR | Rhome Bepc - … - Roanoke Sw (RNKSW_ELZBTHCK) | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ETT, ONCOR | Riley - Krum West Sw (SKRWRI15) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ETT, ONCOR | Riley - Krum West Sw (SKRWRI25) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | White Tap 1 - Trinity | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced |  | Oncor (Project Completion in 2018) | PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Sw (105) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD |  |  | Oncor (Remove Bus MTEs - Additions) | Replaces: Carrollton Northwest Bus #1. Need to specific impacted circuit.
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Sw (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  | Oncor (Remove Bus MTEs - Additions) | Replaces: Carrollton Northwest Bus #1. Need to specific impacted circuit.
ONCOR | Jewett - Singleton (260) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD |  |  | Oncor (Remove Bus MTEs - Additions) | Replaces: Jewett Bus #1 (CB 3900, etc.)
ONCOR | Carrollton Northwest Bus #1 | BUS | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  | Oncor (Remove Bus MTEs) | While the bus outage likely contributed to the congestion observed in 17/4, the actual impactful outage would be the double circuit lines between Carrollton NW and Lewisville. Oncor recommends replacing the bus MTE with the two corresponding line MTEs.
ONCOR | Jewett Bus #1 (CB 3900, etc.) | BUS | 345 | 16/11 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT, ST | Planned, Forced |  | Oncor (Remove Bus MTEs) | While the bus outage likely contributed to the congestion observed in 11/16, the actual impactful outage would be the Jewett - Singleton (260_A) line outage. Oncor recommends replacing the bus MTE with the corresponding line MTE.
ONCOR | Paris Sw Bus BB2 (CB 6790, etc.) | BUS | 345 | 2017 | Paris switch – Valley and Valley south 345 kV Dckt | Paris 345/138 kV auto | ADD |  |  | Oncor (Remove Bus MTEs) | The issue here is having CB 8635 open. With this CB open, the contingency forces all Lamar Power Partners generation through the Paris Switch Auto. Since CB 8635 is already on the MTE list, this bus should be removed.
ONCOR | Benbrook Sw - Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced
ONCOR | Brownwood - … - Brownwood Sw | LN | 138 | 17/2, 17/3, 17/4, 17/5 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6185) | LN | 138 | 17/4, 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265), Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned |  |  | Remove all "overloads" except for Eagle Mountain Ses - Morris Dido 138kV (6265). PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6190) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced
ONCOR | Carrollton Northwest - … - Plano Tennyson (840) | LN | 138 | 16/1, 16/6 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Lewisville Sw Auto FMR2 345/138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Fort Worth Sub - West Denton 138 kV | RT | Planned |  |  | Remove Carrollton Northwest - Lakepoint Tnp 138kV overload (and corresponding contingency: DCKT Carrollton Northwest to Lewisville Sw 345 kV) PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Cedar Crest Sw - … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced |  |  | Remove all overloaded elements except for the two Cedar Crest Sw - Oak Cliff South 138 kV lines and Industrial Blvd - Compton St. PETE ID: 976. Upgrade the 7.2-mile 138kV Mountain Creek Sw. Sta. - TRIRA line using a conductor rated 2071 or greater. Actual in-service date 6/30/2016. PETE ID: 2188. Rebuild the TRIRA - Norwood Switching Station 138kV line using a conductor rated 2071 or greater. Actual in-service date 6/23/2017.
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced |  |  | Remove all overloaded elements except for the two Cedar Crest Sw - Oak Cliff South 138 kV lines and Industrial Blvd - Compton St. PETE ID: 976. Upgrade the 7.2-mile 138kV Mountain Creek Sw. Sta. - TRIRA line using a conductor rated 2071 or greater. Actual in-service date 6/30/2016. PETE ID: 2188. Rebuild the TRIRA - Norwood Switching Station 138kV line using a conductor rated 2071 or greater. Actual in-service date 6/23/2017.
ONCOR | Centerville Road Sw - Forney Sw | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | ADD
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH1) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH2) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
ONCOR | Comanche Peak Ses - Everman Sw | LN | 345 | 2017 | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6016) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6062) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Cushing Southest Tap - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Forced
ONCOR | East Levee Sw - West Netowrk | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned
ONCOR | Elkton - Forney Sw | LN | 345 | 2017, 17/11 | Trinidad - Enterprise and - Stryker DCKT | Elkton 345/138 kV auto | ADD, RT | Planned
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned |  |  | Remove all "overloads" except for Lewisville Sw - Jones Street Tnp 138kV. PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Euless - … - Roanoke Sw (1065) | LN | 138 | 16/12, 17/1, 17/2, 17/3, 16/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned |  |  | Remove all "overloads" except for Lewisville Sw - Jones Street Tnp 138kV. PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements. The overloaded element: Tyler Northwest - Shamburger Sw 138 kV and corresponding contingency: DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV are not valid for this MTE (electrically and geographically isolated) and should be removed.
ONCOR | Forney Sw - Royse Sw (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Forney Sw - Royse Sw (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Hackberry - … - Norwood Sw (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned |  |  | Remove all "overloads" except for Lewisville Sw - Jones Street Tnp 138kV. PETE ID: 2642 (TPIT 5488). Upgrade the 2.1 -mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepointe (TNMP) 138kV line using a conductor 3200 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - … - Saginaw Sw (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT, ST | Planned, Forced |  |  | Remove Wagley Robertson - Summerfield overload. PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements.
ONCOR | Hicks Sw - … - Saginaw Sw (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Poi - Eagle Mountain Ses 138 kV | RT, ST | Planned, Forced |  |  | Remove Wagley Robertson - Summerfield overload and Eagle Mountain Poi - Eagle Mountain Ses 138kV overload. PETE ID: 4061 (TPIT 6779). Upgrade the 11.5-mile Wagley Robertson - Saginaw 138kV double-circuit line section using a conductor rated 1649 A or greater. Estimated in-service date 12/2018. Given that the uprate will be completed well before 3/1/2019, Oncor recommends that these elements be removed from the MTE list pro-actively to prevent an excessive amount of short-term additions, which creates administrative challenges for tracking individual HITE elements. PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Hicks Sw - Alliance (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y
ONCOR | Hutto - … - Round Rock (1660) - … - Georgetown South (1680) 138 kV | LN | 138 | 16/9 | DCKT Temple Sw to Knob Creek Sw 345 kV & Bell County 138 kV | Round Rock - Chief Brady 138 kV | RT | Planned
ONCOR | Johnson Sw (Oncor) - Comanche Peak Ses | LN | 345 | 17/5, 17/9, 18/4 | Comanche Peak Ses to Mitchell Bend Sw 345 kV | Wolf Hollow 345 Sw - Comanche Peak Ses 345 kV | RT | Planned
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned
ONCOR | Lufkin Sw - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Moss Sw - Yukon Sw | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Odessa EHV Sw. - North McCamey | LN | 345 | 2018 |  | McCamey GTC | ADD
ONCOR | Paris Sw – Monticello Ses | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Roanoke Sw - Hicks Sw | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT, ST | Planned | Y |  | Remove overload "Eagle Mountain Ses - Eagle Miountain Compressor 138 kV". PETE ID: 556. Reconductor the 6.6-mile 138kV double-circuit Eagle Mountain - Wagley Robertson line section using a conductor rated 1649 A or greater. Actual in-service date 5/5/2017.
ONCOR | Royse Sw Auto #1 | XF | 345 | 15/9 | Royse Sw Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned
ONCOR | Sandow Sw - Austrop (440) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Austrop (450) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Bell County East Sw (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced
ONCOR | Sandow Sw - Bell County East Sw (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced
ONCOR | Sargent Road - West Levee Sw 345 kV | LN | 345 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Wink Sub - Yucca Drive Sw | LN | 138 | 18/3 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV | RT | Planned
ONCOR | Wink Sub Auto Fmr1 138/69 kV | XF | 138 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto MR2L 138/69 kV | RT | Planned
ONCOR | Wolf Switching Station - Ward Gulf Tap | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Yucca Drive Sw - … - Holt Sw | LN | 138 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned