## Slide 1
Discussion of Re-power Definition
John Bernecker
Supervisor, Resource Integration
August 22, 2018

## Slide 2: Background
The term “re-power” is in existing use in the Planning Guide
Planning Guide Section 5.1.1 - Applicability
  New resources
    Aggregate power output (gross MW minus aux load) of 10 MW or greater; and
    Transmission-connected
  Existing resources
    Upgrading summer or winter Net Dependable Capability by 10 MW or greater in a single year;
    Change of POI; or
    Re-powers
Re-power applicability only comes into play if the incremental capacity change is less than 10 MW

## Slide 3: What is a Re-power?
Change in:
  Reactive behavior
  Short circuit current contribution
  Dynamic response
  Sub-synchronous behavior
Results in an updated dynamic model / sub-synchronous model
Does not include replacement in-kind of existing equipment

## Slide 4: Examples of Re-powers (Wind)
Control system software upgrades resulting in a new dynamic model
Change in inverter
Blade replacement (not replacement in-kind)
Change in turbine manufacturer
Change in turbine type (E.g. type 1 to type 3 or type 3 to type 4)
Potentially other changes we have not seen / thought of yet

## Slide 5: Examples of Re-powers (Synchronous Generation)*
Change in exciter (not replacement in-kind)
Change in governor (not replacement in-kind)
*Best-guess based on limited experience

## Slide 6: Examples of Re-powers (Solar)*
Control system software upgrades resulting in a new dynamic model
Change in inverter
*Best-guess based on limited experience

## Slide 7: Strawman Proposal for Definition of Re-power
Re-power
Any change in equipment or control system software, other than replacement in-kind of existing equipment, to an All-Inclusive Resource that results in a change to the steady-state real or reactive output, short circuit current, dynamic response, or sub-synchronous behavior requiring the submittal and potential study of new model parameters. Examples include, but are not limited to: control system upgrade, inverter change, blade replacement, manufacturer change, turbine type change, governor change, automatic voltage regulation system change, etc. Addition of new equipment to an existing site, such as inlet cooling, would not be considered a re-power.