## Slide 1
ERCOT Frequency Control Report
April 2020
ERCOT
Operations Planning
PDCWG | May 29th, 2020

## Slide 2: Summary of April 2020
CPS1: 168.91%
Current CPS1 12-Month Rolling Average: 174.34%
0 BAAL Exceedance
6 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 15.93 mHz
  Min: 12.25 mHz
  Max: 20.00 mHz
Energy Statistics
  Total Energy: 26,926,064 MWh
  Wind Energy: 7,396,274 MWh
  Percent Energy from Wind: 27.47%
  Solar Energy: 419,973 MWh
  Percent Energy from Solar: 1.49%
Minimum System Inertia
  Mean: 171,265
  Max: 200,438 on Apr 17th
  Min: 139,592 on Apr 8th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Apr-20 CPS1 (%): 168.91
Notes: Outliers:
1. 70.8% @ 16:00 4/19/2020:
Expected gen deviation:
Large expected gen deviation in the middle of the hour and the end of the hour. (-1834 MW @16:36; -1445 MW @16:54)
Negative throughout the hour. (-650 MW on average).
Two thermal units contribute significantly to total expected gen deviation from 16:35 to16:40.
Wind Ramp:
Consistent Wind down ramp throughout the Hour.
Large wind down ramps 301 MW/5min @16:20 and 229 MW/5min @ 16:25
2. 58.8% @ 17:00 4/19/2020:
Expected gen deviation:
Large expected gen deviation in the middle of the hour and the end of the hour. (-1306 MW @17:27; -1854 MW @17:49 )
Negative throughout the hour (-690 MW on average).
One unit had a runback due to losing BFP.
Large expected gen are mostly from renewables.
Wind Ramp:
Consistent Wind down ramp throughout the Hour.
Large wind down ramps 263 MW/5min @17:25 and 10005 MW/20min @ 17:40
3. 21.9% @ 18:00 4/19/2020:
Expected gen deviation:
Large expected gen deviation throughout the hour. (-1808 MW @18:38; )
Negative throughout the hour (-847 MW on average).
Large expected gen deviations are from both thermal units and renewables.
Three resources are not following there basepoints.
Wind Ramp:
Consistent Wind and solar down ramp throughout the Hour.
Average wind down ramp 258 MW/5min.
655 MW of Solar down ramp throughout the hour.
4. 77.1% @ 17:00 4/28/2020:
Expected gen deviation:
Large expected gen deviation at the end of the hour. (-1537 MW @17:54)
Significant bp deviation from solar resources at the beginning of the hour.
Negative throughout the hour (-357 MW on average).
Loss of Generation Event: 332 MW
Wind/solar Ramp:
Over 100 MW solar down ramp within 5 minutes.
5. 9.6% @ 18:00 4/28/2020:
Expected gen deviation:
Large expected gen deviation throughout the hour. (-1844 MW @18:43; )
Negative throughout the hour (-707 MW on average).
Large expected gen deviations are from both thermal units and renewables.
A thermal resource has significant deviation due to runback.
Wind Ramp:
Wind is fairly consistent throughout the hour.
Solar ramps down for roughly 900 MW.
DC Tie (import) ramps down for roughly 600 MW.
6. 96.3% @ 8:00 4/29/2020:
Expected gen deviation:
Large expected gen deviation at the end of the hour.
Frequency trending high at the end of the hour and reg-down being exausted.
Suspected cause of frequency incline is due to nonconforming load drop.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance in April

## Slide 6: 15-Minute Average CPS1%
Apr-20 CPS1 (%): 168.91

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.34%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 26,926,064 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,396,274 MWh

## Slide 23: % Energy from Wind Generation
Notes: 27.4%

## Slide 24: Total Energy From Solar Generation
Notes: 553,191 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.05%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 140,684 MW*s on 4/27/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 168,047
Max: 221,369 on Apr 8th
Min: 140,684 on Apr 27th

## Slide 28: Questions?
Thank you!