## Slide 1
ERCOT Frequency Control Report
May 2020
ERCOT
Operations Planning
PDCWG | June 16th, 2020

## Slide 2: Summary of May 2020
CPS1: 170.82%
Current CPS1 12-Month Rolling Average: 174.07%
4 BAAL Exceedances
5 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 16.13 mHz
  Min: 12.70 mHz
  Max: 18.69 mHz
Energy Statistics
  Total Energy: 31,167,811 MWh
  Wind Energy: 7,791,056 MWh
  Percent Energy from Wind: 25.00%
  Solar Energy: 859,972 MWh
  Percent Energy from Solar: 2.76%
Minimum System Inertia
  Mean: 192,543
  Max: 235,009 on May 29th
  Min: 131,096 on May 1st

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
May-20 CPS1 (%): 170.82
Notes: Outliers:
1. 78.4% @ 17:00 5/2/2020:
Expected gen deviation:
Large expected gen deviation in the middle of the hour.(-1712 MW @17:24)
Solar resources and one combine cycle contribute significantly to total expected gen deviation from 17:15 to17:30.
Wind/Solar Ramp:
Solar ramps down from 2207 MW to 1803 MW within a 20 min interval from 17:05 to 17:25.
2. 97.7% @ 00:00 5/12/2020:
Expected gen deviation:
Large expected gen deviation during the first half of the hour. (-1312 MW @00:08; -1838 MW @00:26 )
Large expected gen deviations are from one combine cycle and renewables.
Wind Ramp:
Consistent Wind down ramp throughout the first half of the Hour.
Consistent wind down ramp from 15209 MW to 13819 MW over 25 min period.
3. 60.0% @ 1:00 5/12/2020:
Expected gen deviation:
Large expected gen deviation during the first 20 minutes. (-2409 MW @1:20 )
Negative throughout the hour.
Large expected gen deviations are mostly from wind resources.
Wind Ramp:
Consistent Wind down ramp throughout the Hour.
Steep wind down ramp during the first 20 minutes.
(1769 MW over 20 minutes)
4. 61.3% @ 16:00 5/15/2020:
Expected gen deviation:
Large expected gen deviation from 16:40 to 16:50. (-2535 MW @16:50)
A 200 MW resource went off line at 16:45.
Wind Ramp:
Steep wind down ramp @16:40 (700MW down ramp within 10 minutes)
5. 58.2% @ 21:00 5/24/2020:
Expected gen deviation:
Large expected gen deviation from 21:20 to 21:45.. (-2099 MW @21:27; )
Large expected gen deviations are from wind resources.
Wind Ramp:
Consistent wind down ramp throughout the hour.
(Over 2000 MW wind down ramp within 15 minutes @21:15.)

## Slide 5: BAAL Exceedances & Violations
There were 4 BAAL exceedances in May
Notes: 2 exceedances on 5/12 and 2 exceedances on 5/31 due to loss of generation events.

## Slide 6: 15-Minute Average CPS1%
May-20 CPS1 (%): 170.82

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.07%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 31,167,811 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,791,056 MWh

## Slide 23: % Energy from Wind Generation
Notes: 25.00%

## Slide 24: Total Energy From Solar Generation
Notes: 859,972 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.76%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 131,096 MW*s on 5/1/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 192,543
Max: 235,009 on May 29th
Min: 131,096 on May 1st

## Slide 28: Questions?
Thank you!