## Slide 1
PDCWG
May 14, 2021
Balancing Operations Planning Staff
Update on Intra-Hour Solar Forecast and SCR811

## Slide 2
Discussion Outline
Update on SCR811
Intra-Hour Photo Voltaic Forecast and Predicted Solar Ramp Rate Forecast Performance
Summary & Next Steps

## Slide 3: Background on SCR811
SCR811 will incorporate a intra-hour solar forecast based ramp into Generation To Be Dispatched (GTBD) to give Security Constrained Economic Dispatch (SCED) a indication of how the solar units may ramp.
In absence of this today, SCED dispatches uncurtailed solar units to their HSL.
  This means that SCED assumes output of uncurtailed solar units will persist for the next 5-min at the unit’s HSL that was telemetered at the start of the interval.
  What if solar ramps? or What if an FME occurs as the sun is setting? Regulation deployment is used to make up for gain/loss of solar MW but depending upon the circumstance frequency recovery could potentially be delayed.
Equation
GTBD = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLDRR + K4*Regulation Deployed + K5*ACE Integral – K6*5*PWRR + K7*5*DCTRR – K8*5*PSRR
|PSRR| ≤ Max PSRR Feedback
NEW ADDITIONS

## Slide 4: SCR811 Update
As a part of implementing SCR811, ERCOT is in the process of integrating a 5-min Intra-hour Photo Voltaic Power forecast into ERCOT’s Energy Management System (EMS)
ERCOT’s EMS is being setup to compute a Predicted Solar Ramp Rate (PSRR) using
  Hourly Short-Term Photo Voltaic Power Potential (STPPF) forecast
  5-min Intra-hour Photo Voltaic Power forecast
  Note that at any given 5-min SCED interval only one amongst the above two methods for PSRR calculations will be active for use in GTBD.
ERCOT will on track to complete the software changes associated with SCR811 in the 2021 R3 release (scheduled to be implemented in Production systems between May 25 and May 27).

## Slide 5: Predicted Solar Ramp Error
Chart: Histogram of PSSR Error
| -9999 to -300 | -300 to -250 | -250 to -200 | -200 to -150 | -150 to -100 | -100 to -50 | -50 to 0 | 0 to 50 | 50 to 100 | 100 to 150 | 150 to 200 | 200 to 250 | 250 to 300 | 300 to 9999
Persistence | 48 | 54 | 89 | 115 | 154 | 282 | 748 | 875 | 315 | 186 | 111 | 79 | 43 | 47
Intra-Hour Solar Forecast | 18 | 16 | 46 | 73 | 149 | 348 | 962 | 874 | 331 | 158 | 86 | 44 | 23 | 18
STPPF | 18 | 15 | 30 | 77 | 171 | 350 | 809 | 1037 | 366 | 146 | 77 | 32 | 12 | 6
Performance Metric | Persistence (4/23 – 5/10) | Intra-Hour Solar Forecast (4/23 – 5/10) | Short-term Solar Forecast (STPPF) (4/23 – 5/10)
MAE (MW) | 79.29 | 60.12 | 57.60
MAE (MW) when 5-Min. Solar Ramp > 100 MW | 190.12 | 114.38 | 105.64
MAE (MW) when 5-Min. Solar Ramp < -100 MW | 195.40 | 109.68 | 113.03
Over Forecast
Under Forecast

## Slide 6: Predicted Solar Ramp Error
Chart: April 23,2021 - May 10, 2021
Persistence Error | 0 | 0 | 0 | 0 | 0 | 0 | 0.35072 | 75.8553 | 165.8002 | 62.1564 | 41.2022 | 30.5184 | 26.9973 | 3.4163 | -5.7511 | -22.1569 | -17.8322 | -30.4237 | -99.0424 | -178.5467 | -45.1734 | -0.53273 | -0.098381 | 0.00055714
PSRR Error (Intra-Hour) | 0 | 0 | 0 | 0 | 0 | 0 | 0.047293 | -0.99862 | -19.8876 | 7.351 | 2.1139 | 9.8566 | 2.3454 | -3.6072 | -5.9237 | -5.8633 | 6.4884 | 4.365 | 35.6973 | -8.7163 | -15.6259 | -0.53273 | -0.098381 | 0.00055714
PSRR Error (STPPF) | 0 | 0 | 0 | 0 | 0 | 0 | -12.3505 | -7.8958 | 28.7892 | -27.3324 | -9.196 | -3.5887 | 3.8345 | -2.7088 | -2.0805 | -13.3923 | -7.216 | 8.5445 | 27.0747 | -39.368 | 17.0889 | 2.5115 | 0.058322 | 0.060309
Average of Solar HSL | 0 | 0 | 0 | 0 | 0 | 0 | 355.2908 | 431.6334 | 2320.9688 | 3576.3919 | 4118.0553 | 4474.8074 | 4822.6991 | 4936.9284 | 4910.751 | 4691.362 | 4485.7261 | 4210.1232 | 3307.8609 | 1391.1239 | 67.4423 | 3.4716 | 1.3237 | 1.3237

## Slide 7: Potential Impact of Predicted Solar Ramp in GTBD
Chart: 5-Min. SCED GTBD Error Due to Solar Ramp (4/11/2021 19:05 - 4/11/2021 20:00)
| 44297.798611111109 | 44297.802083333336 | 44297.805555555555 | 44297.809027777781 | 44297.8125 | 44297.815972222219 | 44297.819444444445 | 44297.822916666664 | 44297.826388888891 | 44297.829861111109 | 44297.833333333336
Persistent Error | -325.4316 | -287.0283 | -234.9147 | -307.3648 | -94.9059 | -97.9198 | -66.0851 | -149.0777 | -111.0999 | -62.734 | -58.6094
PSRR Error (STPPF Method) | -129.9766 | -104.2116 | -64.7363 | -149.8248 | 49.9957 | 34.3436 | 53.5399 | -42.091 | -16.7515 | 18.976 | 10.4622
PSRR(Intra-Hour Forecast Method) | -49.7316 | -38.8283 | -20.9147 | -88.9648 | 82.3941 | 71.8802 | 89.2149 | -18.8777 | 14.6001 | 29.366 | 20.5906
Solar HSL | 1529.358 | 1242.3297 | 1007.415 | 700.0502 | 605.1443 | 507.2245 | 441.1394 | 292.0617 | 180.9618 | 118.2278 | 59.6184

## Slide 8: Summary & Next Steps
ERCOT will implement SCR811 during 2021 R3 between May 25 and May 27.
Initially, K8 will be set to 0 so that it will not impact GTBD calculation.
ERCOT is planning to tune K8 (K8 becomes non-zero) and potentially other GTBD parameters in the first week of June.
A market notice will be sent out prior to activation of K8 to a non-zero value.