## Slide 1
Public Utility Commission of Texas (PUCT) Oversight Project No. 46304 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC
Directive #9 : Ancillary Services
July ROS, 2021
ERCOT Staff

## Slide 2: Background of Project and PUCT Directives
Southern Cross Transmission LLC/Pattern Power Marketing LLC received FERC approval (FERC Docket No. TX 11-1-001) to interconnect DC Tie line.
PUCT imposed conditions for interconnection of the SCT DC Tie line in two PUCT proceedings:
  City of Garland docket – Docket No. 45624
  Oversight proceeding arising out of City of Garland docket – Project No. 46304
As part of the oversight proceeding, PUCT issued 14 Directives to ERCOT, requiring certain studies and determinations be made to accommodate the SCT DC Tie.

## Slide 3: Summary of Directive 9
Directive 9 requires ERCOT to evaluate what modifications to existing and additional ancillary services, if any, are necessary for reliable interconnection of the Southern Cross DC Tie (SCT DC Tie).
Determination (summarized from the whitepaper):
  Procurement of additional new Ancillary Services will be unnecessary because NPRR 1034, Frequency-Based Limits on DC Tie Imports and Exports, will give ERCOT authority to establish limits on DC Tie transfers and to curtail DC Tie Schedules when necessary to address the risk of unacceptable frequency deviations.
  SCT DC Tie is proposed to built as a bi-pole DC Tie that is capable of operating in single-pole mode. NERC Reliability Standard BAL-003-2, clarifies that the loss of a bi-pole DC Tie that is capable of operating in single-pole mode would count as two separate contingencies. While the loss of the SCT DC Tie at its maximum import of 2,000 MW would exceed ERCOT’s single largest contingency of 1,420 MW, no adjustment to Responsive Reserve Service (RRS) or Non-Spinning Reserve Service is necessary if the proposed design is implemented.
  No changes to Regulation Service are necessary because DC Tie ramp will be adequately addressed by SCR 800, Addition of DC Tie Ramp to GTBD Calculation, and NPRR 999, DC Tie Ramp Limitations.

## Slide 4: Summary of Directive 9
Directive 9 requires ERCOT to evaluate what modifications to existing and additional ancillary services, if any, are necessary for reliable interconnection of the Southern Cross DC Tie (SCT DC Tie).
Basis for Determination (summarized from the whitepaper):
  ERCOT studied the potential Ancillary Service needs associated with the interconnection of the SCT DC Tie.
  Studies considered the operational impacts of a loss of the SCT DC Tie when importing up to its maximum import capability of 2,000 MW and when exporting up to its maximum export capability of 2,100 MW.
  ERCOT identified potential needs under each of its existing Ancillary Services—RRS, Non-Spinning Reserve Service, and Regulation Service—and considered whether any new Ancillary Service would be needed.

## Slide 5: Summary of Directive 9
Directive 9 requires ERCOT to evaluate what modifications to existing and additional ancillary services, if any, are necessary for reliable interconnection of the Southern Cross DC Tie (SCT DC Tie).
Basis for Determination (summarized from the whitepaper):
Ancillary Services for Significant Frequency Excursions
  When importing energy over the SCT DC Tie:
    Studies initially determined that ERCOT would need to procure additional RRS to address the potential negative impact on frequency because the SCT DC Tie could import 2,000 MW, which would become the single largest contingency on the ERCOT system and which would therefore increase ERCOT’s RLPC (then known as Resource Contingency Criteria (RCC)) from 2,750 MW to 3,275 MW.
    Subsequently, NERC BAL-003-2, which became effective on December 1, 2020, clarified that the loss of a bi-pole DC Tie that is capable of operating in single-pole mode would count as two separate contingencies.
    Southern Cross has informed ERCOT that the SCT DC Tie project will be built using a bi-pole configuration. Assuming this design is implemented, and the tie is able to operate in single-pole mode, the loss of each pole can be regarded as a separate contingency, in accordance with BAL-003-2.
    As a result, the interconnection of SCT DC Tie is not expected to impact ERCOT’s RLPC or require additional RRS to address the risk of an import-side frequency deviation.
  When exporting energy over the SCT DC Tie:
    ERCOT’s studies identified risk of unacceptable frequency overshoot in the event of the loss of the SCT DC Tie when exporting above certain levels under certain low-inertia conditions.
    ERCOT determined that a new Ancillary Service (or a new form of RRS) that could provide a rapid generation reduction in response to a trip of the tie when exporting during certain low inertia hours would be necessary address this concern.
    ERCOT also determined that if the SCT DC Tie were subject to an export limit during those certain hours, then a new Ancillary Service (such as a new form of RRS) would not be necessary.
    Southern Cross submitted NPRR 1034, Frequency-Based Limits on DC Tie Imports and Exports, to enable ERCOT to establish import or export limits on DC Ties during operating conditions of concern. NPRR 1034 also provides that ERCOT will curtail DC Tie Schedules when one or more DC Tie Schedules would exceed an established import or export limit. NPRR 1034 was approved on February 9, 2021. This NPRR will avoid the need for procuring additional Ancillary Services to address the risk of an unacceptable frequency deviation when the SCT DC Tie is exporting from ERCOT.

## Slide 6: Summary of Directive 9
Directive 9 requires ERCOT to evaluate what modifications to existing and additional ancillary services, if any, are necessary for reliable interconnection of the Southern Cross DC Tie (SCT DC Tie).
Basis for Determination (summarized from the whitepaper):
Non-Spinning Reserve Service
  ERCOT procures Non-Spinning Reserve Service to ensure sufficient capacity is available to cover large net load forecast errors or to replace deployed RRS. ERCOT has identified no Non-Spin impact under this criteria due to the interconnection of the SCT DC Tie.
  At the time of ERCOT’s study, ERCOT had a Non-Spin procurement floor equal to ERCOT’s current Most Severe Single Contingency (MSSC) for hours ending 7 through 22, which was then equivalent to 1,375 MW. However, ERCOT has modified its procurement practices in 2019 to eliminate the Non-Spin floor. Therefore, interconnection of the SCT DC Tie will not impact the Non-Spin quantities to be procured.
Regulation Service
  Each December, ERCOT identifies minimum quantities of Regulation Up and Regulation Down for each hour of the next year based on (1) the amount of Regulation historically deployed in that hour, and (2) net-load variability, as adjusted for projected growth in installed of wind and solar generation capacity.
  ERCOT has determined that the following changes to ERCOT rules and systems should be sufficient to address frequency issues due to ramping of the Southern Cross DC Tie and will avoid any need for additional Regulation Service procurement due to the interconnection of the Southern Cross DC Tie.
    System Change Request (SCR) 800, Addition of DC Tie Ramp to GTBD Calculation, which was approved in December 2019, will integrate scheduled DC Tie ramp into the Generation to be Dispatched (GTBD) value used by SCED
    NPRR 999, DC Tie Ramp Limitations, which was approved in October 2020, clarifies ERCOT’s authority to curtail DC Tie Schedules that would otherwise exceed the ramp capability of the system, and potentially impact system frequency

## Slide 7: Next Steps
Request that ROS endorse the Directive 9 whitepaper as presented and posted with the ROS materials.
ERCOT will next seek Technical Advisory Committee (TAC’s) endorsement of this whitepaper at its July 28, 2021 meeting.
ERCOT staff continues to work with stakeholders on remaining Directives
  http://www.ercot.com/mktrules/puctDirectives/southernCross