## Public Submissions (MTE 2022)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Addition, Removal, or Correction | Reason for Addition, Removal, or Correction | Requestor | OCITF Consensus | Decision | Discussion Items
AEP | Aransas Pass - … - Dupon Swith Ingleside | LN | 138 | 17/8, 17/4 | Rockport to Rincon 138 kV, Lon Hill to Coleto Creek 345 Kv | Gregory - Rincon 69 kV, Lon Hill - Pawnee Switching Station 345 kV | Removal | Gregory - Rincon 69 kV line has been upgraded. 345 kV line will not be overloaded | AEP
AEP | West Batesville Bus #1 (CB 1005, etc.) | BUS | 138 | 15/4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | Removal | Addition of 345 kV line Lobo - Cenizo - Del Sol - North Edinburg to alleviate overload on 138 kV | AEP
AEP | Cotulla Sub - … - Freer Sub | LN | 69 | 22/1 | Fowlerton - Lobo 345 kV | Bruni Sub 138/69 kV | Correction | The TDSP should STEC. STEC owns the MTE, Contingency and Overload equipment. | AEP
AEP, ETT | Live Oak AEP - … - San Angelo Power Station | LN | 138 | 22/4, 19/9 | Carver - Friend Ranch 138 kV, San Angelo Coke Street to San Angelo Red Creek 138 kV | Atlantic Sonora - Sonora 69 kV, San Angelo Power Station - San Angelo South 69 kV | Removal | MTE no longer valid. Previously LVOK - SANTIAGO-SAPOWER. W/ Maddux energized (Early May 2022), SAPOWER 1 & 2 - MADDUX - SANTIAGO - LVOK. Additional 138 kV should alleviate overload on 69kV | AEP
AEP | Pig Creek - Solstice | LN | 138 | 21/4 | Yucca Drive Sw-Lotebush 138 kV | Wickett Tnp - Pyote Tnp 138 kV | Removal | Overloads alleviated with new 345 kV at Solstice | AEP
AEP | Treadwell - Yellow Jacket | LN | 138 | 22/4 | Carver - Friend Ranch 138 kV | Atlantic Sonora - Sonora 69 kV | Removal | Maddux station cut-in completed Early May 2022, this should alleviate overload on the 69kV | AEP
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | Removal | ONCOR replaced the autotransformer with a 750/900 MVA autotransformer. The load flow has been altered such that the line will no longer overload for the stated contingency. | BEPC
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | Removal | ONCOR replaced the autotransformer with a 750/900 MVA autotransformer. The load flow has been altered such that the line will no longer overload for the stated contingency. | BEPC
BRAZOS, TMPA | Gibbons Creek - Keith Switch 138 kV | LN | 138 | 16/10 | Gibbons Creek to Btu_East 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | Removal | Since Gibbons Creek Generation no longer exists, line no longer overloads for stated contingency. | BEPC
BRAZOS | Hasse Auto Xfm1 138/69 kV | XF | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | Removal | Both autotrasnformers at Hasse have been replaced with 60 MVA and this is not expected to overload for the stated contingency. | BEPC
BRAZOS | Hilltop Lakes - Watson Chapel | LN | 138 | 17/8 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | Removal | Since Gibbons Creek Generation no longer exists, line no longer overloads for stated contingency. | BEPC
BRAZOS, TNMP | Jones Street Tnp - Lewisville Switch | LN | 138 | 20/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | TI Tnp - West Tnp 138 kV | Removal | TNMP or ONCOR rebuilt this line and the line no longer overloads for the stated contingency. | BEPC
BRAZOS | Krugerville - … - Navo | LN | 138 | 15/10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | Removal | Brazos rebuilt the line to double circuit and no longer overloads for the stated contingency. | BEPC
BRAZOS | Whitney Bus 1525 (CB 5075, etc.) | BUS | 138 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | Removal | ONCOR rebuilt the Bosque Switch to Elm Mott 138 kV transmission line and this no longer overloads for the stated contingency. | BEPC
BRAZOS | Whitney Bus BB1 (CB 210, etc.) | BUS | 69 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | Removal | ONCOR rebuilt the Bosque Switch to Elm Mott 138 kV transmission line and this no longer overloads for the stated contingency. | BEPC
BPUB | Power Plant Substation - Sixth Street Substation | LN | 138 | 18/4, 18/3 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | Removal | Major Transmission Element (Power Plant Substation - Sixth Street Substation) was modified to add a new 138 KV Substation (Rio Grande) on 09/2020. Power Plant Substation to Sixth Street Substation Line was split into Power Plant Substation to Rio Grande Substation Line and Sixth Street Substation to Rio Grande Substation Line. | BPUB
BTU | Btu_Atkins - Btu_Dansby | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | Removal | BTU requests that this contengency be removed due to changes in our load forcasting methodology | BTU
BTU | Btu_Dowling - Btu_Enterprise | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | Removal | BTU requests that this contengency be removed due to changes in our load forcasting methodology | BTU
BTU | Btu_East - Btu_Shady_Lane 69 | LN | 69 | 16/6 | Btu_Atkins Auto FMR1 138/69 kV | Btu_Briarcrest - Btu_Nall_Lane 69 kV | Removal | BTU requests that this contengency be removed due to changes in our load forcasting methodology and the upgrade of Btu_Briarcrest - Btu_Nall_Lane 69 kV | BTU
CNPE | Center - PH Robinson | LN | 345 | 20/1, 19/12, 19/5 | PH Robinson to Meadow 345 kV, Basecase | Alvin Tnp - Mainland Tnp 138 kV, Cedar Bayou Plant - Center 345 kV | Removal | UPGRADE OVERLOADED ELEMENT - As of 10/31/2022, upgrades to Cedar Bayou -Center 345kV should mitigate this issue. | CNPE
CNPE | Chambers - Jordan | LN | 345 | 21/11, 21/10 | Cedar Bayou Plant - Jordan 345 kV & Chambers - Jordan 345 kV, Jordan - King 345 kV & Jordan - North Belt 345 kV | Cedar Bayou - Cedar Bayou Plant 138 kV, Cedar Bayou Plant - Decker 138 kV, Bigvue - Lyondell 138 kV, Lychem - Power Systems Arco Cogen 138 kV | Removal | UPGRADE OVERLOADED ELEMENT - As of 12/31/2022, upgrades to Cedar Bayou - Cedar Bayou Plant should mitigate this issue on this overloaded element. | CNPE
AEP, CPS, STEC | Goddard - Tango | LN | 345 | 22/2, 22/1, 21/11 | Fowlerton - San Miguel Gen 345 kV, Grissom - Lon Hill 345 kV, Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV | George West Switch Station - Sigmor 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, North Carbide - Sea Drift Coke 138 kV | Correction | The MTE, Contigency, and Overload are outside of CPS Energy Transmission System. CPS Energy has no visibility, or control and does not monitor any of the listed elements. CPS Energy would not be able to identify the Contingency with our internal studies. | CPS
AEP, CPS, STEC | Pawnee Switching Station - Tango | LN | 345 | 22/2, 22/1, 21/11 | Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV, Grissom - Lon Hill 345 kV, Fowlerton - San Miguel Gen 345 kV | North Carbide - Sea Drift Coke 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, George West Switch Station - Sigmor 138 kV | Correction | The MTE, Contigency, and Overload are outside of CPS Energy Transmission System. CPS Energy has no visibility, or control and does not monitor any of the listed elements. CPS Energy would not be able to identify the Contingency with our internal studies. | CPS
LCRA | Cibolo - Marion | LN | 138 | 22/1 | GPI Switch - Loop 337 - GPI 138 kV & GPI Switch - Marion - Sheriffs Posse - Schumansville 138 kV | Cibolo - Marion 138 kV | Removal | This MTE should be removed because the congestion was due to multiple simultaneous outages: T302 CIBOLO-MARION and T304 CIBOLO-SCHERTZ. | LCRA
LCRA | Fayette Plant 3 - Lytton Springs | LN | 345 | 22/3 | AEN Dunlap - Lost Pines AEN 345 kV & Austrop - Lost Pines AEN 345 kV | Sim Gideon - Winchester 138 kV | Removal | This MTE should be removed because the congestion was due to multiple simultaneous outages: T255 FPPYD2-LYTTON_S and CKT_3121 HOLMAN-LYTTON SPRINGS | LCRA
LCRA | Goehmann Lane -… - Fredericksburg & Live Oak | LN | 69 | 19/11 | Ferguson to Sandy Creek Switchyard 138 kV | Gilles Auto AT1 138/69 kV | Removal | This MTE should be removed because there is a PCAP for "High Fredericksburg area load" | LCRA
LCRA | Mccarty Lane - Ranch Road 12 | LN | 138 | 22/1 | Hutto Switch - Zorn 345 kV & Clear Springs - Gilleland Creek 345 kV | Rattler - Redwood 138 kV | Removal | This MTE should be removed because there there was a combination of impactful outages: T699 MCCALA-RNRD12, T205 MCCALA-ZORN, T324 MCCALA-HUNTER, T233 MCCALA-HENNE | LCRA
LCRA | Smithville … Sim Gideon | LN | 138 | 22/3 | AEN Dunlap - Lost Pines AEN 345 kV & Austrop - Lost Pines AEN 345 kV | Sim Gideon - Winchester 138 kV | Removal | This MTE should be removed because the congestion was due to multiple simultaneous outages: T255 FPPYD2_LYTTON_S and CKT_3121 HOLMAN-LYTTON SPRINGS | LCRA
ONCOR | Eagle Mountain SES - Rosen Heights Tap 1 | LN | 138 | 21/5 | DBCKT Deen Switch -…- Hicks Switch 138 kV | Eagle Mountain Ses - Morris Dido 138 kV | Removal | Remove this MTE due to completion of upgrading Eagle Mountain SES - Morris Dido 138 kV - ISD 12/2021 as part of TPIT# 6273 upgrade Saginaw Sw-Eagle Mountain 138 kV double ckt line. | Oncor
ONCOR | Midland County Northwest Switch - Midland East (6462) | LN | 138 | 20/10 | DCKT Falcon Seaboard-Morgan Creek SES & Midline East 345 kV | Tall City - Sharyland Utilities - Telephone Road - Sharyland Utilities 138 kV | Removal | Remove this MTE due to completion of upgrading SL Telephone Road Sub - Tall City Sub 138kV Line: Rebuild - ISD 05/2021 as part of TPIT# 57915 Tall City - Telephone Road 138 kV Line Rebuild. | Oncor
ONCOR | Alliance - Hicks Switch | LN | 345 | 22/3, 2021 | DCKT Hicks Switch - Deen Switch 138 kV, Krum West Switch - Lewisville Switch 345 kV & Krum West Switch - West Denton 345 kV | Rosen Heights Tap2 - Deen Switch 138 kV, Courtland - Timberview Switch 345 kV | Removal | Remove Rosen Heights Tap2 - Deen Switch 138 kV overload element and its associated contingency DCKT Hicks Switch - Deen Switch 138 kV due to upgrading overloaded element Rosen Heights Tap2 - Deen Switch 138 kV line (ISD - 11/12/2021) as a part of TPIT project 6273 "Upgrade the Saginaw (Deen Switch) - Eagle Mountain 138 kV Double Circuit Line" The congestion experienced on Courtland - Timberview Switch constraint in March of 2022 is due to multiple simultaneous outages in the area: * Everman 345 kV and Auto 3 (ONC00501494 - 02/27/2022 - 03/10/2022) * Timberview - Venus Switch 345 kV (ONC00510345 - 02/28/2022 - 03/20/2022) * Anna Switch - Cedar Elm Sw 345 kV (ONC00497260 - 03/01/2022 - 03/14/2022) * Anna Switch - Krum West Sw 345 kV (ONC00498515 - 03/01/2022 - 03/14/2022) * Parker Switch BKR 6800/9865 345 kV (ONC00500390 - 03/08/2022 - 03/09/2022) | Oncor
ONCOR | Alliance - Roanoke Switch | LN | 345 | 22/3, 2021 | DCKT Hicks Switch - Deen Switch 138 kV, Krum West Switch - Lewisville Switch 345 kV & Krum West Switch - West Denton 345 kV | Rosen Heights Tap2 - Deen Switch 138 kV, Courtland - Timberview Switch 345 kV | Removal | Remove Rosen Heights Tap2 - Deen Switch 138 kV overload element and its associated contingency DCKT Hicks Switch - Deen Switch 138 kV due to upgrading overloaded element Rosen Heights Tap2 - Deen Switch 138 kV line (ISD - 11/12/2021) as a part of TPIT project 6273 "Upgrade the Saginaw (Deen Switch) - Eagle Mountain 138 kV Double Circuit Line" The congestion experienced on Courtland - Timberview Switch constraint in March of 2022 is due to multiple simultaneous outages in the area: * Everman 345 kV and Auto 3 (ONC00501494 - 02/27/2022 - 03/10/2022) * Timberview - Venus Switch 345 kV (ONC00510345 - 02/28/2022 - 03/20/2022) * Anna Switch - Cedar Elm Sw 345 kV (ONC00497260 - 03/01/2022 - 03/14/2022) * Anna Switch - Krum West Sw 345 kV (ONC00498515 - 03/01/2022 - 03/14/2022) * Parker Switch BKR 6800/9865 345 kV (ONC00500390 - 03/08/2022 - 03/09/2022) | Oncor
ONCOR | Deen Switch -…- Morris Dido | LN | 138 | 21/8, 21/5 | DBCKT Deen Switch -…- Hicks Switch 138 kV | Blue Mound - Rosen Heights Tap 1 138 kV, Calmont Switch - Carswell 138 kV | Removal | Remove Blue Mound - Rosen Heights Tap 1 138 kV overload element due to upgrading overloaded element Blue Mound - Rosen Heights Tap 1 138 kV line (ISD - 12/2021) as a part of TPIT project 6273 "Upgrade the Saginaw (Deen Switch) - Eagle Mountain 138 kV Double Circuit Line" The Congestion experienced on Calmont Switch - Carswell 138 kV constraint in 2021 Is Due To Multiple Simultaneous Outages In The Area: * Eagle Mountain Ses - Morris Dido (6265_A) And Morries Dido - Rosen Heights Tap 2 (6256_D) (Group Name 21-05056 - 02/22/2021 - 05/11/2021) * Blue Mound Swt 558 - Deen Switch Bkr 16280/16285 (6260_F), Blue Mound Swt 558 - Rosen Heights Tap 1 (6260_A), Eagle Mountain Ses Bkr 530 - Rosen Heights Tap 1 (6260_C), Rosen Heights Tap 1 - Rosen Heights Swt 534 (6260_E) (ONC00452746 - 03/14/2021 - 05/05/2021) * Handley Ses Bkr 4140 - Randol Mill Tap West (6405_C), Randol Mill Swt 4143 - Randol Mill Tap West (6405_E), Richland Hills Swt 4052/4102/4114 - Randol Mill Tap West (6405_F) 138 Kv (ONC00465768 - 04/21/2021 - 05/14/2021) * Benbrook Switch Bkr 7595 345 Kv (Group Name 21-06279 - 05/03/2021 - 05/03/2021) | Oncor
ONCOR | Hicks Switch - Roanoke Switch | LN | 345 | 22/3, 2021 | Krum West Switch - Lewisville Switch 345 kV & Krum West Switch - West Denton 345 kV, DCKT Hicks Switch - Deen Switch 138 kV | Courtland - Timberview Switch 345 kV, Rosen Heights Tap2 - Deen Switch 138 kV | Removal | Remove Rosen Heights Tap2 - Deen Switch 138 kV overload element and its associated contingency DCKT Hicks Switch - Deen Switch 138 kV due to upgrading overloaded element Rosen Heights Tap2 - Deen Switch 138 kV line (ISD - 11/12/2021) as a part of TPIT project 6273 "Upgrade the Saginaw (Deen Switch) - Eagle Mountain 138 kV Double Circuit Line" The congestion experienced on Courtland - Timberview Switch 345 kV constraint in March of 2022 is due to multiple simultaneous outages in the area: * Everman 345 kV and Auto 3 (ONC00501494 - 02/27/2022 - 03/10/2022) * Timberview - Venus Switch 345 kV (ONC00510345 - 02/28/2022 - 03/20/2022) * Anna Switch - Cedar Elm Sw 345 kV (ONC00497260 - 03/01/2022 - 03/14/2022) * Anna Switch - Krum West Sw 345 kV (ONC00498515 - 03/01/2022 - 03/14/2022) * Parker Switch BKR 6800/9865 345 kV (ONC00500390 - 03/08/2022 - 03/09/2022) | Oncor
ONCOR | Everman Switch - Rocky Creek | LN | 345 | 22/2, 22/1, 21/12 | DBCKT Marrs Switch -…- Wedgwood Switch 138 kV | Hemphill - Mistletoe Heights 138 kV | Removal | The congestion experienced onHemphill - Mistletoe Heights 138 kV in Jan/Feb of 2022 and Dec 2021 is due to multiple simultaneous outages in the area: * Everman - Sycamore Creek (6000_B) (ONC00463723 - 12/04/2021 - 12/22/2021) * Eagle Mountain SES - Morris Dido (6265_A) (ONC00500919 - 12/16/2021- 12/22/2021) * Blue Mound - Deen Switch (6270_A) (ONC00497000 - 12/17/2021 - 12/29/2021) * Calmount Switch 138 kV West Bus (ONC00495642 - 12/17/2021 - 12/21/2021) * Everman - Timberview (TVBP1_A) (ONC00505715 - 1/15/2022 - 02/02/2022) * Everman Switch 345 kV Bus D (ONC00503873 - 1/18/2022 - 01/21/2022) * Everman Switch 345 kV Bus D (ONC00507731 - 1/31/2022 - 02/01/2022) | Oncor
ONCOR | Century - Sherry Switch | LN | 345 | 21/5 | DBCKT Everman Switch -…- Handley Ses 138 kV | Hemphill - Mistletoe Heights 138 kV | Removal | The congestion experienced on Hemphill - Mistletoe Heights 138 kV in May of 2021 is due to multiple simultaneous outages in the area: * Eagle Mountain SES - Morris Dido (6265_A) (ONC00467388, ONC00469275 - 02/22/2021 - 05/11/2021) * Eagle Mountain SES - Rosen Height Tap 1 (6260_C) (ONC00455560 - 02/25/2021 - 05/11/2021) * Brookhollow - Brookhollow 2 Tap (6435_A) (ONC00465335 - 04/21/2021 - 05/14/2021) * Eagle Mountain SES - Morris Dido (6265_A) (ONC00469275 - 05/12/2021 - 05/14/2021) | Oncor
ONCOR | Allen Switch … Renner Switch (853) | LN | 138 | 21/5 | Anna Switch - Collin Switch 345 kV | Allen Switch - Plano Custer Road 138 kV | Removal | The congestion experienced in May of 2021 is due to multiple simultaneous outages in the area: * Plano Custer Road - Plano Coit Rd 138 kV 853_B (ONC00435148: 04/23/2021-05/16/2021) * Rockhill - Prolina POI 138 kV (830_I) (ONC00466387 - 04/29/2021-05/05/2021) * Carrollton Northwest - Collin Sw 345 kV (70_A) (ONC00457885 - 04/30/2021 - 05/04/2021) * Carrollton Northwest - Carrollton Frankford Rd 138 kV (815_H) (ONC00457951 - 04/30/2021 -05/04/2021) | Oncor
ONCOR | Everman Switch - Timberview Switch | LN | 345 | 22/3 | Comanche Peak Ses - Johnson Switch (Oncor) 345 kV | Kennedale - Timberview Switch 345 kV | Removal | The congestion experienced in March of 2022 is due to multiple simultaneous outages in the area: * Everman 345 kV and Auto 3 (ONC00501494 - 02/27/2022 - 03/10/2022) * Timberview - Venus Switch 345 kV (ONC00510345 - 02/28/2022 - 03/20/2022) * Timberview 345 kV East Bus (22-05974 - 03/09/2022 - 03/11/2022) (21.72%) * Century - Sherry 345 kV (320_C) (ONC00511311 - 03/09/2022 - 03/09/2022) | Oncor
ONCOR | Courtland - Timberview Switch | LN | 345 | 22/3, 22/2 | Cleburne Switch -…- Godley 138 kV & Johnson Switch (Oncor) - Venus Switch 345 kV, DBCKT Everman Switch -…- Handley Ses 138 kV, Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV, Comanche Peak Ses - Johnson Switch (Oncor) 345 kV | Everman Switch AXFMR3 345/138 kV, Kennedale - Timberview Switch 345 kV, Hemphill - Mistletoe Heights 138 kV, Argyle - Highlands Tnp 138 kV | Removal | The congestion experienced on Everman Switch AXFMR3 345/138 kV in March of 2022 is due to multiple simultaneous outages in the area: * Timberview Breaker's outages (21-25650 - 12/03/2022 - 02/27/2022) * Everman Auto 4 (ONC00507104 - 02/06/2022 to 02/16/2022) * Everman - Venus (61_B) (ONC00508117 - 02/06/2022 to 02/16/2022) The congestion experienced on Kennedale - Timberview Sw in March of 2022 is due to multiple simultaneous outages in the area: * Everman 345 kV and Auto 3 (ONC00501494 - 02/27/2022 - 03/10/2022) * Timberview - Venus Switch 345 kV (ONC00510345 - 02/28/2022 - 03/20/2022) * Timberview 345 kV East Bus (22-05974 - 03/09/2022 - 03/11/2022) * Century - Sherry 345 kV (320_C) (ONC00511311 - 03/09/2022 - 03/09/2022) Oncor's LODF analysis showed marginal impact on Hemphill - Mistletoe Heights 138 kV for DBCKT Everman Switch -…- Handley Ses 138 kV contingency due to this MTE. This MTE does not appear to be linked to the contingency/constraint so remove Hemphill - Mistletoe Heights 138 kV overload element and its associated contingency DBCKT Everman Switch -…- Handley Ses 138 kV. Oncor's LODF analysis showed marginal impact on Argyle - Highlands Tnp 138 kV for Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV contingency due to this MTE. This MTE does not appear to be linked to the contingency/constraint so remove Argyle - Highlands Tnp 138 kV overload element and its associated contingency Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV. Driver of congetion is other MTEs (Anna Switch-Krum West Sw & Anns Sw-Cedar Elm Sw). | Oncor
ONCOR | Plano Tennyson … Renner Switch | LN | 138 | 21/5 | Anna Switch - Collin Switch 345 kV | Allen Switch - Plano Custer Road 138 kV | Removal | Oncor's LODF analysis showed that this MTE is reducing the flow on the constraint. The congestion experienced in May of 2021 is due to multiple simultaneous outages in the area: * Plano Custer Road - Plano Coit Rd 138 kV 853_B (ONC00435148: 04/23/2021-05/16/2021) * Rockhill - Prolina POI 138 kV (830_I) (ONC00466387 - 04/29/2021-05/05/2021) * Carrollton Northwest - Collin Sw 345 kV (70_A) (ONC00457885 - 04/30/2021 - 05/04/2021) * Carrollton Northwest - Carrollton Frankford Rd 138 kV (815_H) (ONC00457951 - 04/30/2021 -05/04/2021) | Oncor
ONCOR | Barton Chapel Wind Farm - Graham Switch | LN | 138 | 21/10 | DBCKT Graham Ses - Parker Switch 345 kV | Barton Chapel Wind Farm - Oran Sub 138 kV | Removal | Oncor's LODF analysis showed that this MTE is reducing the flow on the constraint. | Oncor
ONCOR | Buffalo … Stanton East | LN | 138 | 22/3 | Big Spring Switch -…- Natural Dam 138 kV | Big Spring West - Stanton East 138 kV | Removal | Oncor's LODF analysis showed that this MTE is reducing the flow on the constraint. Driver of congestion is another MTE on the list (Grady - ... - Vealmoor 138 kV). | Oncor
ONCOR | Odessa EHV Switch - Liquid Air | LN | 138 | 21/10 | Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | General Tire Switch - Rexall 138 kV | Removal | This MTE is a radial line and an outage of this element does not significantly contribute to any congestion. | Oncor
ONCOR | Brown Switch - Killeen Switch | LN | 345 | 21/6, 20/12 | DBCKT Killeen Switch - Salado Switch 345 kV, Comanche Sw (Oncor)-Comanche Peak 345 kV | Killeen Switch AXFMR1 345/138 kV, Comanche Tap - Comanche Switch (oncor) 138 kV | Correction | Remove overloaded element Killeen Switch AXFMR1 345/138 kV and its associated contingency DBCKT Killeen Switch - Salado Switch 345 kV because Oncor's LODF analysis showed that this MTE (line 35090_A) is reducing the flow on the Killeen Switch AXFMR1 345/138 kV for loss of DBCKT Killeen Switch - Salado Switch 345 kV constraint and also Killeen Auto #2 has been upgraded due to TPIT# 5624 (Killeen Sw. Sta. 345/138 kV Autotransformer Replacement) in May 2022. | Oncor
ONCOR | Knob Creek Switch - Salado Switch | LN | 345 | 19/9 | DCKT Austrop to Daffin Gin and AEN Dunlap to Decker Power Plant 138 kV, DCKT Temple Elm Creek to Belton 138 kV | AEN Dunlap - Techridge 138 kV, Temple Southeast - Temple Switch 138 kV | Correction | Remove overload element AEN Dunlap - Techridge 138 kV line and associated contingency DCKT Austrop to Daffin Gin and AEN Dunlap to Decker Power Plant 138 kV as AEN has upgraded AEN Dunlap - Techridge 138 kV line from 2000A to 3000A operation in December 2021 (TPIT - 07TPIT0050). | Oncor
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 19/1, 18/12, 18/10, 18/8, 18/7, 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV, DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Nacogdoches Se - Redland Switch 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | Correction | Remove contingency 'DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses' as it looks like duplicate | Oncor
ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV, Gilleland Creek - Mcneil 138 kV | Correction | Change overload element from 'Round Rock - Round Rock Northeast 138 kV' to 'Round Rock - Round Rock Northeast 138 kV (1661_A)' | Oncor
ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV, Gilleland Creek - Mcneil 138 kV | Correction | Change overload element from 'Round Rock - Round Rock Northeast 138 kV' to 'Round Rock - Round Rock Northeast 138 kV (1661_A)' | Oncor
ONCOR | Liggett Switch - Venus Switch (528) | LN | 345 | 19/11 | Liggett Switch to Venus Switch 345 kV | Britton Road - Venus Switch 345 kV | Correction | Change overload element from 'Britten Road - Venus Switch 345 kV' to 'Britten Road - Venus Switch 345 kV (530_C)' | Oncor
ONCOR | Liggett Switch - Venus Switch (529) | LN | 345 | 19/9 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV | Britton Road - Venus Switch 345 kV | Correction | Change overload element from 'Britten Road - Venus Switch 345 kV' to 'Britten Road - Venus Switch 345 kV (530_C)' | Oncor
ONCOR | Tri Corner - Watermill Switch (215) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV, DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV, Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | Correction | Change overload element from 'Britten Road - Venus Switch 345 kV' to 'Britten Road - Venus Switch 345 kV (530_C)' | Oncor
ONCOR | Tri Corner - Watermill Switch (515) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Parkdale Switch - Centerville Road Switch 138 kV,DCKT Big Onion - Watermill Switch 345 kV & Elrod Switch - Watermill Switch 345 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Britton Road - Venus Switch 345 kV, Kleberg Tap - Seagoville 138 kV | Correction | Change overload element from 'Britten Road - Venus Switch 345 kV' to 'Britten Road - Venus Switch 345 kV (530_C)' | Oncor
ONCOR | Benbrook Switch - Parker Switch | LN | 345 | 21/10 | Comanche Peak Ses - Mitchell Bend Switch 345 kV & Comanche Peak Ses - Wolf Hollow 345 Switch 345 kV, DBCKT Comanche Peak Ses - Parker Switch 345 kV | Benbrook Switch - Parker Switch 345 kV | Correction | Change overload element from 'Benbrook Switch - Parker Switch 345 kV' to 'Benbrook Switch - Parker Switch 345 kV (6042_A)' | Oncor
ONCOR, TMPA | Jack_Creek - Twin Oak Switch | LN | 345 | 20/11 | DCKT GibbonsCreek-Limestone 345 kV | Jewett - Singleton 345 kV | Correction | Change overload element from ‘Jewett - Singleton 345 kV ’ to ‘Jewett - Singleton 345 kV (260_A)' | Oncor
ONCOR | Grady -…- Vealmoor | LN | 138 | 22/4, 22/3, 21/6, 21/5 | Big Spring Switch -…- Natural Dam 138 kV, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Wett_Grelton - Wett_Long_Draw 345 kV, Odessa EHV Switch - Wett_Grelton 345 kV, Midland East Auto MR2 345/138 kV, Buffalo - Midland East 138 kV | Big Spring West - Stanton East 138 kV, Luther - Vealmoor 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Tall City - Telephone Road 138 kV | Correction | Change MTE from 'Grady -…- Vealmoor' to 'Grady -...- Brown-Buzzard Draw Switch-...-Vealmoor 138 kV' Remove overloaded element Tall City - Telephone Road 138 kV and its associated contingencies Midland East Auto MR2 345/138 kV and Buffalo - Midland East 138 kV due to completion of upgrading SL Telephone Road Sub - Tall City Sub 138kV Line: Rebuild - ISD 05/2021 as part of TPIT# 57915 Tall City - Telephone Road 138 kV Line Rebuild. | Oncor
ONCOR | Ennis West -Ennis Switch | LN | 138 | 19/6 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _A | Ennis West - Wahaxhachie - Sterrett | Correction | Change MTE element from 'Ennis West -Ennis Switch' to 'ENNIS WEST SWITCH -...- SHANKLE SWITCH 138 kV (941)' Change contingency from 'ENNIS SWITCH to ENNIS WEST SWITCH LIN _A' to 'ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943)' Change overload element from 'Ennis West - Wahaxhachie - Sterrett' to 'Ennis West Switch- Wahaxhachie - Sterrett' | Oncor
ONCOR | Ennis West -Ennis South | LN | 138 | 19/4 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | Ennis West -Ennis Switch | Correction | Change MTE element from 'Ennis West -Ennis South' to 'Ennis West Switch -Ennis South (941_C)' Change overload element from 'Ennis West -Ennis Switch' to 'ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943)' | Oncor
ONCOR | Ennis West - Wahaxhachie - Sterret | LN | 138 | 18/11 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _C | ENNIS WEST SWITCH - ENNIS SWITCH 138 kV | Correction | Change MTE element from ‘Ennis West - Wahaxhachie - Sterret’ to ‘Ennis West Switch -…- Sterrett (940)' Change contingency from 'ENNIS SWITCH to ENNIS WEST SWITCH LIN _C' to 'ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (941)' Change overload element from 'ENNIS WEST SWITCH - ENNIS SWITCH 138 kV' to 'ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943)' | Oncor
ONCOR | Big Spring Switch - Natural Dam | LN | 138 | 21/11, 21/10 | Grady -…- Vealmoor 138 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV | Big Spring West - Stanton East 138 kV | Correction | Change MTE element from ‘Big Spring Switch - Natural Dam’ to ‘Big Spring Switch -…- Natural Dam' Change contingency from 'Grady -…- Vealmoor 138 kV' to 'Grady - Brown 138 kV' | Oncor
ONCOR | Benbrook Swith - … - Everman Switch | LN | 345 | 20/10, 19/11, 17/3, 17/2 | DCKT Wedgewood Sw-…-Benbrook 138 kV, DCKT Everman Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV | Hemphill - Mistletoe Heights 138 kV | Correction | Change MTE element from ‘Benbrook Swith - … - Everman Switch’ to ‘Benbrook Swith - … - Timberview Switch' Change contingency from 'DCKT Wedgewood Sw-…-Benbrook 138 kV' to 'DCKT Wedgewood Sw - Benbrook Switch 138 kV' Change contingency from 'DCKT Everman Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV' to 'DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV' | Oncor
ONCOR | Elkins Road Pod - Midland East | LN | 138 | 21/11 | Grady -…- Vealmoor 138 kV | Big Spring West - Stanton East 138 kV | Correction | Change contingency from 'Grady -…- Vealmoor 138 kV' to 'Grady -…- Brown 138 kV' | Oncor
ONCOR | Johnson Switch - Venus Switch | LN | 345 | 19/11, 19/10 | DCKT Everman Switch to Venus Switch 345 kV, DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV, Concord Auto CRD1 345/138 kV | Cedar Hill Switch - Fish Creek Switch 138 kV (3180), Hemphill - Mistletoe Heights 138 kV, Concord Auto CRD2 345/138 kV | Correction | Change contingency from 'DCKT Everman Switch to Venus Switch 345 kV' to 'DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV ' Oncor's LODF analysis showed marginal impact on Hemphill - Mistletoe Heights 138 kV for DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV contingency due to this MTE. This MTE does not appear to be linked to the contingency/constraint so remove Hemphill - Mistletoe Heights 138 kV overload element and its associated contingency DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV. | Oncor
ONCOR | Cedar Hill Switch - Courtland | LN | 345 | 19/10, 18/9, 18/5 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV, DCKT Everman Switch to Venus Switch 345 kV | Britten Road - Venus Switch 345 kV, Cedar Hill Switch - Fish Creek Switch (3180) 138 kV | Correction | Change contingency from 'DCKT Everman Switch to Venus Switch 345 kV' to 'DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV ' Change overload element from 'Britten Road - Venus Switch 345 kV' to 'Britten Road - Venus Switch 345 kV (530_C)' | Oncor
ONCOR | Mitchell Bend Switch - Rocky Creek | LN | 345 | 19/11, 19/10 | DCKT Comanche Peak SES - Johnson Switch & Everman Switch 345 kV, DCKT Everman Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV | Carmicheal Bend Switch - Mitchell Bend Switch 345 kV, Hemphill - Mistletoe Heights 138 kV | Correction | Change contingency from 'DCKT Comanche Peak SES - Everman Switch & Johnson Switch 345 kV' to 'DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV' Oncor's LODF analysis showed marginal impact on Hemphill - Mistletoe Heights 138 kV for DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV contingency due to this MTE. This MTE does not appear to be linked to the contingency/constraint so remove Hemphill - Mistletoe Heights 138 kV overload element and its associated contingency DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV. | Oncor
ONCOR | Comanche Peak Ses - Mitchell Bend Switch | LN | 345 | 20/3 | DCKT Comanche Peak SES - Everman Switch & Johnson Switch 345 kV | Comanche Peak SES - Wolf Hollow 345 Switch 345 kV, Mitchell Bend Switch - Wolf Hollow 345 Switch 345 kV | Correction | Change contingency from 'DCKT Comanche Peak SES - Everman Switch & Johnson Switch 345 kV' to 'DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV' | Oncor
AEP, ONCOR | Clear Crossing - Willow Creek Switch | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV, Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV, Abilene Mulberry Creek - Bluff Creek 345 kV |  | Overloaded element (Abilene Mulberry Creek - Bluff Creek 345 kV) owned by AEP, AEP to provide comments as necessary. | Oncor
ONCOR | Graham SES - Tonkawa Switch | LN | 345 | 21/11 | Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Bluff Creek 345 kV |  | Overloaded element (Abilene Mulberry Creek - Bluff Creek 345 kV) owned by AEP, AEP to provide comments as necessary. | Oncor
GAR, LCRA | King Mountain Switchyard - North McCamey | LN | 345 | 19/10 | Moss Switch to Odessa EHV Switch (34600_A) 345 kV | Odessa EHV Switch Auto MR2 345/138 kV | Correction | Oncor Comments: No overload expected on Odessa EHV Switch Auto MR2 345/138 kV for Moss Switch to Odessa EHV Switch (34600_A) 345 kV contingency due to completion of ERCOT TPIT 46094 (add Wolf Switch 345 kV, ISD - 06/2020) | Oncor
LCRA, STEC | Bakersfield - Cedar Canyon | LN | 345 | 22/4, 19/9 | Moss Switch to Odessa EHV Switch 138 kV, Midessa South Sw - Odessa EHV Switch 345 kV & Morgan Creek Ses -…- Quail Switch 345 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | Odessa EHV Auto MR2 345/138 kV, Midessa South SW AXFMR1 345/138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Odessa - Odessa North 138 kV | Correction | Oncor Comments: No overload expected on Odessa EHV Switch Auto MR2 345/138 kV for loss of Moss Switch to Odessa EHV Switch 138 kV contingency due to completion of ERCOT TPIT 46094 (add Wolf Switch 345 kV, ISD - 06/2020) so remove Odessa EHV Auto MR2 345/138 kV and its associated contingency Moss Switch to Odessa EHV Switch 138 kV and Congestion Year/Month 19/9. | Oncor
TNMP | 16th Street Tnp - … - Rio Pecos | LN | 138 | 20/11, 20/10, 20/9 | Yucca Drive Sw-Lotebush 138 kV | Lynx - Tombstone 138 kV | Removal | Remove- This line does not exist. Multiple station rebuilds with new configurations. | TNMP
TNMP | Friendswood Tnp - Seminole Tnp | LN | 138 | 19/4 | Meadow - PH Robinson 345 kV | Alvin Tnp - Mainland Tnp 138 kV | Removal | Remove - Alvin-Mainland has been reconductored. This overload does not show in latest studies. | TNMP
TNMP | Gaf - Greenbelt Tnp | LN | 138 | 16/2 | Freeway Park Tnp to Heights Tnp 138 kV | Heights Tnp - Ph Robinson 138 kV | Removal | Remove - Reconductoring and addition of Attwater Station | TNMP
CNPE, TNMP | Gaf Tnp - Ph Robinson | LN | 138 | 18/1 | Caddo Sw Sta Tnp to Greenbelt Tnp 138 kV | Tejas Tnp - Comanche Sw Tnp 138 kV | Removal | Remove - This event does not show in studies. Near future work will reduce loading further for this contingency. | TNMP