## Slide 1: LFL-31 and 38: UFLS Obligations
Assumptions (from Jan.26 ERCOT presentation at LFLTF):
Flexible Load
  A Load, that has registered with ERCOT and in response to an ERCOT instruction may reduce or increase power consumption or interrupt to support system reliability or mitigate transmission constraints. Types of Flexible Loads include: a Load Resource or Interruptible Load.
Interruptible Load:
  Load interconnected to the ERCOT System that has registered with ERCOT and has designated a QSE. The Load is not in SCED but is curtailable via instruction to the Load’s QSE to maintain system reliability.

## Slide 2: LFL-31 and 38: UFLS Obligations
Assumptions:
LFL’s will Register with ERCOT as:
  Firm or Flexible/Interruptible Load
  Controllable Load Resource or,
  Load Resource (ERS, Ancillary Services)
LFL will assume UFLS Obligation for 100% of Load (Firm/Flexible)
  Registers with Texas RE as “Distribution Provider (DP) UFLS Only”
  Subject to NERC/TRE audits
    Risk based, typically 6+ years.
  Subject to ERCOT Annual “Survey”
    Turn in report of percentages for each frequency level.
  Spring Testing/compliance the obligation of QSE/LFL/ERCOT
    At a minimum, ensure they have a scheme in place
    QSE responsibility to ERCOT

## Slide 3: LFL-31 and 38: UFLS Obligations
The UFLS obligation should belong to the LFL for compliance (i.e., 5-10-10)
  The 5-10-10 is applicable to 25% of site load.
  Design so that the load is not shed at the transmission level breaker or that the load shed is not excessively above each step requirement.
  ERCOT may require P.E. attestation for correct installation of breakers provided to ERCOT and TO.
  LFL UFLS requirement will not be in the denominator for TO load shed obligation.
Above would apply unless the Transmission Operator assumes the UFLS obligation
  Details of responsibility defined in Facilities Extension Agreement (FEA) or Interconnection Agreement (IA)

## Slide 4: LFL-31 and 38: UFLS Obligations
Summary:
Simple Implementation
Implement UFLS Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
  Important that the Load does not curtail 25% of its load at one time.

## Slide 5: UFLS example on an LFL site
5800
6895
5000
5500
6000
6800
H
LD
-
1
LD
-
2
LD
-
3
LD
-
4
LD
-
5
LD-6
-
5%
UFLS
10%
UFLS
10%
UFLS
Total
25%
UFLS
Frequency Threshold | LFL Load Relief
59.3 Hz | At least 5% of the LFL Load
58.9 Hz | A total of at least 15% of the LFL Load
58.5 Hz | A total of at least 25% of the LFL Load
Notes: Simple Implementation
Implement Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
Allow optional treatment for these loads but then based on this selection having clear rules.
Address complications for TO’s due to LFL being more responsive to market