## Slide 1: Interconnection Process Comments
October 23, 2023 Large Flexible Load Task Force Meeting
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 2: Agenda Item 2 – Applicability of LLISP (24-months)
Description
Unanticipated ERCOT involvement in load interconnection requests that do not meet the two LLISP thresholds (75MW+24months or less) may create unexpected delays to in-service dates for customers.
Proposal
Include affirmative statements that ERCOT will not intervene in interconnections that do not meet both the size and timeline criteria, and/or
Establish a standard interaction with ERCOT at the beginning of a 75MW or larger interconnection request, for ERCOT to definitively confirm whether the load will be subject to LLIS or not.
Remove the requirement to demonstrate that a Large Load ready to energize will not violate various ERCOT operational standards (9.6(1)(b))
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 3: Agenda Item 2 – Applicability of LLISP (negligible increases in customer demand)
Description
A 74MW load increasing its demand by 1MW would be required to go through the LLISP:
    “A modification of an existing Load Facility not co-located with a Generation Resource such that, after modification, the Load Facility qualifies as a Large Load” (9.2.1(1)(b)(iii) and (iv)
Proposal
A load that did not initially go through LLISP should become subject to LLISP if it increases its demand by 25MW or more within one year of initial energization.
Strikes balance between de minimis load increases by a customer, and a customer seeking to circumvent LLISP.
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 4: Agenda Item 4 – Confidentiality of LLIS Data
Description
LLIS draft and final reports should be subject to different posting and dissemination processes than generation interconnections.
Proposal
LLIS-related study information to only be accessible to TDSPs directly affected by the proposed interconnection request.
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 5: Agenda Item 5 – Steady-State Analysis Provisions
Description
It is unclear how some of the load registration types are expected to be studied and dispatched in the planning cases.
Proposal
CLR and RCL dispatch procedures should be developed and described in the SSWG Procedure Manual
CLR/RCL study assumptions should be codified in the Planning Guide
Address any necessary changes to the Maintenance Outage Reliability Criteria through a standalone Planning Guide revision
Load Resources and RCLs should be treated as firm loads in Planning, so that system issues can be properly identified and addressed.
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 6: Agenda Item 6 – Modeling of Loads/SSWG Cases
Description
PGRR111 prohibits TSPs from entering a load in the SSWG cases unless/until an interconnection agreement has been executed (6.6.1), conflicting with statutory provisions that require TSPs to plan for forecasted load without an interconnection agreement.
Proposal
Remove the prohibition, and modify the PGRR language such that the TSP shall model a load in the SSWG cases once an agreement has been signed
      To function as a “no later than,” rather than a prohibition (6.6.1(1) and (2))
Remove requirement for Load modifications/increases to be entered in the SSWG cases once an IA has been signed (may not require IA)
©2023 Oncor Electric Delivery Company LLC. All rights reserved.

## Slide 7: Agenda Item 7 – Load Commissioning Plans
Description
It is unclear which Loads are required to have Load Commissioning Plans.
Proposal
Oncor proposes that only Large Loads subject to LLISP be required to have Load Commissioning Plans
The interconnecting TSP should provide Load Commissioning Plans to ERCOT when required
Recommend the term “Load Service Plan” or similar
©2023 Oncor Electric Delivery Company LLC. All rights reserved.