## Slide 1
ERCOT Annual Inertia Analysis
05/15/2024
ERCOT Staff

## Slide 2: Effect of Synchronous Inertia on System Frequency
With the increasing integration of inverter-based resources (IBRs), fewer synchronous machines are online, potentially resulting in extended periods of lower overall system inertia
  Higher system inertia → Lower RoCoF
  Lower system inertia → Higher RoCoF
UFLS trigger
RoCoF: Rate of Change of Frequency

## Slide 3: Inertia Calculation
In 2013, as instantaneous wind power penetration reached 30%, ERCOT started analyzing impacts of IBR on system inertia
In 2015, ERCOT implemented a real-time inertia calculation using inertia parameters of each individual synchronous generator and its status (on/off) telemetry
where I is the set of online synchronous generators or condensers, MVAi is MVA base of on-line synchronous generator or synchronous condenser i, and Hi is inertia constant for on-line generator or synchronous condenser i in a system (in seconds on machine MVAi)

## Slide 4: Wind Generation Capacity
+1,893 MW
+3,198 MW
+2,625 MW
+2,247 MW
+1,384 MW
+4,587 MW
+3,908 MW
+2,802 MW
+2,977 MW
+1,788 MW

## Slide 5: Solar Generation Capacity
+696 MW
+3,429 MW
+4,780 MW
+4,003 MW
+7,335 MW

## Slide 6
Inertia Analysis

## Slide 7: Total Inertia 2013-2023
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 1:00 AM | 2022 03/21 2:00 AM | 2023 04/18 3:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 116.6 | 115.0 | 124.3
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 31,767 | 33,784 | 35,578
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 66 | 65 | 61
Red circles denote inertia at max IRR penetration (= IRR Gen/Total Gen)

## Slide 8: Total Inertia by Group 2018-2023
In 2023, less hours below 150 GW*s and more hours above 350 GW*s

## Slide 9: Lowest 100 Hours of Total Inertia 2018-2023
 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Lowest Inertia Hour (GW*s) | 129 | 135 | 131 | 117 | 115 | 124
100th Lowest Inertia Hour (GW*s) | 155 | 152 | 147 | 135 | 125 | 146
Similar trends for 2020 and 2023

## Slide 10: Net Load during the Lowest 100 Inertia Hours 2018-2023
Similar trends for 2020 and 2023

## Slide 11: Total Inertia by Month 2018-2023
In 2023, the spring (Mar and Apr) and summer (Aug to Oct) show higher inertia compared to previous years

## Slide 12
Observation 1

## Slide 13: Correlation between Inertia and Net Load
Inertia and net load exhibit a strong correlation

## Slide 14: Net Load by Month 2018-2023
In 2023, the average inertia increased significantly due to the higher summer (Aug-Oct) net load
  Net Load = Load – Wind Generation – Solar Generation

## Slide 15: Low Inertia Group (< 150 GW*s) by Month 2018-2023
In the spring of 2023, inertia increased drastically in the low inertia group, but net load did not increase significantly

## Slide 16
Observation 2

## Slide 17: Inertia Group by Unit Type 2018-2023
In the low inertia group, CC inertia increased rapidly in 2023
Two coal units retired (3.085 GW*s)

## Slide 18: Correlation between CC Generation and Total Inertia
CC Generation and Total Inertia exhibit a strong correlation

## Slide 19: CC Generation in Low Inertia Period by Month 2018-2023
In the spring of 2023 (Mar-Apr), CC Generation increased significantly compared to Spring 2022 during the low inertia period

## Slide 20: Natural Gas Prices 2015-2023
May 2023
$2.14
Source: Macrotrends (Natural Gas Prices)

## Slide 21: Summary
Lowest system inertia in 2023 was 124 GW*s
2023 experienced less hours below 150 GW*s than in previous years; more hours above 350 GW*s
In 2023, the average inertia increased significantly due to the higher summer (Aug-Oct) net load
  Higher total load offset the increase in IRR generation
In 2023, higher contribution from combined cycle units was correlated with the lowest system-wide inertia hours
  CC generation was significantly increased in Spring (Mar, Apr)
  Lower natural gas prices led to more dispatch of CC units during the lower inertia period

## Slide 22: Thank you!
Questions