## Slide 1
GE Recommendation RRS Limit Draft NPRR and NOGRR
ERCOT
Operations Planning
PDCWG | May 15, 2024

## Slide 2: Overview of changes
The NPRR and NOGRR have been developed to adopt an amended version of GEs recommendation, which proposes that a maximum limit of RRS-PFR from a single Resource could be established. This limit is recommended to address the risk of common mode failure i.e. risk of too much RRS-PFR from one Resource which would degrade system frequency response.
ERCOT recommends 157 MW as a static limit on the maximum amount of RRS-PFR a single Resource can provide. This value was selected based on ERCOT studies as an extension of the GE recommendation so that the expected frequency degradation due to failure to perform from a single RRS-PFR Resource stays below 50mHz under a variety of historic inertia conditions.
NPRR section updated:
  3.16, Standards for Determining Ancillary Service Quantities
  3.18, Resource Limits in Providing Ancillary Service
NOGRR sections updated:
  2.3.1.2.1, Limit on Generation Resources and Controllable Load Resources Providing RRS
  Section 8 Attachment N: Procedure for Calculating RRS MW Limits for Individual Resources to provide RRS using Primary Frequency Response

## Slide 3: Examples of RRS Limits
2.3.1.2.1, Limit on Generation Resources and Controllable Load Resources Providing RRS
(2) The default maximum MW limit of Primary Frequency Response shall be set to lower of 20% of its High Sustained Limit (HSL) and maximum amount of RRS an individual Resource can provide using Primary Frequency Response for any newly RRS-qualified Generation Resource or Generation Resource not yet evaluated per Section 8, Attachment N, Procedure for Calculating RRS Limits for Individual Resources, for measuring actual performance.
Recommended RRS MW Limit: 157 MW
Unit | HSL (A) | Default RRS % Limit | Verified Droop % | Verified RRS % Limit (B) | Calculated RRS MW Limit C=(A*B) | Final RRS MW Limit Min(C, 157)
Unit 1 | 50 | 20 | 0.01 | 100 | 50 | 50
Unit 2 | 100 | 20 | 0.01 | 100 | 100 | 100
Unit 3 | 150 | 20 | 0.01 | 100 | 150 | 150
Unit 4 | 200 | 20 | 0.01 | 100 | 200 | 157
Unit 5 | 800 | 20 | 0.05 | 20 | 160 | 157
Unit 6 | 900 | 20 | 0.05 | 20 | 180 | 157
Unit 7 | 1000 | 20 | 0.05 | 20 | 200 | 157

## Slide 4: Questions?
Thank you!