## Slide 1
SCR819 Implementation
CMWG

## Slide 2: NPRR1111 & SCR819 Review
General description
  IRR units behind a binding GTC with a shift factor impact greater than 2% on the GTC flow should NOT exceed their SCED BP when NTE is triggered.
SCR819 parameters:
  Triggering condition: Trigger conditions being considered are:
    When GTC loading is above 85% of calculated limit
    When GTC constraint is activated/ binding in SCED
  Discount factor: Reliability limit will be discounted in a less-conservative manner, closer to 1.0.
  IRR shift factor threshold: IRR units with shift factor greater than 2% on a GTC cannot exceed their SCED BP.

## Slide 3: Benefits of NTE Concept
Should allow ERCOT to bind at a higher limit, resulting in more MW production from IRRs behind IROL when binding
Keeps ERCOT from exceeding SOLs and IROLs
More efficient way of meeting reliability requirements, especially when GTC limit constraints are binding
Additional advantages to real-time operations
  Requires less operator attention
  Provides greater certainty in managing flow

## Slide 4: Resource Shift Factor Distribution per GTC
Number of IRRs, per GTC, per shift factor bin

## Slide 5: Implementation Plan
Implementation May 30, 2024
Start initially North Edinburg to Lobo GTC
  Issue Market Notice prior to implementation
  Monitor Performance for 2 weeks
    Determine how well IRRs are performing or controlling Base Points
Enable Panhandle IROL
  Issue Market Notice prior to implementation
  Monitor Performance for 2 weeks
    Determine how well IRRs are performing or controlling Base Points
West Texas, McCamey GTCs and South Texas Export IROL
  Issue Market Notice prior to implementation
  Monitor Performance for 2 weeks
Enable for other GTCs