## Slide 1
PDCWG Report to ROS
Chair: Kevin Bunch, EDF Trading North America
Vice Chair: Chad Mulholland, NRG
ROS
June 6th, 2024

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    Annual Inertia Presentation
    NOGRR Draft – RRS Limitations
    NOGRR 263
    ERCOT Frequency Control Metrics and Regulation Reports
    Analysis of Disturbances/Frequency Events
    TRE Report
      SAR Draft (BAL-001 for ESRs)
      PFR by Resource Type
    ROS Open Action Items
    Other Items
      NDA List Review
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of April
  Frequency Control Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 395 MW/0.1 Hz
IMFR Performance currently
1236.68 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
April 2024

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 15.31 mHz on avg for April 2024

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections

## Slide 11: ERCOT Total Energy
Notes: 33,644,368 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   11,622,240 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 34.54% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 3,472,621 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 10.32% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in April 2024 = 133,953.45 MW*s on April 6th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
April Data:
Mean: 184,725 MW*s
Max: 236,951 MW*s on April 17th
Min: 133,953.45 MW*s on April 6th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on February 25th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.
^ indicates a partial year.