## Slide 1
2025 Ancillary Service Methodology
Discussion
Ancillary Services & Operations Analytics
ERCOT

## Slide 2: Stakeholder Discussion Timeline
July 23, 2024 – WMWG
July 24, 2024 – PDCWG
August 15, 2024 – OWG (Proposed)
August 21, 2024 – PDCWG (Proposed)
August 30, 2024 – WMWG (Proposed)
September 09, 2024 – ROS
September 11, 2024 – WMS
September 25, 2024 – TAC
October 10, 2024 – BoD
Nov or Dec 2024 – PUC

## Slide 3: Discussion Scope for Today
This presentation will discuss the proposed methodology to determine Ancillary Service (A/S) quantities for 2025.
  ERCOT is not considering any changes in the methodology used to compute Responsive Reserve Service requirements for 2025.
    NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT for the 2025 Operating Year (OY) determined that the 2025 minimum RRS-PFR limit would be 1,365 MW.
  ERCOT is proposing one change each in the methodology to calculate Regulation Service and Non-Spinning Reserve Service and three changes in methodology used to calculate ERCOT Contingency Reserve Service.
  The Ancillary Service (A/S) quantities for 2025 contained in this presentation are based on the methodology that was approved in December 2023. The quantities for 2025 reflect moving forward the historic data on which these are based, unless otherwise noted.
  ERCOT is seeking stakeholder feedback on these proposes changes for the 2025 A/S Methodology.

## Slide 4
Responsive Reserve Service

## Slide 5: Responsive Reserve Service (RRS) Methodology
ERCOT is not proposing any change to the methodology used to compute RRS requirements in 2025.
The preliminary RRS quantities for January 2025 through July 2025 in subsequent slides have been computed using 2023 and 2024 system inertia conditions and updated RRS table.
Updates to RRS Table:
  The RRS table tracks RRS requirements for different inertia conditions.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2025 assessment for ERCOT shows a increase in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2025 will change to 1,365 MW.
  The RRS table was updated in 2024 to use a minimum RRS-PFR limit of 1,365 MW.
Responsive
Responsive Reserve Service (RRS) is reserved capacity that is procured to respond to low frequency events typically triggered by generating unit trips.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW
OY2024 IFRO – 395 MW/0.1 Hz | Limit 1,185 MW
OY2025 IFRO – 455 MW/0.1 Hz | Limit 1,365 MW

## Slide 6: 2025 RRS Table
Scenario | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5,960 | 5,563 | 5,200 | 4,892 | 4,622 | 4,329 | 4,114 | 3,920 | 3,744 | 3,522 | 3,314 | 3,139
*RRS Curr IFRO (MW) | 3,293 | 3,234 | 3,178 | 3,128 | 3,086 | 2,998 | 2,960 | 2,916 | 2,880 | 2,808 | 2,716 | 2,654
**RRS Upd IFRO (MW) | 3,320 | 3,273 | 3,227 | 3,183 | 3,145 | 3,068 | 3,031 | 2,982 | 2,941 | 2,863 | 2,767 | 2,699
Scenario | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3,004 | 2,890 | 2,784 | 2,686 | 2,595 | 2,510 | 2,421 | 2,353 | 2,290 | 2,230 | 2,173 | 2,119 | 2,068
*RRS Curr IFRO (MW) | 2,606 | 2,560 | 2,529 | 2,491 | 2,444 | 2,412 | 2,373 | 2,342 | 2,290 | 2,230 | 2,173 | 2,119 | 2,068
**RRS Upd IFRO (MW) | 2,645 | 2,595 | 2,558 | 2,514 | 2,463 | 2,425 | 2,380 | 2,343 | 2,290 | 2,230 | 2,173 | 2,119 | 2,068
*RRS quantity is calculated for RCC of 2,805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,185 MW.
**RRS quantity is calculated for RCC of 2,805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,365 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.

## Slide 7: Hourly Average RRS Comparison
2025 RRS:
On avg. 13 MW increase from prev. year
Largest increase is in Feb by 122 MW
Largest decrease is in Jan by 59 MW

## Slide 8: RRS Comparison February
2025 RRS:
Range: 2,982 – 3,145 MW;
Avg: 3,073 MW (122 MW increase from prev. year)

## Slide 9: RRS Comparison April
2025 RRS:
Range: 2,941 – 3,145 MW;
Avg: 3,045 MW (42 MW increase from prev. year)

## Slide 10: RRS Comparison July
2025 RRS:
Range: 2,342 – 2,491 MW;
Avg: 2,426 MW (6 MW increase from prev. year)

## Slide 11
Regulation Service

## Slide 12: Regulation Service Methodology
ERCOT is proposing one change to the methodology used to compute the minimum Regulation Service requirements in 2025.
    Specifically, ERCOT is proposing to set regulation quantities based on the error in forecasting the net load forecast that is used in to set dispatch target for SCED (i.e. GTBD).
The preliminary Regulation quantities for January 2025 through July 2025 in subsequent slides have been computed using proposed methodology (with 2023 and 2024 five minute ahead Net load forecast error) and updated Wind and Solar Over Forecast Adjustment tables.
Regulation
Regulation Service is reserved capacity that is deployed every 4 seconds to balance supply and demand and maintain frequency close to 60Hz between 5-minute SCED runs.

## Slide 13: Regulation Up/Down Methodology: Summary of changes
 | 2024 Methodology | 2025 Methodology (proposed)
Data Input | 5-min Netload Ramp (2-yr) Historical Reg Deployment (2-yr) | 5-min SCED Netload Forecast Error (2- yr)
Calculation Method | Max(95th of 5-min Netload Ramp, 95th of Historical Reg Deployment) | 95th of 5-min SCED Netload Forecast Error
Wind/Solar Adjustment | GE Table - Increased netload variability/ramp per 1,000 MW installed wind/solar capacity increase | New GE Table - Increased wind/solar forecast error per 1,000 MW installed capacity increase
FRRS Component | 95th of historical FRRS Deployment (2-yr) | No Change
ACE Integral Component | Average of ACE Integral Change (2-yr) | No Change
Load Adjustment (LFL Ramps) | Not considered | No Change

## Slide 14: Generation To Be Dispatched (GTBD)
ERCOT has incorporated intra-hour wind/solar forecast- based ramp into GTBD to give SCED an indication of how renewables may ramp.
  Predicted Wind Ramp Rate (PWRR) was incorporated in GTBD in Dec.2018
  Predicted Solar Ramp Rate (PSRR) was incorporated in GTBD in Jun.2021
In absence of PSRR/PWRR, SCED dispatches uncurtailed solar/wind units to their max output (HSL).
  This means that SCED assumes output of uncurtailed solar/wind units will persist for the next 5-min at the unit’s HSL that was telemetered at the start of the interval.
GTBD = Total Gen
+K3*5*PLDRR
+K4*Regulation Deployed
+ K5*ACE Integral
– K6*5*PWRR
+ K7*5*DCTRR
– K8*5*PSRR
5-min Load Ramp Forecast
Previous Reg Deployment
Historical Accumulated ACE
5-min Wind Ramp Forecast
5-min DC Tie Ramp Forecast
5-min Solar Ramp Forecast

## Slide 15: Recap – Dynamic PSRR Threshold in GTBD
Chart: Dynamic PSRR Threshold
 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 0 | 0 | 0
ERCOT started to apply a dynamic PSRR threshold in GTBD calculation on 6/12/2023
PSRR thresholds change with 4 pre-defined day periods - Night, Sunrise, Sunset and Other
ERCOT started with a threshold of 80MW/min for Sunrise and Sunset periods on 6/12 and subsequently increased it to 100MW/min on 6/15
ERCOT plans to update the thresholds and the definition of day periods seasonally* (4 times a year)
Night
* Seasons will be defined by shift in solar ramping patterns

## Slide 16: SCED Manual Offset and Reg-Up Exhaustion
Sunset hours: HE 19 - 21
Chart: SCE Manual Offest Interval Count
| 6 (Pre) | 6 (Post) | 7 | 8 | 6 | 7 | 2023 Summer | 2024 Summer
<=100 MW | 1 | 2 | 17
100-200 MW | 7 | 1 | 17 | 25 | 6 | 10
200-300 MW | 5 | 5 | 14 | 20 | 7 | 10
300-400 MW | 9 | 2 | 8 | 2 | 1
400-500 MW | 2 | 4
Reg Up Exhaustion (Sunset) | 0.05303 | 0.068713 | 0.02509 | 0.026 | 0.013 | 0.016
Notes: FME: Frequency Measurable Event

## Slide 17: LFL Analysis - LFL Ramp vs. Regulation Exhaustion
*NSFL – Non-SCED Dispatched Flexible Load
**Additional LFL Analysis shared with PDCWG
Key Takeaway: Currently with the set of LFLs within the ERCOT system there is no correlation between LFL ramping and regulation exhaustion.
Notes: For each 2024 5-min interval, NSFL ramp rate values were examined in bins of 10 MWs (as tracked on x-axis) and the average rate of intervals during which regulation was exhausted (i.e.average remaining regulation was less than 5 MW) was computed (as tracked on y-axis). For example using the dot (-240, 0.2) as an example, this dot represents that in 2024, regulation was exhausted 20% of the time during which the ramp was between -250 and -240 MW. No dot represents there was no intervals of an NSFL ramp in the bin.

## Slide 18: Hourly Average Regulation Comparison
Reg-Up 2025:
On avg. 77 MW increase from prev. year
Largest increase is in July by 96 MW
Reg-Up 2025 (Proposed):
On avg. 33 MW increase from prev. year
Largest increase is in July by 49 MW
Reg-Down 2025:
On avg. 68 MW increase from prev. year
Largest increase is in Jan by 83 MW
Reg-Down 2025 (Proposed):
On avg. 23 MW increase from prev. year
Largest increase is in July by 40 MW

## Slide 19: Regulation Comparison January
2025 Reg-Up:
Range: 183 – 1,319 MW;
Avg: 458 MW (73 MW increase from prev. year)
2025 Reg-Up (Proposed):
Range: 234 – 725 MW;
Avg: 382 MW (3 MW decrease from prev. year)
2025 Reg-Down:
Range: 213 – 1,239 MW;
Avg: 425 MW (83 MW increase from prev. year)
2025 Reg-Down (Proposed):
Range: 227 – 689 MW;
Avg: 369 MW (27 MW increase from prev. year)

## Slide 20: Regulation Comparison March
2025 Reg-Up:
Range: 179 – 1,032 MW;
Avg: 493 MW (61 MW increase from prev. year)
2025 Reg-Up (Proposed):
Range: 271 – 742 MW;
Avg: 461 MW (29 MW increase from prev. year)
2025 Reg-Down:
Range: 231 – 1,093 MW;
Avg: 490 MW (60 MW increase from prev. year)
2025 Reg-Down (Proposed):
Range: 273 – 674 MW;
Avg: 431 MW (1 MW increase from prev. year)

## Slide 21: Regulation Comparison June
2025 Reg-Up:
Range: 113 – 865 MW;
Avg: 497 MW (79 MW increase from prev. year)
2025 Reg-Up (Proposed):
Range: 273 – 663 MW;
Avg: 451 MW (33 MW increase from prev. year)
2025 Reg-Down:
Range: 210 – 679 MW;
Avg: 440 MW (52 MW increase from prev. year)
2025 Reg-Down (Proposed):
Range: 223 – 612 MW;
Avg: 419 MW (31 MW increase from prev. year)

## Slide 22
ERCOT Contingency Reserve
Service

## Slide 23: ERCOT Contingency Reserve Service (ECRS) Methodology
ECRS is reserved capacity that can respond in 10 minutes to recover frequency, cover forecast errors or ramps and replace deployed reserves.
Currently, ECRS requirements are computed as to account for capacity needed to recover frequency following a large unit trip and capacity needed to support net load forecast errors during sustained net load ramps.
For 2025, ERCOT is proposing to compute the minimum ECRS requirements as the larger of the capacity needed to recover frequency and capacity needed to support net load forecast errors. Along with these ERCOT is proposing to make the following two modifications
  Compute the capacity needed to recover frequency based on 70th percentile of historic inertia.
  Remove the risk coverage during sunset hours to be at least 90th percentile in the calculation used to compute capacity needed for net load forecast error.
The preliminary ECRS quantities for January 2025 through July 2025 in subsequent slides have been computed using proposed methodology (2023 and 2024 Intra-Hour Net load and Net load Forecast, 2023 and 2024 system inertia conditions ) and updated Intra-hour Solar Over-Forecast Error Adjustment table.
  Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Notes: (b) change was to recognize the fact that during ECRS deployments that are triggered by unit trips, initially both Regulation and ECRS will be relied on to recover frequency and then ECRS will be used to recover deployed Regulation.

## Slide 24: ECRS Methodology 2025
 | 2024 Methodology | 2025
Data Input | 30-MA Netload Forecast Error (2-yr) | No Change
Calculation Method | 80th - 95th percentile of 30-MA Netload Forecast Error (2-yr) Calculate Netload Up Ramp Risk factor Assign a coverage (80th-95th percentile) based in risk factor | No Change
Solar Adjustment | GE Table- Increased wind/solar forecast error per 1,000 MW installed capacity increase | No Change
Frequency Recovery | Expected capacity needed to recover frequency following a supply-side trip (2-yr, 60th percentile coverage) | Expected capacity needed to recover frequency following a supply-side trip (2-yr, 70th percentile coverage)
Calculation | NLFE+SolarAdjustment+Frequency Response | Max(NLFE+SolarAdjustment, Frequency Recovery)

## Slide 25: Hourly Average ECRS Comparison
2025 ECRS proposed:
On avg. 217 MW decrease compared to previous year
On avg. 518 MW decrease compared to 2025 (30MA)

## Slide 26: ECRS Comparison January
2025 ECRS (30MA):
Range 1207 - 2540 MW,
On avg. 145 MW increase from prev. year
2025 ECRS proposed:
Range 738 - 2151 MW,
On avg. 465 MW decrease compared to 2025 (30MA)

## Slide 27: ECRS Comparison March
2025 ECRS (30MA):
Range 875 - 2829 MW,
On avg. 243 MW increase from prev. year
2025 ECRS proposed:
Range 580 - 2648 MW,
On avg. 351 MW decrease compared to 2025 (30MA)

## Slide 28: ECRS Comparison July
2025 ECRS (30MA):
Range 1320 - 4177 MW,
On avg. 637 MW increase from prev. year
2025 ECRS proposed:
Range 723 - 3386 MW,
On avg. 824 MW decrease compared to 2025 (30MA)

## Slide 29
Non-Spinning Reserve Service

## Slide 30: Non-Spinning Reserve Methodology
Non-Spin is reserved capacity that can be started in 30 minutes to cover forecast errors, ramps or forced outages and replace deployed reserves until additional resources can be committed.
ERCOT is proposing one change to the methodology used to compute the minimum Non-Spin requirements in 2025. Specifically,
  Non-Spin quantities for HE23 to HE06 are calculated using 4 Hours Ahead (HA) hourly average net load forecast error while rest of the year will be computed using 6 HA hourly average net load forecast error.
The preliminary Non-Spin quantities for January 2025 through July 2025 in subsequent slides have been computed using proposed methodology (2022, 2023 and 2024 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 31: Off Status Hourly HSL by Season (12/2020 - 07/2024)

## Slide 32: Hourly Average NSRS Comparison
2025 NSRS (6HA):
On avg. 246 MW increase from prev. year
Largest increase is in Jan by 388 MW
2025 NSRS (6HA+4HA):
On avg. 169 MW increase from prev. year
Largest increase is in Mar by 311 MW
On avg. 77 MW decrease compared to 2025 (6HA)
Largest decrease is in Feb by 189 MW

## Slide 33: Non-Spin Comparison January
2025 NSRS (6HA):
Range: 2,303 – 3,704 MW;
Avg: 3,333 MW (388 MW increase from prev. year)
2025 NSRS (6HA+4HA):
Range: 2,083 – 3,704 MW;
Avg: 3,182 MW (151 MW decrease compared to 2025 (6HA))

## Slide 34: Non-Spin Comparison March
2025 NSRS (6HA):
Range: 1,830 – 3,691 MW;
Avg: 2,837 MW (308 MW increase from prev. year)
2025 NSRS (6HA+4HA):
Range: 1,822 – 3,691 MW;
Avg: 2,840 MW (3 MW decrease compared to 2025 (6HA))

## Slide 35: Non-Spin Comparison July
2025 NSRS (6HA):
Range: 1,908 – 3,772 MW;
Avg: 2,606 MW (103 MW increase from prev. year)
2025 NSRS (6HA+4HA):
Range: 1,908 – 3,772 MW;
Avg: 2,567 MW (39 MW decrease compared to 2025 (6HA))
Proposed = On-peak 6HA (HE07-HE22) + Off-peak 4HA (HE23-HE06)

## Slide 36: Summary
Based on the analysis ERCOT has conducted thus far,
  ERCOT is not considering any changes in the methodologies used to compute Responsive Reserve Service for 2025.
  ERCOT is considering changes in the methodology used to compute the Regulation Service, ERCOT Contingency Reserve Service, and Non-Spinning Reserve Service requirements for 2025.
The proposed timeline for this review is included alongside.
Similar to last year, to make the AS Methodology review process more efficient, ERCOT plans to provide all relevant details on the proposed methodology during the July/August working group discussions and provide just a summary of the proposed changes during the September/October discussions.
2025 Methodology Review Timeline
July 23, 2024 – WMWG
July 24, 2024 – PDCWG
August 15, 2024 – OWG (Proposed)
August 21, 2024 – PDCWG (Proposed)
August 30, 2024 – WMWG (Proposed)
September 09, 2024 – ROS
September 11, 2024 – WMS
September 25, 2024 – TAC
October 10, 2024 – BoD
Nov or Dec 2024 – PUC
Interested Stakeholders are requested to attend August PDCWG and/or WMWG meetings to provide any feedback on the proposed 2025 AS Methodology.

## Slide 37
Suggestions?

## Slide 38
Appendix

## Slide 39: NSRS Deployment (01/2023 – 06/2024)
Year | Average MW Deployed | Deployment Duration | Number of Events
2023 | 629 | 2.07 Hrs | 44
2024 | 1,087 | 4.09 Hrs | 8

## Slide 40: ECRS Deployment (06/2023 – 06/2024)
Chart: ECRS Average Responsibility by Resource Type
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Quick Start Resources | 581.082 | 566.8098 | 608.3786 | 599.5557 | 597.7546 | 604.6014 | 625.6582 | 669.8183 | 750.0552 | 844.0631 | 794.1117 | 750.0363 | 707.1585 | 697.4784 | 694.6902 | 711.3104 | 711.1527 | 687.3519 | 635.3861 | 589.5612 | 581.5451 | 600.5792 | 591.4235 | 603.6915
Other Thermal | 532.5713 | 517.1387 | 548.3863 | 537.4459 | 533.2612 | 514.0071 | 537.5186 | 573.5615 | 685.3437 | 722.1757 | 702.4377 | 676.0361 | 633.6134 | 616.262 | 627.3104 | 633.0352 | 638.6448 | 604.5833 | 521.2915 | 507.8243 | 495.8568 | 520.7934 | 534.1836 | 536.1967
Combined Cycles | 9.5781 | 8.7493 | 8.0888 | 9.0391 | 8.1538 | 7.4869 | 10.2568 | 19.6762 | 48.7918 | 61.8964 | 44.385 | 35.9883 | 40.4697 | 46.5257 | 61.4585 | 74.324 | 98.3964 | 120.138 | 120.7896 | 102.271 | 88.0112 | 57.2183 | 22.1615 | 9.4197
Energy Storage Resources | 50.3291 | 48.125 | 57.3194 | 45.2142 | 65.7617 | 65.5168 | 136.0014 | 238.5592 | 368.2733 | 483.3757 | 447.4983 | 442.1443 | 447.2759 | 472.1884 | 536.0539 | 563.9785 | 576.7898 | 598.2207 | 528.2479 | 413.4812 | 322.5177 | 229.7504 | 160.6583 | 79.688
Hydro Resources | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Controllable Load Resources | 29.6596 | 28.4251 | 27.511 | 25.9347 | 29.0762 | 27.3607 | 38.5519 | 53.6505 | 79.0383 | 81.5992 | 75.2322 | 70.271 | 62.1385 | 61.7311 | 69.1667 | 58.8514 | 53.5727 | 60.5191 | 50.0795 | 54.0085 | 54.1719 | 59.8896 | 50.4213 | 29.3227
Non-Controllable Load Resources | 72.6656 | 71.0738 | 71.8301 | 70.7978 | 75.456 | 91.9503 | 120.8708 | 147.4191 | 166.8071 | 173.0697 | 157.4292 | 133.0833 | 126.4828 | 131.2139 | 135.9598 | 131.9093 | 141.2134 | 167.406 | 140.5317 | 142.3637 | 129.9145 | 125.2508 | 102.8246 | 88.7891
Total ECRS Responsibility | 1275.8857 | 1240.3218 | 1321.5142 | 1287.9874 | 1309.4636 | 1310.9231 | 1468.8577 | 1702.6848 | 2098.3094 | 2366.1798 | 2221.2144 | 2107.5593 | 2017.1387 | 2025.3996 | 2124.6394 | 2173.4088 | 2219.7698 | 2238.219 | 1996.3264 | 1809.5099 | 1672.0172 | 1593.4818 | 1461.6728 | 1347.1076
Year | Average ECRS Deployed | Deployment Duration | Number of Events | Reason for Deployment
2023 | 23.50% | 1.14 Hrs | 31 | Available capacity not sufficient for projected Net Load
 | 27.10% | 0.09 Hrs | 11 | Frequency below 59.91Hz
2024 | 28.50% | 1.33 Hrs | 5 | Available capacity not sufficient for projected Net Load
 | 36.07% | 0.09 Hrs | 5 | Frequency below 59.91Hz