## Slide 1
Interconnection Requirements for Self-Limiting Facilities
Bill Blevins
Director, Grid Coordination
RIWG
August 21, 2024

## Slide 2: SLFs – Current Issues
ERCOT has observed confusion around interconnection requirements for Self-Limiting Facilities (SLFs) in recent months.
Currently, SLF interconnection requests are classified as “small generation” projects if
  The SLF injection limit is less than 10 MW OR
  The request would change an existing injection limit by less than 10 MW
This is creating an expectation among some Interconnecting Entities (IEs) that this classification allows for some portions of the interconnection process, such as the QSA, to be skipped.

## Slide 3: SLFs – Current Issues
Planning Guide Section 5.4.4 paragraph (1):
  “ERCOT may delay the synchronization, testing, or commissioning of any generator to the extent it deems necessary to study transmission system impacts of this generator and any other proposed or existing generators. If, as a result of this study or any previous study, ERCOT determines that the generator would create or contribute to a reliability concern, ERCOT may prohibit the synchronization, testing, or commissioning of the generator until the reliability concern is addressed.”

## Slide 4: SLFs – Current Issues
Many SLFs consist of hundreds of MW of inverter-based generation.
These devices have the potential to significantly impact existing Generic Transmission Constraints (GTCs), or require the creation of new GTCs, even if the SLF injection limit is 10 MW or less.
The stability of the ERCOT system requires that these projects be evaluated in the QSA.

## Slide 5: SLFs – Path Forward
Going forward, ERCOT will require any SLF that adds more than 10 MW of nameplate capacity to be included in the QSA prior to Initial Synchronization.
ERCOT will be submitting a PGRR to reclassify SLF interconnection requests as “large generation” unless the request adds less than 10 MW of new equipment.