## ESR Details
NOTE: Modifying the formatting of this document will cause it to be rejected by ERCOT, requiring you to resubmit. Instructions: • Do NOT copy the contents of this file and paste into another file. The formatting will change, and your submission will be rejected. • Do not modify layout settings of this file. • Every row requires a response. • Existing rows cannot be deleted. • Hover over the column header for more information about the data requested.
Resource Entity:
Progress | Unit Information |  |  |  | Unit Information - Ratings and Design | [9 empty] | Controlled Fault Current Magnitude (Multiple of Full Load Current) of ESR
% Complete | Substation(Site Code) | ESR Name(Existing) | Unit Name(Existing) | CLR Name(Existing) | Maximum Charging Rate (MW) | Maximum Discharging Rate (MW) | Maximum State of Charge (MWhr) | Minimum State of Charge (MWhr) | Roundtrip Efficiency(%) | Self-discharge Rate(%/day) | Maximum cycles per day(#) | Life Expectancy (Yrs.) | Low Reasonability Limit Self Limiting | High Reasonability Limit Self Limiting | Instantaneous(p.u) | At 2 to 3 Cycles (p.u) | At +4 Cycles (p.u)
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on G7: Maximum Charging Rate of the ESR expressed as a positive number.
Note on H7: Maximum Discharging Rate of the ESR expressed as a positive number.
Note on I7: The maximum amount of State of Charge
Note on J7: The minimum amount of State of Charge
Note on K7: Roundtrip Efficiency of an ESS at the POI. Roundtrip Efficiency should take into account all energy used to complete the cycle of “withdraw/store/inject” as seen from the POI and should include the energy required for thermal management even though that may be metered and/or provided through a separate feed. Answer must be expressed as a decimal percentage.
Note on L7: % Energy loss/day expressed as a decimal percentage.
Note on M7: Number of times the ESR can release energy level it was designed for after re-charge
Note on N7: Estimated ESR life expectancy in years
Note on O7: Limit for maximum MW withdrawal of Self-Limiting Facility above which the Self-Limiting Facility is not expected to operate. This field should not be used by Resources that are not part of Self-Limiting Facility
Note on P7: Limit for maximum MW injection for Self-Limiting Facility above which the Self-Limiting Facility is not expected to operate. This field should not be used by Resources that are not part of Self-Limiting Facility
Note on Q7: Inverter instantaneous fault current magnitude in per unit of full load current.
Note on R7: Inverter fault current magnitude at 2 – 3 cycles after a fault in per unit of full Load current.
Note on S7: Inverter fault current magnitude at 4+ cycles after a fault in per unit of full Load current.

## ESR Reactive Capability
Progress | Unit Information |  |  |  | Reactive Capability - Charging
% Complete | Substation(Site Code) | ESR Name(Existing) | Unit Name(Existing) | CLR Name(Existing) | Is your reactive capability data from your NDCRC test data?(Y/N) | If yes, what date was the NDCRC test perform?(mm/dd/yyyy) | Consumption MW1(MW) | MVAR Lagging Limit Associated with MW1(MVAR) | MVAR Leading Limit Associated with MW1(MVAR) | Consumption MW2(MW) | MVAR Lagging Limit Associated with MW2(MVAR) | MVAR Leading Limit Associated with MW2(MVAR) | Consumption MW3(MW) | MVAR Lagging Limit Associated with MW3(MVAR) | MVAR Leading Limit Associated with MW3(MVAR) | Consumption MW4(MW) | MVAR Lagging Limit Associated with MW4(MVAR) | MVAR Leading Limit Associated with MW4(MVAR) | Consumption MW5(MW) | Maximum Lagging Operating Capability (MVAR) | Maximum Leading Operating Capability(MVAR)
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on G4: Indicate (Y/N) if the reactive capability data is from test data
Note on H4: The Reactive Test Date, if the Reactive Capability Data Provided is from NDCRC test data
Note on I4: Minimum charging value expressed as a positive number.
Note on J4: The Lagging Reactive Power capability associated with the MW1 curve point, in MVAr.
Note on K4: The Leading Reactive Power capability associated with the MW1 curve point, in MVAr; input as negative number
Note on L4: Select MW 2 breakpoint which provides the best straight line fit between MW points 1 and 4.
Note on M4: The Lagging Reactive Power capability associated with the MW2 curve point, in MVAr.
Note on N4: The Leading Reactive Power capability associated with the MW2 curve point, in MVAr; input as negative number
Note on O4: Select MW 3 breakpoint which provides the best straight line fit between MW points 1 and 4.
Note on P4: The Lagging MVAR Limit Associated With Mw3 Output
Note on Q4: The Leading MVAR Limit Associated With Mw3 Output
Note on R4: Maximum charging value expressed as a positive number.
Note on S4: The Lagging MVAR Limit Associated With Mw4 Output
Note on T4: The Leading MVAR Limit Associated With Mw4 Output
Note on U4: The MW output at Unity power factor (zero MVAr)
Note on V4: Enter the largest magnitude value for lagging MVArs associated with MW points 1-4. Input as positive number
Note on W4: Enter the largest magnitude value for leading MVArs associated with MW points 1-4. Input as negative number

## ESR Configuration
[5 empty] | Fill out the following sections for each different PCS Configuration that exists within the ESR Unit | [5 empty] | Additional fields if more than one (1) PCS Configuration. Total of two (2) different PCS Configurations | [5 empty] | Additional fields if more than two (2) PCS Configuration Total of three (3) different PCS Configurations
Progress | Unit Information |  |  |  | ESR Configuration | [5 empty] | ESR Configuration | [5 empty] | ESR Configuration
% Complete | Substation(Site Code) | ESR Name(Existing) | Unit Name(Existing) | CLR Name(Existing) | PCS Identifier | Qty. of PCS Identifiers | Battery Unit Identifier | Qty. of Battery Modules per PCS Identifier | Power Plant Controller Manufacturer | Power Plant Controller Model Number | PCS Identifier | Qty. of PCS Identifiers | Battery Unit Identifier | Qty. of Battery Modules per PCS Identifier | Power Plant Controller Manufacturer | Power Plant Controller Model Number | PCS Identifier | Qty. of PCS Identifiers | Battery Unit Identifier | Qty. of Battery Modules per PCS Identifier | Power Plant Controller Manufacturer | Power Plant Controller Model Number
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on G4: PCS Identifier from the PCS Configuration & Battery spreadsheet.
Note on H4: Enter the total number of PCS Configurations Identifiers for the Unit E.g. If there are 33 TYPE1 in ESR UNIT 1, then enter 33
Note on I4: This should be one of the items from the "Battery Unit Identifier" column on the "Battery" worksheet.
Note on J4: Enter the total number of Battery Modules within the selected PCS Configuration
Note on K4: From name-plate or manufacturer data sheet
Note on L4: From name-plate or manufacturer data sheet
Note on M4: PCS Identifier from the PCS Configuration & Battery spreadsheet.
Note on N4: Enter the total number of PCS Configurations Identifiers for the Unit E.g. If there are 33 TYPE1 in ESR UNIT 1, then enter 33
Note on O4: This should be one of the items from the "Battery Unit Identifier" column on the "Battery" worksheet.
Note on P4: Enter the total number of Battery Modules within the selected PCS Configuration
Note on Q4: From name-plate or manufacturer data sheet
Note on R4: From name-plate or manufacturer data sheet
Note on S4: PCS Identifier from the PCS Configuration & Battery spreadsheet.
Note on T4: Enter the total number of PCS Configurations Identifiers for the Unit E.g. If there are 33 TYPE1 in ESR UNIT 1, then enter 33
Note on U4: This should be one of the items from the "Battery Unit Identifier" column on the "Battery" worksheet.
Note on V4: Enter the total number of Battery Modules within the selected PCS Configuration
Note on W4: From name-plate or manufacturer data sheet
Note on X4: From name-plate or manufacturer data sheet

## PCS Configuration Impedances
|  | Identify the different PCS configurations that exist within the substation. |  |  |  | PCS Configuration - Inverter | [9 empty] | PCS Configuration - Inverter | [7 empty] | PCS Configuration - Inverter
Progress | Existing Unit/CLR/ESR Information | PCS Configuration Identifier |  |  |  | Unsaturated Impedances | [9 empty] | Saturated Impedances | [7 empty] | Grounding Impedance
% Complete | Substation(site code) | PCS Identifier | Inverter Manufacturer | Inverter Model | Inverter Model Rating (MVA) | InverterBase MVA | Inverter Base kV | Subtransient Reactance X" (p.u) | Transient Reactance X' (p.u) | Positive Sequence ResistanceR1(p.u) | Synchronous ReactanceX1(p.u) | Negative Sequence ResistanceR2(p.u) | Negative Sequence ReactanceX2(p.u) | Zero Sequence ResistanceR0(p.u) | Zero Sequence ReactanceX0(p.u) | Subtransient ReactanceX"(p.u) | Transient ReactanceX'(p.u) | Positive Sequence ResistanceR1(p.u) | Positive Sequence ReactanceX1(p.u) | Negative Sequence ResistanceR2(p.u) | Negative Sequence ReactanceX2(p.u) | Zero Sequence ResistanceR0(p.u) | Zero Sequence ReactanceX0(p.u) | Is Inverter grounded?(Y/N) | Zero Sequence ResistanceR0(p.u based on 100MVA) | Zero Sequence ReactanceX0(p.u based on 100MVA)
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on D4: Unique identifier to use for a given PCS Configuration (e.g. PCS1, PCS2)
Note on E4: From name-plate or manufacturer data sheet
Note on F4: From name-plate or manufacturer data sheet
Note on G4: Nameplate AC capacity of the inverter output.
Note on H4: The MVA base of the inverter for the stated unsaturated and saturated impedances
Note on I4: The kV base of the inverter for stated unsaturated and saturated impedances
Note on J4: Enter the instantaneous subtransient reactance (unsaturated) for the inverter. It may be calculated as X"d = 1/Imax, where Imax is the maximum instantaneous fault current contribution in per unit of full load current.
Note on K4: Enter the transient reactance (unsaturated) of the inverter for the first 2-3 cycles of the fault. Fault current contribution in per unit of full load current between 2-3 cycles may be used to calculate X'd = 1/I fault current contribution at 2-3 cycles
Note on L4: Enter the positive sequence resistance (unsaturated) for system models. For inverter-based systems, R can be entered as zero if the net effect of reflecting the short circuit current is already in the reactance
Note on M4: Enter the synchronous reactance (unsaturated) of the inverter after 4 cycles of the fault. Fault current contribution in per unit of full load current after 4 cycles may be used to calculate Xd = 1/I fault current contribution after 4 cycles.
Note on N4: Enter the negative sequence resistance (unsaturated) of the inverter for system models. R may be entered as zero if the net effect of reflecting the short circuit current is already in the reactance.
Note on O4: Enter the negative sequence reactance (unsaturated) for system models. For inverter-based systems can calculate X negative sequence = 1/I negative sequence fault current contribution, where I negative sequence fault current contribution is in per unit of full load current. If negative sequence fault current contribution is zero, then enter 99999. This is normally a very high impedance
Note on P4: Enter the zero sequence resistance (unsaturated) for system models. For inverter-based systems, R may be entered as zero if the net effect of reflecting the short circuit current is already in the reactance.
Note on Q4: Enter the zero sequence reactance (unsaturated) of the inverter for system models. You may calculate X = 1/I zero sequence fault current contribution, where I zero sequence fault current contribution is in per unit of full load current. If zero sequence fault current contribution is zero, then enter 99999.
Note on R4: Enter the instantaneous subtransient reactance (saturated). (Can enter the same as the unsaturated value.) For inverter-based systems, can calculate X"d = 1/Imax, where Imax is the maximum instantaneous fault current contribution in per unit of full load current .
Note on S4: Enter the transient reactance (saturated) of the inverter for the first 2-3 cycles of the fault. (You may enter the same as the unsaturated value.) Fault current contribution in per unit of full load current between 2 - 3 cycles may be used to calculate X'd = 1/I fault current contribution at 2-3 cycles
Note on T4: Enter the positive sequence resistance (saturated) of the inverter for system models. R may be entered as zero if the net effect of reflecting the short circuit current is already in the reactance.
Note on U4: Enter the synchronous reactance (saturated) after 4 cycles of the fault. (Can enter the same as the unsaturated value.) For inverter-based systems, fault current contribution in per unit of full load current after 4 cycles can be used to calculate Xd = 1/I fault current contribution after 4 cycles.
Note on V4: Enter the negative sequence resistance (saturated) for system models. For inverter-based systems, R may be entered as zero if the net effect of reflecting the short circuit current is already in the reactance.
Note on W4: Enter the negative sequence reactance (saturated) of the inverter for system models. (You may enter the same as the unsaturated value.) You may calculate X = 1/I negative sequence fault current contribution, where I negative sequence fault current contribution is in per unit of full load current. If negative sequence fault current contribution is zero, then enter 99999.
Note on X4: Enter the zero sequence resistance (saturated) for system models. For inverter-based systems, R can be entered as zero if the net effect of reflecting the short circuit current is already in the reactance.
Note on Y4: Enter the zero sequence reactance (saturated) of the inverter for system models. (You may enter the same as the unsaturated value.) You may calculate X = 1/I zero sequence fault current contribution, where I zero sequence fault current contribution is in per unit of full load current. If zero sequence fault current contribution is zero, then enter 99999.
Note on Z4: Indicated (Y/N) for an impedance grounded inverted
Note on AA4: The value must be specified on a 100 MVA base. For inverter-based systems that are ungrounded, enter Grounding Resistance R = 99999.
Note on AB4: The value must be specified on a 100 MVA base. For inverter-based systems that are ungrounded, enter Grounding Reactance X = 99999.

## PCS Configuration
|  | Identify the different PCS configurations that exist within the substation. | PCS Configuration - Inverter |  |  | PCS Configuration - Transformer
Progress | Existing Unit/CLR/ESR Information | PCS Configuration Identifier | Controlled Fault Current Magnitude (Multiple of Full Load Current) of Inverter |  |  | Transformer Data per PCS
% Complete | Substation(site code) | PCS Identifier | Instantaneous(p.u) | At 2 to 3 Cycles (p.u) | At +4 Cycles (p.u) | Transformer MVA Base | Nominal High Side Voltage Level (kV) | Nominal Low Side Voltage Level (kV) | High Side Voltage Connection | Low Side Voltage Connection | Positive Sequence ImpedanceZ1(p.u) | Positive Sequence X1/R1 Ratio | Zero Sequence ImpedanceZ0(p.u) | Zero Sequence X0/R0 Ratio | Qty. of Inverters for this Transformer
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
0% |  | Enter Identifier on PCS Configuration Impedances worksheet
Note on D4: Unique identifier to use for a given PCS Configuration (e.g. PCS1, PCS2)
Note on E4: Inverter instantaneous fault current magnitude in per unit of full load current.
Note on F4: Inverter fault current magnitude at 2 – 3 cycles after a fault in per unit of full Load current.
Note on G4: Inverter fault current magnitude at 4+ cycles after a fault in per unit of full Load current.
Note on H4: Enter the base MVA upon which the per unit Skid/Array Transformer data is provided.
Note on I4: Enter the voltage level (in kV) on the high-voltage side of the Skid/Array Transformer.
Note on J4: Enter the voltage level (in kV) on the low-voltage side of the Skid/Array Transformer.
Note on K4: Identify the type of connection used for the windings on the high side voltage of the Skid/Array Transformer
Note on L4: Identify the type of connection used for the windings on the low side voltage of the Skid/Array Transformer
Note on M4: Enter the positive sequence impedance of the Skid/Array Transformer.
Note on N4: Enter the ratio of the positive sequence reactance to the positive sequence resistance of the Skid/Array Transformer
Note on O4: Enter the zero sequence impedance of the Skid/Array Transformer
Note on P4: Enter the ratio of the zero sequence reactance to the zero sequence resistance of the Skid/Array Transformer
Note on Q4: Total number of inverters within the PCS Configuration.

## Battery
Identify the different battery modules that exist within the PCS Configuration
Progress | Existing Unit/CLR/ESR Information | Battery Unit
% Complete | Substation(site code) | Battery Unit Identifier | Battery Manufacturer | Battery Model | Battery Model kW Rating(kW) | Battery Model kWh Rating(kWh) | Battery Model Maximum Charging Rate (kW/min) | Battery Model Maximum Discharging Rate (kW/min)
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on D4: Unique name of a given Battery Module used more than once.
Note on E4: From name-plate or manufacturer data sheet
Note on F4: From name-plate or manufacturer data sheet
Note on G4: From name-plate or manufacturer data sheet
Note on H4: From name-plate or manufacturer data sheet
Note on I4: From name-plate or manufacturer data sheet
Note on J4: From name-plate or manufacturer data sheet