## Slide 1
NOGRR 255 Changes for NOG Section 6.1:
Disturbance Monitoring Requirements
Requirements for Generation Resources and Energy Storage Resources
Patrick Gravois
ERCOT – Operations Engineer
RIWG
October 24, 2024

## Slide 2: NOGRR 255
NOGRR 255 went into effect on August 1, 2024
Market Notice M-A101724-01 went out on October 17, 2024
Changes to NOG Section 6.1 include equipment location requirements, data requirements, recording requirements, data retention requirements, reporting requirements, and maintenance and testing requirements for disturbance monitoring equipment (DME).
DME includes fault recording (FR), sequence of events (SOE) recording, dynamic disturbance recording (DDR), and phasor measurement unit (PMU) equipment
Facility owners shall have at least 50% of required DME installed and configured by August 1, 2026, and 100% installed and configured by August 1, 2028
Facility owners shall begin using the required retention periods, data provision timelines, and maintenance and testing timelines for existing equipment immediately or as soon as practicable

## Slide 3: Section 6.1.1.1 Applicability
All Generation Resources and ESR Facilities that are not Inverter-Based Resources (IBR) Facilities shall follow requirements in Sections 6.1.2 and 6.1.3
All Generation Resource and ESR Facilities that are IBR Facilities shall follow requirements in Section 6.1.4
Note: ERCOT identified a minor grammatical error in Section 6.1.1.1 that has caused confusion on which sections are applicable to ESRs. It will be to be corrected in a subsequent NOGGR. In the interim, most ESRs are IBRs and should follow requirements in Section 6.1.4

## Slide 4: Significant Changes for non-IBR Generation Resources and ESRs
Section 6.1.2.1 Fault Recording Requirements
  Provide continuous fault recording or triggering for the following:
    Neutral overcurrent of 0.2 p.u. or less of rated current
    Any phase under-voltage below 0.85 p.u. for two cycles or longer
    Any phase overcurrent above emergency current rating or protective relay tripping
  Minimum recording rate of 16 samples per cycle
  Minimum record length of 60 cycles (exclusion for older existing equipment that cannot meet this requirement)
Section 6.1.2.2 Fault Recording and Sequence of Events Recording Equipment Location Requirements
  All Generation Resources or ESRs connected to ERCOT System at or above 60 kV with an aggregated gross generating nameplate capacity above 100 MVA
  ERCOT may require FR and SOE equipment to be installed at any Generation Resource or ESR that experienced a ride-though failure during a system disturbance if root cause is unidentified
Small changes in Section 6.1.2.3 FR and SOE Recording Data Requirements

## Slide 5: Significant Changes for non-IBR Generation Resources and ESRs
Section 6.1.2.4 FR and SOE Recording Data Retention and Reporting Requirements
  Data shall be maintained and retrievable at a minimum for:
    20 days for equipment installed or replaced after June 1, 2024
    10 days for equipment installed prior to June 1, 2024
  Data shall be provided to ERCOT within 7 days of request
Minimal changes to DDR section (non-PMU) since all Generation Resources and ESRs in service after 1/1/2017 required to have PMU
Section 6.1.3.2.2 PMU Location Requirements
  All Generation Resources and ESRs over 20 MVA connected at or above 60 kV in service after 1/1/2017
  Generation Resources and ESRs over 20 MVA connected at or above 60 kV following any modification described in Planning Guide Section 5.2.1
  ERCOT may require PMU to be installed at any Generation Resource or ESR that experienced a ride-though failure during a system disturbance if root cause is unidentified

## Slide 6: Significant Changes for non-IBR Generation Resources and ESRs
Minimal changes to Section 6.1.3.2.3 PMU Data Recording and Redundancy Requirements
Section 6.1.3.2.4 PMU Data Retention and Data Reporting Requirements
  Data shall be maintained and retrievable at a minimum for:
    A rolling 20 calendar day period
    3 years for event data used for model validation (typically ERCOT identified)
    3 years for data provided to ERCOT for event analysis via written request
  Data shall be provided to ERCOT within 7 days of request

## Slide 7: NOGRR 255 Changes for IBR Facilities
Section 6.1.4 FR, SOE, and PMU Requirements for IBRs
  Requirements in all of Section 6.1.4 are for all IBR Facilities operating at 60 kV and above with aggregated gross nameplate capacity of 20 MVA and above at a single site, regardless of in-service date
  Facility owners shall have at least 50% of new required DME installed and configured by August 1, 2026, and 100% installed and configured by August 1, 2028
  Facility owners shall begin using the required retention periods, data provision timelines, and maintenance and testing timelines immediately or as soon as practicable
Section 6.1.4.1.2 FR Data and Triggering Requirements
  Required FR data signals listed in Section 6.1.4.1.2 (1)(a)
  Have either continuous data recording or triggering for the following at high side of MPT:
    Neutral overcurrent of 0.20 p.u. or less of rated current
    Any phase under-voltage set between 0.85 and 0.90 p.u.
    Any phase over-voltage greater than 1.10 p.u.
    Frequency below 59.5 Hz or above 60.5 Hz
  Minimum recording rate of:
    64 samples per cycle for FR equipment installed or replaced after June 1, 2024
    16 sample per cycle for FR equipment installed prior to June 1, 2024
  Minimum 2 second record length

## Slide 8: NOGRR 255 Changes for IBR Facilities
Section 6.1.4.3 PMU Equipment Requirements
  PMUs shall be time synchronized with GPS-based clock with accuracy and performance within +/- 100 milliseconds
  Recorded electrical quantities shall have continuous recording and be:
    Provided in C37.118.1-2011 IEEE Standard or later unless equipment was installed pre-2017
    Minimum output recording rate of 60 samples per second
    May be transmitted to ERCOT or stored locally
  Data should include or provide ability to determine the following:
    Time stamp
    Phase-to-neutral, or phase-to-phase, voltage magnitude and angle for each phase for at least one generator-connected bus
    Single phase current magnitude and angle for each phase on high or low side of MPT
    Frequency and rate-of-change-of-frequency (df/dt) from generator-connected bus (typically same measurement location as voltage/current)
    Calculated active and reactive power output from high or low side of MPT
  Additional notes:
    Voltage, current, and frequency data typically measured at high side of each MPT but not a specific requirement in NOG; PRC-028 is placing requirement on high side of MPT
    ERCOT RI may request additional PMU locations at Facilities with mixed generation types, e.g. solar and battery, to monitor separately

## Slide 9: NOGRR 255 Changes for IBR Facilities
Section 6.1.4.4 Data Retention and Reporting Requirements for FR, SOE, and PMU
  Data shall be maintained and retrievable at a minimum for:
    A rolling 20 calendar day period
    3 years for event data used for model validation
      Typically, this has been identified by ERCOT but new NERC Standards and NOGRR245 will place new requirement on GOs/REs to self identify events and perform model validation
    3 years for data provided to ERCOT for event analysis via written request
  Data shall be provided to ERCOT within 7 days of request
  Some standard formats are included in Section 6.1.4.4 (2)(c-f)
    ERCOT requests PMU data to be sent in .csv format with appropriate time stamps and column headers for voltage magnitude/angle, current magnitude/angle, and frequency
    ERCOT requests FR data in COMTRADE and CEV formats
    ERCOT typically does not request SOE data but may do so in .csv format; SOE is usually requested via RFI question

## Slide 10: DME Maintenance and Testing Requirements
Section 6.1.5 Maintenance and Testing Requirements
  Each Market Participant with required DDR, PMU, FR, and SOE recording equipment shall maintain and test its equipment as follows
    Calibrate and configure at installation or when data records indicate a problem
    Ensure data stored locally is available by request by either:
    Verifying data availability and quality at least once every 60 calendar days, or
    Instituting an automated notification system to detect when equipment ceases recording data or fails to refresh continuously recorded data
  Each Market Participant with required DDR, PMU, FR, and SOE recording equipment shall, within 90 days of discovering equipment recording failure:
    Restore the recording capability, or
    Notify and submit to ERCOT a plan and timeline for restoring the equipment recording capabilities