## CB_DATA_ (hidden)
Crystal Ball Data
Workbook Variables | Last Var Column | 0
Name:
Value:
Worksheet Data | Last Data Column Used
2
Sheet Ref
#REF! | #REF!
Sheet Guid
162bf5f6-f421-4de0-85f4-d908ee7629cc | 12115544-690e-42fd-8adb-150c253b8934
Deleted sheet count
Last row used
28 | 26
Data blocks
CB_Block_0
㜸〱敤㕣㕢㙣ㅣ㔷ㄹ摥㤹摤㔹敦慣敤搸㡤搳㑢㐲㘹㕤㑡改挵挱㡤搳愶愵㐰〸扥挴㐹㡡ㄳ扢戱㤳ㄶ〱摡㡣㜷捦搸搳散捣戸㌳戳㡥㕤㉡㈸扤㈱敥㔰㠹㝢愱㔵㠵㤰㜸攱昲㐰㘹愱て㈰㈱㠱㔰㉢昱〰て㐸㍣ㄴ㠴攰㠱㡢㈲昱挲〳㔲昹扥㌳㌳扢戳扢摥戱扢㙤挱㐵㍥改ㅥ㥦㌹户㌹攷扦㥦晦㍦搳㡣㤲挹㘴㕥㐶攲㕦愶ㅣぢ㔷捥慦晢㠱戰㐷㈷摤㙡㔵㤴〳换㜵晣搱㜱捦㌳搶㘷㉣㍦挸愲㐳扥㘴愱摤搷㑡扥㜵扦㈸㤴㔶㠵攷愳㤳㤶挹ㄴち扡㡡㜶㑥挲摦㘰晣愰㜳㔴㕦づ搹挲攴挴散攲扤㤸㜵㍥㜰㍤戱㝦昸㙣㌸昶昰搸搸攸搸攸愱〳户摥㌶㝡㘰晦昰㘴慤ㅡ搴㍣㜱搸ㄱ戵挰㌳慡晢㠷攷㙡㡢㔵慢晣㍥戱扥攰㥥ㄷ捥㘱戱㜸攰㤶㐵攳搶㜷㡣摤㝡攸㤰㜹挷ㅤ敦攸挳慢㌳愷㈶㈷收㍣㘱晡慦搱㥣ㅡ㤷㝣敢㤴㈸㕢摣㥢㄰㥥攵㉣㡤㑥㑥攰扦挴晡昱㜴晢攸晣戲㄰〱㕦㉤㍣攱㤴㠵慦㘳㘰慦㍤敥晢㌵㝢㠵挰搳敤㘹㙣戵㙣昸㠱㘶㑦㡡㙡㔵户攳㔹ぢ昶㉣㘰㔷㌵搶晢散㜹攱昸㔶㘰慤㕡挱㝡摥㕥挰㐴㤵㝥晢㡣㉦㑥ㅢ捥㤲㌸㘵搸㐲戳㡦搵慣㑡㉥㑣㤹散昵昱ㄴ挹㠵挹敤㡦㡥晢昶攴戲攱挹ㄵ昹〴㑣㑡摦㘹慦摣摣昷摡捥昳㜲改昲つ㥣昳扡捥晤搰㜲搶昰敡㍤㐷㍡昷㡣㌶摦扣㠲㥢㍢昷㑦挰愸㜹捣㡤㥤挷㐸㔰㌶昷㔶㝡㈳晡㤶㄰挵㘶昴㍣戳ㅥ㘶〵㘶㐴愰㕥㘴搶换慣て㤹㤲晢㈷戸㈴㌹㤰㑤㙡挹㔰㑢㡢㙡愹慣㤶㉡㙡㐹愸㈵㔳㉤㉤愹愵㘵戵㘴愹愵㝢搵搲㜹昴㠹㔳愱愷㐷㡤搲て㡦㥡㍦㝤敡㠱㙦㑤㍦昹攴㕦㍦昲昷挷ㅥ晥㑡摦㉥㜴扡㉢㕡搴㤴㘷㕣〰愹㌵愸昸攰攸〱晥摢㥣㉢挰ㄴ收㈱昳㜶㜳㙣慣㜲攸㠰㜱㡢愱㜱㕢㈹挸㙦㈲㤴㐱昴敤㌳敦戶㥣㡡㝢㐱攲敥捡〹挳ㄷつ挰㡤㐴㙤ㄳ㙥捤愹昸㙦摡戸㜱㍥㌰〲戱慦戵慤㌱㐹摢戰㜹戰㤵昰攵晢慥㙡ㅤ㜶搶愸搶挴昸㥡ㄵ㌶扦戹愵搹㥥昳摣挵捥慤搳㥥戸慦摥摡戶愲㜱〸戵㔵㌹㜷摢㉥挳愶㜰㕤挳㤳换慥㉦ㅣ戹扣ㄱ㝢捥㉡㥦ㄷ摥扣愰㐸ㄴㄵ戹搵㑢搹ㄴ㜱晤挸慣㠳㡤㠲㕢㉢㙦㐹搶㥡㐷搷〲㌰戳愸㘰扤㉢挲ぢ搶ㄷ㡣挵慡戸慣愹㑢昸㑥㌴散㙤慡㥥㜶换㌵㝦搲㜵〲捦慤㌶户㡣㔷㔶つ㐸㥡捡㐹户㈲㜲戹㡣ㄴち㄰戸搹慣愲㘴㙥敡捣ぢㄲㄱ〹ㄴ㤳㤱慦㘸㈶扢搱搳搸ㅤ㜶㔱ㄵ愴㐹昵慤㥢㑣挶昵㑡ㄹ㤳挲㠱㠹㍤㔱㝦昰愵㌷㙣㌲㙤ㅤ㜳慦㙦㘷㔵ㅤ㡡㜶㝦㜴㔵㌸挱㜱挳愹㔴㠵㤷慡晤ㄴ慥㐸ㅦ㐰愶㕤㠴㐰攸〸㍤慡㍡㘵㑤㔹搷㉥㔸㤵㘰㌹扦㉣慣愵攵〰㜵搰㤰㠵〲㐱摢㤶昴㑢㔰愵敦㘶㌶㠴慣㔸捣攴昷戰㔳扥㠸㤴搱㈸㥤㔲㜸戹㐹㤰㜳㕣ㄳ㉦昷㤹搳㔶㌵㄰愱㔰ㅥ㌰㠱㤱㔰慢㐹昴昵㤳㐴㍤愳ㅣ㉡㡣㍤收㈴愸搴戰㥣㘰扤挱户㙤㕣ㄲㄲ搱㡥㉣搸㜶戲㠰愲愰㔹ㅥ愴昰ㅡ㠸愶㐵ㅡ愴㜷㑥㄰ㄱ搹㈰㐵戳㘳收㘶㈲㘳晦ㄴㄹ㠱晥㐹㈲㘴敦〳㥤㘵〴㠹扤㥤㐸㌹愸㈳㍦敥㐸戳㡤㙣昹㔰㥡㕤ち挰改㤷㌱扢㥣搹ㄵ捣昶㈲㔳晥っ〹㐷㈹㠷㜲㜳搲摦㠴㘷晤㑡㘶㙦㐶〶昹愴㔳收㐴愲㡡㌶搴㔶散㐸昶敢㠷㥤㉣㡤攲㔰ㄴ搱㌲慥摢㤹晤戶㐴㜴㘴㜵㙥て㕤㥢㤳㍡昶㙤㥤㘹㌳戹ㅤ㔲㘴㑡搷攴㕥㌷改㥡〴〴扢㜶愹户慥挶㔰㝤㤸搹㌵挸㡡晡㕢㤸㐳戹搰攰摤㥡㐵㑦㤳昲つ㘱ㄶ㠵挶㔰㤷ち㍥㈲㘴ㅥ〱㔲㠴㕣摢昱㘵挷㠶愶㌹㌸㘲扥攱㙤攸晤㥤昹㍢㐲㝡㡢摥摣搱㍢昴ㄷ扤㐲㉢晡㕡戰㤷昲晢㡥㍡收㍡㌴敢㙦㘳㜶㍤戲ㄶㅤ挳搳昷㉢昵ㄴ㐸戳搸㑥㘰㙥㌷扤㉥搲捡㕤㔸㕦ㄱ㔲〳昵㤹ぢ㠶户㈴〲㜸㌰㑥㑣挱ㄶ㜶㍤㑦㔴㜱愸慤挸ち㥥㕦㉥㙦慥昴愷㍤搷㘶晤㡥㡤散扦㈱ㄴ㐳㉥愷㘶㌳㉤㌶㜲㡡慤㤹昰㌹㈵㈸㠷㍡昸㤶捥㐲㈲㌱愸㤹扣㌸㉥晤㝣戹㈳㐹扡㤰㈴㌷〲慣晡㑤挸㈰㈵㤴摦㜶㤴㈸晢搹敤敤戲㕢戳挵㑡て㕦捡改愴挵㠷搸㈶㐷㝡㐳㠷敤〴晣〷㝥扦㍤㙦搹㜵㘱搱㙢捦〹慦っ摦㠲㔵ㄵ挵搰㉤㑢㔱戳㈳㉢摥㈰戲㈲㥢㙤㍢㑦愷昸搷㈴㥤戴㐸㠹㔴㙥㑦㙤㑣㌹㡢㌷㠸㡡㙥㐸ち㤵ㄴ搷㔰㕤〲㤱昲搸㜷㐷挴㜴㈱㘲㙥〶攰昴〳捣挶㤸ㅤ㐴愶扤〸㐹戳㔵挰㌳ㅣ搶戳㑡㤷㜶愹㤴㈹㄰つ搲㐵昸㐲㐷㘱㜵㠸慦戹㡤搹敤挸㕡捣ㅦ㍡㈰㔳〸㔱愲㍣㐱㠸㌲㡣㘱㥥戵挴〵搲挰㉥ㄳ㠱愵挹㥡ㅦ戸㌶㈳㑢晤收㤴㝢捡つ愶㉣㝦〵㤱愸㈱㌳㉡摣扤㉣ㅣ㔰㤷〷摢愷愵捥㕤㔹ㄱㄵ摤㥣㜷㙢㄰㙤㈷愶戶挳挱ㅣ攰㠰㉤㈹捦收慡㠲搴摤昹ㄸ㔳㈸㠰戴昴户搲ㅢ扢㈵敦㌷て㝤〳つ㠸㉥㔸㐱㔵昴㥡㈱搳戱㕣㌰〱㐵㐴づ㉡㍤收挲戲㈷挴㔴扦㜹捣戳㉡㔵换ㄱ㐴〶㙣㑣〶敢㘶挴ㄲ愲〴㜳㉥㘳㠰慥搳㙦㉥㜸㠶攳慦ㄸっ㈸慥敦㙥㝡㤲㘱ㄱ捤㥣戰ㅣㅦ慦㤱㔸㘴㜹挰㥣㕦㜶㉦㈰㘲㕢戳㥤㘳挶㡡扦㉤戰㐲愲て㤳㐴㡤愲㉡慡慡ㄴ搴㐲户昸攱㠱㍣㤳㈱敦攵㤸㐹㕣㘵㌴晡捣㔳戴㌷敤晡㈸㐶㐳㍢㥤㙢敡㐳昴愸㕥㤹㑤㤵挲攴㔴晤づ㡥㜹㈷戲㍢㡦㥤㌹搱㠸捣扤慡㤸戵㐶㉦㝦㡡㡣㤷㘴㔱て㠴搰㐷户㉢㈴ㄵ搶㤱㜲挰㠱挰㌸㥦㕡挹慦㘸捡㍥愴扥㕤㡤攲㌴㈲㐹㝤收㡣戱㈸慡㠸㐷摢㐶戰㉢㝣愰ㄹ㙢ㅢ㔵㍦㙡㥢㜴㙤摢㈰㘹㤱㉣攷换〶㈹㜸扣ㄶ戸㈷㉤㐷㌷㤱㐹晡㡢慡㡣㌵㔴ㄹ㙢戲慡捦㍣捤搰愰㉣㜳㉥㜷挹昰慣㘰搹戶捡〵㍥㌰㝣户㉤㘸ㄲ㑣㑥挹ㅢ愷㔸㘶っ户㔸昳㘷㘰戲昹愳㐰昷㈸攴㈸㐱㐷昴㠳㜲㔵㈵㡦㝦㑡㤷㡥㈵〸ㄸ改㈹搵摦㡤搹㌴㜹㍢〲㈲㐷愶㡢昱ㅤ㡣㡢ㅦ㐵㑤㈸㠴㠸昵ㄴㄲ㠱㔷㌰㈱攴改攲捥㥢㘷ㅣ㉢〰昶㠸戱㘹㉢㤸昲㠱㜲㘴㈸捡攳敤㍥㠹搵挴愰㤱扡㔶戸扡扤愹㐹㑤㕣搵摥㥥搴ㅢ㙦摤愰㌹搴㈸〹㐵戲㔹㈷愹㔹㌶㔸攳㜶㔲㌵㡡㔴摣戱戶㔱搲摣愶つ戸㔳㡡扣ち挵㈴㘹㈶愳扦㐷ㄲち〲扤㤱㡥愲捦㍥㥤㍣ㄲㄱㅢ摡〰㐵敡愹戰慥㍦ち〹㥥挰戵㤳㡡㈸㐶㑦攰敦㕤㔱㜱戶ㄶ㌴戵ㄸ㙢㐳㔱换㜸戵㍡敢挰㑡㈸ㅢ㕥㘵㥢戰㌴昶ㄶ㙡ㄸ挹㥤摤㙡晦㄰扣〹㐶㡣搸㤰㘱㤱ㄴ㍦㌰搸㄰捣㤵㠸愸搲㍡敢㈷愸敢搵〵㍥㥤ㄴ㠶㈳㌱㌰ㅦ㔴愶挴慡㌴挳ㅡ㤶晣㤰ㅣ㔰㍦㉤㑡㌹慡㥢攳㡢㍥㔴㝡㐰㌹ㅥ㤵㈴㠳敢收㘹扡愵㜰㠹〱㘲㌷㉡捤㤵〳㠴㜶敢ㄳ昰㘴戰㝤戰〳㠸㠴愱ㄳ㕡㘷㤴愰昹ㄴ挲㙤摥〴㜹愷㑢㡣㐲㤰㥡㌲晤攳㠸昲戵慦㌲㝤攷㐸㈶㉥㐴㑣挴㜰㔷㡡昵〰攴㈶㈳㤳攴愲愱㌸㘰ㅥ㑡㌶㈹戴晡攲㍡㥡ㄸ晤㌴昹扣〰户㜸ㄸ换ㅡ㈰摢㔴㜱捦㉤戰愰㑤慢敢扢捣ㄳ㑥戹㕡慢〸愹㡡㘳㔹㉤㌵昲戶挰㤷扣〲ㄸ㜲㔳ち㕣㈲愰㥣挰㔱㡡㕢㈶㤲扡户扢昵㈳ㄸ㉥㠵ㅣ收〸㔵ㅦ〳㤰㈹㙥㌹ㄹ㄰㙢扢愷㐰晢㜰㜷攳〲㠳扣㍣〷㤱搶㔶㐵㔹㌶㠳晢㜸昵㈸戲攴戶㐴户ㄹ㜷挶愵捤㥥愸㍡㙥㠵㔵摢〲㐷搸㘷㈸昰昲㜹ㄸ㈳㕤㜲〷㈷挹㕣㡣愲扢ㄷ㍦㉡ㅦ㌳ㄷ㠱ち㠹〱㠵㌱㕥㥥㠲㌲㠰㉡ㄸ㠹〶户摡戰扡ㄵ㐶㝦㘹㜹敢攳挸ㄴ㠶㠱㘹搰愲㘷㘸攰㑣愲扣戹㠱㜳㌵㝡愵㐴㐸㤳挱㔴挶㈸㠷攰戰〷搲挰㑤㍣㐸㉦戸㔰㐲挱ㅥ㜹㌱㉣扥㥢㌸㘲攳〸攴㝡㤷戵㔴捥ㄹ〱慥扦㌸㝢㕢慡挷㉢ㄵ㥡扢昰捦㙤ぢ慣攲敡㐶㘸㡥敥㘹戹㤴㈵昷㐴晢敥摡㤶㠶攸戲攰挱愹搱攳㐶㔰㕥㥥て搶挳㡢㕢摤㤲㠴昶㍣晣ㄱㅢ扥㥤㌶㜳捥攱㐵搴㔵挲扥㜸摥㜱㉦㌸㜲㕤㥡捦㕢㝦愰㄰㕣愱散攱㈲㡢㤹㤷昱㑦㈶㌵愳晤〴㌳㙥㘵搹㥣愰攱㈰攱㍣㌲㠵搲㘰ㄸ攵ㄴ㍡㠱敤㕥扦㌵㐰㍡搹搳㐲㈷㔲㄰散㄰㡡戳昴㥡ㄱ㡡昲㘳愰㤵挴ㄲㅥ挹〱昳㙦㠳昵㤵攷㔰㐳㠴攳㌹ㄲ㈳摡㌵㈸愵愰㑥ち昲攸㡡〷㉦㠴晣晦㘰㈹收收つ搹改扦挰捣捡戳慤㈸扡㡡㈸晡㔱ㅢ㡡ㄴ㕥〳㤱晣㝢㘷㔴攰㠳挶昰散㉢ち㠴㜳㑦㍢〷搰搷晤挲敦晦昰〰㍡〳っ㌳㐹ㅢつ愱戶敢㔰慥㥢〸搹㌶ㄳ㠱挱㝢㘹㈲㥣攴ㄸ㐶昱㐳ㄳ㈱昲㠱捣愲㘲㜳ㄳ㠱戱扤ㄴ㐳㌰ㄱ㙡㑤戸㌵㜸〲扢捣愶㝦散㌸㉥摥ちㅦ昱㝣㈸㉤㝦ㄲㅥ愹换摢慢攷っ捦戰昷捡晡㘳㥥㠰㌲昳ㄶ㜰㤳㕢づ攱㠸㝤ㅢ戶挸㐱ㅢ昸㉡㘲㉦晢㡥㍦㘵㙢昷搷㠱愹㌰㠵敥㝢愵愰攴㕦㠵愷㐴攱戹㈱昳攱㍤摦㍤昶㠷晢ㅦ㌹挲摢㙡ㄱ慤㙡㌷愱摣㑤挸㥥昶〴㠲扡㠹㡢㈲㤷昲挳㥣㤳昸㐴挹㕡愹㡡〹挳㤳㔶㤰慦摢㜱㌱㈴扣〴㘱㠶挴户ㅤ㑣㑣摣㝢〸㑤捣搱ㄶ㜷愷晣戰㐹扡〸㐷ㄳぢ㤷㍥扤㌸㙣愸㜴㔴㘴㕤㕡㥢摡昷愱㡡㕥攱㐲㥡慤㐴㥥㍡㤹ㄴ攵㝢慤扡敥㄰㜵㕤㜸㤰㘱搸㍦㤶㔲㠸㍦㤰㐲㤲〷ㄹ㕥〸㤰㔲敡㌴ち摡捤挸㔲㈲㙢慤㈱㕥晡〳㜶㠴㠰愸㕦晡敢昲㈳ㄶ㐰ㄱ㔸㡣㝤昱摤㥥㘸㘹㡢挶慡㠹愱㕡㘹搳捣愳㈰て㉦慣ㄸ㡢㙢ㄷ㔰㠸㤳㜶㄰愵㉤扢愳昸㤲㝥㍢っ扣㠵㡣慤搹昴戵ㄵ敤愳㑥つ㌷㍦愰㘷昲㔲㘱㌸扢㔹㡤〳愹㡣搱㠵㕤㡢㘱ㄵ昳㠱戰㔸ㅦ搴ㅢ㌵㐱㘷㌹㝢㜱㉡㐵昰㡦㕦ち戱㝤愴㌱昵愵慤㉤搴㜱㑥て㌶挸ㅦ散慦慢㔲ㄸㅢ㙦㈵挷㐰挲㙥愹㔷㈱扣ㅥ㝥〶㐳戸改㡣愲㌷㡡昲㔹㌹㠴㍦㌱㘷㘵搵㌶晤捦攸戵攴慣戳ㅣ捤㌰㜶㤳晥扦〷ㄵ㥢敡㝦㠵戱㌷㠹挸昷㐷〵㘹㥣㌲㝥戲㘹挸㠶㄰㠱㘷ㅢ挱ㅢ㜹㌰搶㘵㤱㈱敦戰㌴㡦㡦㔷挳㘶㈹挱攱昷捡戵㕥㡤愸㡦愵㙤摢摢㔱〰㌲㌶愴㝤ㅢ㈲愸攳昸㘶戹ㄵ㥦㙥昳ㅦ挰挰㍤㈷慤戲攷晡慥ㄹっ捦㈳攸㍢捣㙦捦㑣搸㍣攳捡户㕡㠵摡戵㠰㐴摦㠷㌰收搴㉣〴昶㈹ㄱ扣㔶戱㐸㐶ㄶ戶ㄶ挹攰㜷㐸㠳㠹昰ㄲ戵㠳㝦㠹㜹㔷捤愸攲搳搵㔹昸㍡〳㔶㙤ぢ㘵ㄷ㝡㥣㕢㙦㘸㄰㜴戸愳昵㍥昸㠳㐴㜵ㄴ挱㌱戹㠵て㝣㠸㜰㙤㠵㐱㜳摦㘸㙦㍥㝢㜶攷㜳㉢㙡㑦〳愷㕢㝢㑢㌳挹昰㥤晣㈲戹愸㤷㤸攳搲晥ㄱ晣摤扡㠳㤶戳つ㠱捥愳て扡改〸ㅢ愹挲㝤戶㠵攸昷㌹っ㔵挶㤹攱愷ㅢ㔱㠱てち扤㝣㘴㐵攵㥢搸ㄶㄹ〰攵㑣扥㡣慣㌳㔵㍦戱ㄱ㔵て摥㠹㌱攴㔷㕤㈰敢捦㉡㍣㙡㤰㉡㡢捡搷搰㥦㔰ぢ㜷扦挴㍡ㅣ㍤攴㤱〲㘵㍤㈹挹ㄵㅥ㈹攴㝡扥㡣〱昵昵摣㡢摡捥敢昹攲㐶敢㔱㘸っ挸晤㈶攷ㅦ㡣㤵㠹㙥昳搵づ㌳㤷搹ち戲挱戸攷〰挵㈴昷㤲て㐳つ捦ㄱ㔳㐸扦㡥晥扥㜴攴挵ㄷ㤸晥㜶㐴㤱㠲ㄱ㑤捤扢愰㘰㤴扢昸㙣㜲ㄷ㍥㙡㍢敦攲搳ㅢ敤㘲㤰㌲㔳㐲戵㠶〲愰㕡挲ㅦ戹慢㔵ㄴ〸㔰晥㤴㜳捣昰㙢㕡挵愰㠱ㅡ㌹㜶つ㠵晥慣㐶挴扣慢戳㜶愱昱ㄸ㝦ち㡢攰㐰搳㌷慦㐷昱つ敢㍡愳摤㔹㝣挲慦㐹㔵㤸㔳摦搹摤㕣戱㌹㑡㑤愶㝤ㅣ扢㝥ㄵ昳㜰搳つ㥦㈳㘷摣㠷㕦〱㐱〸㤲㤹〴挹晤㈸挴㠰搲㠸昵㤴㉦㥢愴㜱挸㕢愰㜴㘴攵㐳㑦㜴㍥㌴〹ち㜶攴㠲摥ㄶ㠲ㄱ㕢攲愷挲ㅤ昵㔹扥换敢つ捡愳㌱ㄵㅥ㍦ㅥ㝦㌶愶㐶〱㌷㜰㐱㘸㡥㤳㙢〸㐸攵㤱戸昳て㥥㘹昸㡢搱㠰〴㔶〹㍢㤳扢㘴攷㠷攳捥〷昱㐹㥡散㤳㈱㐱㌱扤ㄴ㜷㈶ㄷ捡捥て挵㥤晦㝡㜰㙦扤㜳捣㜴攱捣ㅡ㌹㈲挵搰㤷㐷㥦挴攷改〳攸慥㤹㌴ㅥ㝡捤戰㥡㠴㈸攳收㔵㘹㍥昴攱㈶㡣㠷て挴㘷㜰戱ぢ昷㕦愰㘱挲晦㑦挴〹㕣昸㥡㌲〲〳摦㝦慦㈲搲敥改昲㠹㠳昳收慣㠷㡡ㅥ昳㠴㡦〳㘵㘵㕢㤱〸㙣愱㕣〸摦㑤㈲ㄲ㈹㜶㜳〳ㅥ㜱㠴㔰攵〵㥡敥㌴愷㡣㉡攵㤴〷㘳捣㘶ㅥ㙣搰㡣晥㌱㈰〷㍡〱㌹ぢ晡㐳挸挳㈸搴ㅥ㔶っ㔲搸㐹㐹昶〸ㅢㅥ㘵昶ㄸ戲愲㐲挹㐶㍡挸㝦ㅣ搹㐰晣㝦改ㄸ㕥㤵捥㈲㔵㔹㡢㕦㤶㈴㈳晤ㄳㅣ昰㐹㘴㔹昸慥㤵㠸〸㡢晡愷㔰㤳㝣㈹〵㠷㝣改㘷搸昰㔹㘶㥦㐳㔶搴戸搸㉤㐳㡤㝢敡㔲㙤㝦ㅥ㐳ㄵ㠲㠲㜳攸㕦㠸ち㝣㔰〸〷㡡㜳挵挱づ㈹㐳愹㙤ち㙡㕥㈱㙣㘴㠳ㅤ㌵ㅣ㤶つ㡡㐲㜸挹㠶㙡搴㐰㕤愶㝦ㄱ㤹㐲㜸㜰㑦晡㤷昸㐴㌰挸ㄷ㝥㌹㉡挸ㄷㄲ〶㜲昸㜲换ぢ〹ㄷ搹戰搴昲㐲挲㑡㌶㤸挹ㄷ㝥㥤㤳捡㡤愱搰慣慥戸㐱〹敦㙦愰搰㥦ㅤ攰摡敥挶㑦㕤㔳捡攷㉡攷捥晤㙢㈰㌷扣㉦㜷捦㝢晢扥晡搲慦晥昸昸㙦㍥㜸昸㉦晦㝥攲㠹摦晣改昱ㄷ晥晤晣攲攱㕦㍣晤昴捦敦㝣昲㠵㍦敥㌶㥦㔲㥦昹搷捣㔳て㡣㥤㝦攰㍥昳捣㑤挷ㅥ㜸晦扤㜷㡤捤㕤㌲㤲捤昶昴㕣㍦昴换㉢㙥ㄸ㝣昰扥㘷㤵㥦晤敥㜲㐷㤱摢挵ぢ㥡㤷挱㙤换㘵㍣㠹〲㤶挱ㄵ扦慥换攰㜶㈵愰捥㐵㠰㥡㐰㐵〱捥て㉥㐰㌶㤴㥡ㅢ㝡晦〳㠷ㄲ扤摤
Decisioneering:7.0.0.0

## Cover
Monthly Outlook for Resource Adequacy (MORA)
Reporting Month: January 2025
Disclaimer
This ERCOT report has been developed from data provided by ERCOT Market Participants, ERCOT, and ERCOT's consultants. The data may contain errors or become obsolete shortly after the report is released. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of this report and its accuracy should be confirmed by each ERCOT Market Participant that contributed data for this report. Note that resource data is based on a mid-month Resource Integration and Ongoing Operations (RIOO) system snapshot. Resource quantities can differ from monthly reports prepared subsequent to the MORA report, such as the Generator Interconnection Status (GIS) report, which is released at the beginning of the subsequent month.
MORA Release Schedule
MORA releases are targeted for the first Friday of each month. A MORA is released two months prior to the reporting month; for example, the planned release of the MORA report for August would be the first Friday in June. ERCOT may post one or more revised versions of a MORA report if material data errors are discovered. ERCOT recommends that readers check for postings of a revised report around mid-month. Information about one or more data corrections for a revised report will be summarized in the box below.
Data Corrections
Report Contents
| Tab Name | Description
| Monthly Outlook | Contains the following sections Introduction Risk Outlook Highlights and Resource Adequacy Measures Hourly Risk Assessment of Capacity Available for Operating Reserves Deterministic Scenarios Notable Load and Resource Developments
| Winter Storm Risk Analysis | A chart that shows the risk of an EEA and controlled outages for various winter storm severities
| Capacity by Resource Category | Summary table of generation resources by resource category
| Resource Details | List of registered resources and megawatt (MW) capabilities for the reporting month
| PRRM Percentile Results | Probabilistic model results: deciles for (1) hourly gross demand, (2) hourly solar and wind generation, and (3) daily unplanned thermal unit outages
| Background | Covers certain MORA methodology topics in detail

## Monthly Outlook
INTRODUCTION
The MORA report adopts two approaches to evaluate resource adequacy for the upcoming assessment month:
● | Determine the risk that ERCOT may face emergency conditions for the monthly peak load day — specifically, the chances, during a range of hours, that it may need to issue an Energy Emergency Alert (EEA) or begin to order controlled outages to maintain grid reliability. This evaluation is done through probabilistic modeling using ERCOT's Probabilistic Reserve Risk Model, PRRM. (See the Background tab for more information.)
● | Given a predetermined set of future grid conditions (deterministic scenarios), evaluate the extent that resource capacity can provide sufficient operating reserves for the hour with the highest risk of a reserve shortage. The focus of the MORA's deterministic scenario is on typical grid conditions.
Deterministic scenarios allow one to gauge how individual grid conditions influence a range of fixed outcomes while probabilistic simulation quantifies the uncertainty around the outcomes and produces likelihood estimates for them. These approaches complement each other to provide a richer perspective on reserve shortage risks for the ERCOT region.
Risk Outlook Highlights and Resource Adequacy Measures
● | Probabilistic modeling results indicate a low risk of ERCOT having to declare an EEA. Hourly probabilities peak at 8.51% for Hour Ending 8:00 a.m., Central Standard Time (CST). HE 8:00 a.m. is also the forecasted peak load hour for January. Another increase in hourly load, with an accompanying increase in EEA risk, occurs for HE 6:00 p.m. through HE 10:00 p.m. The ramping down of solar production contributes to the higher EEA risk during the early evening hours. There is some EEA risk throughout the nighttime and early morning hours. This risk pattern is influenced by recent and forecasted additions of large loads, such as data centers, that are expected to operate on a continuous "24x7 hour" basis and thereby flatten the hourly load pattern from what is seen historically for the winter months. The model accounts for the risk of coastal wind curtailment needed to avoid overloads on lines that make up the South Texas export interface.
● | Under typical grid conditions, the deterministic scenario indicates that there should be sufficient generating capacity available for the hour with the highest reserve shortage risk, Hour Ending 8 a.m., CST. The total peak hour load forecast for January, also occurring at Hour Ending 8 a.m., is 71,545 MW (which includes a 1,985 MW Large Load Adjustment as well as 1,565 MW of expected load for which interconnection requests have yet to be signed with the transmission providers). This forecast excludes "Officer Letter Loads" associated with House Bill 5066 (a letter from a TSP officer has been received by ERCOT attesting to the confidence that the expected customer load growth will materialize).
● | The possibility of low wind production remains a significant risk for maintaining adequate reserves for the January peak demand day. January thermal unplanned outage risk is higher than for December.
● | The monthly capacity reserve margin, expressed as a percentage, is 51.9% for the highest risk hour, Hour Ending 8:00 a.m.
Reserve Margin formula: ((Total Resources / (Peak Demand - Emergency Resources)) - 1) * 100
● | The ratio of installed dispatchable to total capacity is 59%. The ratio of available dispatchable to available total capacity for the hour with the highest reserve shortage risk, Hour Ending 8 a.m. is 84%. This latter measure helps indicate the extent that the grid relies on dispatchable resources to meet the peak load.
Hourly Risk Assessment of Capacity Available for Operating Reserves (CAFOR)
The table below provides hour-by-hour probabilities that Capacity Available for Operating Reserves (CAFOR) will be at a level indicative of (1) normal system conditions, (2) the risk of an Energy Emergency Alert (EEA), and (3) the risk that ERCOT may need to order controlled outages. As a guideline to interpret these probabilities, ERCOT considers an EEA probability at or below 10% to indicate that the reserve adequacy risk is low for the monthly peak load day. An EEA probability above 10% indicates an elevated reserve adequacy risk. Note that this probability forecast is not intended to predict specific capacity reserve outcomes. The CAFOR definition is provided at the top of the Background tab.
Winter Storm Risk Analysis
Deterministic results based on normal system conditions for the hour with highest risk of reserve shortages (Hour Ending 8 a.m.)
|  |  | Loads and Resources (MW) | Hour with the Highest Reserve Shortage Risk (Hour Ending 8 a.m., CST)
|  |  | Load Based on Average Weather [1] | 69560
|  |  | Large Load Adjustment [2] | 1985
|  |  | Total Load | 71545
Generation Resource Stack
|  |  | Dispatchable [3] | 83234.7598
|  |  | Thermal | 77026.0964
|  |  | Energy Storage [4] | 5804.5095
|  |  | Hydro | 404.1539
|  |  | Expected Thermal Outages | 8543
|  |  | Planned | 331
|  |  | Unplanned | 8212
|  |  | Total Available Dispatchable | 74691.7598
Non-Dispatchable [5]
|  |  | Wind | 15697
|  |  | Solar | 15.0002
|  |  | Total Available Non-Dispatchable | 15712.0002
|  |  | Non-Synchronous Ties, Net Imports | 719.8
|  |  | Total Available Resources (Normal Conditions) | 91123.56
Emergency Resources
Available prior to an Energy Emergency Alert
|  |  | Emergency Response Service | 1336
|  |  | Distribution Voltage Reduction | 551
|  |  | Large Load Curtailment | 1886
|  |  | Total Available prior to an Energy Emergency Alert | 3773
Available during an Energy Emergency Alert
|  |  | LRs providing Responsive Reserves | 1765.62
|  |  | LRs providing Non-spin | 30.6
|  |  | LRs providing ECRS | 306
|  |  | TDSP Load Management Programs | 41
|  |  | Total Available during an Energy Emergency Alert | 2143.22
|  |  | Total Emergency Resources | 5916.22
|  |  | Capacity Available for Operating Reserves, Normal Conditions | 23351.56
|  |  | Capacity Available for Operating Reserves, Emergency Conditions | 25494.78
Less than 2,500 MW indicates risk of EEA Level 1
Less than 1,500 MW indicates risk of EEA Level 3 Load Shed
[1] The 8 a.m. load value comes from ERCOT’s monthly load forecast. The typical peak load assumes average weather conditions for the reporting month.
[2] See the bottom of the Background tab for information on forecasting cypto-mining electricity consumption and the Large Load adjustment.
[3] Dispatchable resources comprise nuclear, coal, gas, biomass and energy storage. Non-dispatchable resources comprise wind and solar. Dispatchable in this context means that the resource can both increase or decrease output based on ERCOT dispatch instructions.
[4] Battery storage capacity is based on each hour's State of Charge (SOC) capacity factor, which is the hourly average aggregate State of Charge divided by installed capacity for the reporting month. For normal grid conditions, the capacity factor is 57% for the January highest reserve risk hour, Hour Ending 8 a.m.
[5] Wind and solar values for 8 a.m. represent the 50th percentile values from hourly synthetic generation profiles used in the PRRM. See the Background tab for more information.
Notable Load and Resource Developments
A Switchable Generation Resource owner notified ERCOT that one of their units (179 MW winter rating) was unavailable to ERCOT beginning January 1, 2025. ERCOT expects installed capacity to increase by 2,583 MW from December 1st to January 1st. Increases by generation type comprise 1,302 MW of solar and 1,281 MW of battery energy storage.

## Winter Storm Risk Analysis
Extreme Winter Weather Event
Background and Methodology
This analysis looks at the EEA risk given extreme winter storm conditions over a range of associated high demand levels that occur during the forecasted peak load day of January. To create the simulations, the model is configured to produce resource outage levels typical of historical winter storm events, and accounting for the impacts of the Public Utility Commission of Texas (PUCT) weatherization standards. The magnitude of thermal and wind outages vary based on the extreme low temperature selected for each of the 10,000 model runs. A simulation is conducted at peak demand levels starting at 75,000 MW and up to 96,000 MW in 1,000 MW increments. The 75,000 MW starting point was selected since it yields an EEA probability of just under 10% and slightly higher than the EEA probability for the base simulation. An EEA probability of 10% is the level at which the probability is considered "elevated". The 96,000 MW maximum is the peak demand expected during a storm event at least as severe as Winter Storm Uri. The simulations assume that price-responsive customer demand reduction, other than for Large Loads like Bitcoin mining, can range from 0 MW to 536 MW. This incremental demand response is triggered when Capacity Available for Operating Reserves (CAFOR) falls below 3,000 MW. The probabilities of the model selecting any value within the 0-to-536 MW range are all equal, so the average demand reduction amount across all 10,000 CAFOR outcomes is 268 MW. As with the base simulation, the risk of coastal wind curtailment due to South Texas transmission constraints is reflected in the simulation results.
Extreme Winter Storm Event Simulation Results
The chart below provides EEA and controlled load shed (EEA3) probabilities for Hour Ending 8:00 a.m. during an extreme January winter storm event given a range of corresponding high demand amounts (75,000 MW to 96,000 MW).
Note: As described above, the simulations assume that price-responsive customer demand reduction ranges from 0 MW to 536 MW across the 10,000 simulation outcomes. If actual price-responsive demand is significantly above the modeled MW range, then the EEA risk is reduced accordingly.

## Capacity by Resource Category
Hour with the Highest Reserve Shortage Risk (Hour Ending 8 a.m., CST)
Operational Resources, MW [1] | Installed Capacity Rating [2] | Expected Available Capacity [3]
Thermal | 88487.71 | 76733.6964
Natural Gas | 68506.32 | 57950.8964
Combined-cycle | 46583.35 | 37657.1964
Combustion Turbine | 10078.72 | 8841.6
Internal Combustion Engine | 900.6 | 899.6
Steam Turbine | 10943.65 | 10552.5
Compressed Air Energy Storage | 0 | 0
Coal | 14713.39 | 13629.6
Nuclear | 5268 | 5153.2
Renewable, Intermittent [6] | 66252.77 | 15710.725
Solar | 26719.45 | 13.725
Wind | 39533.32 | 15697
Coastal | 5436.42 | 2162.7385
Panhandle | 4668.53 | 1858.2935
Other | 29428.37 | 11675.968
Renewable, Other | 749.35 | 566.9539
Biomass | 174.25 | 162.8
Hydroelectric [4] | 575.1 | 404.1539
Energy Storage, Available State of Charge | 9140.79 | 5082.861
Batteries | 9140.79 | 5082.861
Other | 0 | 0
DC Tie Net Imports | 1220 | 719.8
Planned Resources [5]
Thermal | 151 | 129.6
Natural Gas | 151 | 129.6
Combined-cycle | 0 | 0
Combustion Turbine | 121 | 99.6
Internal Combustion Engine | 30 | 30
Steam Turbine | 0 | 0
Compressed Air Energy Storage | 0 | 0
Diesel | 0 | 0
Renewable, Intermittent [6] | 2460.9 | 1.2753
Solar | 2460.9 | 1.2753
Wind | 0 | 0
Coastal | 0 | 0
Panhandle | 0 | 0
Other | 0 | 0
Energy Storage, Available State of Charge | 1266.05 | 721.6485
Batteries | 1266.05 | 721.6485
Other | 0 | 0
Total Resources, MW | 169728.57 | 99666.56
NOTES:
[1] Operational resources are those for which ERCOT has approved grid synchronization or full commercial operations. Unit level details for each resource category can be found in the Resource Details tab.
[2] Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. All gas-fired Private-Use Network (PUNs) units are reflected in the combined cycle fuel type row above.
[3] Expected Available Capacity for operational units accounts for thermal seasonal sustained capability ratings, hourly capacity contribution estimates for intermittent renewables, planned retirements, reductions due to co-located loads, unavailable Switchable Generation Resources (SWGRs), mothballed capacity, and expected Private Use Network (PUN) generator net exports to the grid. For planned projects, Expected Available Capacity is based on the maximum capacity reported by the developers and accounts for net changes due to repower or upgrade projects greater than one MW, and the established limits on the total MW Injection for designated Self-Limiting Facilities. Unit level details for each resource group above can be found in the Resource Details tab.
[4] Includes a small amount of hydro units that are considered intermittent resources (run-of-river DG hydro units).
[5] Planned resources are those for which ERCOT expects to be approved for grid synchronization or has been assigned a “Model Ready Date" (for Small Generators) by the first of the month.
[6] Wind and solar values represent the 50th percentile values from hourly synthetic output profiles used in the PRRM. See the Background tab for more information.

## Resource Details
Unit Capacities - January 2025
| UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | WINTER CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1235
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1225
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1353.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1340
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 605
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 449
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 199.2 | 199.2
30 | ARTHUR VON ROSENBERG 1 CTG 2 | 25INR0531 | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 176
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 218.5
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 20
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 325
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 188
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 188
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 234
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
43 | BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
44 | BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
45 | BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8
46 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 170.9
47 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 170.9
48 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 168.5
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 85.2
50 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 226.7
51 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
52 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
53 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 270
54 | BROTMAN POWER STATION U1 |  | BTM_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
55 | BROTMAN POWER STATION U2 |  | BTM_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
56 | BROTMAN POWER STATION U3 |  | BTM_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
57 | BROTMAN POWER STATION U4 |  | BTM_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
58 | BROTMAN POWER STATION U5 |  | BTM_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
59 | BROTMAN POWER STATION U6 |  | BTM_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
60 | BROTMAN POWER STATION U7 |  | BTM_UNIT7 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 46.5
61 | BROTMAN POWER STATION U8 |  | BTM_UNIT8 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8
62 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-GT | WEST | 1987 | 75 | 75
63 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-GT | WEST | 1987 | 75 | 75
64 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 49.8
65 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 49.8
66 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 49.8
67 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 49.8
68 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 173
69 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 173
70 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 186
71 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745
72 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749
73 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 87 | 87
74 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 79.6
75 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.7 | 86.7
76 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 77.9
77 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 107.2 | 107.2
78 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 110.7 | 110.7
79 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 360.2
80 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 359.6
81 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 490.5
82 | COLORADO BEND ENERGY CENTER CTG 11 |  | CBEC_GT11 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39
83 | COLORADO BEND ENERGY CENTER CTG 12 |  | CBEC_GT12 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39
84 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 185
85 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 182
86 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 181
87 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 144
88 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 48
89 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 50
90 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 110
91 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54
92 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54
93 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54
94 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54
95 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 88
96 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 87
97 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 86
98 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 86
99 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 203 | 203
100 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 215 | 215
101 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 203 | 203
102 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 215 | 215
103 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 190
104 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290 | 290
105 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
106 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
107 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
108 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
109 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 170.4
110 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 170.4
111 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 245
112 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 116
113 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 40
114 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 40
115 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 40
116 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 40
117 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 180
118 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 180
119 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 194
120 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 195
121 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185
122 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185
123 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 195
124 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185
125 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185
126 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 418
127 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 418
128 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 160.7
129 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 160.7
130 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 161.1
131 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 161.1
132 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 179.8
133 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 179.7
134 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119
135 | FRONTERA ENERGY CENTER CTG 1 |  | FRONT_EC_CT1 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
136 | FRONTERA ENERGY CENTER CTG 2 |  | FRONT_EC_CT2 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
137 | FRONTERA ENERGY CENTER STG |  | FRONT_EC_ST | HIDALGO | GAS-CC | SOUTH | 2023 | 184.5 | 184.5
138 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 239 | 239
139 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390 | 390
140 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 67
141 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 68
142 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 69
143 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 53
144 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 72
145 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 67
146 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
147 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
148 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
149 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 165
150 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 165
151 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75
152 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167
153 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167
154 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167
155 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167
156 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 203
157 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 203
158 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375
159 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435
160 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435
161 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 239
162 | HAYS ENERGY FACILITY CSG 2 | 22INR0586 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 240
163 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 242
164 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 243
165 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 150
166 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 150
167 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 176
168 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 165
169 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 165
170 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 182
171 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 182
172 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 300
173 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295
174 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 177
175 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106
176 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392
177 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523
178 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 186
179 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 178
180 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 178
181 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 186
182 | LAMAR ENERGY CENTER STG 1 | 23INR0486 | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
183 | LAMAR ENERGY CENTER STG 2 | 23INR0674 | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
184 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 97.4
185 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 94.4
186 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
187 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
188 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
189 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
190 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 44
191 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 44
192 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 183
193 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 183
194 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 192
195 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 218.6
196 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 218.6
197 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 257.9
198 | MIDLOTHIAN ENERGY FACILITY CTG 1 | 23INR0489 | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 258 | 258
199 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 256 | 256
200 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 255 | 255
201 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 258 | 258
202 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 276 | 276
203 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 278 | 278
204 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 82
205 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80
206 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80
207 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 81
208 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80
209 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 82
210 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122
211 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118
212 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568
213 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165
214 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165
215 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 325
216 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420
217 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410
218 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 195.2 | 195.2
219 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 189.1 | 189.1
220 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 195.2 | 195.2
221 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 189.1 | 189.1
222 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 217
223 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 217
224 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 49.8
225 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 49.8
226 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 224
227 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 224
228 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 316
229 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 222
230 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 209
231 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 325
232 | PANDA TEMPLE II POWER CTG 1 | 23INR0524 | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
233 | PANDA TEMPLE II POWER CTG 2 | 23INR0524 | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
234 | PANDA TEMPLE II POWER STG 1 | 23INR0524 | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 333.6
235 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 87
236 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 87
237 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 79
238 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 176
239 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 176
240 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 169
241 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
242 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
243 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
244 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
245 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 79
246 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 76
247 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 78
248 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 75
249 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 79
250 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
251 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
252 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
253 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
254 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
255 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
256 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
257 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
258 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65
259 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65
260 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65
261 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65
262 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 64
263 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65
264 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5
265 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36
266 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 84
267 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 86
268 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 81
269 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 81
270 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98
271 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98
272 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 116 | 116
273 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 116 | 116
274 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75 | 75
275 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120 | 120
276 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208
277 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 95 | 95
278 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107
279 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146
280 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
281 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
282 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
283 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
284 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
285 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
286 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
287 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8
288 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3 | 56.3
289 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3 | 56.3
290 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3 | 56.3
291 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3 | 56.3
292 | REMY JADE POWER STATION U1 |  | JAD_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
293 | REMY JADE POWER STATION U2 |  | JAD_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
294 | REMY JADE POWER STATION U3 |  | JAD_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
295 | REMY JADE POWER STATION U4 |  | JAD_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
296 | REMY JADE POWER STATION U5 |  | JAD_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
297 | REMY JADE POWER STATION U6 |  | JAD_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
298 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 203 | 203
299 | RIO NOGALES POWER CTG 2 | 25INR0665 | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 193 | 193
300 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 203 | 203
301 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 319
302 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
303 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 51
304 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
305 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40
306 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 87
307 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 87
308 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48
309 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48
310 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48
311 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48
312 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 175
313 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 48
314 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 48
315 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 150
316 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46
317 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 49
318 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 21
319 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130
320 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135
321 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 340
322 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
323 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
324 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167
325 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502 | 502
326 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 16
327 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
328 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
329 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
330 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
331 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
332 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 69
333 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 69 | 69
334 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 69 | 69
335 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
336 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
337 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
338 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
339 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
340 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65
341 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
342 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
343 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4
344 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4
345 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4
346 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 131.5
347 | TEXAS GULF SULPHUR CTG 1 | 24INR0605 | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 77.9
348 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235
349 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
350 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
351 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
352 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
353 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
354 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
355 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
356 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
357 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
358 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8
359 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
360 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
361 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
362 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47
363 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217
364 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230
365 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412
366 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 49.8
367 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 49.8
368 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 49.8
369 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 49.8
370 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 171
371 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 132
372 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13
373 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
374 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
375 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 258
376 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 552
377 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
378 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
379 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
380 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46
381 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46
382 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46
383 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46
384 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 263.8
385 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 263.8
386 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298 | 298
387 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 240.4
388 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 235.4
389 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 269
390 | WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 360 | 353.3
391 | WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 360 | 354.6
392 | WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 511.2 | 473.1
393 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105
394 | BIOENERGY AUSTIN-WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8
395 | BIOENERGY TEXAS-COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6
396 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2
397 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4
398 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2
399 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4
400 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2
401 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4
402 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2
403 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8
404 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 75030.84 | 70121
405
406 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
407 | REMY JADE POWER STATION U7 | 24INR0736 | JAD_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
408 | REMY JADE POWER STATION U8 | 24INR0736 | JAD_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 49.8
409 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 121 | 99.6
410
411 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | 0 | 0
412 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 75151.84 | 70220.6
413
414 | Operational Resources (Hydro)
415 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
416 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
417 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8
418 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9
419 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
420 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
421 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17
422 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5
423 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5
424 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 1928 | 9.6 | 9.6
425 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
426 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
427 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
428 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
429 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
430 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1928 | 6 | 6
431 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14
432 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21
433 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20
434 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
435 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
436 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
437 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
438 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
439 | Operational Capacity Total (Hydro) | [6 empty] | 567.9 | 557.4
440 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  | HYDRO |  |  | 567.9 | 399
441
442 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
443 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 1928 | 1.4 | 1.4
444 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7
445 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6
446 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2
447 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 14.9 | 14.9
448 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  | HYDRO |  |  | 14.9 | 10.6658
449
450 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  | HYDRO |  |  | -7.7 | -5.5118
451 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  | HYDRO |  |  | 575.1 | 404.1539
452
453 | Operational Resources (Switchable)
454 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
455 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
456 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
457 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 200
458 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 200
459 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 200
460 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
461 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
462 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
463 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400
464 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 162
465 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
466 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 178
467 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 389
468 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185
469 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185
470 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 330 | 330
471 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185
472 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185
473 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 330 | 330
474 | Switchable Capacity Total | [6 empty] | 4066.12 | 4016
475
476 | Switchable Capacity Unavailable to ERCOT
477 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0
478 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0
479 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0
480 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | 0 | 0
481 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | 0 | 0
482 | ELK STATION CTG 3 |  | AEEC_ELK_3_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2025 | 0 | 0
483 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | -179
484 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2023 | -185 | -185
485 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201_UNAVAIL | FANNIN | GAS-CC | NORTH | 2023 | 0 | 0
486 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST_UNAVAIL | FANNIN | GAS-CC | NORTH | 2023 | 0 | 0
487 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2023 | 0 | 0
488 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -6 | -364
489
490 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | GAS-ST |  |  | 0 | 0
491
492 | Private-Use Network Capacity Contribution |  | PUN_CAP_CONT |  | GAS-CC |  |  | 9450 | 3023.8964
493 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS-CC
494
495 | Operational Resources (Wind)
496 | AGUAYO WIND U1 |  | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9
497 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7
498 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8
499 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7
500 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8
501 | ANCHOR WIND U2 |  | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2024 | 98.9 | 98.9
502 | ANCHOR WIND U3 |  | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2024 | 90 | 90
503 | ANCHOR WIND U4 |  | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2024 | 38.7 | 38.7
504 | ANCHOR WIND U5 |  | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2024 | 19.3 | 19.3
505 | APOGEE WIND U1 |  | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2024 | 25 | 25
506 | APOGEE WIND U2 |  | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2024 | 14 | 14
507 | APOGEE WIND U3 |  | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2024 | 30.2 | 30.2
508 | APOGEE WIND U4 |  | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2024 | 115 | 115
509 | APOGEE WIND U5 |  | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2024 | 110 | 110
510 | APOGEE WIND U6 |  | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2024 | 24 | 24
511 | APOGEE WIND U7 |  | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2024 | 75 | 75
512 | APPALOOSA RUN WIND U1 |  | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2024 | 157.9 | 157.9
513 | APPALOOSA RUN WIND U2 |  | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2024 | 13.9 | 13.9
514 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9
515 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4
516 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7
517 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8
518 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1
519 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6
520 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.3 | 199.3
521 | BLACKJACK CREEK WIND U1 |  | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
522 | BLACKJACK CREEK WIND U2 |  | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
523 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100
524 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102
525 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2
526 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5
527 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120
528 | BLUE SUMMIT WIND 1 A |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8
529 | BLUE SUMMIT WIND 1 B |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9
530 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 92.5
531 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.9 | 6.9
532 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4
533 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4
534 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162
535 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8
536 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120
537 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108
538 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9
539 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7
540 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6
541 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5
542 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117
543 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2
544 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88
545 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90
546 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2
547 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4
548 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4
549 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1
550 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165
551 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5
552 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120
553 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1
554 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7
555 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5
556 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9
557 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5
558 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 79.42 | 77.7
559 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 78.04 | 76.4
560 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.3 | 173.3
561 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5
562 | CHAPMAN RANCH WIND IA (SANTA CRUZ) | 24INR0627 | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6
563 | CHAPMAN RANCH WIND IB (SANTA CRUZ) | 24INR0627 | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4
564 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4
565 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220
566 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
567 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
568 | DESERT SKY WIND 1 A |  | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 53.1
569 | DESERT SKY WIND 1 B |  | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 50.4
570 | DESERT SKY WIND 2 A |  | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 18.7
571 | DESERT SKY WIND 2 B |  | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 8
572 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
573 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
574 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98
575 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96
576 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9
577 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2016 | 101.31 | 98.9
578 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2016 | 134.29 | 131.1
579 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6
580 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6
581 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2
582 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2 | 163.2
583 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200
584 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8
585 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6
586 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5 | 186.5
587 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8
588 | FOREST CREEK WIND | 25INR0578 | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2
589 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80
590 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6
591 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6
592 | GOODNIGHT WIND U1 |  | GOODNIT1_UNIT1 | ARMSTRONG | WIND-P | PANHANDLE | 2024 | 121 | 121
593 | GOODNIGHT WIND U2 |  | GOODNIT1_UNIT2 | ARMSTRONG | WIND-P | PANHANDLE | 2024 | 137.1 | 137.1
594 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82
595 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76
596 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4
597 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8
598 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_BRAZ_WND1 | SCURRY | WIND-O | WEST | 2023 | 120 | 120
599 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_BRAZ_WND2 | SCURRY | WIND-O | WEST | 2023 | 62.4 | 62.4
600 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
601 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7
602 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9
603 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
604 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
605 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9
606 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5
607 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 99.9 | 99.9
608 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 100 | 100
609 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5
610 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5
611 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52
612 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98
613 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100
614 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4
615 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46
616 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 52 | 52
617 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
618 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.5 | 122.5
619 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
620 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.6 | 127.6
621 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.6 | 101.6
622 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1
623 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9
624 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230
625 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184
626 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4
627 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115
628 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95
629 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102
630 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8
631 | INERTIA WIND U1 |  | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.7 | 67.7
632 | INERTIA WIND U2 |  | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.72 | 27.7
633 | INERTIA WIND U3 |  | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.86 | 205.9
634 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7
635 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230
636 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96
637 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74
638 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30
639 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2
640 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6
641 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
642 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
643 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4
644 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2014 | 110 | 110
645 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
646 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
647 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5 | 40.5
648 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
649 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160
650 | LACY CREEK WIND U1 |  | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2024 | 135.4 | 135.4
651 | LACY CREEK WIND U2 |  | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2024 | 15.12 | 15.1
652 | LACY CREEK WIND U3 |  | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2024 | 138.2 | 138.2
653 | LACY CREEK WIND U4 |  | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2024 | 12.6 | 10.1
654 | LAS MAJADAS WIND U1 |  | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110
655 | LAS MAJADAS WIND U2 |  | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24
656 | LAS MAJADAS WIND U3 |  | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6
657 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7
658 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3
659 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8
660 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194
661 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98
662 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100
663 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
664 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
665 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48
666 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51
667 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5
668 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24
669 | LOS VIENTOS III WIND | 26INR0507 | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200
670 | LOS VIENTOS IV WIND | 26INR0507 | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200
671 | LOS VIENTOS V WIND | 26INR0507 | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110
672 | LOS VIENTOS WIND I | 26INR0507 | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1
673 | LOS VIENTOS WIND II | 26INR0507 | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6
674 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8
675 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5
676 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
677 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
678 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6
679 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1
680 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6
681 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2
682 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4
683 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3
684 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22
685 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20
686 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8
687 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150
688 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
689 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
690 | MIAMI WIND G1 |  | MIAM1_G1 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
691 | MIAMI WIND G2 |  | MIAM1_G2 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
692 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8
693 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2017 | 196.6 | 196.6
694 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6
695 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60
696 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 54.6 | 54.6
697 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2
698 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
699 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
700 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9
701 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
702 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
703 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2
704 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6
705 | PANTHER CREEK WIND 1 | 24INR0578 | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5
706 | PANTHER CREEK WIND 2 | 24INR0582 | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5
707 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9
708 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5
709 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9
710 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1
711 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7
712 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8
713 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8
714 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6
715 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8
716 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2
717 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 131.2 | 131.2
718 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 137.7 | 137.7
719 | RANCHERO WIND U1 |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
720 | RANCHERO WIND U2 |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
721 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 104.6
722 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 102.7
723 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6
724 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4
725 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48
726 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1
727 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8
728 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9
729 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4
730 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114
731 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95
732 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150
733 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
734 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
735 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160
736 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
737 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
738 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64
739 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110
740 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2016 | 95.25 | 95.2
741 | SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4
742 | SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1
743 | SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4
744 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150
745 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78
746 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2
747 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1
748 | SHANNON WIND | 25INR0583 | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1
749 | SHEEP CREEK WIND |  | SHEEPCRK_UNIT1 | EASTLAND | WIND-O | NORTH | 2024 | 150 | 150
750 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132
751 | SILVER STAR WIND |  | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8
752 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102
753 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98
754 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5
755 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8
756 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2
757 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161
758 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98
759 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96
760 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120
761 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201
762 | STEPHENS RANCH WIND 1 | 25INR0439 | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2
763 | STEPHENS RANCH WIND 2 | 25INR0439 | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.7
764 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5 | 42.5
765 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8 | 16.8
766 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8 | 110.8
767 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6 | 33.6
768 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6 | 118.6
769 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125 | 125
770 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112 | 112
771 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85 | 85
772 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150
773 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150
774 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7
775 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42
776 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8
777 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42
778 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2
779 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150
780 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23
781 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5
782 | TRENT WIND 1 A |  | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3
783 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6
784 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5
785 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3
786 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8
787 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4
788 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6
789 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2
790 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5
791 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2016 | 125.6 | 125.6
792 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105
793 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6
794 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12
795 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2
796 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
797 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22
798 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
799 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
800 | VORTEX WIND U1 |  | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2024 | 153.6 | 153.6
801 | VORTEX WIND U2 |  | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2024 | 24.2 | 24.2
802 | VORTEX WIND U3 |  | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2024 | 158.4 | 158.4
803 | VORTEX WIND U4 |  | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2022 | 14 | 14
804 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9
805 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3
806 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6
807 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2
808 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6
809 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141
810 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57
811 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3
812 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3
813 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9
814 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3
815 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6
816 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5
817 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
818 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
819 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5
820 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6
821 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30
822 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 121.5 | 121.5
823 | Operational Capacity Total (Wind) | [6 empty] | 34530.54 | 34419.3
824
825 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
826 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2024 | 16 | 16
827 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2025 | 195 | 195
828 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2025 | 145 | 145
829 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2024 | 108.8 | 108.8
830 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2024 | 190.4 | 190.4
831 | CANYON WIND U1 | 18INR0030 | CANYONWD_UNIT1 | SCURRY | WIND-O | WEST | 2024 | 146.64 | 144
832 | CANYON WIND U2 | 18INR0030 | CANYONWD_UNIT2 | SCURRY | WIND-O | WEST | 2024 | 2.52 | 2.5
833 | CANYON WIND U3 | 18INR0030 | CANYONWD_UNIT3 | SCURRY | WIND-O | WEST | 2024 | 59.22 | 58.2
834 | CANYON WIND U4 | 18INR0030 | CANYONWD_UNIT4 | SCURRY | WIND-O | WEST | 2024 | 20.16 | 19.8
835 | CANYON WIND U5 | 18INR0030 | CANYONWD_UNIT5 | SCURRY | WIND-O | WEST | 2024 | 67.68 | 66.5
836 | CANYON WIND U6 | 18INR0030 | CANYONWD_UNIT6 | SCURRY | WIND-O | WEST | 2024 | 12.6 | 12.4
837 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2024 | 90 | 90
838 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2024 | 26.6 | 26.6
839 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2024 | 126 | 126
840 | CRAWFISH U1 | 19INR0177 | CRAWFISH_UNIT1 | WHARTON | WIND-O | SOUTH | 2024 | 163.2 | 159
841 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2024 | 153 | 153
842 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2024 | 148.5 | 148.5
843 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2024 | 130.2 | 130.2
844 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2024 | 84 | 84
845 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2024 | 54 | 54
846 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2024 | 162.1 | 162.1
847 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2024 | 182.4 | 182.4
848 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2024 | 201.6 | 201.6
849 | MONTGOMERY RANCH WIND U1 | 20INR0040 | MONT_WND_UNIT1 | FOARD | WIND-O | WEST | 2024 | 106.13 | 105.9
850 | MONTGOMERY RANCH WIND U2 | 20INR0040 | MONT_WND_UNIT2 | FOARD | WIND-O | WEST | 2024 | 92.87 | 92.7
851 | PIONEER DJ WIND U1 | 23INR0387 | PIONR_DJ_UNIT1 | MIDLAND | WIND-O | WEST | 2024 | 124.08 | 124.1
852 | PIONEER DJ WIND U2 | 23INR0387 | PIONR_DJ_UNIT2 | MIDLAND | WIND-O | WEST | 2024 | 16.24 | 16.2
853 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2024 | 153 | 153
854 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2024 | 147 | 147
855 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2024 | 187.2 | 187.2
856 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2024 | 115.2 | 115.2
857 | ROADRUNNER CROSSING WIND II | 21INR0515 | RRC_WIND_UNIT1 | EASTLAND | WIND-O | NORTH | 2024 | 98.7 | 98.7
858 | ROADRUNNER CROSSING WIND U2 | 21INR0515 | RRC_WIND_UNIT2 | EASTLAND | WIND-O | NORTH | 2024 | 27.72 | 27.7
859 | ROADRUNNER CROSSING WIND 1 | 19INR0117 | RRC_WIND_UNIT3 | EASTLAND | WIND-O | NORTH | 2024 | 126.9 | 126.9
860 | SHAMROCK WIND U1 | 22INR0502 | SHAMROCK_UNIT1 | CROCKETT | WIND-O | WEST | 2024 | 203.1 | 203
861 | SHAMROCK WIND U2 | 22INR0502 | SHAMROCK_UNIT2 | CROCKETT | WIND-O | WEST | 2024 | 20.9 | 20.9
862 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2024 | 209.4 | 209.4
863 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2024 | 209.5 | 209.5
864 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2024 | 18.38 | 18.4
865 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2024 | 48 | 48
866 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2024 | 6.3 | 6.3
867 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2024 | 54.6 | 54.6
868 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2024 | 52.8 | 52.8
869 | YOUNG WIND U1 | 21INR0401 | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2024 | 197.4 | 197.4
870 | YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2024 | 152.28 | 152.3
871 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2024 | 149.46 | 149.5
872 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 5002.78 | 4992.7
873
874 | Operational Resources (Solar)
875 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10
876 | AIRPORT ROAD LONEWOLFE PHASE ONE |  | AIRPRTRD_LONEWOLFE | MITCHELL | SOLAR | WEST | 2023 | 1 | 1
877 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10
878 | ANDROMEDA SOLAR U1 |  | ANDMDSLR_UNIT1 | SCURRY | SOLAR | WEST | 2024 | 158.8 | 158
879 | ANDROMEDA SOLAR U2 |  | ANDMDSLR_UNIT2 | SCURRY | SOLAR | WEST | 2024 | 162.4 | 162
880 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
881 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
882 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185
883 | AUREOLA SOLAR U1 |  | AURO_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2024 | 201.66 | 200.4
884 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9
885 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5
886 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1
887 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1
888 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6
889 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3
890 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30
891 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100
892 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15
893 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6
894 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50
895 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
896 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
897 | BPL FILES SOLAR |  | FILESSLR_PV1 | HILL | SOLAR | NORTH | 2023 | 146.09 | 145
898 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2023 | 53.4 | 50
899 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
900 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
901 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
902 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
903 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180
904 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10
905 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10
906 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5
907 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7
908 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6
909 | CORAL SOLAR U1 |  | CORALSLR_SOLAR1 | FALLS | SOLAR | NORTH | 2024 | 97.7 | 96.2
910 | CORAL SOLAR U2 |  | CORALSLR_SOLAR2 | FALLS | SOLAR | NORTH | 2024 | 56.3 | 55.4
911 | CROWN SOLAR |  | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 101.3 | 100.1
912 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
913 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
914 | DILEO SOLAR |  | DILEOSLR_UNIT1 | BOSQUE | SOLAR | NORTH | 2023 | 71.4 | 71.4
915 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144
916 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10
917 | EIFFEL SOLAR |  | EIFSLR_UNIT1 | LAMAR | SOLAR | NORTH | 2023 | 241 | 240
918 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4
919 | ELLIS SOLAR |  | ELLISSLR_UNIT1 | ELLIS | SOLAR | NORTH | 2023 | 81.3 | 80
920 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108
921 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6
922 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1
923 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 6.8 | 6.8
924 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150
925 | FRFWS_FAIRFIELD |  | FRFWS_FAIRFIELD | FREESTONE | SOLAR | NORTH | 2024 | 9.9 | 9.9
926 | FRYE SOLAR U1 |  | FRYE_SLR_UNIT1 | SWISHER | SOLAR | PANHANDLE | 2024 | 250.9 | 250
927 | FRYE SOLAR U2 |  | FRYE_SLR_UNIT2 | SWISHER | SOLAR | PANHANDLE | 2024 | 251.1 | 250
928 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22
929 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1
930 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 250 | 250
931 | GALLOWAY 2 SOLAR |  | GALLOWAY_SOLAR2 | CONCHO | SOLAR | WEST | 2024 | 111.1 | 110
932 | GOLINDA SOLAR |  | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 101.1 | 100.1
933 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6
934 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4
935 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5
936 | GRIZZLY RIDGE SOLAR |  | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100
937 | HALO SOLAR |  | HALO_SLR_UNIT1 | BELL | SOLAR | NORTH | 2024 | 251.15 | 250.4
938 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3
939 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6
940 | HOLLYWOOD SOLAR U1 |  | HOL_UNIT1 | WHARTON | SOLAR | SOUTH | 2024 | 176.14 | 175.3
941 | HOLLYWOOD SOLAR U2 |  | HOL_UNIT2 | WHARTON | SOLAR | SOUTH | 2024 | 178.95 | 178.1
942 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2
943 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3
944 | HOPKINS SOLAR U1 |  | HOPKNSLR_UNIT1 | HOPKINS | SOLAR | NORTH | 2024 | 175.35 | 174.8
945 | HOPKINS SOLAR U2 |  | HOPKNSLR_UNIT2 | HOPKINS | SOLAR | NORTH | 2024 | 76.17 | 75.8
946 | HORIZON SOLAR |  | HRZN_SLR_UNIT1 | FRIO | SOLAR | SOUTH | 2024 | 203.5 | 200
947 | HPWHSOL_WILDHORSESOLAR |  | HPWHSOL_WILDHORSESOLAR | HOWARD | SOLAR | WEST | 2024 | 10 | 10
948 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5
949 | JADE SOLAR U1 |  | JADE_SLR_UNIT1 | SCURRY | SOLAR | WEST | 2024 | 158.8 | 158
950 | JADE SOLAR U2 |  | JADE_SLR_UNIT2 | SCURRY | SOLAR | WEST | 2024 | 162.4 | 162
951 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1
952 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5
953 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8
954 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5
955 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7
956 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10
957 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6
958 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5
959 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3
960 | LONGBOW SOLAR |  | LON_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2024 | 78.2 | 77
961 | LSSEALY_LOCALSUNSEALY |  | LSSEALY_LOCALSUNSEALY | AUSTIN | SOLAR | SOUTH | 2023 | 1.6 | 1.6
962 | MALAKOFF |  | MALAKOFF | HENDERSON | SOLAR | NORTH | 2024 | 5 | 5
963 | MANDORLA SOLAR |  | MAND_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2024 | 251.45 | 250.5
964 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3
965 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10
966 | MCLEAN (SHAKES) SOLAR |  | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200
967 | MEXIA_MEXIA |  | MEXIA_MEXIA | LIMESTONE | SOLAR | NORTH | 2024 | 4 | 4
968 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4
969 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6
970 | MUSTANG CREEK SOLAR U1 |  | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 61 | 60
971 | MUSTANG CREEK SOLAR U2 |  | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 91.25 | 90
972 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5
973 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7
974 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3
975 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2
976 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180
977 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2
978 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4
979 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5
980 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 22INR0600 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6
981 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100
982 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2016 | 110.2 | 110.2
983 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112
984 | PEGASUS_PEGASUS |  | PEGASUS_PEGASUS | UPTON | SOLAR | WEST | 2024 | 10 | 10
985 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.1
986 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.1
987 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9
988 | PITTS DUDIK SOLAR U1 |  | PITTSDDK_UNIT1 | HILL | SOLAR | NORTH | 2023 | 49.6 | 49.6
989 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6
990 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6
991 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150
992 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5
993 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4
994 | PISGAH RIDGE SOLAR U1 |  | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2024 | 189.4 | 186.5
995 | PISGAH RIDGE SOLAR U2 |  | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2024 | 64.4 | 63.5
996 | QUEEN SOLAR U1 |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
997 | QUEEN SOLAR U2 |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
998 | QUEEN SOLAR U3 |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5
999 | QUEEN SOLAR U4 |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5
1000 | RADIAN SOLAR U1 |  | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9
1001 | RADIAN SOLAR U2 |  | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9
1002 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200
1003 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) |  | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8
1004 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
1005 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
1006 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222
1007 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28
1008 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2
1009 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150
1010 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8
1011 | ROWLAND SOLAR I |  | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100
1012 | ROWLAND SOLAR II |  | ROW_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2024 | 200.7 | 200
1013 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50
1014 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5
1015 | SPARTA SOLAR U1 |  | SPARTA_UNIT1 | BEE | SOLAR | SOUTH | 2023 | 147.5 | 146
1016 | SPARTA SOLAR U2 |  | SPARTA_UNIT2 | BEE | SOLAR | SOUTH | 2023 | 104.9 | 104
1017 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10
1018 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 118.3
1019 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
1020 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
1021 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6
1022 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5
1023 | SUNRAY |  | SUN_SLR_UNIT_1 | UVALDE | SOLAR | SOUTH | 2024 | 203.5 | 200
1024 | SUN VALLEY U1 |  | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2024 | 165.75 | 165.8
1025 | SUN VALLEY U2 |  | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2024 | 86.19 | 86.2
1026 | TALCOWST_TALCO |  | TALCOWST_TALCO | TITUS | SOLAR | NORTH | 2024 | 7.5 | 7.5
1027 | TAVENER U1 (FORT BEND SOLAR) |  | TAV_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 149.5 | 149.5
1028 | TAVENER U2 (FORT BEND SOLAR) |  | TAV_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 100.4 | 100.4
1029 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9
1030 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9
1031 | TAYGETE SOLAR 2 U1 |  | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
1032 | TAYGETE SOLAR 2 U2 |  | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
1033 | TEXAS SOLAR NOVA U1 |  | NOVA1SLR_UNIT1 | KENT | SOLAR | WEST | 2024 | 126.81 | 126
1034 | TEXAS SOLAR NOVA U2 |  | NOVA1SLR_UNIT2 | KENT | SOLAR | WEST | 2024 | 126.7 | 126
1035 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8
1036 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1
1037 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10
1038 | TRN_TRINITYBAY |  | TRN_TRINITYBAY | CHAMBERS | SOLAR | HOUSTON | 2024 | 1.5 | 1.5
1039 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7
1040 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 112.7
1041 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120
1042 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10
1043 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182
1044 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7
1045 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5
1046 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100
1047 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
1048 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
1049 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
1050 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
1051 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10
1052 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10
1053 | WHSOLAR_WILDHORSE_SOLAR |  | WHSOLAR_WILDHORSE_SOLAR | HOWARD | SOLAR | WEST | 2024 | 10 | 10
1054 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5
1055 | ZIER SOLAR |  | ZIER_SLR_PV1 | KINNEY | SOLAR | SOUTH | 2024 | 161.28 | 160
1056 | Operational Capacity Total (Solar) | [6 empty] | 16849.82 | 16713.8
1057
1058 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
1059 | 7V SOLAR | 21INR0351 | 7RNCHSLR_UNIT1 | FAYETTE | SOLAR | SOUTH | 2024 | 139.66 | 139.2
1060 | 7V SOLAR U2 | 21INR0351 | 7RNCHSLR_UNIT2 | FAYETTE | SOLAR | SOUTH | 2024 | 95.54 | 95.2
1061 | 7V SOLAR U3 | 21INR0351 | 7RNCHSLR_UNIT3 | FAYETTE | SOLAR | SOUTH | 2024 | 5.57 | 5.6
1062 | ANGELO SOLAR | 19INR0203 | ANG_SLR_UNIT1 | TOM GREEN | SOLAR | WEST | 2024 | 195.41 | 195
1063 | BAKER BRANCH SOLAR U1 | 23INR0026 | BAKE_SLR_UNIT1 | LAMAR | SOLAR | NORTH | 2024 | 234.84 | 233.9
1064 | BAKER BRANCH SOLAR U2 | 23INR0026 | BAKE_SLR_UNIT2 | LAMAR | SOLAR | NORTH | 2024 | 234.57 | 233.9
1065 | BIG ELM SOLAR | 21INR0353 | BELM_SLR_UNIT1 | BELL | SOLAR | NORTH | 2024 | 200.99 | 200.2
1066 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2024 | 132.27 | 130
1067 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2024 | 70.83 | 70
1068 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2024 | 69 | 69
1069 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2024 | 141 | 141
1070 | BRIGHT ARROW SOLAR U1 | 22INR0242 | BR_ARROW_UNIT1 | HOPKINS | SOLAR | NORTH | 2024 | 127.3 | 127
1071 | BRIGHT ARROW SOLAR U2 | 22INR0242 | BR_ARROW_UNIT2 | HOPKINS | SOLAR | NORTH | 2024 | 173.9 | 173
1072 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2024 | 217.5 | 217.5
1073 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2024 | 221.3 | 221.3
1074 | CHEVRON ALLEN SOLAR (HAYHURST TEXAS SOLAR) | 22INR0363 | CHAL_SLR_SOLAR1 | CULBERSON | SOLAR | WEST | 2024 | 25.22 | 24.8
1075 | CHILLINGHAM SOLAR U1 | 23INR0070 | CHIL_SLR_SOLAR1 | BELL | SOLAR | NORTH | 2024 | 174.3 | 173
1076 | CHILLINGHAM SOLAR U2 | 23INR0070 | CHIL_SLR_SOLAR2 | BELL | SOLAR | NORTH | 2024 | 178.1 | 177
1077 | COTTONWOOD BAYOU SOLAR I U1 | 19INR0134 | CTW_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2024 | 175.69 | 175
1078 | COTTONWOOD BAYOU SOLAR I U2 | 19INR0134 | CTW_SOLAR2 | BRAZORIA | SOLAR | COASTAL | 2024 | 175.71 | 175
1079 | DANISH FIELDS SOLAR U1 | 20INR0069 | DAN_UNIT1 | WHARTON | SOLAR | SOUTH | 2024 | 301.3 | 300
1080 | DANISH FIELDS SOLAR U2 | 20INR0069 | DAN_UNIT2 | WHARTON | SOLAR | SOUTH | 2024 | 151 | 150.2
1081 | DANISH FIELDS SOLAR U3 | 20INR0069 | DAN_UNIT3 | WHARTON | SOLAR | SOUTH | 2024 | 150.5 | 149.8
1082 | DELILAH SOLAR 1 U1 | 22INR0202 | DELILA_1_G1 | LAMAR | SOLAR | NORTH | 2025 | 153.54 | 150
1083 | DELILAH SOLAR 1 U2 | 22INR0202 | DELILA_1_G2 | LAMAR | SOLAR | NORTH | 2025 | 153.54 | 150
1084 | EASTBELL MILAM SOLAR | 21INR0203 | EBELLSLR_UNIT1 | MILAM | SOLAR | SOUTH | 2024 | 244.86 | 240
1085 | ESTONIAN SOLAR FARM U1 | 22INR0335 | ESTONIAN_SOLAR1 | DELTA | SOLAR | NORTH | 2024 | 88.4 | 88.3
1086 | ESTONIAN SOLAR FARM U2 | 22INR0335 | ESTONIAN_SOLAR2 | DELTA | SOLAR | NORTH | 2024 | 114.4 | 114.1
1087 | FENCE POST SOLAR U1 | 22INR0404 | FENCESLR_SOLAR1 | NAVARRO | SOLAR | NORTH | 2024 | 138.88 | 138
1088 | FENCE POST SOLAR U2 | 22INR0404 | FENCESLR_SOLAR2 | NAVARRO | SOLAR | NORTH | 2024 | 97.98 | 98
1089 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2025 | 179.5 | 179.6
1090 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2025 | 171.8 | 171.9
1091 | FIVE WELLS SOLAR U1 | 24INR0015 | FIVEWSLR_UNIT1 | BELL | SOLAR | NORTH | 2024 | 194.42 | 194.4
1092 | FIVE WELLS SOLAR U2 | 24INR0015 | FIVEWSLR_UNIT2 | BELL | SOLAR | NORTH | 2024 | 126.97 | 127
1093 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2024 | 7.41 | 7.4
1094 | JACKALOPE SOLAR U1 | 23INR0180 | JKLP_SLR_PV1 | SAN PATRICIO | SOLAR | COASTAL | 2024 | 81.38 | 80
1095 | JACKALOPE SOLAR U2 | 23INR0180 | JKLP_SLR_PV2 | SAN PATRICIO | SOLAR | COASTAL | 2024 | 71.74 | 70
1096 | MARKUM SOLAR | 20INR0230 | MRKM_SLR_PV1 | MCLENNAN | SOLAR | NORTH | 2024 | 161.5 | 161
1097 | MERCURY SOLAR U1 | 21INR0257 | MERCURY_PV1 | HILL | SOLAR | NORTH | 2024 | 203.5 | 203.5
1098 | MERCURY SOLAR U2 | 23INR0153 | MERCURY_PV2 | HILL | SOLAR | NORTH | 2024 | 203.5 | 203.5
1099 | MORROW LAKE SOLAR | 19INR0155 | MROW_SLR_SOLAR1 | FRIO | SOLAR | SOUTH | 2024 | 202.2 | 200
1100 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2024 | 171.6 | 167.2
1101 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2024 | 149.6 | 145.8
1102 | PHOTON SOLAR 3 | 23INR0111 | PHO3_SOLAR3 | WHARTON | SOLAR | SOUTH | 2024 | 109.99 | 109.6
1103 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2024 | 270 | 257
1104 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2024 | 270 | 257
1105 | PORTER SOLAR U1 | 21INR0458 | PORT_SLR_UNIT1 | DENTON | SOLAR | NORTH | 2024 | 245.83 | 245
1106 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2024 | 254 | 250
1107 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2024 | 137.8 | 135.6
1108 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2024 | 116.2 | 114.4
1109 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2025 | 128.42 | 125
1110 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2025 | 128.42 | 125
1111 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2025 | 128.42 | 125
1112 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2025 | 128.42 | 125
1113 | SBRANCH SOLAR PROJECT | 22INR0205 | SBE_UNIT1 | WHARTON | SOLAR | SOUTH | 2024 | 233.5 | 233.5
1114 | STAMPEDE SOLAR U1 | 22INR0409 | STAM_SLR_SOLAR1 | HOPKINS | SOLAR | NORTH | 2024 | 77.75 | 77
1115 | STAMPEDE SOLAR U2 | 22INR0409 | STAM_SLR_SOLAR2 | HOPKINS | SOLAR | NORTH | 2024 | 178.55 | 178
1116 | TEXAS BLUEBONNET SOLAR | 24INR0580 | BONETSLR_UNIT1 | MCLENNAN | SOLAR | NORTH | 2024 | 9.75 | 9.7
1117 | TEXAS SOLAR NOVA 2 U1 | 20INR0269 | NOVA2SLR_UNIT1 | KENT | SOLAR | WEST | 2024 | 202.37 | 200
1118 | TIERRA BONITA SOLAR U1 | 21INR0424 | TRBT_SLR_PV1 | PECOS | SOLAR | WEST | 2024 | 150 | 149.6
1119 | TIERRA BONITA SOLAR U2 | 21INR0424 | TRBT_SLR_PV2 | PECOS | SOLAR | WEST | 2024 | 156.9 | 156.3
1120 | TRES BAHIAS SOLAR | 20INR0266 | TREB_SLR_SOLAR1 | CALHOUN | SOLAR | COASTAL | 2024 | 196.29 | 195
1121 | TRUE NORTH SOLAR U1 | 23INR0114 | TNS_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 119.35 | 118.8
1122 | TRUE NORTH SOLAR U2 | 23INR0114 | TNS_SLR_UNIT2 | FALLS | SOLAR | NORTH | 2024 | 119.45 | 118.9
1123 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 9869.63 | 9771.7
1124
1125 | Operational Resources (Storage)
1126 | ANCHOR BESS U1 |  | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2023 | 35.2 | 35.2
1127 | ANCHOR BESS U2 |  | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2023 | 36.3 | 36.3
1128 | ANEMOI ENERGY STORAGE |  | ANEM_ESS_BESS1 | HIDALGO | STORAGE | SOUTH | 2024 | 200.9 | 200
1129 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6
1130 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1131 | BAY CITY BESS (DGR) |  | BAY_CITY_BESS | MATAGORDA | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1132 | BELDING TNP (TRIPLE BUTTE BATTERY) (DGR) |  | BELD_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5
1133 | BLUE JAY BESS |  | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2023 | 51.6 | 50
1134 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30
1135 | BOCO BESS |  | BOCO_ESS_ESS1 | BORDEN | STORAGE | WEST | 2024 | 154 | 150
1136 | BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 10 | 10
1137 | BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 10 | 10
1138 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10 | 10
1139 | BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 10 | 10
1140 | BRP DICKENS BESS U1 |  | DKNS_ESS_BES1 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1141 | BRP DICKENS BESS U2 |  | DKNS_ESS_BES2 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1142 | BRP DICKENS BESS U3 |  | DKNS_ESS_BES3 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1143 | BRP DICKENS BESS U4 |  | DKNS_ESS_BES4 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1144 | BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10 | 10
1145 | BRP LIBRA BESS |  | LBRA_ESS_BES1 | GUADALUPE | STORAGE | SOUTH | 2024 | 201.02 | 200
1146 | BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 10 | 10
1147 | BRP LOPENO (DGR) |  | LOPENO_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 10 | 10
1148 | BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 10 | 10
1149 | BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 10 | 10
1150 | BRP PAVO BESS U1 |  | PAVO_ESS_BESS1 | PECOS | STORAGE | WEST | 2024 | 87.9 | 87.5
1151 | BRP PAVO BESS U2 |  | PAVO_ESS_BESS2 | PECOS | STORAGE | WEST | 2024 | 87.9 | 87.5
1152 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 10 | 10
1153 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 10 | 10
1154 | BRP RANCHTOWN (DGR) |  | K0_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 10 | 10
1155 | BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 10 | 10
1156 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 10 | 10
1157 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 10 | 10
1158 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50
1159 | CALLISTO I ENERGY CENTER U1 |  | CLO_BESS1 | HARRIS | STORAGE | HOUSTON | 2024 | 101.5 | 100
1160 | CALLISTO I ENERGY CENTER U2 |  | CLO_BESS2 | HARRIS | STORAGE | HOUSTON | 2024 | 101.5 | 100
1161 | CAMERON STORAGE (SABAL STORAGE) |  | CAMWIND_BESS1 | CAMERON | STORAGE | COASTAL | 2024 | 16.67 | 16.4
1162 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9
1163 | CATARINA BESS (DGR) |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9
1164 | CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1165 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 0
1166 | CONTINENTAL BESS (DGR) |  | CONTINEN_BESS1 | STARR | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1167 | COMMERCE ST ESS (DGR) |  | X4_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10
1168 | CORAL STORAGE U1 |  | CORALSLR_BESS1 | FALLS | STORAGE | NORTH | 2023 | 48.4 | 47.6
1169 | CORAL STORAGE U2 |  | CORALSLR_BESS2 | FALLS | STORAGE | NORTH | 2023 | 52.2 | 51.4
1170 | COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1171 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1172 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1173 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1174 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1175 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1176 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1177 | DIBOLL BESS (DGR) |  | DIBOL_BESS | ANGELINA | STORAGE | NORTH | 2024 | 9.95 | 9.9
1178 | EBONY ENERGY STORAGE |  | EBNY_ESS_BESS1 | COMAL | STORAGE | SOUTH | 2024 | 201.2 | 200
1179 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50
1180 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3
1181 | FALFURRIAS BESS (DGR) |  | FALFUR_BESS | BROOKS | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1182 | FARMERSVILLE BESS (DGR) |  | FRMRSVLW_BESS | COLLIN | STORAGE | NORTH | 2024 | 9.9 | 9.9
1183 | FAULKNER BESS (DGR) |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1184 | FIVE WELLS STORAGE |  | FIVEWSLR_BESS1 | BELL | STORAGE | NORTH | 2024 | 228.54 | 220
1185 | FLAT TOP BATTERY (DGR) |  | FLAT_TOP_FLATU1 | REEVES | STORAGE | WEST | 2020 | 9.9 | 9.9
1186 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100
1187 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100
1188 | GARDEN CITY EAST BESS (DGR) |  | GRDNE_BESS | GLASSCOCK | STORAGE | WEST | 2024 | 9.95 | 9.9
1189 | GEORGETOWN SOUTH (RABBIT HILL ESS) (DGR) |  | GEORSO_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2019 | 9.9 | 9.9
1190 | GIGA TEXAS ENERGY STORAGE |  | GIGA_ESS_BESS_1 | TRAVIS | STORAGE | SOUTH | 2024 | 125.31 | 125
1191 | GOMEZ BESS (DGR) |  | GOMZ_BESS | REEVES | STORAGE | WEST | 2023 | 9.95 | 9.9
1192 | HAMILTON BESS (DGR) U1 |  | HAMILTON_BESS | VAL VERDE | STORAGE | WEST | 2024 | 9.9 | 9.9
1193 | HIGH LONESOME BESS |  | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2023 | 51.1 | 50
1194 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2
1195 | HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1196 | HOUSE MOUNTAIN BESS |  | HOUSEMTN_BESS1 | BREWSTER | STORAGE | WEST | 2023 | 61.5 | 60
1197 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1198 | JOHNSON CITY BESS (DGR) |  | JOHNCI_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3
1199 | JUDKINS BESS (DGR) |  | JDKNS_BESS | ECTOR | STORAGE | WEST | 2024 | 10 | 10
1200 | JUNCTION BESS (DGR) |  | JUNCTION_BESS | KIMBLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1201 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5
1202 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 50
1203 | LIMOUSIN OAK STORAGE |  | LMO_BESS1 | GRIMES | STORAGE | NORTH | 2024 | 100.42 | 100
1204 | LONESTAR BESS (DGR) |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1205 | LUFKIN SOUTH BESS (DGR) |  | LFSTH_BESS | ANGELINA | STORAGE | NORTH | 2024 | 10 | 10
1206 | MADERO GRID U1 |  | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1207 | MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1208 | MAINLAND BESS (DGR) |  | MAINLAND_BESS | GALVESTON | STORAGE | HOUSTON | 2024 | 9.9 | 9.9
1209 | MINERAL WELLS EAST BESS (DGR) |  | MNWLE_BESS | PALO PINTO | STORAGE | NORTH | 2024 | 9.95 | 9.9
1210 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5
1211 | MUSTANG CREEK STORAGE |  | MUSTNGCK_BES1 | JACKSON | STORAGE | SOUTH | 2024 | 71.49 | 70.5
1212 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1213 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1214 | NORTH ALAMO BESS (DGR) |  | N_ALAMO_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1215 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 51.75 | 50
1216 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1217 | NORTH MERCEDES BESS (DGR) |  | N_MERCED_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1218 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7
1219 | OLNEY BESS (DGR) |  | OLNEYTN_BESS | YOUNG | STORAGE | WEST | 2023 | 9.95 | 9.9
1220 | PAULINE BESS (DGR) |  | PAULN_BESS | HENDERSON | STORAGE | NORTH | 2024 | 10 | 10
1221 | PAVLOV BESS (DGR) |  | PAVLOV_BESS | MATAGORDA | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1222 | PORT LAVACA BATTERY (DGR) |  | PRTLAVS_BESS1 | CALHOUN | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1223 | PYOTE TNP (SWOOSE BATTERY) (DGR) |  | PYOTE_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9
1224 | PYRON BESS 2A |  | PYR_ESS2A | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1225 | PYRON BESS 2B |  | PYR_ESS2B | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1226 | PYRON ESS |  | PYR_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1227 | QUEEN BESS |  | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2023 | 51.1 | 50
1228 | RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1229 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50
1230 | RIVER VALLEY STORAGE U1 |  | RVRVLYS_ESS1 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50
1231 | RIVER VALLEY STORAGE U2 |  | RVRVLYS_ESS2 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50
1232 | RODEO RANCH ENERGY STORAGE U1 |  | RRANCHES_UNIT1 | REEVES | STORAGE | WEST | 2023 | 150.4 | 150
1233 | RODEO RANCH ENERGY STORAGE U2 |  | RRANCHES_UNIT2 | REEVES | STORAGE | WEST | 2023 | 150.4 | 150
1234 | ROSELAND STORAGE |  | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2023 | 51.6 | 50
1235 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1236 | SANDLAKE BESS (DGR) |  | SANDLAK1_BESS | REEVES | STORAGE | WEST | 2024 | 9.99 | 10
1237 | SARAGOSA BESS (DGR) |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1238 | SCREWBEAN BESS (DGR) |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2023 | 9.95 | 9.9
1239 | SHEEP CREEK STORAGE |  | SHEEPCRK_BESS1 | EASTLAND | STORAGE | NORTH | 2024 | 142.1 | 135.1
1240 | SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1241 | SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1242 | SMT ELSA (DGR) |  | ELSA_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1243 | SMT GARCENO BESS (DGR) |  | GARCENO_BESS | MATAGORDA | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1244 | SMT LOS FRESNOS (DGR) |  | L_FRESNO_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1245 | SMT MAYBERRY BESS (DGR) |  | MAYBERRY_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1246 | SMT RIO GRANDE CITY BESS (DGR) |  | RIO_GRAN_BESS | STARR | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1247 | SMT SANTA ROSA (DGR) |  | S_SNROSA_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1248 | SNYDER (DGR) |  | DPCRK_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 10 | 10
1249 | SP TX-12B BESS |  | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2023 | 25.1 | 25.1
1250 | ST. GALL I ENERGY STORAGE |  | SGAL_BES_BESS1 | PECOS | STORAGE | WEST | 2024 | 101.5 | 100
1251 | SUN VALLEY BESS U1 |  | SUNVASLR_BESS1 | HILL | STORAGE | NORTH | 2023 | 54.08 | 53.3
1252 | SUN VALLEY BESS U2 |  | SUNVASLR_BESS2 | HILL | STORAGE | NORTH | 2023 | 47.32 | 46.7
1253 | SWEETWATER BESS (DGR) |  | SWTWR_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9
1254 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100
1255 | TIMBERWOLF BESS |  | TBWF_ESS_BES1 | CRANE | STORAGE | WEST | 2023 | 150.34 | 150
1256 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9
1257 | TURQUOISE STORAGE |  | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190
1258 | VAL VERDE BESS (DGR) |  | MV_VALV4_BESS | HIDALGO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1259 | VORTEX BESS |  | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2023 | 121.8 | 121.8
1260 | WEST COLUMBIA (PROSPECT STORAGE) (DGR) |  | WCOLLOCL_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1261 | WEST HARLINGEN BESS (DGR) |  | W_HARLIN_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1262 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 10 | 10
1263 | WEIL TRACT BESS |  | WEIL_TRC_BESS | NUECES | STORAGE | COASTAL | 2024 | 9.95 | 9.9
1264 | WOLF TANK STORAGE |  | WFTANK_ESS1 | WEBB | STORAGE | SOUTH | 2023 | 150.4 | 150
1265 | WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9 | 9.9
1266 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2 | 2
1267 | ZIER STORAGE U1 |  | ZIER_SLR_BES1 | KINNEY | STORAGE | SOUTH | 2024 | 40.08 | 40
1268 | Operational Capacity Total (Storage) | [6 empty] | 6414.32 | 6229.5
1269
1270 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1271 | AE-TELVIEW ESS (DGR) | 23INR0541 | TV_BESS | FORT BEND | STORAGE | HOUSTON | 2024 | 10 | 10
1272 | AL PASTOR BESS | 24INR0273 | ALP_BESS_BESS1 | DAWSON | STORAGE | WEST | 2024 | 103.1 | 100.3
1273 | ANGELO STORAGE | 23INR0418 | ANG_SLR_BESS1 | TOM GREEN | STORAGE | WEST | 2024 | 102.97 | 100
1274 | BIG STAR STORAGE | 21INR0469 | BIG_STAR_BESS | BASTROP | STORAGE | SOUTH | 2022 | 80 | 80
1275 | BRIGHT ARROW STORAGE U1 | 22INR0302 | BR_ARROW_BESS1 | HOPKINS | STORAGE | NORTH | 2023 | 49.34 | 48.3
1276 | BRIGHT ARROW STORAGE U2 | 22INR0302 | BR_ARROW_BESS2 | HOPKINS | STORAGE | NORTH | 2023 | 52.77 | 51.7
1277 | BRP HYDRA BESS | 22INR0372 | HYDR_ESS_BES1 | PECOS | STORAGE | WEST | 2023 | 200.8 | 200
1278 | BRP PALEO BESS | 22INR0322 | PALE_ESS_BES1 | HALE | STORAGE | PANHANDLE | 2023 | 200.8 | 200
1279 | BRP TORTOLAS BESS | 23INR0072 | TORT_ESS_BESS1 | BRAZORIA | STORAGE | COASTAL | 2023 | 50.3 | 50
1280 | CONNOLLY STORAGE | 23INR0403 | CNLY_ESS_BESS_1 | WISE | STORAGE | NORTH | 2024 | 125.41 | 125
1281 | CISCO BESS (DGR) | 24INR0588 | CISC_BESS | EASTLAND | STORAGE | NORTH | 2024 | 9.9 | 9.9
1282 | DANISH FIELDS STORAGE U1 | 21INR0450 | DAN_BESS1 | WHARTON | STORAGE | SOUTH | 2024 | 77.8 | 76.3
1283 | DANISH FIELDS STORAGE U2 | 21INR0450 | DAN_BESS2 | WHARTON | STORAGE | SOUTH | 2024 | 75.1 | 73.7
1284 | ESTONIAN ENERGY STORAGE | 22INR0336 | ESTONIAN_BES1 | DELTA | STORAGE | NORTH | 2023 | 101.6 | 101.6
1285 | FENCE POST BESS U1 | 22INR0405 | FENCESLR_BESS1 | NAVARRO | STORAGE | NORTH | 2023 | 72.01 | 70
1286 | GREAT KISKADEE STORAGE | 23INR0166 | GKS_BESS_BESS1 | HIDALGO | STORAGE | SOUTH | 2024 | 100 | 100
1287 | GREGORY BESS | 23INR0539 | GREGORY_BESS1 | SAN PATRICIO | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1288 | HOLY ESS U1 | 24INR0147 | HLY_BESS1 | HARRIS | STORAGE | HOUSTON | 2024 | 104.66 | 102.2
1289 | HOLY ESS U2 | 24INR0147 | HLY_BESS2 | HARRIS | STORAGE | HOUSTON | 2024 | 104.66 | 102.2
1290 | HUMMINGBIRD STORAGE | 22INR0327 | HMNG_ESS_BESS1 | DENTON | STORAGE | NORTH | 2024 | 100.38 | 100
1291 | INERTIA BESS | 22INR0328 | INRT_W_BESS_1 | HASKELL | STORAGE | WEST | 2023 | 13 | 13
1292 | JADE STORAGE U1 | 24INR0629 | JADE_SLR_BESS1 | SCURRY | STORAGE | WEST | 2024 | 78.53 | 78.1
1293 | JADE STORAGE U2 | 24INR0629 | JADE_SLR_BESS2 | SCURRY | STORAGE | WEST | 2024 | 82.27 | 81.9
1294 | LONGBOW BESS | 25INR0328 | LON_BES1 | BRAZORIA | STORAGE | COASTAL | 2024 | 180.8 | 174
1295 | MIDWAY BESS U1 | 23INR0688 | MIDWY_BESS1 | ECTOR | STORAGE | WEST | 2024 | 10 | 10
1296 | MYRTLE STORAGE U1 | 21INR0442 | MYR_BES1 | BRAZORIA | STORAGE | COASTAL | 2023 | 76.93 | 76.3
1297 | MYRTLE STORAGE U2 | 21INR0442 | MYR_BES2 | BRAZORIA | STORAGE | COASTAL | 2023 | 74.27 | 73.7
1298 | PHOTON STORAGE | 23INR0460 | PHO_1_BES1 | WHARTON | STORAGE | SOUTH | 2025 | 152.74 | 150
1299 | REGIS MOORE FIELD BESS | 23INR0498 | MOORE_FL_BESS1 | HIDALGO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1300 | REGIS PALACIOS BESS | 22INR0602 | PALACIOS_BESS1 | MATAGORDA | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1301 | RIVER BEND (BRAZOS BEND BESS) | 23INR0363 | RBN_BESS1 | FORT BEND | STORAGE | HOUSTON | 2024 | 101.64 | 100
1302 | RUSSEK STREET BESS (DGR) | 24INR0614 | RUSSEKST_BESS | REAGAN | STORAGE | WEST | 2024 | 9.9 | 9.9
1303 | STAMPEDE BESS U1 | 22INR0410 | STAM_SLR_BESS1 | HOPKINS | STORAGE | NORTH | 2023 | 72.19 | 70
1304 | WIGEON WHISTLE BESS | 24INR0312 | WIG_ESS_BES1 | COLLIN | STORAGE | NORTH | 2024 | 122.9 | 120
1305 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 2726.47 | 2687.8
1306
1307 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0
1308
1309 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0
1310
1311 | Non-Synchronous Tie Resources
1312 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600
1313 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220
1314 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100
1315 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300
1316 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220
1317
1318 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies ``
1319 | BEACHWOOD II POWER STATION (U7-U8) | 23INR0506 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 121 | 99.6
1320 | CEDAR BAYOU5 | 23INR0029 |  | CHAMBERS | GAS-CC | HOUSTON | 2027 | 0 | 0
1321 | COYOTE SPRINGS AGR1 (DGR) | 24INR0645 |  | REEVES | DIESEL | WEST | 2025 | 0 | 0
1322 | ENCHANTED ROCK NEWPP | 22INR0546 |  | HARRIS | GAS-IC | HOUSTON | 2024 | 30 | 30
1323 | OLNEY AGR1 (DGR) | 24INR0647 |  | YOUNG | DIESEL | WEST | 2025 | 0 | 0
1324 | REMY JADE II POWER STATION (U9-U10) | 24INR0382 |  | HARRIS | GAS-GT | HOUSTON | 2025 | 0 | 0
1325 | SADDLEBACK AGR1 (DGR) | 24INR0646 |  | REEVES | DIESEL | WEST | 2025 | 0 | 0
1326 | UHLAND MAXWELL (TIMMERMAN POWER PLANT) | 25INR0223 |  | CALDWELL | GAS-IC | SOUTH | 2025 | 0 | 0
1327 | UHLAND MAXWELL EXPANSION (TIMMERMAN POWER PLANT) | 25INR0503 |  | CALDWELL | GAS-IC | SOUTH | 2026 | 0 | 0
1328 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Diesel, Biomass) | [6 empty] | 151 | 129.6
1329
1330 | Planned Wind Resources with Executed SGIA
1331 | AQUILLA LAKE 3 WIND | 22INR0499 |  | HILL | WIND-O | NORTH | 2027 | 0 | 0
1332 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2025 | 0 | 0
1333 | BUG TUSSLE WIND PROJECT | 23INR0441 |  | LAMAR | WIND-O | NORTH | 2026 | 0 | 0
1334 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2026 | 0 | 0
1335 | FORTUNA WIND | 22INR0301 |  | JACK | WIND-O | NORTH | 2026 | 0 | 0
1336 | GOODNIGHT WIND II | 23INR0637 |  | ARMSTRONG | WIND-P | PANHANDLE | 2026 | 0 | 0
1337 | HART WIND 2 | 24INR0116 |  | CASTRO | WIND-P | PANHANDLE | 2025 | 0 | 0
1338 | HONEY MESQUITE WIND FARM | 26INR0447 |  | GLASSCOCK | WIND-O | WEST | 2026 | 0 | 0
1339 | HYFUELS WESTERN FARMLAND WIND | 26INR0021 |  | VICTORIA | WIND-O | SOUTH | 2026 | 0 | 0
1340 | LA CASA WIND | 21INR0240 |  | STEPHENS | WIND-O | NORTH | 2025 | 0 | 0
1341 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2025 | 0 | 0
1342 | MEITNER WIND | 26INR0113 |  | GRAY | WIND-P | PANHANDLE | 2027 | 0 | 0
1343 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2026 | 0 | 0
1344 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2025 | 0 | 0
1345 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2025 | 0 | 0
1346 | MONTE CRISTO 1 WIND | 19INR0054 |  | HIDALGO | WIND-O | SOUTH | 2025 | 0 | 0
1347 | PEYTON CREEK WIND II | 20INR0155 |  | MATAGORDA | WIND-C | COASTAL | 2025 | 0 | 0
1348 | RAY GULF WIND | 22INR0517 |  | WHARTON | WIND-O | SOUTH | 2025 | 0 | 0
1349 | RUBICON ALPHA WIND | 24INR0291 |  | HASKELL | WIND-O | WEST | 2027 | 0 | 0
1350 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2026 | 0 | 0
1351 | YELLOW CAT WIND | 25INR0018 |  | NAVARRO | WIND-O | NORTH | 2026 | 0 | 0
1352 | Planned Capacity Total (Wind) | [6 empty] | 0 | 0
1353
1354 | Planned Solar Resources with Executed SGIA
1355 | ADAMSTOWN SOLAR | 21INR0210 |  | WICHITA | SOLAR | WEST | 2026 | 0 | 0
1356 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2026 | 0 | 0
1357 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1358 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2026 | 0 | 0
1359 | ANSON SOLAR CENTER, PHASE II | 20INR0242 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1360 | ARGENTA SOLAR | 25INR0060 |  | BEE | SOLAR | SOUTH | 2026 | 0 | 0
1361 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2026 | 0 | 0
1362 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2028 | 0 | 0
1363 | ASH CREEK SOLAR | 21INR0379 |  | HILL | SOLAR | NORTH | 2025 | 0 | 0
1364 | AUSTIN BAYOU SOLAR | 25INR0102 |  | BRAZORIA | SOLAR | COASTAL | 2027 | 0 | 0
1365 | AZALEA SPRINGS SOLAR | 19INR0110 |  | ANGELINA | SOLAR | NORTH | 2025 | 0 | 0
1366 | BARRETT SOLAR | 24INR0477 |  | RAINS | SOLAR | NORTH | 2025 | 0 | 0
1367 | BLEVINS SOLAR | 23INR0118 |  | FALLS | SOLAR | NORTH | 2025 | 0 | 0
1368 | BLUE BIRD SOLAR | 24INR0075 |  | JOHNSON | SOLAR | NORTH | 2025 | 0 | 0
1369 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2025 | 0 | 0
1370 | BOTTOM GRASS SOLAR | 23INR0082 |  | COLORADO | SOLAR | SOUTH | 2026 | 0 | 0
1371 | BYNUM SOLAR PROJECT | 24INR0181 |  | CORYELL | SOLAR | NORTH | 2026 | 0 | 0
1372 | MILLER'S BRANCH I | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1373 | BUZIOS SOLAR | 24INR0399 |  | MOTLEY | SOLAR | PANHANDLE | 2026 | 0 | 0
1374 | CACHENA SOLAR SLF | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2027 | 0 | 0
1375 | CALICHE MOUND SOLAR | 23INR0056 |  | DEAF SMITH | SOLAR | PANHANDLE | 2025 | 0 | 0
1376 | CAMP CREEK SOLAR SLF | 23INR0385 |  | ROBERTSON | SOLAR | NORTH | 2026 | 0 | 0
1377 | CANTALOUPE SOLAR | 23INR0116 |  | REEVES | SOLAR | WEST | 2028 | 0 | 0
1378 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2025 | 0 | 0
1379 | CASCADE SOLAR | 23INR0091 |  | BRAZORIA | SOLAR | COASTAL | 2026 | 0 | 0
1380 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2026 | 0 | 0
1381 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2025 | 0 | 0
1382 | CLUTCH CITY SOLAR PHASE I | 22INR0279 |  | BRAZORIA | SOLAR | COASTAL | 2026 | 0 | 0
1383 | COMPADRE SOLAR | 24INR0023 |  | HILL | SOLAR | NORTH | 2024 | 406.1 | 406.1
1384 | CONCHO PEARL SOLAR | 25INR0174 |  | CONCHO | SOLAR | WEST | 2027 | 0 | 0
1385 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2028 | 0 | 0
1386 | CRADLE SOLAR | 23INR0150 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1387 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1388 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2026 | 0 | 0
1389 | CUCHILLAS SOLAR | 24INR0059 |  | WEBB | SOLAR | SOUTH | 2026 | 0 | 0
1390 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2025 | 0 | 0
1391 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2026 | 0 | 0
1392 | DEVILLE SOLAR | 22INR0262 |  | CALLAHAN | SOLAR | WEST | 2026 | 0 | 0
1393 | DIAMONDBACK SOLAR | 20INR0162 |  | STARR | SOLAR | SOUTH | 2027 | 0 | 0
1394 | DIVER SOLAR | 25INR0105 |  | LIMESTONE | SOLAR | NORTH | 2026 | 0 | 0
1395 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2027 | 0 | 0
1396 | DORADO SOLAR | 22INR0261 |  | CALLAHAN | SOLAR | WEST | 2025 | 0 | 0
1397 | DORI BQ SOLAR | 23INR0040 |  | HARRIS | SOLAR | HOUSTON | 2025 | 0 | 0
1398 | DOVE RUN SOLAR | 21INR0326 |  | DUVAL | SOLAR | SOUTH | 2026 | 0 | 0
1399 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2025 | 0 | 0
1400 | DRY CREEK SOLAR I | 23INR0286 |  | RUSK | SOLAR | NORTH | 2026 | 0 | 0
1401 | DUFFY SOLAR | 23INR0057 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1402 | EASTBELL MILAM SOLAR II | 24INR0208 |  | MILAM | SOLAR | SOUTH | 2024 | 150.6 | 150.6
1403 | EL PATRIMONIO SOLAR | 23INR0207 |  | BEXAR | SOLAR | SOUTH | 2026 | 0 | 0
1404 | ELDORA SOLAR | 24INR0337 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1405 | ELIZA SOLAR | 21INR0368 |  | KAUFMAN | SOLAR | NORTH | 2024 | 151.7 | 151.7
1406 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2028 | 0 | 0
1407 | ERATH COUNTY SOLAR | 23INR0202 |  | ERATH | SOLAR | NORTH | 2026 | 0 | 0
1408 | ERIKA SOLAR | 24INR0303 |  | KAUFMAN | SOLAR | NORTH | 2026 | 0 | 0
1409 | ERIN SOLAR | 23INR0058 |  | WHARTON | SOLAR | SOUTH | 2027 | 0 | 0
1410 | FAGUS SOLAR PARK 1 SLF | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2025 | 0 | 0
1411 | FEWELL SOLAR | 23INR0367 |  | LIMESTONE | SOLAR | NORTH | 2027 | 0 | 0
1412 | GAIA SOLAR | 24INR0141 |  | NAVARRO | SOLAR | NORTH | 2025 | 0 | 0
1413 | GALACTIC SOLAR | 23INR0144 |  | GRAYSON | SOLAR | NORTH | 2027 | 0 | 0
1414 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2026 | 0 | 0
1415 | GLASGOW SOLAR | 24INR0206 |  | NAVARRO | SOLAR | NORTH | 2027 | 0 | 0
1416 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2025 | 0 | 0
1417 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2025 | 0 | 0
1418 | GRANSOLAR TEXAS ONE | 22INR0511 |  | MILAM | SOLAR | SOUTH | 2025 | 0 | 0
1419 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2025 | 0 | 0
1420 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2026 | 0 | 0
1421 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2026 | 0 | 0
1422 | GRIMES COUNTY SOLAR | 23INR0160 |  | GRIMES | SOLAR | NORTH | 2025 | 0 | 0
1423 | PHOTON SOLAR 1 2 | 25INR0493 |  | WHARTON | SOLAR | SOUTH | 2025 | 0 | 0
1424 | HANSON SOLAR | 23INR0086 |  | COLEMAN | SOLAR | WEST | 2027 | 0 | 0
1425 | HICKERSON SOLAR | 21INR0359 |  | BOSQUE | SOLAR | NORTH | 2026 | 0 | 0
1426 | HIGH CHAP SOLAR | 25INR0068 |  | BRAZORIA | SOLAR | COASTAL | 2027 | 0 | 0
1427 | HIGH NOON SOLAR | 24INR0124 |  | HILL | SOLAR | NORTH | 2027 | 0 | 0
1428 | HONEYCOMB SOLAR | 22INR0559 |  | BEE | SOLAR | SOUTH | 2025 | 0 | 0
1429 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2025 | 602.4 | 602.4
1430 | HORNET SOLAR II SLF | 25INR0282 |  | CASTRO | SOLAR | PANHANDLE | 2026 | 0 | 0
1431 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2026 | 0 | 0
1432 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2026 | 0 | 0
1433 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2027 | 0 | 0
1434 | ISAAC SOLAR | 25INR0232 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1435 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2025 | 0 | 0
1436 | LANGER SOLAR | 23INR0030 |  | BOSQUE | SOLAR | NORTH | 2027 | 0 | 0
1437 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2024 | 243.5 | 243.5
1438 | LEIGHTON SOLAR SLF | 24INR0298 |  | LIMESTONE | SOLAR | NORTH | 2026 | 0 | 0
1439 | LEON SOLAR PARK | 26INR0023 |  | LEON | SOLAR | NORTH | 2026 | 0 | 0
1440 | LIMEWOOD SOLAR | 23INR0249 |  | BELL | SOLAR | NORTH | 2025 | 0 | 0
1441 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1442 | LUNIS CREEK SOLAR SLF | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2026 | 0 | 0
1443 | MALDIVES SOLAR (ALTERNATE POI) | 25INR0400 |  | SCURRY | SOLAR | WEST | 2027 | 0 | 0
1444 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2025 | 0 | 0
1445 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2025 | 0 | 0
1446 | MEITNER SOLAR | 25INR0080 |  | GRAY | SOLAR | PANHANDLE | 2027 | 0 | 0
1447 | MIDPOINT SOLAR | 24INR0139 |  | HILL | SOLAR | NORTH | 2025 | 0 | 0
1448 | MIRANDA SOLAR PROJECT | 24INR0161 |  | MCMULLEN | SOLAR | SOUTH | 2026 | 0 | 0
1449 | MOCCASIN SOLAR | 26INR0269 |  | STONEWALL | SOLAR | WEST | 2027 | 0 | 0
1450 | MRG GOODY SOLAR | 23INR0225 |  | LAMAR | SOLAR | NORTH | 2025 | 0 | 0
1451 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2026 | 0 | 0
1452 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 0 | 0
1453 | NIGHTFALL SOLAR SLF | 21INR0334 |  | UVALDE | SOLAR | SOUTH | 2026 | 0 | 0
1454 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2025 | 0 | 0
1455 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2025 | 0 | 0
1456 | NORTHINGTON SOLAR | 25INR0319 |  | WHARTON | SOLAR | SOUTH | 2026 | 0 | 0
1457 | NEW HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2026 | 0 | 0
1458 | OCI COBB CREEK SOLAR | 25INR0229 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1459 | ORIANA SOLAR | 24INR0093 |  | VICTORIA | SOLAR | SOUTH | 2025 | 0 | 0
1460 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2025 | 0 | 0
1461 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2026 | 0 | 0
1462 | PARLIAMENT SOLAR | 23INR0044 |  | WALLER | SOLAR | HOUSTON | 2025 | 0 | 0
1463 | PAYNE BATTLECREEK | 24INR0106 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1464 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 301.3 | 301.3
1465 | PIEDRA SOLAR | 25INR0168 |  | FREESTONE | SOLAR | NORTH | 2026 | 0 | 0
1466 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2025 | 0 | 0
1467 | PINK SOLAR | 22INR0281 |  | HUNT | SOLAR | NORTH | 2027 | 0 | 0
1468 | PINNINGTON SOLAR | 24INR0010 |  | JACK | SOLAR | NORTH | 2026 | 0 | 0
1469 | PITTS DUDIK II | 24INR0364 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1470 | PORTSIDE ENERGY CENTER (SOLAR) SLF | 24INR0401 |  | VICTORIA | SOLAR | SOUTH | 2026 | 0 | 0
1471 | QUANTUM SOLAR | 21INR0207 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1472 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2026 | 0 | 0
1473 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2026 | 0 | 0
1474 | RENEGADE PROJECT (DAWN SOLAR) | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2025 | 0 | 0
1475 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2026 | 0 | 0
1476 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2026 | 0 | 0
1477 | ROSS SOLAR | 26INR0155 |  | REFUGIO | SOLAR | COASTAL | 2027 | 0 | 0
1478 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2025 | 0 | 0
1479 | SANPAT SOLAR | 25INR0052 |  | SAN PATRICIO | SOLAR | COASTAL | 2026 | 0 | 0
1480 | SANPAT SOLAR II | 25INR0081 |  | SAN PATRICIO | SOLAR | COASTAL | 2027 | 0 | 0
1481 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2025 | 0 | 0
1482 | DAMAZO (SECOND DIVISION) SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 100.2 | 100.2
1483 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2025 | 0 | 0
1484 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2026 | 0 | 0
1485 | SHORT CREEK SOLAR | 24INR0201 |  | WICHITA | SOLAR | WEST | 2027 | 0 | 0
1486 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2024 | 51.8 | 51.8
1487 | SKULL CREEK SOLAR | 23INR0289 |  | ANDERSON | SOLAR | NORTH | 2026 | 0 | 0
1488 | SOLACE SOLAR | 23INR0031 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1489 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2026 | 0 | 0
1490 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2026 | 0 | 0
1491 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2025 | 0 | 0
1492 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2024 | 136.7 | 136.7
1493 | STILLHOUSE SOLAR | 24INR0166 |  | BELL | SOLAR | NORTH | 2025 | 0 | 0
1494 | STONERIDGE SOLAR | 24INR0031 |  | MILAM | SOLAR | SOUTH | 2025 | 0 | 0
1495 | SUN CACTUS SOLAR | 25INR0109 |  | DUVAL | SOLAR | SOUTH | 2026 | 0 | 0
1496 | SUNSCAPE RENEWABLE ENERGY SOLAR SLF | 27INR0047 |  | NUECES | SOLAR | COASTAL | 2027 | 0 | 0
1497 | SWIFT AIR SOLAR | 24INR0421 |  | ECTOR | SOLAR | WEST | 2025 | 0 | 0
1498 | SYPERT BRANCH SOLAR PROJECT | 24INR0070 |  | MILAM | SOLAR | SOUTH | 2025 | 0 | 0
1499 | ORANGE GROVE SOLAR | 21INR0393 |  | JIM WELLS | SOLAR | SOUTH | 2025 | 0 | 0
1500 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1501 | THREE W SOLAR | 25INR0055 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1502 | TOKIO SOLAR | 23INR0349 |  | MCLENNAN | SOLAR | NORTH | 2027 | 0 | 0
1503 | TORMES SOLAR | 22INR0437 |  | NAVARRO | SOLAR | NORTH | 2027 | 0 | 0
1504 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2026 | 0 | 0
1505 | TULSITA SOLAR | 21INR0223 |  | GOLIAD | SOLAR | SOUTH | 2024 | 256.2 | 256.2
1506 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2025 | 0 | 0
1507 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2026 | 0 | 0
1508 | UMBRA (STOCKYARD) SOLAR | 23INR0155 |  | FRANKLIN | SOLAR | NORTH | 2027 | 0 | 0
1509 | VALHALLA SOLAR | 26INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2026 | 0 | 0
1510 | VIKING SOLAR | 21INR0520 |  | SOMERVELL | SOLAR | NORTH | 2026 | 0 | 0
1511 | WOLF SPRING SOLAR | 25INR0172 |  | DICKENS | SOLAR | PANHANDLE | 2027 | 0 | 0
1512 | XE BONHAM SOLAR 1 | 25INR0199 |  | LIMESTONE | SOLAR | NORTH | 2026 | 0 | 0
1513 | XE HERMES SOLAR | 23INR0344 |  | BELL | SOLAR | NORTH | 2025 | 0 | 0
1514 | XE MURAT [ADLONG] SOLAR | 22INR0354 |  | HARRIS | SOLAR | HOUSTON | 2024 | 60.4 | 60.4
1515 | YAUPON SOLAR SLF | 24INR0042 |  | MILAM | SOLAR | SOUTH | 2026 | 0 | 0
1516 | ZEISSEL SOLAR | 24INR0258 |  | KNOX | SOLAR | WEST | 2028 | 0 | 0
1517 | Planned Capacity Total (Solar) | [6 empty] | 2460.9 | 2460.9
1518
1519 | Planned Storage Resources with Executed SGIA
1520 | ABILENE ELMCREEK BESS | 25INR0701 |  | TAYLOR | STORAGE | WEST | 2025 | 0 | 0
1521 | ABILENE INDUSTRIAL PARK BESS | 25INR0702 |  | TAYLOR | STORAGE | WEST | 2025 | 0 | 0
1522 | ADELITE STORAGE | 23INR0502 |  | MILAM | STORAGE | SOUTH | 2026 | 0 | 0
1523 | ALDRIN 138 BESS | 25INR0421 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1524 | ALDRIN 345 BESS | 25INR0425 |  | BRAZORIA | STORAGE | COASTAL | 2027 | 0 | 0
1525 | AMADOR STORAGE | 24INR0472 |  | VAN ZANDT | STORAGE | NORTH | 2025 | 0 | 0
1526 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1527 | ANATOLE RENEWABLE ENERGY STORAGE | 24INR0355 |  | HENDERSON | STORAGE | NORTH | 2026 | 0 | 0
1528 | ANDROMEDA STORAGE SLF | 24INR0630 |  | SCURRY | STORAGE | WEST | 2024 | 160.5 | 160.5
1529 | ANGLETON BESS | 24INR0547 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 9.9 | 9.9
1530 | ANOLE BESS | 23INR0299 |  | DALLAS | STORAGE | NORTH | 2025 | 0 | 0
1531 | ANSON BAT | 22INR0457 |  | JONES | STORAGE | WEST | 2025 | 0 | 0
1532 | ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2025 | 0 | 0
1533 | APACHE HILL BESS | 25INR0231 |  | HOOD | STORAGE | NORTH | 2026 | 0 | 0
1534 | ARGENTA STORAGE | 25INR0061 |  | BEE | STORAGE | SOUTH | 2026 | 0 | 0
1535 | ARROYO STORAGE | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2025 | 0 | 0
1536 | AVILA BESS | 23INR0287 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1537 | BACKBONE CREEK BESS | 24INR0313 |  | BURNET | STORAGE | SOUTH | 2026 | 0 | 0
1538 | BERKMAN STORAGE | 24INR0395 |  | GALVESTON | STORAGE | HOUSTON | 2027 | 0 | 0
1539 | BEXAR ESS | 23INR0381 |  | BEXAR | STORAGE | SOUTH | 2025 | 0 | 0
1540 | BIG ELM STORAGE | 23INR0469 |  | BELL | STORAGE | NORTH | 2025 | 0 | 0
1541 | BIRD DOG BESS | 22INR0467 |  | LIVE OAK | STORAGE | SOUTH | 2025 | 0 | 0
1542 | BLACK & GOLD ENERGY STORAGE | 24INR0386 |  | MENARD | STORAGE | WEST | 2027 | 0 | 0
1543 | BLACK SPRINGS BESS SLF | 24INR0315 |  | PALO PINTO | STORAGE | NORTH | 2025 | 0 | 0
1544 | BLANQUILLA BESS | 24INR0528 |  | NUECES | STORAGE | COASTAL | 2026 | 0 | 0
1545 | BLEVINS STORAGE | 23INR0119 |  | FALLS | STORAGE | NORTH | 2025 | 0 | 0
1546 | BLUE SKIES BESS | 25INR0046 |  | HILL | STORAGE | NORTH | 2027 | 0 | 0
1547 | BOCANOVA BESS | 25INR0467 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1548 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2025 | 0 | 0
1549 | BOTTOM GRASS BESS | 23INR0083 |  | COLORADO | STORAGE | SOUTH | 2026 | 0 | 0
1550 | BRACERO PECAN STORAGE | 26INR0034 |  | REEVES | STORAGE | WEST | 2026 | 0 | 0
1551 | BROTHERTON STORAGE | 25INR0432 |  | ANDERSON | STORAGE | NORTH | 2026 | 0 | 0
1552 | BUFFLEHEAD BESS | 24INR0274 |  | COLLIN | STORAGE | NORTH | 2026 | 0 | 0
1553 | BURKSOL BESS (DONEGAL BESS) | 23INR0103 |  | DICKENS | STORAGE | PANHANDLE | 2025 | 0 | 0
1554 | BYPASS BATTERY STORAGE | 23INR0336 |  | FORT BEND | STORAGE | HOUSTON | 2025 | 0 | 0
1555 | CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2025 | 0 | 0
1556 | CALLISTO II ENERGY CENTER | 22INR0558 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1557 | CAMP CREEK STORAGE SLF | 23INR0423 |  | ROBERTSON | STORAGE | NORTH | 2026 | 0 | 0
1558 | CANTALOUPE STORAGE | 23INR0117 |  | REEVES | STORAGE | WEST | 2028 | 0 | 0
1559 | CANVASBACK BESS | 25INR0160 |  | CALHOUN | STORAGE | COASTAL | 2027 | 0 | 0
1560 | CARAMBOLA BESS (SMT MCALLEN II) | 24INR0436 |  | HIDALGO | STORAGE | SOUTH | 2026 | 0 | 0
1561 | CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2025 | 0 | 0
1562 | CARTWHEEL BESS 1 | 23INR0494 |  | HOPKINS | STORAGE | NORTH | 2025 | 0 | 0
1563 | CASTOR BESS | 23INR0358 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1564 | CENTURY BESS | 24INR0610 |  | TARRANT | STORAGE | NORTH | 2024 | 9.9 | 9.9
1565 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2025 | 0 | 0
1566 | CITRUS CITY BESS | 24INR0591 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1567 | CITRUS FLATTS BESS | 24INR0294 |  | CAMERON | STORAGE | COASTAL | 2026 | 0 | 0
1568 | CITY BREEZE BESS | 25INR0271 |  | MATAGORDA | STORAGE | COASTAL | 2026 | 0 | 0
1569 | CONCHO PEARL STORAGE | 25INR0175 |  | CONCHO | STORAGE | WEST | 2027 | 0 | 0
1570 | CONEFLOWER STORAGE PROJECT | 23INR0425 |  | CHAMBERS | STORAGE | HOUSTON | 2027 | 0 | 0
1571 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1572 | COTULLA BESS 2 | 24INR0638 |  | LA SALLE | STORAGE | SOUTH | 2025 | 0 | 0
1573 | CROCKETT BESS | 25INR0642 |  | HARRIS | STORAGE | HOUSTON | 2024 | 9.9 | 9.9
1574 | CROSBY BESS | 24INR0546 |  | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1575 | CROSS TRAILS STORAGE | 23INR0372 |  | SCURRY | STORAGE | WEST | 2025 | 0 | 0
1576 | CROWNED HERON BESS | 24INR0405 |  | FORT BEND | STORAGE | HOUSTON | 2025 | 0 | 0
1577 | DAMON BESS 2 (DGR) | 23INR0603 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1578 | DAMON STORAGE | 23INR0523 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 5 | 5
1579 | DESERT WILLOW BESS | 23INR0195 |  | ELLIS | STORAGE | NORTH | 2025 | 0 | 0
1580 | DESNA BESS | 24INR0128 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1581 | DESTINY STORAGE | 24INR0397 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1582 | DOGFISH BESS | 23INR0219 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1583 | DORI BQ BESS | 24INR0196 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1584 | ELDORA BESS | 24INR0338 |  | MATAGORDA | STORAGE | COASTAL | 2026 | 0 | 0
1585 | ELIO BESS | 25INR0103 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1586 | ELIZA STORAGE | 22INR0260 |  | KAUFMAN | STORAGE | NORTH | 2025 | 0 | 0
1587 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2028 | 0 | 0
1588 | EVELYN BATTERY ENERGY STORAGE SYSTEM | 24INR0460 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1589 | FALFUR BESS (DGR) | 24INR0593 |  | BROOKS | STORAGE | SOUTH | 2025 | 0 | 0
1590 | FARMERSVILLE WEST BESS 2 | 23INR0618 |  | COLLIN | STORAGE | NORTH | 2025 | 9.9 | 9.9
1591 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2026 | 0 | 0
1592 | FORT DUNCAN BESS | 23INR0350 |  | MAVERICK | STORAGE | SOUTH | 2025 | 0 | 0
1593 | FORT MASON BESS | 23INR0500 |  | MASON | STORAGE | SOUTH | 2024 | 9.8 | 9.8
1594 | FORT WATT STORAGE | 24INR0498 |  | TARRANT | STORAGE | NORTH | 2026 | 0 | 0
1595 | GAIA STORAGE | 24INR0140 |  | NAVARRO | STORAGE | NORTH | 2025 | 0 | 0
1596 | GEARS BESS | 24INR0595 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1597 | GLASGOW STORAGE | 24INR0207 |  | NAVARRO | STORAGE | NORTH | 2027 | 0 | 0
1598 | GOLDENEYE BESS | 25INR0100 |  | BELL | STORAGE | NORTH | 2026 | 0 | 0
1599 | GREAT ROCK BESS | 25INR0230 |  | LEON | STORAGE | NORTH | 2026 | 0 | 0
1600 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2026 | 0 | 0
1601 | GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2023 | 9.9 | 9.9
1602 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2025 | 0 | 0
1603 | GUNNAR BESS | 24INR0491 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1604 | HANSON STORAGE | 24INR0057 |  | COLEMAN | STORAGE | WEST | 2027 | 0 | 0
1605 | HEADCAMP BESS | 23INR0401 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1606 | HIDDEN LAKES BESS | 23INR0617 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1607 | HIDDEN VALLEY BESS | 24INR0594 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1608 | HIGH NOON STORAGE | 24INR0126 |  | HILL | STORAGE | NORTH | 2027 | 0 | 0
1609 | HONEYCOMB STORAGE SLF | 23INR0392 |  | BEE | STORAGE | SOUTH | 2025 | 0 | 0
1610 | HORNET STORAGE II SLF | 25INR0283 |  | CASTRO | STORAGE | PANHANDLE | 2026 | 0 | 0
1611 | IEP ORCHARD BESS | 23INR0556 |  | FORT BEND | STORAGE | HOUSTON | 2025 | 0 | 0
1612 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2027 | 0 | 0
1613 | IRON BELT ENERGY STORAGE | 25INR0208 |  | BORDEN | STORAGE | WEST | 2026 | 0 | 0
1614 | JARVIS BESS | 24INR0265 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 308.4 | 308.4
1615 | JUNCTION NORTH BESS | 23INR0619 |  | KIMBLE | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1616 | LARKSPUR ENERGY STORAGE | 23INR0340 |  | UPTON | STORAGE | WEST | 2026 | 0 | 0
1617 | LAURELES BESS (DGR) | 23INR0499 |  | CAMERON | STORAGE | COASTAL | 2025 | 0 | 0
1618 | LEAKEY BESS (DGR) | 23INR0548 |  | REAL | STORAGE | SOUTH | 2025 | 0 | 0
1619 | LIGGETT SWITCH BESS | 24INR0660 |  | DALLAS | STORAGE | NORTH | 2024 | 9.9 | 9.9
1620 | LIMEWOOD STORAGE | 23INR0248 |  | BELL | STORAGE | NORTH | 2028 | 0 | 0
1621 | LONG POINT STORAGE | 21INR0444 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1622 | LOWER RIO BESS | 22INR0468 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1623 | LUCKY BLUFF BESS SLF | 24INR0295 |  | ERATH | STORAGE | NORTH | 2025 | 0 | 0
1624 | LUMBERJACK STORAGE | 23INR0324 |  | CHEROKEE | STORAGE | NORTH | 2026 | 0 | 0
1625 | MAYBERRY II BESS | 23INR0807 |  | HIDALGO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1626 | MEDINA CITY BESS (DGR) | 24INR0502 |  | BANDERA | STORAGE | SOUTH | 2025 | 0 | 0
1627 | MEDINA LAKE BESS (DGR) | 24INR0499 |  | BANDERA | STORAGE | SOUTH | 2024 | 9.8 | 9.8
1628 | MIDPOINT STORAGE | 24INR0138 |  | HILL | STORAGE | NORTH | 2025 | 0 | 0
1629 | MILTON BESS (DGR) | 23INR0552 |  | KARNES | STORAGE | SOUTH | 2025 | 0 | 0
1630 | MRG GOODY STORAGE | 24INR0305 |  | LAMAR | STORAGE | NORTH | 2025 | 0 | 0
1631 | MUENSTER BESS | 22INR0590 |  | COOKE | STORAGE | NORTH | 2024 | 9.9 | 9.9
1632 | MUSTANG BAYOU BESS | 24INR0599 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 10 | 10
1633 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2025 | 0 | 0
1634 | OCI COBB CREEK ESS | 25INR0233 |  | HILL | STORAGE | NORTH | 2026 | 0 | 0
1635 | ORANGE GROVE BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2027 | 0 | 0
1636 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2026 | 0 | 0
1637 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 51.1 | 51.1
1638 | PALMVIEW BESS | 24INR0628 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1639 | PEARSALL BESS | 24INR0560 |  | FRIO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1640 | PHOTON BESS2 | 25INR0691 |  | WHARTON | STORAGE | SOUTH | 2025 | 0 | 0
1641 | PICADILLO BESS | 24INR0275 |  | MARTIN | STORAGE | WEST | 2026 | 0 | 0
1642 | PIEDRA BESS | 25INR0169 |  | FREESTONE | STORAGE | NORTH | 2026 | 0 | 0
1643 | PINE FOREST BESS | 22INR0526 |  | HOPKINS | STORAGE | NORTH | 2025 | 0 | 0
1644 | PINTAIL PASS BESS | 24INR0302 |  | SAN PATRICIO | STORAGE | COASTAL | 2025 | 0 | 0
1645 | PLATINUM STORAGE | 22INR0554 |  | FANNIN | STORAGE | NORTH | 2025 | 0 | 0
1646 | PORTSIDE ENERGY CENTER (BESS) SLF | 24INR0403 |  | VICTORIA | STORAGE | SOUTH | 2026 | 0 | 0
1647 | PROJECT LYNX BESS | 25INR0329 |  | NUECES | STORAGE | COASTAL | 2026 | 0 | 0
1648 | RADIAN STORAGE SLF | 24INR0631 |  | BROWN | STORAGE | NORTH | 2024 | 160.25 | 160.25
1649 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2027 | 0 | 0
1650 | RED EGRET BESS | 24INR0281 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1651 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2026 | 0 | 0
1652 | RIO GRANDE CITY BESS 2 | 24INR0592 |  | STARR | STORAGE | SOUTH | 2025 | 0 | 0
1653 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2026 | 0 | 0
1654 | ROCK ROSE ENERGY BESS | 26INR0201 |  | FORT BEND | STORAGE | HOUSTON | 2026 | 0 | 0
1655 | ROCKEFELLER STORAGE | 22INR0239 |  | SCHLEICHER | STORAGE | WEST | 2027 | 0 | 0
1656 | ROGERS DRAW BESS | 24INR0514 |  | GILLESPIE | STORAGE | SOUTH | 2026 | 0 | 0
1657 | ROSS STORAGE | 26INR0156 |  | REFUGIO | STORAGE | COASTAL | 2027 | 0 | 0
1658 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2027 | 0 | 0
1659 | SE EDINBURG BESS | 24INR0642 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1660 | SEVEN FLAGS BESS | 23INR0351 |  | WEBB | STORAGE | SOUTH | 2025 | 0 | 0
1661 | SHAMROCK ENERGY STORAGE (SLF) | 24INR0568 |  | CROCKETT | STORAGE | WEST | 2025 | 0 | 0
1662 | SHEPARD ENERGY STORAGE | 25INR0262 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1663 | SKIPJACK ENERGY STORAGE | 26INR0189 |  | BRAZORIA | STORAGE | COASTAL | 2027 | 0 | 0
1664 | SODA LAKE BESS 1 | 23INR0501 |  | CRANE | STORAGE | WEST | 2025 | 0 | 0
1665 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 206.3 | 206.3
1666 | SOHO II BESS | 25INR0162 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 206.3 | 206.3
1667 | SOSA STORAGE | 25INR0131 |  | MADISON | STORAGE | NORTH | 2026 | 0 | 0
1668 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2025 | 0 | 0
1669 | SP JAGUAR BESS | 24INR0039 |  | MCLENNAN | STORAGE | NORTH | 2025 | 0 | 0
1670 | SPENCER BESS | 24INR0545 |  | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1671 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2026 | 0 | 0
1672 | STONERIDGE BESS | 25INR0389 |  | MILAM | STORAGE | SOUTH | 2025 | 0 | 0
1673 | SUNSCAPE RENEWABLE ENERGY STORAGE SLF | 27INR0048 |  | NUECES | STORAGE | COASTAL | 2027 | 0 | 0
1674 | TANZANITE STORAGE | 22INR0549 |  | HENDERSON | STORAGE | NORTH | 2025 | 0 | 0
1675 | TE SMITH STORAGE | 22INR0555 |  | ROCKWALL | STORAGE | NORTH | 2025 | 0 | 0
1676 | THIRD COAST BESS | 23INR0361 |  | JACKSON | STORAGE | SOUTH | 2025 | 0 | 0
1677 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2025 | 0 | 0
1678 | TIERRA SECA BESS | 23INR0364 |  | VAL VERDE | STORAGE | WEST | 2025 | 0 | 0
1679 | TORRECILLAS BESS | 23INR0529 |  | WEBB | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1680 | TWO BROTHERS BATTERY ENERGY STORAGE SYSTEM | 24INR0425 |  | VICTORIA | STORAGE | SOUTH | 2026 | 0 | 0
1681 | TWO FORKS BESS | 24INR0198 |  | COOKE | STORAGE | NORTH | 2027 | 0 | 0
1682 | TYNAN BESS | 24INR0759 |  | BEE | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1683 | UMBRA (STOCKYARD) BESS | 23INR0156 |  | FRANKLIN | STORAGE | NORTH | 2027 | 0 | 0
1684 | UTOPIA BESS (DGR) | 24INR0501 |  | BANDERA | STORAGE | SOUTH | 2025 | 0 | 0
1685 | WALSTROM BESS | 22INR0540 |  | AUSTIN | STORAGE | SOUTH | 2025 | 0 | 0
1686 | WHARTON BESS (DGR) | 22INR0608 |  | WHARTON | STORAGE | SOUTH | 2025 | 0 | 0
1687 | WIZARD BESS | 25INR0300 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1688 | WOLF SPRING STORAGE | 25INR0173 |  | DICKENS | STORAGE | PANHANDLE | 2027 | 0 | 0
1689 | XE HERMES STORAGE | 24INR0365 |  | BELL | STORAGE | NORTH | 2025 | 0 | 0
1690 | XE MURAT STORAGE | 24INR0329 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1691 | YAUPON STORAGE SLF | 24INR0169 |  | MILAM | STORAGE | SOUTH | 2025 | 0 | 0
1692 | ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1693 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * |  | PLANNED_SMALL_GEN_NO_MRD |  | STORAGE |  |  | 0 | 0
1694 | Planned Capacity Total (Storage) | [6 empty] | 1266.05 | 1266.05
1695
1696 | Inactive Planned Resources
1697 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60
1698 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2026 | 0 | 0
1699 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS-GT | SOUTH | 2021 | 484 | 484
1700 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1701 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1702 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5
1703 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 11 | 11
1704 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150
1705 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0
1706 | SODA LAKE SOLAR 1 SLF | 20INR0143 |  | CRANE | SOLAR | WEST | 2024 | 203 | 203
1707 | SODA LAKE SOLAR 2 SLF | 23INR0080 |  | CRANE | SOLAR | WEST | 2023 | 202.6 | 202.6
1708 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 30 | 30
1709 | ZEISSEL STORAGE SLF | 24INR0259 |  | KNOX | STORAGE | WEST | 2028 | 0 | 0
1710 | Inactive Planned Capacity Total | [6 empty] | 1793.3 | 1793.3
1711
1712 | Seasonal Mothballed Resources
1713 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5
1714 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57
1715 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61
1716 | Total Seasonal Mothballed Capacity | [6 empty] | 144.75 | 135.5
1717
1718 | Mothballed Resources
1719 | BRANDON (LP&L) (DGR) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20
1720 | CALENERGY-FALCON SEABOARD STG 3 (INDEFINITE MOTHBALL AS OF 7/8/22, DUE TO FORCED OUTAGE) |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 62
1721 | R MASSENGALE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1722 | R MASSENGALE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1723 | R MASSENGALE STG (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38
1724 | RAY OLINGER STG 1 (INDEFINITE MOTHBALL AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78
1725 | TEXAS BIG SPRING WIND B (INDEFINITE MOTHBALL STATUS AS ON 1/1/24) |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6
1726 | TY COOKE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14
1727 | TY COOKE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17
1728 | WICHITA FALLS STG 4 (INDEFINITE MOTHBALL STATUS AS ON 11/1/23) |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 16
1729 | Total Mothballed Capacity | [6 empty] | 335.8 | 287.6
1730
1731 | Retiring Resources Unavailable to ERCOT (since last CDR/MORA)
1732 | Total Retiring Capacity | [6 empty] | 0 | 0
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
For battery storage ("Energy Storage Resources"), the contribution expected for the peak load hours of the month is based on the amount of battery storage energy assumed to be available for dispatch, accounting for hourly average High Sustained Limits and State of Charge for the ESR fleet.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Reources Services (RIOO-RS) system.
Note on I450: Extended outage: McQueeny unit was placed on an extended outage on March 2023, which is expected to end in Summer 2025.
Note on J450: Extended outage: McQueeny unit was placed on an extended outage on March 2023, which is expected to end in Summer 2025.
Note on J492: PRRM simulation result for normal operating conditions, HE 20 (8 p.m).
Note on J1165: Extended Outage starting 12/1/2024 with 13-17 mo. Duration (Dec. 2025 - Apr. 2025)

## PRRM Percentile Results
Probabilistic Reserve Risk Model (PRRM) Percentile Results
Gross Demand by Hour, MW (Accounts for rooftop solar, electric vehicle, and Large Load electricity consumption adjustments; excludes demand response program deployments)
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 52164.0447 | 51664.9316 | 51153.2775 | 51261.2116 | 51096.2574 | 52262.5641 | 53685.0155 | 54478.1626 | 55693.7512 | 56051.3407 | 55917.3709 | 55384.162 | 54847.2258 | 54506.7823 | 54205.1574 | 54267.5877 | 54835.967 | 56559.9528 | 58394.8529 | 58917.4989 | 59014.2294 | 57728.654 | 55613.9843 | 52856.8483
| 10% | 53726.5584 | 53207.23 | 53281.2094 | 53684.9169 | 55016.9854 | 57606.4788 | 61890.1609 | 62804.5316 | 64205.9091 | 63827.9637 | 62915.7154 | 61609.0157 | 60459.1386 | 59415.7504 | 58799.1023 | 59059.8042 | 60143.3957 | 62895.7515 | 66155.1159 | 66463.061 | 65580.8886 | 63526.7123 | 59536.9173 | 56538.3793
| 20% | 55017.489 | 54486.0976 | 54541.601 | 54955.2973 | 56217.9898 | 58768.9129 | 65258.245 | 70114.7096 | 66247.9041 | 65081.1983 | 64004.1516 | 62772.9522 | 61677.9669 | 60651.2531 | 60036.2193 | 60293.3816 | 61375.4149 | 64081.7205 | 67284.2676 | 67611.0253 | 66826.5725 | 64818.6159 | 60866.9156 | 57800.2955
| 30% | 56261.1981 | 55702.5419 | 55705.1201 | 56081.8399 | 57222.1182 | 59673.2098 | 66863.3648 | 71839.2811 | 67877.366 | 66681.9634 | 65255.404 | 63730.3994 | 62627.5135 | 61676.6974 | 61092.0829 | 61321.1064 | 62371.9487 | 65066.4614 | 68876.4167 | 69024.3022 | 67855.3317 | 65837.2036 | 61996.4745 | 58873.7225
| 40% | 57397.2234 | 56796.8542 | 56737.4241 | 57135.4858 | 58188.1457 | 60759.9205 | 68439.5038 | 73532.7151 | 69477.4076 | 68253.8263 | 66793.6393 | 65133.1351 | 63770.1266 | 62642.9685 | 62063.4848 | 62291.4107 | 63355.3285 | 66485.5245 | 70500.0085 | 70651.38 | 69313.7317 | 66980.4005 | 63070.5694 | 59902.2083
| 50% | 58424.7217 | 57804.8456 | 57662.6517 | 58025.1528 | 59015.2888 | 62057.2013 | 69900.7508 | 75102.7068 | 70960.8148 | 69711.1089 | 68219.7456 | 66523.788 | 65131.678 | 63819.1335 | 63113.3596 | 63422.6414 | 64708.0237 | 67905.0522 | 72005.2492 | 72159.8526 | 70793.6443 | 68410.4943 | 63944.6601 | 60738.9466
| 60% | 59481.2739 | 58792.3483 | 58597.0552 | 58931.5063 | 60369.9811 | 63481.7205 | 71505.3182 | 76826.6848 | 72589.7158 | 71311.323 | 69785.7256 | 68050.8374 | 66626.7716 | 65284.0977 | 64562.1229 | 64878.5041 | 66193.3923 | 69463.8084 | 73658.1251 | 73816.2775 | 72418.7079 | 69980.8529 | 65297.2505 | 62002.5724
| 70% | 60514.1345 | 59790.3112 | 59872.0699 | 60340.988 | 61938.6376 | 65131.2326 | 73363.3158 | 78822.9531 | 74475.8905 | 73164.2799 | 71599.0413 | 69819.0737 | 68358.0049 | 66980.4429 | 66239.7082 | 66564.3104 | 67913.3646 | 71268.7594 | 75572.0615 | 75734.3233 | 74300.4392 | 71799.2388 | 66993.9375 | 63613.6503
| 80% | 62360.5487 | 61763.8739 | 61858.4003 | 62342.8753 | 63993.5289 | 67292.0422 | 75797.235 | 81438.0026 | 76946.7208 | 75591.5959 | 73974.4285 | 72135.4083 | 70625.8667 | 69202.6024 | 68437.2929 | 68772.6641 | 70166.4749 | 73633.1891 | 77835.415 | 78125.3488 | 76765.4486 | 74181.2678 | 69216.5446 | 65724.1122
| 90% | 65170.8972 | 64547.3326 | 64646.1188 | 65152.4273 | 66877.4695 | 70324.634 | 79213.1229 | 85108.098 | 80414.4116 | 78998.2164 | 77308.1695 | 75386.2718 | 73808.7011 | 72321.2957 | 71521.4967 | 71871.9818 | 73328.6063 | 76357.989 | 80130.4576 | 80418.8692 | 79126.9276 | 76463.2515 | 71954.2206 | 68587.274
| 100% | 87885.8366 | 85845.8009 | 86511.0226 | 87350.2287 | 88143.4708 | 90179.171 | 91689.2446 | 94696.5946 | 92413.8321 | 91501.3081 | 87557.8133 | 84885.6095 | 83005.3988 | 79667.9416 | 78416.9492 | 78507.927 | 79405.5412 | 80807.4506 | 84767.2218 | 84949.2267 | 83340.8761 | 80535.3445 | 76594.3374 | 73290.5502
Solar Generation by Hour, MW
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3357e-05 | 59.3381 | 621.7953 | 1298.8819 | 1232.8191 | 1182.9065 | 1075.6184 | 879.7714 | 720.6549 | 668.7048 | 35.7265 | 0 | 0 | 0 | 0 | 0 | 0
| 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63135 | 876.2397 | 4150.1765 | 5927.9431 | 4187.1647 | 5139.4453 | 5666.3305 | 5845.3025 | 5568.8898 | 4734.6614 | 434.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9661 | 1410.637 | 5795.8286 | 8180.0672 | 6470.3707 | 7680.5634 | 8147.8382 | 8443.5824 | 8096.2022 | 6147.1966 | 696.0562 | 0 | 0 | 0 | 0 | 0 | 0
| 30% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9491 | 1920.5847 | 7219.6897 | 10071.4447 | 8713.5479 | 9968.5857 | 10407.8819 | 10679.9657 | 10128.9622 | 7404.9876 | 976.446 | 0 | 0 | 0 | 0 | 0 | 0
| 40% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5628 | 2447.8105 | 8539.9464 | 11614.9505 | 10866.0896 | 12137.8122 | 12465.38 | 12698.4456 | 12214.24 | 8490.2325 | 1247.1922 | 0 | 0 | 0 | 0 | 0 | 0
| 50% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.14 | 3026.4271 | 9918.6969 | 13150.8011 | 13065.1546 | 14297.1992 | 14423.8353 | 14703.1415 | 14124.4014 | 9467.7523 | 1548.5535 | 0 | 0 | 0 | 0 | 0 | 0
| 60% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5581 | 3658.241 | 11417.1015 | 14744.03 | 15273.619 | 16369.8433 | 16378.3361 | 16589.0764 | 15843.731 | 10494.6872 | 1891.333 | 0 | 0 | 0 | 0 | 0 | 0
| 70% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5269 | 4442.5504 | 13112.0776 | 16363.6787 | 17461.9346 | 18455.6308 | 18268.7459 | 18424.4718 | 17597.5384 | 11554.2281 | 2311.0625 | 0 | 0 | 0 | 0 | 0 | 0
| 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.385 | 5416.3883 | 15136.0679 | 18163.0363 | 19599.6778 | 20455.8907 | 20201.9903 | 20389.4953 | 19644.2238 | 12831.8276 | 2846.5938 | 0 | 0 | 0 | 0 | 0 | 0
| 90% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.9592 | 6758.224 | 18037.6816 | 20657.5847 | 21967.4031 | 22696.58 | 22286.8537 | 22481.9688 | 21807.3654 | 14525.6609 | 3714.7642 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.4616 | 9674.3457 | 24519.2232 | 25835.4945 | 24687.2658 | 25487.5697 | 25141.2516 | 25486.0591 | 25131.4659 | 19642.852 | 6440.7104 | 0 | 0 | 0 | 0 | 0 | 0
Wind Generation by Hour, MW
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 556.6168 | 679.2129 | 917.4247 | 1033.2985 | 1121.1937 | 1192.7256 | 1158.9139 | 1080.0141 | 699.1456 | 454.3877 | 382.8315 | 544.9679 | 545.1665 | 288.1717 | 290.2696 | 318.9242 | 291.738 | 433.6581 | 632.8231 | 772.0132 | 682.5315 | 679.7192 | 650.9051 | 605.9885
| 10% | 3385.0685 | 4970.5032 | 5364.1295 | 6290.4269 | 5574.7805 | 5754.0059 | 5488.3325 | 5147.3749 | 4223.7119 | 4958.9484 | 5024.1057 | 5048.814 | 4967.8486 | 4817.0833 | 4706.0748 | 4445.8629 | 3789.2028 | 2774.1162 | 4942.0987 | 3842.3034 | 6523.5749 | 4158.1491 | 4518.9896 | 4603.364
| 20% | 7076.7437 | 8036.617 | 8487.8308 | 9364.6678 | 8632.0028 | 8806.465 | 8531.6738 | 7916.2891 | 6485.0855 | 6825.4637 | 7066.4714 | 7073.5182 | 7030.7498 | 6913.6748 | 6748.8605 | 6399.8749 | 5650.7086 | 4493.1028 | 6828.715 | 6164.6748 | 8881.7487 | 6850.9051 | 7269.4419 | 7383.4871
| 30% | 10848.6515 | 11280.6678 | 11540.803 | 12338.4172 | 11748.2663 | 11904.2822 | 11429.4538 | 10790.1658 | 8920.7285 | 8377.5407 | 8748.6089 | 8859.9198 | 8812.3216 | 8684.9625 | 8493.8353 | 8176.505 | 7429.066 | 6486.731 | 8537.2439 | 8554.5708 | 10780.5341 | 9555.7698 | 10113.5503 | 10360.3698
| 40% | 14231.0819 | 14560.5244 | 14828.8193 | 15543.8027 | 14859.7653 | 15024.189 | 14538.7834 | 13684.614 | 11407.5334 | 9980.9754 | 10456.254 | 10570.2655 | 10550.0913 | 10468.7565 | 10325.9185 | 9923.0461 | 9396.9116 | 8708.3587 | 10242.8821 | 11215.5866 | 12558.9457 | 12650.9526 | 13184.5745 | 13627.0211
| 50% | 17580.7002 | 17795.9785 | 18024.4245 | 18727.832 | 18085.7775 | 18057.1785 | 17599.2936 | 16629.3999 | 14224.9219 | 11703.5655 | 12190.3024 | 12386.0098 | 12375.3151 | 12299.6906 | 12119.7205 | 11679.2032 | 11288.8111 | 11290.1503 | 12072.8195 | 14211.7373 | 14396.8505 | 15787.5343 | 16440.7498 | 16741.0417
| 60% | 20813.5679 | 20978.2616 | 21191.5565 | 21867.7776 | 21220.3054 | 21284.1167 | 20759.3588 | 19677.5691 | 17009.777 | 13542.75 | 14131.5484 | 14266.7532 | 14268.3729 | 14260.7085 | 14088.2399 | 13665.9804 | 13575.9722 | 14099.4656 | 14042.6736 | 17254.1411 | 16335.555 | 18983.1073 | 19551.9517 | 19989.8564
| 70% | 24026.3675 | 24142.7258 | 24208.784 | 24852.5423 | 24314.0223 | 24478.0003 | 23847.4172 | 22807.4704 | 19993.1438 | 15625.8739 | 16322.0299 | 16480.8509 | 16571.6399 | 16532.4852 | 16326.3715 | 15931.4812 | 15961.6047 | 17314.2734 | 16417.2171 | 20443.8924 | 18482.4873 | 22137.9303 | 22874.7878 | 23260.4052
| 80% | 27036.6751 | 27132.4507 | 27140.2322 | 27770.9685 | 27064.9007 | 27188.0663 | 26891.6259 | 25827.9998 | 23153.75 | 18355.993 | 19045.3709 | 19324.3478 | 19355.6827 | 19278.7581 | 19157.5898 | 18746.0829 | 18970.7514 | 21088.1967 | 19406.4691 | 23928.7903 | 21287.8703 | 25600.8478 | 26122.584 | 26294.3109
| 90% | 29772.0797 | 29692.8844 | 29647.6124 | 30365.3202 | 29653.7159 | 29746.2421 | 29388.0588 | 28633.9003 | 26505.7722 | 22182.1675 | 23073.3607 | 23378.2833 | 23471.5066 | 23572.9777 | 23420.0381 | 23037.1914 | 22708.0211 | 25226.1492 | 23532.6018 | 27518.4783 | 24784.5608 | 28514.6558 | 28989.3401 | 29180.4192
| 100% | 34913.3693 | 34766.8031 | 34602.0025 | 34908.2391 | 34627.0225 | 34768.3573 | 34564.0586 | 34210.5327 | 33305.8414 | 33089.2967 | 33078.6335 | 33658.8136 | 33766.6341 | 34076.1416 | 34027.2437 | 33964.0981 | 33470.8927 | 33979.804 | 33840.1408 | 34099.8789 | 34133.1419 | 34354.7213 | 34393.4827 | 34448.7221
Unplanned Thermal Outages-Daily, MW
| Percentiles | 1: Unplanned Thermal Outages
| 0% | 1: 9919
| 10% | 1: 13150
| 20% | 1: 14134
| 30% | 1: 14863
| 40% | 1: 15584
| 50% | 1: 16259
| 60% | 1: 16968
| 70% | 1: 17739
| 80% | 1: 18653
| 90% | 1: 19952
| 100% | 1: 23256

## Background
Background
Capacity Available for Operating Reserves (CAFOR)
CAFOR Formula: = Monthly Maximum Expected Resource Generation Capability – Demand – Thermal Outages + Pre-EEA Resources if CAFOR < 3,000 MW + EEA Resources if CAFOR < 2,500 MW Note that winter storm scenarios also account for incremental unplanned wind outages due to severe storm events. The synthetic wind profiles used in the Probabilistic Reserve Risk Model (PRRM) account for normal availability.
The MORA uses CAFOR reserve thresholds of 2,500 and 1,500 MW to indicate, respectively, the risk that an Energy Emergency Alert and controlled outages may be triggered during the time of the forecasted monthly peak load day. These threshold levels are intended to be proxies to the 2,500 and 1,500 MW Physical Responsive Capability (PRC) thresholds. While PRC is a real-time capability measure for Resources that can quickly respond to system disturbance, ERCOT believes that the 2,500 and 1,500 MW CAFOR thresholds are appropriate indicators for the risk of Emergency Conditions given the uncertainties in predicting system conditions months in advance.
Wind and Solar Capacity Values
Hourly capacity contributions for specific wind and solar capacity values come from hourly synthetic generation profiles prepared for existing sites and planned sites expected to generate power by the beginning of the month. Every site has multiple profiles representing hourly generation for each historical weather year going back to 1980. The profiles are used to develop hourly probability distributions for the Probabilistic Reserve Risk Model.
Probabilistic Modeling
For MORA development, ERCOT uses an in-house-developed model called the Probabilistic Reserve Risk Model (PRRM). The model uses Monte Carlo simulation techniques to generate 10,000 outcomes for Capacity Available for Operating Reserves (CAFOR). The model incorporates hourly risk variables, which are the load and resource-specific capacity amounts expressed as hourly or daily probability distributions based on historical data and forecast assumptions.
The risk variables comprise the following:
● | Monthly Peak Load - The Peak load variable is negatively correlated with a system-average temperature probability distribution. (For the winter months, the lower the temperature selected by the model for a simulation, the higher the peak load selected.) The model also uses multiple normalized hourly load shapes to simulate loads for the hourly range; load shapes reflect actual hourly loads for historical monthly peak load days.
● | Wind Production - Hourly probability distributions are fitted to hourly synthetic production profiles. Profiles are developed for each operational and planned wind site with wind output values aggregated to system values. The profiles reflect weather-year variability back to 1980. Temporal correlations between hourly probability distributions are applied to simulate hourly wind speed persistence effects. Note that synthetic wind profiles do not reflect actual observed generation. They are based on meteorological and power conversion models that together simulate what wind production would be for existing and planned sites at the start of the month based on historical hourly weather patterns.
● | Solar Production - Hourly probability distributions are fitted to hourly synthetic production profiles lust like wind. Temporal correlations between hourly probability distributions are applied to simulate hourly solar irradiance persistence effects. Note that synthetic solar profiles do not reflect actual observed generation. They are based on meteorological and power conversion models that together simulate what solar production would be for the existing and planned sites at the start of the month based on historical hourly weather patterns.
● | Low Ambient Temperature Curve - A range of hourly average Texas-wide low temperatures (for the winter months). The low temperature probability distribution is correlated with both the peak load and cold-weather-related thermal outage probability distributions.
● | Typical Unplanned Thermal Outages based on Normal Weather - A range of daily unplanned outage amounts based on assessment month history for the past three years. For the winter months, outages during major winter storms are excluded from the probability distributions.
● | Extreme-Weather-Related Thermal Outages - For the winter months, the probability distribution reflects a range of daily unplanned weather-related outage amounts scaled from zero MW to the maximum amount observed during Winter Storm Uri. The probability distribution is correlated with the Low Ambient Temperature curve.
● | Switchable Generation Resources Currently Serving Neighoring Grids - The model includes individual probability distributions for each SWGR currently serving customers in the Southwest Power Pool that are able to switch to ERCOT if allowed based on prevailing power supply contracts. Such SWGRs are designated as the "Controlling Party" in the most current ERCOT-SPP Coordination Plan. (The Plan is consistent with the "Notices of Unavailable Capacity for Switchable Generation Resources" provided to ERCOT.) The probability distributions are binary—each unit is made available or not, with the probability of being available based on analysis of Current Operating Plan (COP) data covering Winter Storm Elliott and the EEA event on November 6, 2023. This variable is treated an available Pre-EEA resource in the model, and assumes that this SWGR capacity may be available if requested by ERCOT to address an Energy Emergency.
● | Remaining Non-Synchronous Tie Transfers - The model uses the DC Tie capacity contribution amounts cited in recent Capacity, Demand and Reserves (CDR) reports as the base amounts. A probability distribution represents the remaining transfer capability that may be available during an ERCOT Energy Emergency. This variable is treated is an available Pre-EEA resource in the model.
● | Weather-related Outage Reduction Success Rate due to Weatherization - The model uses a triangular probability distribution to reflect a percentage range of outage reduction amounts, currently set to a likeliest value of 85% and minimum and maximum values of 80% and 90%, respectively. The probability distribution will be modified as actual success rate data is accumulated over time.
The model also includes several resource variables that are not associated with probability distributions, but are dynamic in that their capacity values are dependent on other variable values calculated by the model. These include the following:
● | Battery Energy Storage Capacity Contribution - ERCOT calculates the battery storage capacity contribution based on an analysis of SCADA High Sustained Limit (HSL) and State of Charge (SOC) data. Values for all hours are based on SOCs observed for historical representative days in the given month, and are expressed as capacity factors using the expected installed capacity for the start of the forecast month. For non-winter months, the capacity factors will assume an hourly shape similar to the September 6, 2023 EEA2 day if the system peak net load reaches a high threshold level. For winter MORA reports, which account for severe winter storm conditions, the values are based on SOCs observed during Winter Storm Elliott (December 22-23, 2022).
● | Incremental Demand Response - The ERCOT load forecast model accounts for historical demand response impacts. An amount reflecting additional response during high load conditions is selected by the model. Once the hourly loads exceed a given high percentile value, the model selects a fixed amount. The amounts are based on analysis conducted by ERCOT's Market Analysis & Validation Department staff.
● | Private Use Network (PUN) Generator Injection - PUN generator injection comes from hourly historical MW output levels for the assessment months from the last three years. For winter months, the model will also add an incremental amount of PUN generator capacity when the model selects an extremely low temperature, indicative of system stress conditions and opportunities for the PUN owners to take advantage of high market prices.
Estimating Peak Electricity Consumption for Operational Large Flexible Loads
Due to a new influx of Large Flexible Loads (LFLs), an interim solution was implemented to better account for the peak consumption of these loads. The new interim methodology utilizes the 7 hours over each of the past three months of January with the lowest average Physical Responsive Capability and compares historical load zone prices to an ERCOT determined (and industry backed) estimate of the bitcoin mining breakeven cost. This breakeven cost was estimated at $58.4/MWh and is based on the average specifications of an Antminer S19j Pro bitcoin mining rig and a hashprice of 42.75 USD per PH/s/Day as indicated on the Luxor Hashrate Forward Curve for January 2025. If the historical load zone price for the LFL's respective load zone was below the breakeven threshold then the load's peak September consumption was estimated to be the maximum observed consumption at the site according to internal tracking of LFL projects. If the historical load zone price was greater than the breakeven threshold then the LFL was assumed to be fully curtailed and consuming only 3% of the load's maximum capability. The 3% assumption accounts for the idle power draw of ASIC miners and necessary auxiliary cooling on site. The estimated consumption for each LFL, including both co-located and stand-alone loads, was summed for each of the 21 hours analyzed and then averaged to calculate the total estimated average consumption.
Note that roughly every four years the Bitcoin industry undergoes a halving of the reward for mining Bitcoins. Each halving event for the "mining block reward" reduces the amount of new Bitcoin supplies. While a halving event can increase Bitcoin prices in the near term, the overall impact is to reduce mining revenues and incentivize miners to reduce electricity consumption during times of high prices. Price-responsive Bitcoin miners, exposed to the real-time price of electricity, are anticipated to curtail more frequently and at lower breakeven costs following the halving event. Consequently, a significantly smaller amount of operational large flexible load is expected to be consuming electricity during reserve “at risk” hours on average. Note that synthetic profiles are not actual history. They are based on meteorlogical and power curve models that together simulate what wind production would be for each eisting and planned wind site at the start of month based on historical hourly weather patterns.
Large Load Adjustment for the Load Forecast
The original load forecast used for the MORA reports includes an estimate of Large Load electricity consumption. This Large Load estimate excludes the impact of expected future price responsive behavior except for the summer months when Large Loads take advantage of "4 Coincident Peak" (4CP) demand charge savings programs. To provide a timely Large Load consumption forecast estimate that accounts for price responsive behavior during all forecast months, ERCOT's Large Load Integration Department prepares a Large Load consumption adjustment for the MORA reports. This adjustment replaces the original Large Load consumption estimate that accompanies the monthly load forecast.
Modeling of Coastal Wind Generation Curtailment due to New Generic Transmission Constraints
A new contributor to reserve shortage risk is the potential need, under certain grid conditions, to limit power transfers from South Texas into the San Antonio region. Conditions could cause overloads on the lines that make up the South Texas export and import interfaces, necessitating South Texas generation curtailments and potential firm load shedding to avoid cascading outages. The risk is greatest when the ERCOT Region has extremely high net loads in the early evening hours. This issue will be addressed with mitigation measures including the construction of the San Antonio South Reliability Project, which is anticipated to be completed by Summer 2027. To model this generation curtailment risk, ERCOT evaluated the net load and coastal wind curtailment conditions at the time of the November 6th, 2023, Energy Emergency Alert event. To simulate the risk of a similar event, the PRRM was modified in the following ways: 1. Synthetic wind profiles by site were divided into Coastal and Non-coastal aggregation categories, and hourly probability distributions were developed accounting for time-coincident correlations between Non-coastal and Coastal hourly wind generation. 2. With the South Texas wind curtailment functionality turned on, the model will curtail coastal wind generation when (1) total system net load for a given hour reaches a trigger amount, expressed as a percentage of the gross load, and (2) unplanned thermal outages for the hour exceed a trigger amount. Analysis of net load and unplanned thermal outages at the time of the November 6, 2023, EEA event was used to determine the two trigger criteria. 3. CPS Energy is increasing line clearances to provide an Emergency & Loadshed Rating different than the Normal Rating. The rating changes should allow for an additional ~550 MW of generation South of the Interconnection Reliability Operating Limit (IROL). The amount of coastal wind curtailment has been reduced by this amount.