## 2024 RRS Table
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
(MW)
*RRS Curr IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
| Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:01 | 1:01 | 1:01 | 1:01 | 1:01
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068

## 2024_RRS
2024 RRS (Floor = 2300 MW for all hours, new minimum RRS-PFR limit =1185 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov | Dec
1 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342 | 2491 | 2808 | 2998 | 2916
2 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342 | 2491 | 2808 | 2998 | 2916
3 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373 | 2529 | 2880 | 2998 | 2916
4 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373 | 2529 | 2880 | 2998 | 2916
5 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373 | 2529 | 2880 | 2998 | 2916
6 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373 | 2529 | 2880 | 2998 | 2916
7 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342 | 2491 | 2808 | 2960 | 2808
8 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342 | 2491 | 2808 | 2960 | 2808
9 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342 | 2491 | 2808 | 2960 | 2808
10 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342 | 2491 | 2808 | 2960 | 2808
11 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300 | 2373 | 2716 | 2916 | 2808
12 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300 | 2373 | 2716 | 2916 | 2808
13 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300 | 2373 | 2716 | 2916 | 2808
14 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300 | 2373 | 2716 | 2916 | 2808
15 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
16 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
17 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
18 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
19 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
20 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
21 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
22 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300 | 2300 | 2606 | 2880 | 2716
23 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342 | 2491 | 2808 | 2998 | 2916
24 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342 | 2491 | 2808 | 2998 | 2916
Total | 70816 | 70816 | 74112 | 72080 | 63928 | 58088 | 56988 | 55828 | 57936 | 65696 | 70528 | 67520
These 2024 quantities above are based on the 2024 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1185 MW and a floor of 2300 MW for all hours. Note that, NERC’s 2023 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that was approved as a part of the Project 2017-01, Modifications to BAL-003. As a result of this ERCOT the minimum RRS-PFR limit for 2023 has been changed to align with ERCOT's new IFRO.

## 2024_RRS_Details
2024-01-01 | [5 empty] | 2024-02-01 | [5 empty] | 2024-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 1 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 2 | 3178 | 1271 | 1907 | 2.06 | 60.01%
3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 3 | 3178 | 1271 | 1907 | 2.06 | 60.01%
4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4 | 3178 | 1271 | 1907 | 2.06 | 60.01%
5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 5 | 3178 | 1271 | 1907 | 2.06 | 60.01%
6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 6 | 3178 | 1271 | 1907 | 2.06 | 60.01%
7 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 7 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 7 | 3128 | 1251 | 1877 | 1.94 | 60.01%
8 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 8 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 8 | 3128 | 1251 | 1877 | 1.94 | 60.01%
9 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 9 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 9 | 3128 | 1251 | 1877 | 1.94 | 60.01%
10 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 10 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 10 | 3128 | 1251 | 1877 | 1.94 | 60.01%
11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 3086 | 1234 | 1852 | 1.83 | 60.01%
12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 3086 | 1234 | 1852 | 1.83 | 60.01%
13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 3086 | 1234 | 1852 | 1.83 | 60.01%
14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 3086 | 1234 | 1852 | 1.83 | 60.01%
15 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 15 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 15 | 2998 | 1199 | 1799 | 1.74 | 60.01%
16 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 16 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 16 | 2998 | 1199 | 1799 | 1.74 | 60.01%
17 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 17 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 17 | 2998 | 1199 | 1799 | 1.74 | 60.01%
18 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 18 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 18 | 2998 | 1199 | 1799 | 1.74 | 60.01%
19 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 19 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 19 | 2960 | 1185 | 1775 | 1.65 | 59.97%
20 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 20 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 20 | 2960 | 1185 | 1775 | 1.65 | 59.97%
21 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 21 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 21 | 2960 | 1185 | 1775 | 1.65 | 59.97%
22 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 22 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 22 | 2960 | 1185 | 1775 | 1.65 | 59.97%
23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 23 | 3178 | 1271 | 1907 | 2.06 | 60.01%
24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 24 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2024-04-01 | [5 empty] | 2024-05-01 | [5 empty] | 2024-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 1 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 1 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 2 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 2 | 2491 | 1185 | 1306 | 1.15 | 52.43%
3 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 3 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 3 | 2560 | 1185 | 1375 | 1.24 | 53.71%
4 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 4 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 4 | 2560 | 1185 | 1375 | 1.24 | 53.71%
5 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 5 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 5 | 2560 | 1185 | 1375 | 1.24 | 53.71%
6 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 6 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 6 | 2560 | 1185 | 1375 | 1.24 | 53.71%
7 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 7 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 7 | 2529 | 1185 | 1344 | 1.19 | 53.14%
8 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 8 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 8 | 2529 | 1185 | 1344 | 1.19 | 53.14%
9 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 9 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 9 | 2529 | 1185 | 1344 | 1.19 | 53.14%
10 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 10 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 10 | 2529 | 1185 | 1344 | 1.19 | 53.14%
11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 11 | 2342 | 1185 | 1157 | 1.01 | 49.4%
12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 12 | 2342 | 1185 | 1157 | 1.01 | 49.4%
13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 13 | 2342 | 1185 | 1157 | 1.01 | 49.4%
14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 14 | 2342 | 1185 | 1157 | 1.01 | 49.4%
15 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 15 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 15 | 2300 | 1185 | 1115 | 1 | 48.48%
16 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 16 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 16 | 2300 | 1185 | 1115 | 1 | 48.48%
17 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 17 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 17 | 2300 | 1185 | 1115 | 1 | 48.48%
18 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 18 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 18 | 2300 | 1185 | 1115 | 1 | 48.48%
19 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 19 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 19 | 2300 | 1185 | 1115 | 1 | 48.48%
20 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 20 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 20 | 2300 | 1185 | 1115 | 1 | 48.48%
21 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 21 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 21 | 2300 | 1185 | 1115 | 1 | 48.48%
22 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 22 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 22 | 2300 | 1185 | 1115 | 1 | 48.48%
23 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 23 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 23 | 2491 | 1185 | 1306 | 1.15 | 52.43%
24 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 24 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 24 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2024-07-01 | [5 empty] | 2024-08-01 | [5 empty] | 2024-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 1 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 1 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 2 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 2 | 2491 | 1185 | 1306 | 1.15 | 52.43%
3 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 3 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 3 | 2529 | 1185 | 1344 | 1.19 | 53.14%
4 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 4 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 4 | 2529 | 1185 | 1344 | 1.19 | 53.14%
5 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 5 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 5 | 2529 | 1185 | 1344 | 1.19 | 53.14%
6 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 6 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 6 | 2529 | 1185 | 1344 | 1.19 | 53.14%
7 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 7 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 7 | 2491 | 1185 | 1306 | 1.15 | 52.43%
8 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 8 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 8 | 2491 | 1185 | 1306 | 1.15 | 52.43%
9 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 9 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 9 | 2491 | 1185 | 1306 | 1.15 | 52.43%
10 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 10 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 10 | 2491 | 1185 | 1306 | 1.15 | 52.43%
11 | 2300 | 1185 | 1115 | 1 | 48.48% | 11 | 2300 | 1185 | 1115 | 1 | 48.48% | 11 | 2373 | 1185 | 1188 | 1.04 | 50.06%
12 | 2300 | 1185 | 1115 | 1 | 48.48% | 12 | 2300 | 1185 | 1115 | 1 | 48.48% | 12 | 2373 | 1185 | 1188 | 1.04 | 50.06%
13 | 2300 | 1185 | 1115 | 1 | 48.48% | 13 | 2300 | 1185 | 1115 | 1 | 48.48% | 13 | 2373 | 1185 | 1188 | 1.04 | 50.06%
14 | 2300 | 1185 | 1115 | 1 | 48.48% | 14 | 2300 | 1185 | 1115 | 1 | 48.48% | 14 | 2373 | 1185 | 1188 | 1.04 | 50.06%
15 | 2300 | 1185 | 1115 | 1 | 48.48% | 15 | 2300 | 1185 | 1115 | 1 | 48.48% | 15 | 2300 | 1185 | 1115 | 1 | 48.48%
16 | 2300 | 1185 | 1115 | 1 | 48.48% | 16 | 2300 | 1185 | 1115 | 1 | 48.48% | 16 | 2300 | 1185 | 1115 | 1 | 48.48%
17 | 2300 | 1185 | 1115 | 1 | 48.48% | 17 | 2300 | 1185 | 1115 | 1 | 48.48% | 17 | 2300 | 1185 | 1115 | 1 | 48.48%
18 | 2300 | 1185 | 1115 | 1 | 48.48% | 18 | 2300 | 1185 | 1115 | 1 | 48.48% | 18 | 2300 | 1185 | 1115 | 1 | 48.48%
19 | 2300 | 1185 | 1115 | 1 | 48.48% | 19 | 2300 | 1185 | 1115 | 1 | 48.48% | 19 | 2300 | 1185 | 1115 | 1 | 48.48%
20 | 2300 | 1185 | 1115 | 1 | 48.48% | 20 | 2300 | 1185 | 1115 | 1 | 48.48% | 20 | 2300 | 1185 | 1115 | 1 | 48.48%
21 | 2300 | 1185 | 1115 | 1 | 48.48% | 21 | 2300 | 1185 | 1115 | 1 | 48.48% | 21 | 2300 | 1185 | 1115 | 1 | 48.48%
22 | 2300 | 1185 | 1115 | 1 | 48.48% | 22 | 2300 | 1185 | 1115 | 1 | 48.48% | 22 | 2300 | 1185 | 1115 | 1 | 48.48%
23 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 23 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 23 | 2491 | 1185 | 1306 | 1.15 | 52.43%
24 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 24 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 24 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2024-10-01 | [5 empty] | 2024-11-01 | [5 empty] | 2024-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 1 | 2916 | 1185 | 1731 | 1.58 | 59.36%
2 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 2 | 2916 | 1185 | 1731 | 1.58 | 59.36%
3 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 3 | 2916 | 1185 | 1731 | 1.58 | 59.36%
4 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4 | 2916 | 1185 | 1731 | 1.58 | 59.36%
5 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 5 | 2916 | 1185 | 1731 | 1.58 | 59.36%
6 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 6 | 2916 | 1185 | 1731 | 1.58 | 59.36%
7 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 7 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 7 | 2808 | 1185 | 1623 | 1.44 | 57.8%
8 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 8 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 8 | 2808 | 1185 | 1623 | 1.44 | 57.8%
9 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 9 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 9 | 2808 | 1185 | 1623 | 1.44 | 57.8%
10 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 10 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 10 | 2808 | 1185 | 1623 | 1.44 | 57.8%
11 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 11 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 11 | 2808 | 1185 | 1623 | 1.44 | 57.8%
12 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 12 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 12 | 2808 | 1185 | 1623 | 1.44 | 57.8%
13 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 13 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 13 | 2808 | 1185 | 1623 | 1.44 | 57.8%
14 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 14 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 14 | 2808 | 1185 | 1623 | 1.44 | 57.8%
15 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 15 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 15 | 2716 | 1185 | 1531 | 1.39 | 56.37%
16 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 16 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 16 | 2716 | 1185 | 1531 | 1.39 | 56.37%
17 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 17 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 17 | 2716 | 1185 | 1531 | 1.39 | 56.37%
18 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 18 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 18 | 2716 | 1185 | 1531 | 1.39 | 56.37%
19 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 19 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 19 | 2716 | 1185 | 1531 | 1.39 | 56.37%
20 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 20 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 20 | 2716 | 1185 | 1531 | 1.39 | 56.37%
21 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 21 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 21 | 2716 | 1185 | 1531 | 1.39 | 56.37%
22 | 2606 | 1185 | 1421 | 1.28 | 54.53% | 22 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 22 | 2716 | 1185 | 1531 | 1.39 | 56.37%
23 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 23 | 2916 | 1185 | 1731 | 1.58 | 59.36%
24 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 24 | 2916 | 1185 | 1731 | 1.58 | 59.36%

## 2025 RRS Table
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
(MW)
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
**RRS Upd IFRO (MW) | 3320 | 3273 | 3227 | 3183 | 3145 | 3068 | 3031 | 2982 | 2941 | 2863 | 2767 | 2699
| Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:01 | 1:01 | 1:01 | 1:01 | 1:01
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2645 | 2595 | 2558 | 2514 | 2463 | 2425 | 2380 | 2343 | 2290 | 2230 | 2173 | 2119 | 2068

## 2025_RRS
2025 RRS (Floor = 2300 MW for all hours, new minimum RRS-PFR limit =1365 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 3031 | 3145 | 3145 | 3068 | 2699 | 2463 | 2380 | 2300 | 2425 | 2863
2 | 3031 | 3145 | 3145 | 3068 | 2699 | 2463 | 2380 | 2300 | 2425 | 2863
3 | 2982 | 3145 | 3145 | 3145 | 2699 | 2514 | 2463 | 2300 | 2463 | 2863
4 | 2982 | 3145 | 3145 | 3145 | 2699 | 2514 | 2463 | 2300 | 2463 | 2863
5 | 2982 | 3145 | 3145 | 3145 | 2699 | 2514 | 2463 | 2300 | 2463 | 2863
6 | 2982 | 3145 | 3145 | 3145 | 2699 | 2514 | 2463 | 2300 | 2463 | 2863
7 | 2863 | 3068 | 3068 | 3068 | 2699 | 2514 | 2425 | 2300 | 2425 | 2863
8 | 2863 | 3068 | 3068 | 3068 | 2699 | 2514 | 2425 | 2300 | 2425 | 2863
9 | 2863 | 3068 | 3068 | 3068 | 2699 | 2514 | 2425 | 2300 | 2425 | 2863
10 | 2863 | 3068 | 3068 | 3068 | 2699 | 2514 | 2425 | 2300 | 2425 | 2863
11 | 2941 | 3068 | 3068 | 3068 | 2595 | 2425 | 2300 | 2300 | 2380 | 2767
12 | 2941 | 3068 | 3068 | 3068 | 2595 | 2425 | 2300 | 2300 | 2380 | 2767
13 | 2941 | 3068 | 3068 | 3068 | 2595 | 2425 | 2300 | 2300 | 2380 | 2767
14 | 2941 | 3068 | 3068 | 3068 | 2595 | 2425 | 2300 | 2300 | 2380 | 2767
15 | 2767 | 3031 | 2982 | 2982 | 2558 | 2380 | 2300 | 2300 | 2343 | 2645
16 | 2767 | 3031 | 2982 | 2982 | 2558 | 2380 | 2300 | 2300 | 2343 | 2645
17 | 2767 | 3031 | 2982 | 2982 | 2558 | 2380 | 2300 | 2300 | 2343 | 2645
18 | 2767 | 3031 | 2982 | 2982 | 2558 | 2380 | 2300 | 2300 | 2343 | 2645
19 | 2767 | 2982 | 2982 | 2941 | 2558 | 2343 | 2300 | 2300 | 2300 | 2595
20 | 2767 | 2982 | 2982 | 2941 | 2558 | 2343 | 2300 | 2300 | 2300 | 2595
21 | 2767 | 2982 | 2982 | 2941 | 2558 | 2343 | 2300 | 2300 | 2300 | 2595
22 | 2767 | 2982 | 2982 | 2941 | 2558 | 2343 | 2300 | 2300 | 2300 | 2595
23 | 3031 | 3145 | 3145 | 3068 | 2699 | 2463 | 2380 | 2300 | 2425 | 2863
24 | 3031 | 3145 | 3145 | 3068 | 2699 | 2463 | 2380 | 2300 | 2425 | 2863
Total | 69404 | 73756 | 73560 | 73088 | 63232 | 58556 | 56672 | 55200 | 57344 | 66384 | 0 | 0
These preliminary 2025 quantities above are based on the 2025 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1365 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2025 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2025 will change to align with ERCOT's new IFRO.

## 2025_RRS_Details
2025-01-01 | [5 empty] | 2025-02-01 | [5 empty] | 2025-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 1 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 1 | 3145 | 1365 | 1780 | 1.83 | 56.6%
2 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 2 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 2 | 3145 | 1365 | 1780 | 1.83 | 56.6%
3 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 3 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 3 | 3145 | 1365 | 1780 | 1.83 | 56.6%
4 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 4 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 4 | 3145 | 1365 | 1780 | 1.83 | 56.6%
5 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 5 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 5 | 3145 | 1365 | 1780 | 1.83 | 56.6%
6 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 6 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 6 | 3145 | 1365 | 1780 | 1.83 | 56.6%
7 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 7 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 7 | 3068 | 1365 | 1703 | 1.74 | 55.51%
8 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 8 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 8 | 3068 | 1365 | 1703 | 1.74 | 55.51%
9 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 9 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 9 | 3068 | 1365 | 1703 | 1.74 | 55.51%
10 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 10 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 10 | 3068 | 1365 | 1703 | 1.74 | 55.51%
11 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 11 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 11 | 3068 | 1365 | 1703 | 1.74 | 55.51%
12 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 12 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 12 | 3068 | 1365 | 1703 | 1.74 | 55.51%
13 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 13 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 13 | 3068 | 1365 | 1703 | 1.74 | 55.51%
14 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 14 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 14 | 3068 | 1365 | 1703 | 1.74 | 55.51%
15 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 15 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 15 | 2982 | 1365 | 1617 | 1.58 | 54.23%
16 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 16 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 16 | 2982 | 1365 | 1617 | 1.58 | 54.23%
17 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 17 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 17 | 2982 | 1365 | 1617 | 1.58 | 54.23%
18 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 18 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 18 | 2982 | 1365 | 1617 | 1.58 | 54.23%
19 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 19 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 19 | 2982 | 1365 | 1617 | 1.58 | 54.23%
20 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 20 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 20 | 2982 | 1365 | 1617 | 1.58 | 54.23%
21 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 21 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 21 | 2982 | 1365 | 1617 | 1.58 | 54.23%
22 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 22 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 22 | 2982 | 1365 | 1617 | 1.58 | 54.23%
23 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 23 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 23 | 3145 | 1365 | 1780 | 1.83 | 56.6%
24 | 3031 | 1365 | 1666 | 1.65 | 54.97% | 24 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 24 | 3145 | 1365 | 1780 | 1.83 | 56.6%
2025-04-01 | [5 empty] | 2025-05-01 | [5 empty] | 2025-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 1 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 1 | 2463 | 1365 | 1098 | 1.12 | 44.58%
2 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 2 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 2 | 2463 | 1365 | 1098 | 1.12 | 44.58%
3 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 3 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 3 | 2514 | 1365 | 1149 | 1.15 | 45.7%
4 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 4 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 4 | 2514 | 1365 | 1149 | 1.15 | 45.7%
5 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 5 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 5 | 2514 | 1365 | 1149 | 1.15 | 45.7%
6 | 3145 | 1365 | 1780 | 1.83 | 56.6% | 6 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 6 | 2514 | 1365 | 1149 | 1.15 | 45.7%
7 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 7 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 7 | 2514 | 1365 | 1149 | 1.15 | 45.7%
8 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 8 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 8 | 2514 | 1365 | 1149 | 1.15 | 45.7%
9 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 9 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 9 | 2514 | 1365 | 1149 | 1.15 | 45.7%
10 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 10 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 10 | 2514 | 1365 | 1149 | 1.15 | 45.7%
11 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 11 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 11 | 2425 | 1365 | 1060 | 1.08 | 43.71%
12 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 12 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 12 | 2425 | 1365 | 1060 | 1.08 | 43.71%
13 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 13 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 13 | 2425 | 1365 | 1060 | 1.08 | 43.71%
14 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 14 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 14 | 2425 | 1365 | 1060 | 1.08 | 43.71%
15 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 15 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 15 | 2380 | 1365 | 1015 | 1.04 | 42.65%
16 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 16 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 16 | 2380 | 1365 | 1015 | 1.04 | 42.65%
17 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 17 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 17 | 2380 | 1365 | 1015 | 1.04 | 42.65%
18 | 2982 | 1365 | 1617 | 1.58 | 54.23% | 18 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 18 | 2380 | 1365 | 1015 | 1.04 | 42.65%
19 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 19 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 19 | 2343 | 1365 | 978 | 1.01 | 41.74%
20 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 20 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 20 | 2343 | 1365 | 978 | 1.01 | 41.74%
21 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 21 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 21 | 2343 | 1365 | 978 | 1.01 | 41.74%
22 | 2941 | 1365 | 1576 | 1.51 | 53.59% | 22 | 2558 | 1365 | 1193 | 1.19 | 46.64% | 22 | 2343 | 1365 | 978 | 1.01 | 41.74%
23 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 23 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 23 | 2463 | 1365 | 1098 | 1.12 | 44.58%
24 | 3068 | 1365 | 1703 | 1.74 | 55.51% | 24 | 2699 | 1365 | 1334 | 1.33 | 49.43% | 24 | 2463 | 1365 | 1098 | 1.12 | 44.58%
2025-07-01 | [5 empty] | 2025-08-01 | [5 empty] | 2025-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2380 | 1365 | 1015 | 1.04 | 42.65% | 1 | 2300 | 1365 | 935 | 1 | 40.65% | 1 | 2425 | 1365 | 1060 | 1.08 | 43.71%
2 | 2380 | 1365 | 1015 | 1.04 | 42.65% | 2 | 2300 | 1365 | 935 | 1 | 40.65% | 2 | 2425 | 1365 | 1060 | 1.08 | 43.71%
3 | 2463 | 1365 | 1098 | 1.12 | 44.58% | 3 | 2300 | 1365 | 935 | 1 | 40.65% | 3 | 2463 | 1365 | 1098 | 1.12 | 44.58%
4 | 2463 | 1365 | 1098 | 1.12 | 44.58% | 4 | 2300 | 1365 | 935 | 1 | 40.65% | 4 | 2463 | 1365 | 1098 | 1.12 | 44.58%
5 | 2463 | 1365 | 1098 | 1.12 | 44.58% | 5 | 2300 | 1365 | 935 | 1 | 40.65% | 5 | 2463 | 1365 | 1098 | 1.12 | 44.58%
6 | 2463 | 1365 | 1098 | 1.12 | 44.58% | 6 | 2300 | 1365 | 935 | 1 | 40.65% | 6 | 2463 | 1365 | 1098 | 1.12 | 44.58%
7 | 2425 | 1365 | 1060 | 1.08 | 43.71% | 7 | 2300 | 1365 | 935 | 1 | 40.65% | 7 | 2425 | 1365 | 1060 | 1.08 | 43.71%
8 | 2425 | 1365 | 1060 | 1.08 | 43.71% | 8 | 2300 | 1365 | 935 | 1 | 40.65% | 8 | 2425 | 1365 | 1060 | 1.08 | 43.71%
9 | 2425 | 1365 | 1060 | 1.08 | 43.71% | 9 | 2300 | 1365 | 935 | 1 | 40.65% | 9 | 2425 | 1365 | 1060 | 1.08 | 43.71%
10 | 2425 | 1365 | 1060 | 1.08 | 43.71% | 10 | 2300 | 1365 | 935 | 1 | 40.65% | 10 | 2425 | 1365 | 1060 | 1.08 | 43.71%
11 | 2300 | 1365 | 935 | 1 | 40.65% | 11 | 2300 | 1365 | 935 | 1 | 40.65% | 11 | 2380 | 1365 | 1015 | 1.04 | 42.65%
12 | 2300 | 1365 | 935 | 1 | 40.65% | 12 | 2300 | 1365 | 935 | 1 | 40.65% | 12 | 2380 | 1365 | 1015 | 1.04 | 42.65%
13 | 2300 | 1365 | 935 | 1 | 40.65% | 13 | 2300 | 1365 | 935 | 1 | 40.65% | 13 | 2380 | 1365 | 1015 | 1.04 | 42.65%
14 | 2300 | 1365 | 935 | 1 | 40.65% | 14 | 2300 | 1365 | 935 | 1 | 40.65% | 14 | 2380 | 1365 | 1015 | 1.04 | 42.65%
15 | 2300 | 1365 | 935 | 1 | 40.65% | 15 | 2300 | 1365 | 935 | 1 | 40.65% | 15 | 2343 | 1365 | 978 | 1.01 | 41.74%
16 | 2300 | 1365 | 935 | 1 | 40.65% | 16 | 2300 | 1365 | 935 | 1 | 40.65% | 16 | 2343 | 1365 | 978 | 1.01 | 41.74%
17 | 2300 | 1365 | 935 | 1 | 40.65% | 17 | 2300 | 1365 | 935 | 1 | 40.65% | 17 | 2343 | 1365 | 978 | 1.01 | 41.74%
18 | 2300 | 1365 | 935 | 1 | 40.65% | 18 | 2300 | 1365 | 935 | 1 | 40.65% | 18 | 2343 | 1365 | 978 | 1.01 | 41.74%
19 | 2300 | 1365 | 935 | 1 | 40.65% | 19 | 2300 | 1365 | 935 | 1 | 40.65% | 19 | 2300 | 1365 | 935 | 1 | 40.65%
20 | 2300 | 1365 | 935 | 1 | 40.65% | 20 | 2300 | 1365 | 935 | 1 | 40.65% | 20 | 2300 | 1365 | 935 | 1 | 40.65%
21 | 2300 | 1365 | 935 | 1 | 40.65% | 21 | 2300 | 1365 | 935 | 1 | 40.65% | 21 | 2300 | 1365 | 935 | 1 | 40.65%
22 | 2300 | 1365 | 935 | 1 | 40.65% | 22 | 2300 | 1365 | 935 | 1 | 40.65% | 22 | 2300 | 1365 | 935 | 1 | 40.65%
23 | 2380 | 1365 | 1015 | 1.04 | 42.65% | 23 | 2300 | 1365 | 935 | 1 | 40.65% | 23 | 2425 | 1365 | 1060 | 1.08 | 43.71%
24 | 2380 | 1365 | 1015 | 1.04 | 42.65% | 24 | 2300 | 1365 | 935 | 1 | 40.65% | 24 | 2425 | 1365 | 1060 | 1.08 | 43.71%
2025-10-01 | [5 empty] | 2025-11-01 | [5 empty] | 2025-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 1 | [5 empty] | 1
2 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 2 | [5 empty] | 2
3 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 3 | [5 empty] | 3
4 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 4 | [5 empty] | 4
5 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 5 | [5 empty] | 5
6 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 6 | [5 empty] | 6
7 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 7 | [5 empty] | 7
8 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 8 | [5 empty] | 8
9 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 9 | [5 empty] | 9
10 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 10 | [5 empty] | 10
11 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 11 | [5 empty] | 11
12 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 12 | [5 empty] | 12
13 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 13 | [5 empty] | 13
14 | 2767 | 1365 | 1402 | 1.39 | 50.67% | 14 | [5 empty] | 14
15 | 2645 | 1365 | 1280 | 1.28 | 48.39% | 15 | [5 empty] | 15
16 | 2645 | 1365 | 1280 | 1.28 | 48.39% | 16 | [5 empty] | 16
17 | 2645 | 1365 | 1280 | 1.28 | 48.39% | 17 | [5 empty] | 17
18 | 2645 | 1365 | 1280 | 1.28 | 48.39% | 18 | [5 empty] | 18
19 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 19 | [5 empty] | 19
20 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 20 | [5 empty] | 20
21 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 21 | [5 empty] | 21
22 | 2595 | 1365 | 1230 | 1.24 | 47.4% | 22 | [5 empty] | 22
23 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 23 | [5 empty] | 23
24 | 2863 | 1365 | 1498 | 1.44 | 52.32% | 24 | [5 empty] | 24

## Charts
Month | Group | HE | Type | 2024 RRS | 2025 RRS | Month | Oct |  | Responsive Reserve Requirement Comparison for October
Jan | a. HE1-2 & HE23-24 | 1 | RRS | 2998 | 3031 | Type | RRS |  | Range: 2595 MW - 2863 MW; Avg: 2766 MW (29 MW increase from prev year)
Jan | a. HE1-2 & HE23-24 | 2 | RRS | 2998 | 3031
Jan | b. HE3-6 | 3 | RRS | 2998 | 2982 | Row Labels | 2024 RRS | 2025 RRS |  | min | 2595
Jan | b. HE3-6 | 4 | RRS | 2998 | 2982 | a. HE1-2 & HE23-24 | 2808 | 2863 |  | max | 2863
Jan | b. HE3-6 | 5 | RRS | 2998 | 2982 | b. HE3-6 | 2880 | 2863 |  | avg | 2766
Jan | b. HE3-6 | 6 | RRS | 2998 | 2982 | c. HE7-10 | 2808 | 2863 |  | Change | 29
Jan | c. HE7-10 | 7 | RRS | 2916 | 2863 | d. HE11-14 | 2716 | 2767
Jan | c. HE7-10 | 8 | RRS | 2916 | 2863 | e. HE15-18 | 2606 | 2645
Jan | c. HE7-10 | 9 | RRS | 2916 | 2863 | f. HE19-22 | 2606 | 2595
Jan | c. HE7-10 | 10 | RRS | 2916 | 2863
Jan | d. HE11-14 | 11 | RRS | 2960 | 2941
Jan | d. HE11-14 | 12 | RRS | 2960 | 2941
Jan | d. HE11-14 | 13 | RRS | 2960 | 2941
Jan | d. HE11-14 | 14 | RRS | 2960 | 2941
Jan | e. HE15-18 | 15 | RRS | 2916 | 2767
Jan | e. HE15-18 | 16 | RRS | 2916 | 2767
Jan | e. HE15-18 | 17 | RRS | 2916 | 2767
Jan | e. HE15-18 | 18 | RRS | 2916 | 2767
Jan | f. HE19-22 | 19 | RRS | 2916 | 2767
Jan | f. HE19-22 | 20 | RRS | 2916 | 2767
Jan | f. HE19-22 | 21 | RRS | 2916 | 2767
Jan | f. HE19-22 | 22 | RRS | 2916 | 2767
Jan | a. HE1-2 & HE23-24 | 23 | RRS | 2998 | 3031
Jan | a. HE1-2 & HE23-24 | 24 | RRS | 2998 | 3031
Feb | a. HE1-2 & HE23-24 | 1 | RRS | 2998 | 3145
Feb | a. HE1-2 & HE23-24 | 2 | RRS | 2998 | 3145
Feb | b. HE3-6 | 3 | RRS | 2998 | 3145
Feb | b. HE3-6 | 4 | RRS | 2998 | 3145
Feb | b. HE3-6 | 5 | RRS | 2998 | 3145 | Type | RRS |  |  |  | Hourly Average Responsive Reserve Requirement Comparison
Feb | b. HE3-6 | 6 | RRS | 2998 | 3145 | [5 empty] | 2024 RRS: On avg. 4 MW increase from prev year. Largest decrease is in Feb by 59 MW.
Feb | c. HE7-10 | 7 | RRS | 2916 | 3068 | Row Labels | 2024 RRS | 2025 RRS
Feb | c. HE7-10 | 8 | RRS | 2916 | 3068 | Jan | 2950.6667 | 2891.8333 | -58.8333 |  |  | min-change | -58.8333 | Feb
Feb | c. HE7-10 | 9 | RRS | 2916 | 3068 | Feb | 2950.6667 | 3073.1667 | 122.5 |  |  | max-change | 122.5 | 2950.6667
Feb | c. HE7-10 | 10 | RRS | 2916 | 3068 | Mar | 3088 | 3065 | -23 |  |  | AVG-CHANGE | 3.7833
Feb | d. HE11-14 | 11 | RRS | 2960 | 3068 | Apr | 3003.3333 | 3045.3333 | 42
Feb | d. HE11-14 | 12 | RRS | 2960 | 3068 | May | 2663.6667 | 2634.6667 | -29
Feb | d. HE11-14 | 13 | RRS | 2960 | 3068 | Jun | 2420.3333 | 2439.8333 | 19.5
Feb | d. HE11-14 | 14 | RRS | 2960 | 3068 | Jul | 2374.5 | 2361.3333 | -13.1667
Feb | e. HE15-18 | 15 | RRS | 2916 | 3031 | Aug | 2326.1667 | 2300 | -26.1667
Feb | e. HE15-18 | 16 | RRS | 2916 | 3031 | Sep | 2414 | 2389.3333 | -24.6667
Feb | e. HE15-18 | 17 | RRS | 2916 | 3031 | Oct | 2737.3333 | 2766 | 28.6667
Feb | e. HE15-18 | 18 | RRS | 2916 | 3031 | Nov | 2938.6667 |  | #N/A
Feb | f. HE19-22 | 19 | RRS | 2916 | 2982 | Dec | 2813.3333 |  | #N/A
Feb | f. HE19-22 | 20 | RRS | 2916 | 2982
Feb | f. HE19-22 | 21 | RRS | 2916 | 2982
Feb | f. HE19-22 | 22 | RRS | 2916 | 2982
Feb | a. HE1-2 & HE23-24 | 23 | RRS | 2998 | 3145
Feb | a. HE1-2 & HE23-24 | 24 | RRS | 2998 | 3145
Mar | a. HE1-2 & HE23-24 | 1 | RRS | 3178 | 3145
Mar | a. HE1-2 & HE23-24 | 2 | RRS | 3178 | 3145
Mar | b. HE3-6 | 3 | RRS | 3178 | 3145
Mar | b. HE3-6 | 4 | RRS | 3178 | 3145
Mar | b. HE3-6 | 5 | RRS | 3178 | 3145
Mar | b. HE3-6 | 6 | RRS | 3178 | 3145
Mar | c. HE7-10 | 7 | RRS | 3128 | 3068
Mar | c. HE7-10 | 8 | RRS | 3128 | 3068
Mar | c. HE7-10 | 9 | RRS | 3128 | 3068
Mar | c. HE7-10 | 10 | RRS | 3128 | 3068
Mar | d. HE11-14 | 11 | RRS | 3086 | 3068
Mar | d. HE11-14 | 12 | RRS | 3086 | 3068
Mar | d. HE11-14 | 13 | RRS | 3086 | 3068
Mar | d. HE11-14 | 14 | RRS | 3086 | 3068
Mar | e. HE15-18 | 15 | RRS | 2998 | 2982
Mar | e. HE15-18 | 16 | RRS | 2998 | 2982
Mar | e. HE15-18 | 17 | RRS | 2998 | 2982
Mar | e. HE15-18 | 18 | RRS | 2998 | 2982
Mar | f. HE19-22 | 19 | RRS | 2960 | 2982
Mar | f. HE19-22 | 20 | RRS | 2960 | 2982
Mar | f. HE19-22 | 21 | RRS | 2960 | 2982
Mar | f. HE19-22 | 22 | RRS | 2960 | 2982
Mar | a. HE1-2 & HE23-24 | 23 | RRS | 3178 | 3145
Mar | a. HE1-2 & HE23-24 | 24 | RRS | 3178 | 3145
Apr | a. HE1-2 & HE23-24 | 1 | RRS | 3086 | 3068
Apr | a. HE1-2 & HE23-24 | 2 | RRS | 3086 | 3068
Apr | b. HE3-6 | 3 | RRS | 3128 | 3145
Apr | b. HE3-6 | 4 | RRS | 3128 | 3145
Apr | b. HE3-6 | 5 | RRS | 3128 | 3145
Apr | b. HE3-6 | 6 | RRS | 3128 | 3145
Apr | c. HE7-10 | 7 | RRS | 3086 | 3068
Apr | c. HE7-10 | 8 | RRS | 3086 | 3068
Apr | c. HE7-10 | 9 | RRS | 3086 | 3068
Apr | c. HE7-10 | 10 | RRS | 3086 | 3068
Apr | d. HE11-14 | 11 | RRS | 2960 | 3068
Apr | d. HE11-14 | 12 | RRS | 2960 | 3068
Apr | d. HE11-14 | 13 | RRS | 2960 | 3068
Apr | d. HE11-14 | 14 | RRS | 2960 | 3068
Apr | e. HE15-18 | 15 | RRS | 2880 | 2982
Apr | e. HE15-18 | 16 | RRS | 2880 | 2982
Apr | e. HE15-18 | 17 | RRS | 2880 | 2982
Apr | e. HE15-18 | 18 | RRS | 2880 | 2982
Apr | f. HE19-22 | 19 | RRS | 2880 | 2941
Apr | f. HE19-22 | 20 | RRS | 2880 | 2941
Apr | f. HE19-22 | 21 | RRS | 2880 | 2941
Apr | f. HE19-22 | 22 | RRS | 2880 | 2941
Apr | a. HE1-2 & HE23-24 | 23 | RRS | 3086 | 3068
Apr | a. HE1-2 & HE23-24 | 24 | RRS | 3086 | 3068
May | a. HE1-2 & HE23-24 | 1 | RRS | 2808 | 2699
May | a. HE1-2 & HE23-24 | 2 | RRS | 2808 | 2699
May | b. HE3-6 | 3 | RRS | 2916 | 2699
May | b. HE3-6 | 4 | RRS | 2916 | 2699
May | b. HE3-6 | 5 | RRS | 2916 | 2699
May | b. HE3-6 | 6 | RRS | 2916 | 2699
May | c. HE7-10 | 7 | RRS | 2716 | 2699
May | c. HE7-10 | 8 | RRS | 2716 | 2699
May | c. HE7-10 | 9 | RRS | 2716 | 2699
May | c. HE7-10 | 10 | RRS | 2716 | 2699
May | d. HE11-14 | 11 | RRS | 2560 | 2595
May | d. HE11-14 | 12 | RRS | 2560 | 2595
May | d. HE11-14 | 13 | RRS | 2560 | 2595
May | d. HE11-14 | 14 | RRS | 2560 | 2595
May | e. HE15-18 | 15 | RRS | 2491 | 2558
May | e. HE15-18 | 16 | RRS | 2491 | 2558
May | e. HE15-18 | 17 | RRS | 2491 | 2558
May | e. HE15-18 | 18 | RRS | 2491 | 2558
May | f. HE19-22 | 19 | RRS | 2491 | 2558
May | f. HE19-22 | 20 | RRS | 2491 | 2558
May | f. HE19-22 | 21 | RRS | 2491 | 2558
May | f. HE19-22 | 22 | RRS | 2491 | 2558
May | a. HE1-2 & HE23-24 | 23 | RRS | 2808 | 2699
May | a. HE1-2 & HE23-24 | 24 | RRS | 2808 | 2699
Jun | a. HE1-2 & HE23-24 | 1 | RRS | 2491 | 2463
Jun | a. HE1-2 & HE23-24 | 2 | RRS | 2491 | 2463
Jun | b. HE3-6 | 3 | RRS | 2560 | 2514
Jun | b. HE3-6 | 4 | RRS | 2560 | 2514
Jun | b. HE3-6 | 5 | RRS | 2560 | 2514
Jun | b. HE3-6 | 6 | RRS | 2560 | 2514
Jun | c. HE7-10 | 7 | RRS | 2529 | 2514
Jun | c. HE7-10 | 8 | RRS | 2529 | 2514
Jun | c. HE7-10 | 9 | RRS | 2529 | 2514
Jun | c. HE7-10 | 10 | RRS | 2529 | 2514
Jun | d. HE11-14 | 11 | RRS | 2342 | 2425
Jun | d. HE11-14 | 12 | RRS | 2342 | 2425
Jun | d. HE11-14 | 13 | RRS | 2342 | 2425
Jun | d. HE11-14 | 14 | RRS | 2342 | 2425
Jun | e. HE15-18 | 15 | RRS | 2300 | 2380
Jun | e. HE15-18 | 16 | RRS | 2300 | 2380
Jun | e. HE15-18 | 17 | RRS | 2300 | 2380
Jun | e. HE15-18 | 18 | RRS | 2300 | 2380
Jun | f. HE19-22 | 19 | RRS | 2300 | 2343
Jun | f. HE19-22 | 20 | RRS | 2300 | 2343
Jun | f. HE19-22 | 21 | RRS | 2300 | 2343
Jun | f. HE19-22 | 22 | RRS | 2300 | 2343
Jun | a. HE1-2 & HE23-24 | 23 | RRS | 2491 | 2463
Jun | a. HE1-2 & HE23-24 | 24 | RRS | 2491 | 2463
Jul | a. HE1-2 & HE23-24 | 1 | RRS | 2412 | 2380
Jul | a. HE1-2 & HE23-24 | 2 | RRS | 2412 | 2380
Jul | b. HE3-6 | 3 | RRS | 2491 | 2463
Jul | b. HE3-6 | 4 | RRS | 2491 | 2463
Jul | b. HE3-6 | 5 | RRS | 2491 | 2463
Jul | b. HE3-6 | 6 | RRS | 2491 | 2463
Jul | c. HE7-10 | 7 | RRS | 2444 | 2425
Jul | c. HE7-10 | 8 | RRS | 2444 | 2425
Jul | c. HE7-10 | 9 | RRS | 2444 | 2425
Jul | c. HE7-10 | 10 | RRS | 2444 | 2425
Jul | d. HE11-14 | 11 | RRS | 2300 | 2300
Jul | d. HE11-14 | 12 | RRS | 2300 | 2300
Jul | d. HE11-14 | 13 | RRS | 2300 | 2300
Jul | d. HE11-14 | 14 | RRS | 2300 | 2300
Jul | e. HE15-18 | 15 | RRS | 2300 | 2300
Jul | e. HE15-18 | 16 | RRS | 2300 | 2300
Jul | e. HE15-18 | 17 | RRS | 2300 | 2300
Jul | e. HE15-18 | 18 | RRS | 2300 | 2300
Jul | f. HE19-22 | 19 | RRS | 2300 | 2300
Jul | f. HE19-22 | 20 | RRS | 2300 | 2300
Jul | f. HE19-22 | 21 | RRS | 2300 | 2300
Jul | f. HE19-22 | 22 | RRS | 2300 | 2300
Jul | a. HE1-2 & HE23-24 | 23 | RRS | 2412 | 2380
Jul | a. HE1-2 & HE23-24 | 24 | RRS | 2412 | 2380
Aug | a. HE1-2 & HE23-24 | 1 | RRS | 2342 | 2300
Aug | a. HE1-2 & HE23-24 | 2 | RRS | 2342 | 2300
Aug | b. HE3-6 | 3 | RRS | 2373 | 2300
Aug | b. HE3-6 | 4 | RRS | 2373 | 2300
Aug | b. HE3-6 | 5 | RRS | 2373 | 2300
Aug | b. HE3-6 | 6 | RRS | 2373 | 2300
Aug | c. HE7-10 | 7 | RRS | 2342 | 2300
Aug | c. HE7-10 | 8 | RRS | 2342 | 2300
Aug | c. HE7-10 | 9 | RRS | 2342 | 2300
Aug | c. HE7-10 | 10 | RRS | 2342 | 2300
Aug | d. HE11-14 | 11 | RRS | 2300 | 2300
Aug | d. HE11-14 | 12 | RRS | 2300 | 2300
Aug | d. HE11-14 | 13 | RRS | 2300 | 2300
Aug | d. HE11-14 | 14 | RRS | 2300 | 2300
Aug | e. HE15-18 | 15 | RRS | 2300 | 2300
Aug | e. HE15-18 | 16 | RRS | 2300 | 2300
Aug | e. HE15-18 | 17 | RRS | 2300 | 2300
Aug | e. HE15-18 | 18 | RRS | 2300 | 2300
Aug | f. HE19-22 | 19 | RRS | 2300 | 2300
Aug | f. HE19-22 | 20 | RRS | 2300 | 2300
Aug | f. HE19-22 | 21 | RRS | 2300 | 2300
Aug | f. HE19-22 | 22 | RRS | 2300 | 2300
Aug | a. HE1-2 & HE23-24 | 23 | RRS | 2342 | 2300
Aug | a. HE1-2 & HE23-24 | 24 | RRS | 2342 | 2300
Sep | a. HE1-2 & HE23-24 | 1 | RRS | 2491 | 2425
Sep | a. HE1-2 & HE23-24 | 2 | RRS | 2491 | 2425
Sep | b. HE3-6 | 3 | RRS | 2529 | 2463
Sep | b. HE3-6 | 4 | RRS | 2529 | 2463
Sep | b. HE3-6 | 5 | RRS | 2529 | 2463
Sep | b. HE3-6 | 6 | RRS | 2529 | 2463
Sep | c. HE7-10 | 7 | RRS | 2491 | 2425
Sep | c. HE7-10 | 8 | RRS | 2491 | 2425
Sep | c. HE7-10 | 9 | RRS | 2491 | 2425
Sep | c. HE7-10 | 10 | RRS | 2491 | 2425
Sep | d. HE11-14 | 11 | RRS | 2373 | 2380
Sep | d. HE11-14 | 12 | RRS | 2373 | 2380
Sep | d. HE11-14 | 13 | RRS | 2373 | 2380
Sep | d. HE11-14 | 14 | RRS | 2373 | 2380
Sep | e. HE15-18 | 15 | RRS | 2300 | 2343
Sep | e. HE15-18 | 16 | RRS | 2300 | 2343
Sep | e. HE15-18 | 17 | RRS | 2300 | 2343
Sep | e. HE15-18 | 18 | RRS | 2300 | 2343
Sep | f. HE19-22 | 19 | RRS | 2300 | 2300
Sep | f. HE19-22 | 20 | RRS | 2300 | 2300
Sep | f. HE19-22 | 21 | RRS | 2300 | 2300
Sep | f. HE19-22 | 22 | RRS | 2300 | 2300
Sep | a. HE1-2 & HE23-24 | 23 | RRS | 2491 | 2425
Sep | a. HE1-2 & HE23-24 | 24 | RRS | 2491 | 2425
Oct | a. HE1-2 & HE23-24 | 1 | RRS | 2808 | 2863
Oct | a. HE1-2 & HE23-24 | 2 | RRS | 2808 | 2863
Oct | b. HE3-6 | 3 | RRS | 2880 | 2863
Oct | b. HE3-6 | 4 | RRS | 2880 | 2863
Oct | b. HE3-6 | 5 | RRS | 2880 | 2863
Oct | b. HE3-6 | 6 | RRS | 2880 | 2863
Oct | c. HE7-10 | 7 | RRS | 2808 | 2863
Oct | c. HE7-10 | 8 | RRS | 2808 | 2863
Oct | c. HE7-10 | 9 | RRS | 2808 | 2863
Oct | c. HE7-10 | 10 | RRS | 2808 | 2863
Oct | d. HE11-14 | 11 | RRS | 2716 | 2767
Oct | d. HE11-14 | 12 | RRS | 2716 | 2767
Oct | d. HE11-14 | 13 | RRS | 2716 | 2767
Oct | d. HE11-14 | 14 | RRS | 2716 | 2767
Oct | e. HE15-18 | 15 | RRS | 2606 | 2645
Oct | e. HE15-18 | 16 | RRS | 2606 | 2645
Oct | e. HE15-18 | 17 | RRS | 2606 | 2645
Oct | e. HE15-18 | 18 | RRS | 2606 | 2645
Oct | f. HE19-22 | 19 | RRS | 2606 | 2595
Oct | f. HE19-22 | 20 | RRS | 2606 | 2595
Oct | f. HE19-22 | 21 | RRS | 2606 | 2595
Oct | f. HE19-22 | 22 | RRS | 2606 | 2595
Oct | a. HE1-2 & HE23-24 | 23 | RRS | 2808 | 2863
Oct | a. HE1-2 & HE23-24 | 24 | RRS | 2808 | 2863
Nov | a. HE1-2 & HE23-24 | 1 | RRS | 2998
Nov | a. HE1-2 & HE23-24 | 2 | RRS | 2998
Nov | b. HE3-6 | 3 | RRS | 2998
Nov | b. HE3-6 | 4 | RRS | 2998
Nov | b. HE3-6 | 5 | RRS | 2998
Nov | b. HE3-6 | 6 | RRS | 2998
Nov | c. HE7-10 | 7 | RRS | 2960
Nov | c. HE7-10 | 8 | RRS | 2960
Nov | c. HE7-10 | 9 | RRS | 2960
Nov | c. HE7-10 | 10 | RRS | 2960
Nov | d. HE11-14 | 11 | RRS | 2916
Nov | d. HE11-14 | 12 | RRS | 2916
Nov | d. HE11-14 | 13 | RRS | 2916
Nov | d. HE11-14 | 14 | RRS | 2916
Nov | e. HE15-18 | 15 | RRS | 2880
Nov | e. HE15-18 | 16 | RRS | 2880
Nov | e. HE15-18 | 17 | RRS | 2880
Nov | e. HE15-18 | 18 | RRS | 2880
Nov | f. HE19-22 | 19 | RRS | 2880
Nov | f. HE19-22 | 20 | RRS | 2880
Nov | f. HE19-22 | 21 | RRS | 2880
Nov | f. HE19-22 | 22 | RRS | 2880
Nov | a. HE1-2 & HE23-24 | 23 | RRS | 2998
Nov | a. HE1-2 & HE23-24 | 24 | RRS | 2998
Dec | a. HE1-2 & HE23-24 | 1 | RRS | 2916
Dec | a. HE1-2 & HE23-24 | 2 | RRS | 2916
Dec | b. HE3-6 | 3 | RRS | 2916
Dec | b. HE3-6 | 4 | RRS | 2916
Dec | b. HE3-6 | 5 | RRS | 2916
Dec | b. HE3-6 | 6 | RRS | 2916
Dec | c. HE7-10 | 7 | RRS | 2808
Dec | c. HE7-10 | 8 | RRS | 2808
Dec | c. HE7-10 | 9 | RRS | 2808
Dec | c. HE7-10 | 10 | RRS | 2808
Dec | d. HE11-14 | 11 | RRS | 2808
Dec | d. HE11-14 | 12 | RRS | 2808
Dec | d. HE11-14 | 13 | RRS | 2808
Dec | d. HE11-14 | 14 | RRS | 2808
Dec | e. HE15-18 | 15 | RRS | 2716
Dec | e. HE15-18 | 16 | RRS | 2716
Dec | e. HE15-18 | 17 | RRS | 2716
Dec | e. HE15-18 | 18 | RRS | 2716
Dec | f. HE19-22 | 19 | RRS | 2716
Dec | f. HE19-22 | 20 | RRS | 2716
Dec | f. HE19-22 | 21 | RRS | 2716
Dec | f. HE19-22 | 22 | RRS | 2716
Dec | a. HE1-2 & HE23-24 | 23 | RRS | 2916
Dec | a. HE1-2 & HE23-24 | 24 | RRS | 2916