## Slide 1
Oncor Delaware Basin Stages 3 and 4 Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
November 20, 2024

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Delaware Basin Stages 3 and 4 Project for Regional Planning Group (RPG) review in March 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $202.2 million and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in the Culberson, Loving, Reeves, and Ward Counties in the Far West Weather Zone
    Identified as Stage 3 and Stage 4 from ERCOT’s 2019 Delaware Basin Load Integration Study
    Local Transmission Project IDs L1, L3 and L5 from the 2024 Permian Basin Reliability Plan Study were added to the base case

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Culberson, Loving, Reeves, and Ward Counties in the Far West Weather Zone
ERCOT verified the Oncor Delaware Basin Stages 3 and 4 Project are components of the Stage 3 and Stage 4 upgrades identified in the 2019 Delaware Basin Load Integration Study and addresses the need
Contingency Category | Thermal Overloads | Voltage Violations | Unsolved Power Flows
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | None | 16 | 3
P3: G-1+N-1 | None | 2 | 1
P6-2: X-1+N-1 | None | 2 | None

## Slide 5: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Delaware Basin Stages 3 and 4 Project and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 6: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Delaware Basin Stages 3 and 4 Project did not cause a new congestion within the study area
  No potential future generation studied impacts the Delaware Basin Stages 3 and 4 Project
  The load scaling did not have a material impact on the Delaware Basin Stages 3 and 4 Project need

## Slide 7: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Oncor Delaware Basin Stages 3 and 4 Project to address reliability needs in the Culberson, Loving, Reeves, and Ward Counties in the Far West Weather Zone
TSPs expect to implement the upgrades by June 2027
Estimated Capital Cost: $202.2 million

## Slide 8: ERCOT Recommendation
Expand the existing Drill Hole Capacitor station to include a 345/138-kV Switch, including two 600 MVA autotransformers. The Drill Hole 345/138-kV Switch will initially be constructed with an 8-breaker, 345-kV breaker-and-a-half bus arrangement, and a 10-breaker, 138-kV breaker-and-a-half bus arrangement. All terminal and associated equipment will meet or exceed 5000 A for 345-kV and 3200 A for 138-kV;
Construct a loop of the existing Riverton – Owl Hills – Horseshoe Springs 138-kV double-circuit transmission line into the new Drill Hole 138-kV Switch, with normal and emergency rating of at least 614 MVA, approximately 0.1-mile;
Connect the existing Drill Hole 138-kV capacitors to the expanded Drill Hole 138-kV Switch;
Construct a new Drill Hole – Riverton 345-kV transmission line on double-circuit structures, with both circuits in place, operated at 345-kV with a normal and emergency rating of at least 2988 MVA, which will require new right of way (ROW), approximately 22.0-mile;
Install five 5000 A, 345-kV circuit breakers at the existing Riverton 345-kV Switch;
Install one 5000 A, 345-kV circuit breaker at the existing Sand Lake 345-kV Switch;
Convert the existing Riverton – Sand Lake 138-kV transmission line to 345-kV operation with normal and emergency rating of at least 2988 MVA, by terminating both endpoints into the existing 345-kV stations at Riverton and Sand Lake, 40.8-mile;

## Slide 9: ERCOT Recommendation (continued)
Construct a new Riverton – Sand Lake 138-kV transmission line on 138-kV double-circuit structures, with one circuit in place operated at 138-kV with normal and emergency rating of at least 614 MVA, on existing ROW, approximately 40.8-mile; and
Construct a loop of the new Riverton – Sand Lake 138-kV line with normal and emergency rating of at least 614 MVA, into the existing Horsehead Draw 138-kV substation, approximately 0.1-mile.

## Slide 10: ERCOT Recommendation