## Slide 1
RTCBTF
AS Deliverability and IROLs
December 11, 2024

## Slide 2: Undeliverable Ancillary Services - Review
Ancillary Service (AS) Deliverability Risk in the Current Market Design
  The Day-Ahead Market co-optimizes Energy and AS obligations
  If an AS is considered undeliverable in Real-Time, the ERCOT Control Room can move the obligation from one Resource to another within a common QSE
AS deliverability risk in original RTC design
  Discussions in 2019-2020 led to agreement of rules and software that would allow an ERCOT operator to manually limit the amount of Ancillary Services being awarded to an individual Resource
Congestion Impacts of AS deployments
  Brief Frequency Response
    In a frequency event, Ancillary Service deployment is automatic and “system-wide” as Resources increase output to recover frequency (where Resources on both sides of constraint respond and may provide counter-flow). If constraints are briefly stressed, Real-Time Market dispatch redistributes energy within constraint limits within minutes.
  Longer Running Services
    By design the Real-Time Market “deploys” certain longer-running Ancillary Services by converting the capacity in energy. As the market optimization is designed to also manage congestion, that capacity will not be deployed in such a way that it would exacerbate congestion unless it needed to prioritize serving energy over managing the constraint.

## Slide 3: Ancillary Services and IROLs
Interconnection Reliability Operating Limit (IROL)
  A System Operating Limit that, if violated, could lead to instability, uncontrolled separation, or Cascading Outages that adversely impact the reliability of the Bulk Electric System
  9 IROLs
    STEX: E_PASP, E_PATA, I_PASP, I_KALO
    PNHNDL
    N_TO_H
    MCCAMY
    WESTEX
    VALIMP
How could Ancillary Services(AS) deployments lead to an IROL Exceedance?
  When Resources carrying Ancillary Services on the hurting side of an IROL
    If Regulation up is deployed, these MWs could push the IROL flow beyond the IROL limit
      SCED is unaware of these deployments
    If RRS, ECRS or Non-Spin AS MWs are released to SCED, these MW could be undeliverable if converting this capacity to energy would violate the IROL limit subject to IROL constraint Max Shadow price

## Slide 4: How to prevent a potential IROL exceedance
Operational Procedure Proposal
Restrict Ancillary Services on hurting Resources when an IROL is active in SCED and the IROL flow is greater than X% of the limit.
  Ancillary Service restrictions would include Regulation Up, RRS up, Non-Spin, ECRS
  Restrictions would apply to Resources with a hurting/positive shift factor greater than Y%
  This process would be operator triggered in the EMS Transmission Constraint Manager
  No change to governor response requirements
  Retain the ability to apply logic to other non-IROL GTCs, if needed.
This process will be captured in the ERCOT Resource Desk Operating Procedure when updated for RTC+B