## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2023-06-16
3.1.2 | RPG Projects Backed Out For Lack of Approval or Moved Due to ISD Change | Final | 2023-06-14
3.1.2 | Recently Approved RPG Projects | Final | 2023-10-25
3.1.2 | Model Updates & Corrections | Final | 2023-12-08
3.1.3 | Transmission & Generation Outages | Final | 2023-09-14
3.1.5 | Temperatures Used in Dynamic Rating Calculation | Final | 2023-05-08
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2023-06-14
3.2.2 | Renewable Generation Dispatch | Final | 2023-06-09
3.2.3 | Switchable Generation | Final | 2023-04-06
3.2.4 | DC Tie Modeling and Dispatch | Final | 2023-06-09
3.2.5 | Reserve Requirement | Final | 2023-01-04
3.2.6 | Fuel Price Assumptions | Final | 2023-04-05
Demand
3.3 | Load Forecast (Reliability) 90/10 Forecast SSWG Forecast Bounded Higher of Calculations RTP Summer Peak Case Forecast RTP Min Load Case Forecast | Final | 2023-11-06
Other Studies
4.2.2 | Sensitivity Analysis | Final | 2023-11-30

## Start Cases
Date Last Updated: | 2023-06-16 | Back
Status | Final
SSWG Case Version: | 22SSWG Update 1 Final - October 10, 2022
On Peak Cases:
22SSWG_2025_SUM1_U1_Final_10102022.raw
22SSWG_2026_SUM1_U1_Final_10102022.raw
22SSWG_2028_SUM1_U1_Final_10102022.raw
22SSWG_2029_SUM1_U1_Final_10102022.raw
Off Peak Case:
22SSWG_2026_MIN_U1_Final_10102022.raw

## RPG Projects Moved or Removed
Date Last Updated: | 2023-06-14 |  | Back
Status | Final
Based on TPIT dated:
RPG Projects Removed from the RTP Cases
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
64239 | Vineyard Switch-North Lake Switch 138 kV Line | Construct a new 138 kV circuit from Vineyard to Northlake | North Lake Switch | Vineyard Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2025-12-15 | 138 | Tier 3 | N/A | N/A | N/A | 2022, 2386, 12012, 12013, 15030, 15035, 15040 | Y | 70741 | 64239
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North | Shamburger North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6904 |  | 2026-05-15 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2478, 3103, 3201, 3206 | Y | 13696 | 5981
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Shamburger North | Shamburger |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6905 |  | 2026-05-28 | 345 | Tier 3 |  |  |  | 3103, 3223 | Y | 14033 | 6304
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6906 |  | 2024-12-15 | 138 | Tier 3 |  |  |  | 1032, 1333, 11395 | Y | 73625 | 5436
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6908 |  | 2028-05-15 | 138 | Tier 2 |  |  |  | 1881, 2202 | Y | 12436 | 4834
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade the existing 345 kV Line | Sherry | Webb/Kennedale |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6912 |  | 2027-05-15 | 345 | Tier 3 | N/A | N/A | N/A | 1911, 1918, 1930, 1929, 1932, 1934 | Y | 14016 | 6287
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | Royse | Forney |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6913 |  | 2027-05-15 12:00 | 345 | Tier 3 | N/A | N/A | N/A | 2469, 2470, 12471, 2437, 2467, 2471, 2478, 2702, 2472, 2474, 2710, 3223 | Y | 49918 | 5524
69224 | AEP_TCC_PortLavaca-BrookhollowPortLavaca | Rebuild 138 kV Line from Brookhollow to Port Lavaca | Brookhollow | Port Lavaca |  | AEP | Lorraine Timmerman bcogan@aep.com 918-599-2857 |  | 2025-11-30 | 138 | Tier 1 | N/A | N/A | N/A | 8720, 8133, 8536 | Y | 71834 | 69224
50876 | AEP_TCC_PortLavaca-VictoriaRebuild | Retire 69 kV Line on Victoria to Port Lavaca | Port Lavaca | Victoria |  | AEP | Lorraine Timmerman bcogan@aep.com 918-599-2857 |  | 2025-11-30 | 69 | Tier 1 | N/A | N/A | N/A | 8135, 8136, 8169 | Y | 50877 | 50876
67915 | AEP_TCC_Asherton-West Batesville138kVLineRebuild | Rebuild 36.09 miles from Asherton to West Batesville 138 kV line | Asherton | West Batesville |  | AEP | Brandon K Cogan bcogan@aep.com 918-599-2857 |  | 2026-11-30 | 138 | Tier 3 | N/A | N/A | N/A | 8236, 8285, 8283 | Y | 67916 | 67915
55605 | AEP_TCC_NewBarksdale-Rocksprings | New Barksdale to Rocksprings: Rebuild 69 kV line | New Barksdale | Rocksprings |  | AEP | Bill Roberts bcogan@aep.com 918-599-2857 |  | 2026-01-01 | 69 | Tier 3 | N/A | N/A | N/A | 8238, 8365 | Y | 65572 | 55605
55617 | AEP_TCC_Campwood-NewBarksdale | Campwood to New Barksdale: Rebuild 69 kV line | New Barksdale | Campwood |  | AEP | Bill Roberts bcogan@aep.com 918-599-2857 |  | 2026-01-01 | 69 | Tier 3 | N/A | N/A | N/A | 8633, 8365 | Y | 65573 | 55617
54892 | AEP_TNC_Eden-North BradyRehab | Rehab Eden to North Brady 69 kV line | Eden | North Brady |  | AEP | Larry Brown mlforcum@aep.com 918-599-2674 |  | 2027-04-30 | 69 | Tier 3 | N/A | N/A | N/A | 60797, 6372, 6380, 6385 | Y | 65568 | 54892
70941 | TNMP_70941_Cedarvale_345 | Construct new Cedarvale 345kV station, include two 345-138kV transformers. Cut -in to North McCamey-Sand Lake 345 kV double circuit lines. | Cedarvale 138 kV (bus # 38145) | Cedarvale 345 kV (bus # 38144) |  | TNMP | Antonio Cashiola Antonio.Cashiola@tnmp.com |  | 2025-06-01 | 138 | Tier 2 | N/A | N/A | N/A | 11098, 38144, 38145, 38147,38148 | Y | 70942 | 70941
70943 | TNMP_70943_Pyote-Coyanosa_Dbl-Ckt | Double circuit 138 kV tie between TNMP Pyote and Coyanosa substations. | Pyote (bus # 38001) | Coyanosa (bus # 38380) |  | TNMP | Ross Cloninger Ross.Cloninger@tnmp.com |  | 2025-06-01 | 138 | Tier 2 | N/A | N/A | N/A | 38001, 38380 | Y | 70944 | 70943
71178 | Oncor_ME_71178_Seagoville-Watermill 138 kV Line | Rebuild Seagoville-Watermill 138 kV Line | Seagoville | Watermill |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2025-05-15 | 138 | Tier 3 | N/A | N/A | N/A | 23438, 23439, 2321, 3083, 2261, 2967, 2429, 2335, 3076, 2434, 3077, 3079 | Y | 71179 | 71178
52332 | Oncor_FW_52332_Lamesa - Paul Davis Tap 138 kV Line Section | Upgrade the existing 138 kV line | Lamesa | Paul Davis Tap |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2024-12-15 | 138 | Tier 3 | N/A | N/A | N/A | 1163, 1170, 10008, 18880 | Y | 71169 | 52332
71182 | Oncor_FW_71182_Reiter 345-138 kV Switch | Construct a new 345/138 kV switch | Odessa EHV | Wolf/Moss |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2025-12-15 | 345 | Tier 3 | N/A | N/A | N/A | 18544, 18545, 18546, 18547, 1018, 1027, 11010, 11028, 11111, 1111 | Y | 71184 | 71182
71187 | Oncor_FW_71187_Reiter - Tesoro 345 kV Double-Circuit Line | Construct new 2.5-mile 345 kV double-circuit line from Tesoro to Reiter | Tesoro | Reiter |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2025-05-15 | 345 | Tier 2 | N/A | N/A | N/A | 18540, 18544 | Y | 71189 | 71187
45640 | Oncor_FW_45640_Spraberry - Polecat Creek 138 kV Line | Upgrade the existing 138 kV line | Spraberry | Polecat Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2024-12-15 | 138 | Tier 3 | N/A | N/A | N/A | 11350, 11337, 11372, 11394, 1328, 10029, 1329, 1337 | Y | 73413 | 45640
RPG Projects With ISD Changes
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Original Projected In-Service Date (Month/Yr) | New Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
55626 | AEP_TCC_Ganso - Hamilton Road 138 kV Line Rebuild | Rebuild 138 kV line from Ganso to Hamilton Road | Maverick | Hamilton Road |  | AEP | Bill Roberts bcogan@aep.com 918-599-2857 |  | 2025-12-02 | 2026-12-02 | 138 | Tier 3 | N/A | N/A | N/A | 8255, 8267, 8692 | Y | 65576 | 55626

## Recently Approved RPG Projects
Date Last Updated: | 2023-10-25 |  | Back
Status | Final
RPG Project ID | RPG Project Name | TDSP | Approve Date
22RPG038 | CNP Clute Substation Addition Project | CNP | 2022
22RPG040 | Dupont to Joslin 138-kV Line Rebuild Project | AEPSC | 2022
22RPG043 | Haskell to Munday 69-kV Line Rebuild Project | AEPSC | 2023
22RPG044 | Escondido to Hamilton Road 138-kV Line Rebuild Project | AEPSC | 2023
22RPG023 | Hill Country 345/138-kV Autotransformer Replacement Project | CPS | 2022
22RPG031 | Lakeway - Marble Falls Transmission Line Strom Hardening Project | LCRA, PEC | 2022
22RPG021 | REC Tawakoni Area Transmission Project | REC | 2022
22RPG022 | STEC Hondo Creek to Pearson 69-kV Transmission Line Rebuild Project | STEC | 2022
22RPG037 | West Columbia to Burke 138 kV ckt 02 Rebuild Project (Partially in) | CNP | 2022
23RPG007 | Asherton to Uvalde 138-kV Conversion Project | AEPSC | 2023
23RPG008 | Fort Stockton Plant to Lynx 138-kV Line Rebuild Projec | AEPSC | 2023
23RPG009 | Spraberry to Polecat 138-kV Line Rebuild Project | ONCOR | 2023
23RPG011 | Morgan Creek to McDonald Road 138-kV Line Project | ONCOR | 2023
23RPG014 | Lamesa to Jim Payne POI to Paul Davis Tap 138-kV Line Rebuild Project | ONCOR | 2023
23RPG017 | Oncor Watermill 345/138-kV Switch Project | ONCOR | 2023
23RPG022 | McLennan County Transmission Project | ONCOR | 2023
23RPG024 | Big Foot to Dilley Switch 138-kV Conversion Project | AEPSC | 2023
23RPG025 | Britmoore to Bellaire Ckt 24 Upgrade Project | CNP | 2023
23RPG031 | CNP 345-kV Jeanetta Autotransformer Upgrade Project | CNP | 2023
23RPG030 | Walleye Creek 345/138-kV Switch Project | ONCOR | 2023

## Model Updates & Corrections
Date Last Updated: | 2023-12-08 | Back
Status | Final
Model Corrections/Updates Made to the 2023 RTP Cases
Transmission Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Applied IHS new load related topology | Multiple | X | X | X | X | X | Based on IHS new load interconnection information provided by the TSPs
Added Tier 4 project that rebuilds the 138-kV line from Morgan Creek (1032) to Barber Lake Switch (1189) to 614 MVA | Oncor | X | X | X | X | X | MOD ID 71973
Added Tier 4 project with Hayes Loop upgrade | Centerpoint | X | X | X | X | X | MOD ID 57642
Corrected the connection of the Dynamo substation | Oncor | X | X | X | X | X | Based on Oncor's feedback
Added Tier 4 project that rebuild portion of Haggerty-Bells 138 kV line section | Oncor | X | X | X | X | X | MOD ID 71164
Updated the rating of the 138-kV line from Climax POD (2708) and Princeton (2707) to 614 MVA. | Oncor | X | X | X | X | X | MOD ID 52316
Fixed the Killeen (3422) to Salado Switch (3699) 345-kV Line impedence | Oncor |  |  |  |  | X | Based on TSP comments
Updated the line impedances in the Waco area based on Oncor's feedback | Oncor | X | X | X | X | X | Based on TSP comments
Corrected the ratings of the 69-kV line from Olsen TNP to Clifton 1 TNP based on the feedback from TNMP. | TNMP | X | X | X | X | X | Based on TSP comments
Updated the Moore Switch (5827) to Big Foot (8221) 138-kV line parameters based on the Operations model | STEC, AEP | X | X | X | X | X | Updated to match the Operations model
Added the LCRA Tier 4 MOD project 73540 that adds the 138-kV Carlson substation and loops the 138-kV line from Elgin Switch to Kimbro into the new Carlson substation | LCRA | X | X | X | X | X | MOD ID 73540
Added the LCRA Tier 4 MOD project 71956 | LCRA | X | X | X | X | X | MOD ID 71956
Corrected ratings on the Lyle Wolz (7567) to Cooks Point (7569) 138-kV line to match the Operations model | LCRA | X | X | X | X | X | Updated to match the Operations model
Opened the normally open breaker at Pharr (80372-80373) | AEP | X | X | X | X | X | Based on TSP comments
Fixed WAP split bus on Ckt 09 to Stafford | CNP | X | X | X | X | X | Updated to match the Operations model
Removed a capacitor bank at H O Clarke and updated the topology and ratings from H O Clarke to Kirby | CNP | X | X | X | X | X | Updated to match the Operations model
Opened the Tombstone to OXY Century 138-kV line | TNMP | X | X | X | X | X | Based on TNMP's feedback that the line is not effective anymore.
Updated the Hamlin Shell to Hamlin Texas Co Tap 138-kV line rating | AEP | X | X | X | X | X | Based on AEP's feedback.
Added Tier 4 MOD project 70665 | CNP | X | X | X | X | X | MOD ID 70665
Added Tier 4 project that adds a new 138-kV station Cobia along the Carbide to Joslin 138-kV line | AEP | X | X | X | X | X | MOD ID 72479
Updated the ratings and parameters of the 138-kV Brookhollow to Port Lavaca line (part of the tier 1 "AEPSC Port Lavaca Area Improvement Project" that was not included in the SSWG start cases) | AEP | X |  |  |  |  | MOD ID 69224
Added Tier 4 Project that adds the Tidehaven substaion | AEP | X | X | X | X | X | MOD ID 71002
Disconnceted the 345-kV line from HHGT (170246) to Omega (170251) | LCRA | X | X | X | X | X | Based on LCRA feedback
Transformer Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Updated missing Palmito transformer rating | Sharyland | X | X | X | X | X | Based on TO feedback
Updated missing Marion tertiary winder rating | LCRA | X | X | X | X | X | Based on previous year RTP model
Generation Changes | TO/GO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Updated regulated bus to 1906 for Midlothian Energy Facility CTG1, CTG2, CTG5, and CTG6 | ONCOR | X | X | X | X | X | Based on TO feedback
Updated Regulated bus to 11768 for Eiffel solar | ONCOR | X | X | X | X | X | Based on TO feedback
Load Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Applied IHS load forecast | Multiple | X | X | X | X | X | Based on IHS load forecast
Applied Stanton Loop area load update | ONCOR | X | X | X | X | X | Based on TO feedback
Bus Voltage Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Reactive Device Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Added the Oncor Tier 4 MOD project 71901 that installs a 138-kV capacitor bank at Thorndale North | Oncor | X | X | X | X | X | MOD ID 71901
Phase Shifters Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
Synchronous Condensers Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
FACTS Device Changes | TO | [5 empty] | Comments
|  | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM
FACTS device at Tulsyncon (bus 23917) was removed due to a modeling error | ONCOR | X | X | X | X | X | Confirmed by ONCOR
Open and changed the limits of the Brown Switch (bus 11444) FACTS device to 0 | ONCOR | X | X | X | X | X | Confirmed by ONCOR
Open and changed the limits of the Brown Switch (bus 11445) FACTS device to 0 | ONCOR | X | X | X | X | X | Confirmed by ONCOR
FACTS device at North Brady (bus 60201) was removed due to retirement | AEP | X | X | X | X | X | Confirmed by AEP
FACTS device at Beeville (bus 88198) was removed due to retirement | AEP | X | X | X | X | X | Confirmed by AEP
FACTS device at Laredo Statcom station (bus 80012) was derated to -50/50 | AEP | X | X | X | X | X | Data provided by AEP

## Transmission & Gen Outages
Date Last Updated: | 2023-09-14 |  | Back
Status | Final
Case
Outaged Elements | Outage Description | Associated TO/RE | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Notes
Known outages collected by ERCOT from TSPs and Resource Entities were incorporated based on the TSP and ERCOT technical rationale into the known outages impact studies.

## Temp. for Dynamic Ratings
Date Last Updated: | 2023-05-08 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 100
East | 105
Far West | 110
North Central | 110
North | 110
South Central | 105
South | 105
West | 110

## Gen Add. Ret. and Mothball
Date Last Updated: | 2023-06-14 |  | Back
Status | Final
Based on generators met PG Section 6.9 requirements (1)(b) through (1)(d) by 2/1/2023
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
23INR0124 | Copperhead Solar, LLC | Falls | 2023-12-15 | Battery | 99 | Y | Y | Y | Y | Y | Y
22INR0223 | Eiffel Solar | Lamar | 2023-10-30 | Solar | 241 | Y | Y | Y | Y | Y | Y
23INR0339 | Remy Jade Power Station | Harris | 2024-04-01 | Gas | 408 | Y | Y | Y | Y | Y | Y
18INR0058 | Texana Solar | Wharton | 2024-09-27 | Solar | 152.34 | Y | Y | Y | Y | Y | Y
21INR0220 | Maleza Solar | Wharton | 2024-06-01 | Solar | 254.94 | Y | Y | Y | Y | Y | Y
21INR0203 | Eastbell Milam Solar | Milam | 2023-11-01 | Solar | 244.86 | Y | Y | Y | Y | Y | Y
22INR0429 | Sun Valley BESS | Hill | 2023-09-10 | Battery | 101.4 | Y | Y | Y | Y | Y | Y
22INR0549 | Tanzanite Storage | Henderson | 2024-12-01 | Battery | 257.72 | Y | Y | Y | Y | Y | Y
23INR0239 | Giga Texas Energy Storage | Travis | 2023-08-10 | Battery | 131.05 | Y | Y | Y | Y | Y | Y
23INR0524 | Temple II Repower | Bell | 2023-10-15 | Gas | 760 | Y | Y | Y | Y | Y | Y
22INR0349 | BRP Antlia BESS | Val Verde | 2023-12-01 | Battery | 70.95 | Y | Y | Y | Y | Y | Y
22INR0397 | Buckeye Corpus Fuels Solar | Nueces | 2025-02-22 | Solar | 57.59 | Y | Y | Y | Y | Y | Y
22INR0603 | Olney BESS | Young | 2023-06-15 | Battery | 9.95 | Y | Y | Y | Y | Y | Y
20INR0080 | Frye Solar | Swisher | 2024-03-15 | Solar | 514.1 | Y | Y | Y | Y | Y | Y
23INR0419 | SOHO BESS | Brazoria | 2024-06-01 | Battery | 206.32 | Y | Y | Y | Y | Y | Y
21INR0351 | 7V Solar | Fayette | 2024-04-30 | Solar | 240.63 | Y | Y | Y | Y | Y | Y
22INR0524 | St. Gall I Energy Storage | Pecos | 2023-12-01 | Battery | 102.6 | Y | Y | Y | Y | Y | Y
21INR0492 | Stockyard Grid Batt | Tarrant | 2023-07-01 | Battery | 150.6 | Y | Y | Y | Y | Y | Y
23INR0472 | Frontera Energy Center | Hidalgo | 2023-06-30 | Gas | 538.5 | Y | Y | Y | Y | Y | Y
21INR0253 | Ulysses Solar | Coke | 2024-11-01 | Solar | 150 | Y | Y | Y | Y | Y | Y
22INR0552 | Sowers Storage | Kaufman | 2024-12-01 | Battery | 203 | Y | Y | Y | Y | Y | Y
23INR0363 | Brazos Bend BESS | Fort Bend | 2024-04-15 | Battery | 101.21 | Y | Y | Y | Y | Y | Y
23INR0007 | Outpost Solar | Webb | 2024-04-01 | Solar | 513.7 | Y | Y | Y | Y | Y | Y
23INR0522 | Diboll Bess | Angelina | 2023-09-14 | Battery | 9.95 | Y | Y | Y | Y | Y | Y
22INR0495 | TIMBERWOLF BESS 2 | Crane | 2023-09-01 | Battery | 150 | Y | Y | Y | Y | Y | Y
24INR0147 | Citadel BESS | Harris | 2024-05-07 | Battery | 201.32 | Y | Y | Y | Y | Y | Y
21INR0223 | Tulsita Solar | Goliad | 2024-12-31 | Solar | 260.99 | Y | Y | Y | Y | Y | Y
21INR0442 | Myrtle Storage | Brazoria | 2023-12-15 | Battery | 155.04 | Y | Y | Y | Y | Y | Y
21INR0019 | Zier Solar | Kinney | 2023-12-31 | Solar | 162.99 | Y | Y | Y | Y | Y | Y
21INR0027 | Zier Storage | Kinney | 2023-12-31 | Battery | 40.41 | Y | Y | Y | Y | Y | Y
21INR0344 | Lunis Creek Solar SLF | Jackson | 2024-12-31 | Solar | 617.12 | Y | Y | Y | Y | Y | Y
21INR0353 | Big Elm Solar | Bell | 2024-05-17 | Solar | 203.64 | Y | Y | Y | Y | Y | Y
21INR0532 | Brazos Wind Repower | Scurry | 2023-08-14 | Wind | 22.4 | Y | Y | Y | Y | Y | Y
22INR0327 | Hummingbird Storage | Denton | 2023-12-01 | Battery | 103.8 | Y | Y | Y | Y | Y | Y
22INR0368 | Padua Grid BESS | Bexar | 2024-12-31 | Battery | 50.87 | Y | Y | Y | Y | Y | Y
22INR0490 | Callisto I Energy Center | Harris | 2024-06-01 | Battery | 203.04 | Y | Y | Y | Y | Y | Y
23INR0160 | Grimes County Solar | Grimes | 2025-03-15 | Solar | 210 | Y | Y | Y | Y | Y | Y
23INR0166 | Great Kiskadee Storage | Hidalgo | 2024-08-01 | Battery | 103.05 | Y | Y | Y | Y | Y | Y
23INR0506 | Beachwood II Power Station | Brazoria | 2024-03-01 | Gas | 102 | Y | Y | Y | Y | Y | Y
Retired Units
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
DECKER_DPG2 | 420 | X | X | X | X | X | NSO posted
OCI_ALM1_G1 (BT) | 1 | X | X | X | X | X | NSO posted
CALAVER_JTD1 | 420 | X | X | X | X | X | NSO posted
CALAVER_JTD2 | 420 | X | X | X | X | X | NSO posted
DOWGEN_DOW_G37 | 61 | X | X | X | X | X | NSO posted
Generation Resources Unavailable in Planning Studies Prior to NSO
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
COL_COLETOG1 | 655 |  |  |  | X | X | https://mis.ercot.com/secure/data-products/grid/generation?id=PG3-1411-M
BRAUNIG_VHB1 | 217 | X | X | X | X | X
BRAUNIG_VHB2 | 230 | X | X | X | X | X
BRAUNIG_VHB3 | 412 | X | X | X | X | X
CALAVER_OWS1 | 420 |  |  |  | X | X
CALAVER_OWS2 | 410 |  |  |  |  | X
CALAVER_JKS1 | 560 |  |  |  |  | X
Mothballed Units
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
OLINGR_OLING_1 | 78 | X | X | X | X | X | From CDR and NSO posted
DOW_DOW_ST64 | 50 | X | X | X | X | X | NSO posted
FLCNS_UNIT3 | 70 | X | X | X | X | X | NSO posted
BRNDN_U1 | 20 | X | X | X | X | X | NSO posted
MASSENGL_C3 | 38 | X | X | X | X | X | NSO posted
MASSENGL_C1 | 18 | X | X | X | X | X | NSO posted
MASSENGL_C2 | 18 | X | X | X | X | X | NSO posted
TY_COOKE_G2 | 14 | X | X | X | X | X | NSO posted
TY_COOKE_G3 | 17 | X | X | X | X | X | NSO posted
Seasonal Mothballed Units (Offline in the 2026 Min case only)
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
NACPW_UNIT1 | 116.45 | X | X | X | X | X | NSO posted
MCSES_UNIT8 | 568 | X | X | X | X | X | NSO posted
STEA_STEAM_1 | 17.5 | X | X | X | X | X | From CDR and NSO posted
SPNC_SPNCE_4 | 57 | X | X | X | X | X | From CDR and NSO posted
SPNC_SPNCE_5 | 61 | X | X | X | X | X | From CDR and NSO posted
Retirement Units back in service
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
TGF_TGFGT_1 | 78 | X | X | X | X | X | Information received from Resource Adequacy department
PNPI_GT2 | 71 | X | X | X | X | X | NSO posted
Planned Units Removed Due to Project Cancellation
Unit Name | MW For Grid | 2025 SUM | 2026 MIN | 2026 SUM | 2028 SUM | 2029 SUM | Comments
NOTES: Simple model Settlement Only Distributed Generators (SODGs) were added to reflect those currently operational. Battery models were also added to reflect those currently in the Operations model.

## Renewable Generation Dispatch
Date Last Updated: | 2023-06-09 |  | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR_Summer_PeakAveSolarCapacityPercentages_11-23-2021" posted on the ERCOT website under Resource Adequacy. Note: Solar units are offline in the Min case.
* SOLARPEAKPCT Values | 79%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Wind
Information obtained from the spreadsheet "CDR_Summer_PeakAveWindCapacityPercentages_11_23-2020" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Coastal | Summer, Panhandle | Summer, Other
60% | 30% | 21%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Inside Study Region
Summer, Coastal | Summer, Panhandle | Summer, Other
46% | 13% | 10%
Inside and Outside Study Region
Min Case, Coastal | Min Case, Panhandle | Min Case, Other
29% | 49% | 39%
Hydro
Unit specific generation MW dispatch modeled using CDR methodology which is based on historical Settlements HSL dispatch levels during the top 20 load hours of the last three years. Note: All Hydro units are offline in the Min case.
AMI_AMISTAG1 (H1) | 25.45
AMI_AMISTAG2 (H2) | 19.0333
AUS_AUSTING1 (H2) | 8.5967
AUS_AUSTING1 (H1) | 8
BUC_BUCHANG1 (H1) | 16
BUC_BUCHANG2 (H2) | 16
BUC_BUCHANG3 (H3) | 17
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 40
DND_DENISOG2 (H2) | 33.3333
EA_EAGLE_HY1 (H3) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H1) | 0
FAL_FALCONG1 (H1) | 7.45
FAL_FALCONG2 (H2) | 7.4
FAL_FALCONG3 (H3) | 7.1667
INKS_INKS_G1 (H1) | 13.38
MAR_MARBFAG1 (H1) | 20.54
MAR_MARBFAG2 (H2) | 20
MAR_MARSFOG1 (H1) | 33.7813
MAR_MARSFOG2 (H2) | 35.346
MAR_MARSFOG3 (H3) | 34.444
WIR_WIRTZ_G1 (H1) | 29
WIR_WIRTZ_G2 (H2) | 29
WND_WHITNEY1 (H1) | 21.9617
WND_WHITNEY2 (H2) | 21.9617

## Switchable Generation
Date Last Updated: | 2023-04-06 |  | Back
Status | Final
Operational Resources Unavailable to ERCOT (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
ANTELOPE IC 1 | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ANTELOPE IC 2 | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ANTELOPE IC 3 | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ELK STATION CTG 1 | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
ELK STATION CTG 2 | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  |  |  |  | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542

## DC Tie Modeling & Dispatch
Date Last Updated: | 2023-06-09 |  | Back
Status | Final
Reliability Analysis
DC Tie Dispatch - Summer Peak Conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 0
DC_R* | 0
DC Tie Dispatch - Minimum Load Conditions (MW)
DC_E | 0
DC_N | 0
DC_L* | 0
DC_R* | 0
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.

## Reserve Requirement
Date Last Updated: | 2023-01-04 | Back
Status | Final
Reliabity Cases | 3000 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.

## Fuel Price Assumptions
Date Last Updated: | 2023-04-05 |  | Back
Status | Final
Source
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2023 | 5.7024 | 5.4821 | 5.1284 | 5.2785 | 5.4208 | 5.5119 | 5.3497 | 5.427 | 5.4187 | 5.6084 | 5.6072 | 5.8739 | 5.4841
2024 | 4.5172 | 4.3426 | 4.0625 | 4.1814 | 4.2941 | 4.3662 | 4.2378 | 4.299 | 4.2925 | 4.4427 | 4.4418 | 4.653 | 4.3442
2025 | 3.9548 | 3.802 | 3.5567 | 3.6608 | 3.7596 | 3.8227 | 3.7102 | 3.7638 | 3.7581 | 3.8896 | 3.8888 | 4.0737 | 3.8034
2026 | 3.5483 | 3.4112 | 3.1912 | 3.2846 | 3.3732 | 3.4298 | 3.3289 | 3.377 | 3.3718 | 3.4899 | 3.4891 | 3.655 | 3.4125
2027 | 3.3737 | 3.2433 | 3.0341 | 3.1229 | 3.2071 | 3.261 | 3.165 | 3.2108 | 3.2059 | 3.3181 | 3.3174 | 3.4752 | 3.2445
2028 | 3.3824 | 3.2518 | 3.042 | 3.131 | 3.2154 | 3.2694 | 3.1732 | 3.2191 | 3.2142 | 3.3267 | 3.326 | 3.4842 | 3.253
2029 | 3.4833 | 3.3488 | 3.1327 | 3.2244 | 3.3114 | 3.367 | 3.2679 | 3.3151 | 3.3101 | 3.426 | 3.4252 | 3.5881 | 3.35

## Reliability Case-Load Forecast
Date Last Updated | 2023-11-06 | Back
Status | Final
SSWG Load– Based on 21 SSWG cases posted on 10/10/2022 less self-serve load (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2025 | 25429.23 | 3364.01 | 11564.14 | 4795.1 | 31514.75 | 17208.38 | 7916.06 | 2845.93 | 104637.6
2026 | 25632.47 | 3425.41 | 12890.22 | 4821.96 | 32249.95 | 17533.7 | 8020.43 | 2884.32 | 107458.46
2028 | 25919.84 | 3509.83 | 13329.27 | 4882.38 | 33492.89 | 18182.66 | 8230.94 | 2965.845 | 110513.655
2029 | 26102.93 | 3558.66 | 13529.88 | 4910.74 | 34037.63 | 18515.75 | 8347.33 | 3020.56 | 112023.48
ERCOT 90th percentile Load Forecast– less losses for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2025 | 22593.4583 | 3339.5733 | 7064.2818 | 2969.3163 | 28373.9592 | 15493.3505 | 7251.4777 | 2813.124 | 89898.5411
2026 | 22821.8729 | 3358.6502 | 7563.9714 | 3121.8705 | 28519.4118 | 15796.9224 | 7297.858 | 2971.8083 | 91452.3655
2028 | 23273 | 3406 | 8230 | 3282 | 28773 | 16296 | 7390 | 3132 | 93782
2029 | 23495 | 3434 | 8579 | 3289 | 28880 | 16457 | 7435 | 3133 | 94702
2023 RTP load level with self-served load (MW) (based on on 7.5% boundary threshold, ERCOT load review results, and the incorporation of the IHS Markit study Permian Basin load forecast and rooftop PV growth forecast contribution)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2025 | 28595 | 3295 | 12158 | 5224 | 31459 | 16787 | 8095 | 3378 | 108991
2026 | 28884 | 3362 | 13843 | 5354 | 31632 | 17258 | 8115 | 3502 | 111950
2028 | 29507 | 3456 | 14597 | 5494 | 32184 | 17762 | 8168 | 3641 | 114809
2029 | 29848 | 3516 | 14855 | 5501 | 32458 | 17966 | 8234 | 3634 | 116012
2023 RTP load level with self-served load for Off-Peak Case (MW) (based on 2025 SSWG Min Case and adjusted with ERCOT load review results)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2026 | 16103 | 1113 | 8964 | 3330 | 10094 | 7246 | 4423 | 1863 | 53136

## Sensitivity Analysis
Date Last Updated: | 2023-11-30 | Back
Status | Final
For sensitivity 1, the wind and solar output values below reflect their assumed output prior to any redispatch to alleviate transmission constraints. For sensitivity 2, the wind and solar output values below reflect their assumed output after the needed curtailment to maintain system critical intertia and stability limits.
Sensitivity 1: | Low Solar Net Summer Peak
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | South Wind (Coastal) | South Wind (Non-Coastal) | Panhandle | Other
2025 | 88789 | -820 | 3453 | 2971 | 529 | 8358 | 4240 | 19551
2028 | 93124 | -820 | 3453 | 2971 | 529 | 8358 | 4240 | 19551
Sensitivity 2: | High Renewable Light Load
Case | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | Coastal | Panhandle | Other
2026 | 57984 | 100 | 3233 | 2283 | 18422 | 25402 | 49340
* negative sign indicating DC tie import.