## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
4.3 | Start Cases | Final | 2023-05-02
4.3 | Recently Approved RPG Projects | Final | 2023-06-16
4.3 | Model Updates/Corrections | Final | 2023-10-17
3.1.3 | Transmission & Generation Outages | Final | 2023-05-23
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2023-08-09
3.2.2 | Renewable Generation Dispatch | Final | 2023-05-02
3.2.3 | Switchable Generation | Final | 2023-05-18
3.2.4 | DC Tie Modeling and Dispatch | Final | 2023-05-02
3.2.5 | Reserve Requirements | Final | 2023-05-02
3.2.6 | Fuel Price Assumptions | Final | 2023-05-02
3.2.6 | Emission Cost Assumptions | Final | 2023-05-18
Demand
3.3 | Load Forecast (Economic) Weather Year Assumption | Final | 2023-06-20

## Start Cases
Date Last Updated: | 2023-05-02 | Back
Status | Final
Based on 2022 RTP final summer peak reliability cases for years 2025 and 2028

## Recently Approved RPG Projects
| Date Last Updated: | 2023-06-16 | Back
| Status | Final
RPG Project ID | Project Name | TDSP | Approve Date | 2025 | 2028
22RPG002 | Abilene South to Putnam 138 kV Transmission Line Rebuild Project | AEPSC | 2022 | X | X
22RPG020 | Belknap to Fort Griffin 69 kV Line Rebuild Project | AEPSC | 2022 | X | X
22RPG008 | Bowman Switch 345/138 kV Autotransformers Project | Oncor | 2022 | X | X
22RPG030 | Buchanan CTEC – Pitsburg Transmission Line Overhaul Project | LCRA | 2022 | X | X
22RPG038 | CNP Clute Substation Addition Project. | CNP | 2022 | X | X
22RPG040 | Dupont to Joslin 138 kV Line Rebuild Project | AEPSC | 2022 | X | X
22RPG039 | Eagle Mountain 345/138 kV Switch Rebuild Project | Oncor | 2022 | X | X
22RPG009 | Eden to North Brady 69 kV Line Rebuild Project | AEPSC | 2022 | X | X
22RPG029 | Fairland – Lago Vista Transmission Line Rehabilitation Project | LCRA | 2022 | X | X
22RPG011 | Fayetteville – Salem Transmission Line Rehabilitation Project | LCRA | 2022 | X | X
22RPG001 | Greens Bayou to Clinton 138kV Conversion Project | CNP | 2022 | X | X
22RPG043 | Haskell to Munday 69 kV Line Rebuild Project | AEPSC | 2023 | X | X
22RPG005 | Hays Energy – Kendall Corridor Transmission Line Rehabilitation Projects | LCRA | 2022 | X | X
22RPG023 | Hill Country 345/138 kV Autotransformer Replacement Project | CPS | 2022 | X | X
22RPG016 | Hutto East - Brushy Creek 138kV Line Project | Oncor | 2022 | X | X
23RPG005 | La Palma to Steward Road Rebuild and Conversion | AEPSC | 2023 |  | X
22RPG031 | Lakeway - Marble Falls Transmission Line Strom Hardening Project | LCRA, PEC | 2022 | X | X
22RPG007 | Lenorah Area 345/138 kV Project | Oncor, WETT | 2022 | X | X
22RPG018 | Marshall Ford - McNeil Transmission Line Storm Hardening Project | LCRA | 2022 | X | X
22RPG017 | McGregor Phillips – Waco West 69 kV Line Project | Oncor | 2022 | X | X
22RPG033 | Mountain Top-Blanco-Devils Hill Line Rebuild and Voltage Upgrade Project | PEC | 2022 | X | X
22RPG035 | Palestine - Crockett 69 kV Line Rebuild Project | Oncor | 2022 | X | X
22RPG012 | Partial Rebuild 69 kV Deepwater to Clinton Ckt 33 Project | CNP | 2022 | X | X
22RPG019 | Partial Rebuild of 69 kV HOC to Dunlavy Ckt 40 Project | CNP | 2022 | X | X
22RPG046 | Peppervine to Temple 69 kV Line Conversion Project | Oncor | 2023 | X | X
22RPG004 | Pulsar to Victoria 138 kV line rebuild project | AEPSC | 2022 | X | X
22RPG021 | REC Tawakoni Area Transmission Project | REC | 2022 | X | X
22RPG041 | Sienna to Dewalt to Missouri City 138 kV ckt 02 Line Rebuild Project | CNP | 2022 | X | X
22RPG022 | STEC Hondo Creek to Pearson 69 kV Transmission Line Rebuild Project | STEC | 2022 | X | X
22RPG036 | Taylor Switch – Holland 69 kV Line Section Rebuild Project | Oncor | 2022 | X | X
22RPG032 | Tesoro 345/138 kV Switch Project | Oncor | 2022 | X | X
22RPG015 | Tyler Switch – Forest Grove Switch 138 kV Line Project | Oncor | 2022 | X | X
22RPG037 | West Columbia to Burke 138 kV ckt 02 Rebuild Project | CNP | 2022 | X | X
22RPG024 | Wolf - Odessa EHV 138 kV Line Rebuild project | Oncor | 2022 | X | X
22RPG013 | Wolf Switch - Moss Switch 138 kV Line Rebuild Project | Oncor | 2022 | X | X
22RPG025 | Yucca Drive - Courtney Creek 69 kV Line Conversion to 138 kV Project | Oncor | 2022 | X | X
22RPG045 | Yucca to Moss 138 kV Line Project | Oncor | 2023 | X | X
22RPG028 | Ballinger to Santa Anna 69 kV Transmission Line Rebuild Project | AEPSC | 2022 |  | X
22RPG044 | Escondido to Hamilton Road 138 kV Line Rebuild Project | AEPSC | 2023 |  | X
22RPG034 | Temple – Minerva 69 kV Line Rebuild Project | Oncor | 2022 |  | X
23RPG007 | Asherton - Uvalde 138-kV Conversion Project | AEPSC | 2023 | X | X
22RPG047 | Peck to Driver 138-kV Line Project | Oncor | 2023 | X | X
22RPG048 | San Antonio South Reliability Project | CPS | 2023 |  | X
23RPG022 | McLennan County Transmission Project | Oncor | 2023 |  | X

## Model Updates & Corrections
Date Last Updated: | 2023-10-17 | Back
Status | Final
Model Corrections/Updates Made to the 2022 RTP Cases
Transmission Changes | TO | 2025 | 2028 | Comments
Added the tier 4 project that rebuilds the Texaco Mabee Tap - Midland East 138 kV line. | Oncor | X | X | TPIT Project 66571 (Tier 4)
Removed additional line between Brown (1444) and Killeen (3422). |  | X | X | Model correction identified by comparing network topology to June 2023 SSWG cases
Updated capacity multipliers for Spruce-Pawnee. | CPS | X | X | Based on TSP confirmation
Updated impedances on Killeen-Salado ckt with 1912 MVA rating. | Oncor | X | X | Based on TSP confirmation
Added Tier 4 projects that uprate DOW (42500) - Jones Creek (42530) 345-kV circuit 27. | CNP | X | X | TPIT Projects 67270E, 73371G (Tier 4)
Added the RTP project that upgrades Burns (5763) - Heidelburg (5765) and Burns (5763) - Rio Hondo (8319) 138-kV lines. | STEC |  | X | 2022 RTP Project 2022-S8; Project was missing in later year
Added the RTP project that upgrades La Palma (8314) - Haine Drive (8322) 138-kV line. | AEP |  | X | 2022 RTP Project 2022-S9; Project was missing in later year
Added the RTP project that upgrades Wesmer (8347) - Pantera (8033) 138-kV line. | AEP |  | X | 2022 RTP Project 2022-S10; Project was missing in later year
Added the RTP project that upgradesNorth Laredo (8909) - Unitec (8134) - Gateway West Tap (8650) 138-kV line. | AEP |  | X | 2022 RTP Project 2022-S11; Project was missing in later year
Added the tier 4 project that will upgrade the LCRATSC Chief Brady (7343) - Georgetown (7366) 138-kV line. | LCRA | X | X | TPIT Project 70922 (Tier 4)
Added the tier 4 project that will upgrade the LCRATSC Chief Brady (7343) -RoundRock (7366) 138-kV line. | LCRA | X | X | TPIT Project 70200 (Tier 4)
Added the RTP project that upgrades from Illinois (6565) - Pandale (6567) - Ozona Rea (6551) - Ozona (6560) - Friend Ranch (6550) - Atlantic Sonora (6511) 69-kV lines. | AEP | X | X | 2023 RTP Project 2023-FW2
Added the RTP project that upgrades Sterling City (6435) - Camp Elizabeth (6436) 69-kV lines. | AEP | X | X | 2023 RTP Project 2023-W5
Added the RTP project that upgrades Cedar Hills (6423) - Silver Tap (6431) 69-kV line. | AEP | X | X | 2023 RTP Project 2023-W6
Added the RTP project that upgrades Scurry Chevron (1312) - KNDRSACRC_8 (11130) - Knapp (1310) - Bluff Creek Switch (1309) 138-kV lines. | Oncor | X | X | 2023 RTP Project 2023-W10; Part of Permian Basin Load Integration Placeholder Project
Added the RTP project that upgrades Scurry Chevron (1312) - Dermott (11306) 138-kV lines. | Oncor |  | X | 2023 RTP Project 2023-W10; Part of Permian Basin Load Integration Placeholder Project
Added the RTP projects that upgrade the Bluff Creek Switch (1309) - Exxon Sharon Ridge (1300) - Willow Valley Switch (1301) 138-kV line. | Oncor |  | X | 2023-W19 2023-WFW1
Added the RTP project that adds a new Rosenberg (944070) 345-kV substation and 345-kV double-circuit lines from Whaley (44070) - Rosenberg (944070) - Obrien (44500). | CNP | X | X | 2023 RTP Project 2023-C1
Added the RTP project that upgrades Sacroc (1311) - Deep Creek Sub (1304) 138-kV Line Upgrade. | Oncor |  | X | 2023 RTP Project 2021-W5
Added the RTP projects in the Temple/Tin Roof Area. | Oncor | X | X | 2023 RTP Project 2023-NC17 2023 RTP Project 2023-NC36 2023 RTP Project 2023-NC51 2023 RTP Project 2023-NC60 (Partial - Temple Switch transformer addition) 2023 RTP Project 2023-NC61
Generation Changes | TO | 2025 SUM | 2028 SUM | Comments
Put W A PARISH - PETRA NOVA CTG back to year-round service starting 6/28/2023 |  | X | X | Based on ERCOT Market Notice from 5/25/2023
Phase Shifters | TO | 2025 SUM | 2028 SUM | Comments

## Transmission & Gen Outages
Date Last Updated: | 2023-05-23 | Back
Status | Final
Outaged Element | Associated TO/RE | 2025 SUM | 2028 SUM | Notes
Spencer Unit 4 | City of Garland | X | X | NSO posted
Spencer Unit 5 | City of Garland | X | X | NSO posted
Powerlane Plant STG 1 | GEUS | X | X | NSO posted
Nacogdoches Power | Nacogdoches Power, LLC | X | X | NSO posted
Automated maintenance schedules modeled by UPLAN

## Gen Add, Ret. and Mothball
Date Last Updated: | 2023-08-09 | Back
Status | Final
6.9(1) conditions met as of: | 2023-02-01
New generators that met PG 6.9(1) requirements
GINR Reference Number | Project Name | County | Projected Date | Fuel | MW For Grid | Changes From Last Report | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2025 | 2028 | Comments
18INR0058 | Texana Solar | Wharton | 2024-09-27 | SOL | 152.3 |  | 2022-11-03 | X | X
19INR0177 | Crawfish | Wharton | 2023-07-31 | WIN | 163.2 |  | 2022-05-13 | X | X
20INR0035 | Angus Solar | Bosque | 2024-06-01 | SOL | 112 |  | 2022-08-24 | X | X
20INR0047 | Siete | Webb | 2024-10-31 | WIN | 375.1 |  | 2022-07-19 | X | X
20INR0074 | Pitts Dudik Solar | Hill | 2023-05-20 | SOL | 50 |  | 2022-04-27 | X | X
20INR0080 | Frye Solar | Swisher | 2024-03-15 | SOL | 514.1 |  | 2023-01-31 | X | X
20INR0164 | BPL Files Solar | Hill | 2023-03-31 | SOL | 145 |  | 2022-02-10 | X | X
20INR0246 | Ryan Energy Storage | Coryell | 2024-10-21 | OTH | 50 |  | 2022-08-03 | X | X
20INR0249 | Appaloosa Run Wind | Upton | 2023-03-01 | WIN | 171.8 |  | 2022-04-21 | X | X
20INR0250 | Aguayo Wind | Mills | 2022-11-30 | WIN | 196.8 |  | 2022-05-02 | X | X
20INR0269 | Texas Solar Nova 2 | Kent | 2023-12-29 | SOL | 201.1 |  | 2022-07-29 | X | X
21INR0019 | Zier Solar | Kinney | 2023-12-31 | SOL | 163 |  | 2022-09-27 | X | X
21INR0027 | Zier Storage | Kinney | 2023-06-15 | OTH | 40.4 |  | 2022-09-27 | X | X
21INR0203 | Eastbell Milam Solar | Milam | 2023-10-31 | SOL | 244.9 |  | 2022-11-03 | X | X
21INR0220 | Maleza Solar | Wharton | 2024-06-01 | SOL | 254.9 |  | 2022-12-08 | X | X
21INR0223 | Tulsita Solar | Goliad | 2024-12-31 | SOL | 261 |  | 2022-10-03 | X | X
21INR0253 | Ulysses Solar | Coke | 2024-11-01 | SOL | 150 |  | 2022-12-05 | X | X
21INR0257 | Mercury Solar | Hill | 2022-12-31 | SOL | 203.5 |  | 2022-03-21 | X | X
21INR0344 | Lunis Creek Solar SLF | Jackson | 2024-12-31 | SOL | 617.1 |  | 2022-09-27 | X | X
21INR0351 | 7V Solar | Fayette | 2024-04-30 | SOL | 246.3 |  | 2022-10-07 | X | X
21INR0353 | Big Elm Solar | Bell | 2023-10-31 | SOL | 221.8 |  | 2022-09-08 | X | X
21INR0389 | Red Tailed Hawk Solar | Wharton | 2024-03-31 | SOL | 353.4 |  | 2023-02-03 | X | X
21INR0401 | Young Wind | Young | 2022-12-31 | WIN | 499.1 |  | 2022-03-31 | X | X
21INR0442 | Myrtle Storage | Brazoria | 2023-12-15 | OTH | 155.04 |  | 2023-01-31 | X | X
21INR0458 | Porter Solar | Denton | 2024-03-31 | SOL | 245 |  | 2022-08-18 | X | X
21INR0484 | Mustang Creek Storage | Jackson | 2023-03-29 | OTH | 70.5 |  | 2022-02-21 | X | X
21INR0492 | Stockyard Grid Batt | Tarrant | 2023-07-01 | OTH | 150.6 |  | 2022-10-26 | X | X
21INR0499 | Neptune Solar | Jackson | 2023-12-22 | SOL | 206.3 |  | 2022-04-11 | X | X
22INR0223 | Eiffel Solar | Lamar | 2023-10-30 | SOL | 240 |  | 2022-10-28 | X | X
22INR0254 | Pisgah Ridge Solar | Navarro | 2022-07-13 | SOL | 253.8 |  | 2022-02-28 | X | X
22INR0295 | Coral Solar | Falls | 2023-12-15 | SOL | 152 |  | 2022-08-05 | X | X
22INR0302 | Bright Arrow Storage | Hopkins | 2023-02-28 | OTH | 103.6 |  | 2022-08-01 | X | X
22INR0327 | Hummingbird Storage | Denton | 2023-12-01 | OTH | 103.8 |  | 2022-09-20 | X | X
22INR0335 | Estonian Solar | Delta | 2023-06-01 | SOL | 202.5 |  | 2022-04-21 | X | X
22INR0336 | Estonian Storage | Delta | 2023-06-01 | OTH | 101.6 |  | 2022-04-21 | X | X
22INR0338 | Limousin Oak Storage | Grimes | 2023-07-01 | OTH | 104.6 |  | 2022-07-29 | X | X
22INR0349 | BRP Antlia BESS | Val Verde | 2023-12-01 | OTH | 70.9 |  | 2022-11-03 | X | X
22INR0359 | Dileo Solar | Bosque | 2023-03-01 | SOL | 72 |  | 2022-07-06 | X | X
22INR0363 | Hayhurst Texas Solar | Culberson | 2023-08-01 | SOL | 25.7 |  | 2022-04-29 | X | X
22INR0366 | BRP Libra BESS | Guadalupe | 2023-07-28 | OTH | 202.4 |  | 2023-02-10 | X | X
22INR0368 | Padua Grid BESS | Bexar | 2024-03-31 | OTH | 202.6 |  | 2022-08-24 | X | X
22INR0397 | Buckeye Corpus Fuels Solar | Nueces | 2023-12-31 | SOL | 57.6 |  | 2022-12-05 | X | X
22INR0398 | Sabal Storage | Cameron | 2023-05-15 | OTH | 18 |  | 2022-05-02 | X | X
22INR0404 | Fence Post Solar | Navarro | 2023-02-14 | SOL | 236 |  | 2022-04-28 | X | X
22INR0405 | Fence Post BESS | Navarro | 2023-03-03 | OTH | 70 |  | 2022-04-27 | X | X
22INR0409 | Stampede Solar | Hopkins | 2023-02-03 | SOL | 255 |  | 2022-04-11 | X | X
22INR0410 | Stampede BESS | Hopkins | 2023-03-03 | OTH | 70 |  | 2022-04-11 | X | X
22INR0412 | Andromeda Solar | Scurry | 2023-06-30 | SOL | 320 |  | 2022-04-12 | X | X
22INR0429 | Sun Valley BESS | Hill | 2023-09-10 | OTH | 101.4 |  | 2023-01-31 | X | X
22INR0454 | DR Solar | Culberson | 2024-06-01 | SOL | 46 |  | 2022-08-24 | X | X
22INR0455 | Blue Sky Sol | Crockett | 2023-11-24 | SOL | 101.2 |  | 2022-02-07 | X | X
22INR0485 | House Mountain | Brewster | 2023-05-31 | OTH | 63 |  | 2022-04-21 | X | X
22INR0490 | Callisto I Energy Center | Harris | 2023-09-01 | OTH | 203 |  | 2022-09-20 | X | X
22INR0495 | TIMBERWOLF BESS 2 | Crane | 2023-09-01 | OTH | 150 |  | 2023-02-01 | X | X
22INR0509 | Turquoise Storage | Hunt | 2022-12-31 | OTH | 190 |  | 2022-04-27 | X | X
22INR0524 | St. Gall I Energy Storage | Pecos | 2023-08-01 | OTH | 102.6 |  | 2023-01-19 | X | X
22INR0549 | Tanzanite Storage | Henderson | 2023-12-31 | OTH | 257.7 |  | 2022-11-04 | X | X
22INR0551 | Wolf Tank Storage | Webb | 2022-12-01 | OTH | 150 |  | 2022-04-29 | X | X
22INR0552 | Sowers Storage | Kaufman | 2023-10-31 | OTH | 203 |  | 2022-12-05 | X | X
23INR0007 | Outpost Solar | Webb | 2024-04-01 | SOL | 513.7 |  | 2022-11-07 | X | X
23INR0047 | Charger Solar | Refugio | 2024-05-31 | SOL | 406.8 |  | 2022-04-04 | X | X
23INR0054 | Tanglewood Solar | Brazoria | 2025-01-16 | SOL | 257 |  | 2023-02-10 | X | X
23INR0095 | Brotman Power Station | Brazoria | 2023-06-01 | GAS | 356.2 |  | 2022-07-25 | X | X
23INR0124 | Coral Storage | Falls | 2023-12-15 | OTH | 101 |  | 2022-11-07 | X | X
23INR0153 | Mercury II Solar | Hill | 2022-12-31 | SOL | 203.2 |  | 2022-03-21 | X | X
23INR0154 | Ebony Energy Storage | Comal | 2024-02-29 | OTH | 205 |  | 2023-02-10 | X | X
23INR0160 | Grimes County Solar | Grimes | 2024-09-30 | SOL | 210 |  | 2022-09-21 | X | X
23INR0162 | Redonda Solar | Zapata | 2024-12-01 | SOL | 253.2 |  | 2022-04-27 | X | X
23INR0166 | Great Kiskadee Storage | Hidalgo | 2024-08-01 | OTH | 103.1 |  | 2022-09-20 | X | X
23INR0223 | Garcitas Creek Solar | Jackson | 2024-07-30 | SOL | 201.9 |  | 2022-08-24 | X | X
23INR0239 | Giga Texas Energy Storage | Travis | 2023-08-10 | OTH | 131.1 |  | 2023-02-01 | X | X
23INR0339 | Remy Jade Power Station | Harris | 2024-04-01 | GAS | 408 |  | 2022-11-08 | X | X
23INR0343 | Guajillo Energy Storage | Webb | 2024-09-30 | OTH | 201.1 |  | 2022-06-27 | X | X
23INR0363 | Brazos Bend BESS | Fort Bend | 2024-03-29 | OTH | 101.21 |  | 2022-11-16 | X | X
23INR0369 | Anemoi Energy Storage | Hidalgo | 2023-12-20 | OTH | 205 |  | 2022-07-28 | X | X
23INR0371 | Rodeo Ranch Energy Storage | Reeves | 2023-07-17 | OTH | 307.5 |  | 2022-07-28 | X | X
23INR0419 | SOHO BESS | Brazoria | 2024-06-01 | OTH | 206.32 |  | 2023-01-19 | X | X
23INR0472 | Frontera Energy Center | Hidalgo | 2023-06-30 | GAS | 538.5 |  | 2022-11-01 | X | X
23INR0506 | Beachwood II Power Station | Brazoria | 2024-03-01 | GAS | 102 |  | 2022-08-24 | X | X
23INR0551 | Brotman II Power Station | Brazoria | 2023-06-01 | GAS | 102 |  | 2022-07-25 | X | X
24INR0147 | Citadel BESS | Harris | 2024-05-07 | OTH | 201.3 |  | 2023-01-19 | X | X
23INR0111 | GULF STAR SOLAR SLF | Wharton | 2024-02-01 | SOL | 300.5 |  | 2021-11-05 | X | X
21INR0324 | Board Creek Wind | Navarro | 2023-05-01 | WIN | 299.2 |  | 2022-04-05 | X | X
PG 6.9(1) Inactive Projects
INR | Project Name | Fuel | County | Inactive Date | MW
19INR0099a | Kontiki 1 Wind (ERIK) | WIND | Glasscock | 2022-03-10 | 255.3
19INR0099b | Kontiki 2 Wind (ERNEST) | WIND | Glasscock | 2022-03-10 | 255.3
PG 6.9(1) Cancelled Projects
INR | Project Name | Fuel | County | Inactive Date | MW
23INR0042 | Delilah Solar 3 | SOLAR | Lamar | 2023-05-31 | 204.1
23INR0060 | Delialh Solar 4 | SOLAR | Lamar | 2023-05-31 | 90
Retired Units
Unit Name | MW For Grid | 2025 | 2028 | Comments
OCI_ALM1_ASTRO1 | 1 | X | X | NSO posted
DOWG_DOW_G37 | 59.19 | X | X | NSO posted
J T Deely Unit 1 | 420 | X | X | NSO posted
J T Deely Unit 2 | 420 | X | X | NSO posted
Braunig Units 1, 2, and 3 | 859 | X | X | NSO posted
Sommers Unit #1 | 420 |  | X | NSO posted
Coleto Creek | 655 |  | X | NSO posted
Spruce Unit #1 | 560 |  | X | NSO posted
Mothballed Units
Unit Name | MW For Grid | 2025 | 2028 | Comments
RAY OLINGER STG 1 (AS OF 4/5/22) | 78 | X | X | NSO posted
CALENERGY-FALCON SEABOARD STG 3 (AS OF 7/8/22, DUE TO FORCED OUTAGE) | 62 | X | X | NSO posted
BRANDON (LP&L) (DGR) | 25 | X | X | NSO posted
R MASSENGALE CTG 1 (LP&L) | 20 | X | X | NSO posted
R MASSENGALE CTG 2 (LP&L) | 20 | X | X | NSO posted
R MASSENGALE STG (LP&L) | 58.9 | X | X | NSO posted
TY COOKE CTG 1 (LP&L) | 18.7 | X | X | NSO posted
TY COOKE CTG 2 (LP&L) | 26.6 | X | X | NSO posted
WICHITA FALLS COGEN 4 | 17 | X | X | NSO posted
Deer Park Shell Energy Unit 1 | 65 | X | X | NSO posted
Deer Park Shell Energy Unit 2 | 65 | X | X | NSO posted
Deer Park Shell Energy Unit 3 | 30 | X | X | NSO posted
Deer Park Shell Energy Unit 4 | 30 | X | X | NSO posted

## Renewable Generation Dispatch
Date Last Updated: | 2023-05-02 | Back
Status | Final
Solar
http://www.ercot.com/gridinfo/resource
Weather years used for analysis:
Base | 2013
Wind
http://www.ercot.com/gridinfo/resource
Weather years used for analysis:
Base | 2013
Hydro
Unit specific monthly capacity factors modeled based on historical dispatch levels during the last three years.

## Switchable Generation
Date Last Updated: | 2023-05-18 | Back
Status | Final
Operational Resources (Switchable)
Unavailable to ERCOT during summer 6/1-9/30
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2025 | 2028
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 54 | 54
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | 54 | 54
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2016 | 54 | 54
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190 | 190
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | -
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | -727 | -542
Unavailable to ERCOT during winter 12/1-2/28
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2025/2026 | 2027/2028
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | -
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | -185 | -

## DC Tie Modeling & Dispatch
Date Last Updated: | 2023-05-02 | Back
Status | Final
Economic Analysis
DC Tie Dispatch - 8760-hour Assumptions
DC_E | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_N | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_L | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_R | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.

## Reserve Requirement
Date Last Updated: | 2023-05-02 | Back
Status | Final
Economic Analysis | 1784 MW
The reserve requirement used in the economic models are based on a review of ERCOT’s 2023 Responsive Reserve and Regulation Up requirements. Note that the MW contribution of load resources is not an input into the economic model.

## Fuel Price Assumptions
Date Last Updated: | 2023-05-02 | Back
Status | Final
Source | EIA 2023 AEO Reference Case
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2023 | 5.7024 | 5.4821 | 5.1284 | 5.2785 | 5.4208 | 5.5119 | 5.3497 | 5.427 | 5.4187 | 5.6084 | 5.6072 | 5.8739 | 5.4841
2024 | 4.5172 | 4.3426 | 4.0625 | 4.1814 | 4.2941 | 4.3662 | 4.2378 | 4.299 | 4.2925 | 4.4427 | 4.4418 | 4.653 | 4.3442
2025 | 3.9548 | 3.802 | 3.5567 | 3.6608 | 3.7596 | 3.8227 | 3.7102 | 3.7638 | 3.7581 | 3.8896 | 3.8888 | 4.0737 | 3.8034
2026 | 3.5483 | 3.4112 | 3.1912 | 3.2846 | 3.3732 | 3.4298 | 3.3289 | 3.377 | 3.3718 | 3.4899 | 3.4891 | 3.655 | 3.4125
2027 | 3.3737 | 3.2433 | 3.0341 | 3.1229 | 3.2071 | 3.261 | 3.165 | 3.2108 | 3.2059 | 3.3181 | 3.3174 | 3.4752 | 3.2445
2028 | 3.3824 | 3.2518 | 3.042 | 3.131 | 3.2154 | 3.2694 | 3.1732 | 3.2191 | 3.2142 | 3.3267 | 3.326 | 3.4842 | 3.253

## Emission Cost Assumptions
Date Last Updated: | 2023-05-18 | Back
Status | Final
Source | EIA AEO
Emission | $/ton
Nox (Seasonal) | 166
SO2 | 0
CO2 | 0

## Economic Case-Load Forecast
Date Last Updated: | 2023-06-20 | Back
Status | Final
Load forecast (economic)
Weather year assumption | Base: 2013
The peak and hourly profile information will be posted along with the case information
Note that the 2013 weather scenario is the base weather scenario used as the starting point in the economic analysis.