## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2021-07-14
3.1.2 | RPG Projects Backed Out For Lack of Approval or Moved Due to ISD Change | Final | 2021-07-14
3.1.2 | Recently Approved RPG Projects | Final | 2021-10-25
3.1.2 | Model Updates & Corrections | Final | 2021-11-13
3.1.3 | Transmission & Generation Outages | Final | 2021-09-13
3.1.5 | Temperatures Used in Dynamic Rating Calculation | Final | 2021-07-14
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2021-07-14
3.2.2 | Renewable Generation Dispatch | Final | 2021-07-14
3.2.3 | Switchable Generation | Final | 2021-07-13
3.2.4 | DC Tie Modeling and Dispatch | Final | 2021-07-13
3.2.5 | Reserve Requirement | Final | 2021-07-13
3.2.6 | Fuel Price Assumptions | Final | Tuesday, July 6, 2021
Demand
3.3 | Load Forecast (Reliability) 90/10 Forecast SSWG Forecast Bounded Higher of Calculations RTP Summer Peak Case Forecast RTP Min Load Case Forecast | Final | 2021-11-19
Other Studies
4.2.2 | Sensitivity Analysis | Final | 2021-11-29

## Start Cases
Date Last Updated: | 2021-07-14 | Back
Status | Final
SSWG Case Version: | 20SSWG Update 1 Final - October 08, 2020
On Peak Cases:
20SSWG_2023_SUM1_U1_Final_10082020.raw
20SSWG_2024_SUM1_U1_Final_10082020.raw
20SSWG_2026_SUM1_U1_Final_10082020.raw
20SSWG_2027_SUM1_U1_Final_10082020.raw
Off Peak Case:
20SSWG_2024_MIN_U1_Final_10082020.raw

## RPG Projects Moved or Removed
Date Last Updated: | 2021-07-14 |  | Back
Status | Final
Based on TPIT dated: | 2020-10-01
RPG Projects Removed from the RTP Cases
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
48816 | Mulberry Creek: Rebuild 345 kV station | Rebuild Mulberry Creek 345 kV station | Mulberry Creek |  | 1015 - 1193 | AEP TNC | Michael Glueck mlforcum@aep.com 918-599-2674 | 2776 | 2023-05-30 01:00 | 345 | Tier 3 |  |  |  | 6230, 1435, 6235, 60040, 6232, 60788 | Y | 48817 | 48816
5466 | Redland Switch 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Redland Switch previously known as Herty North | Redland | Redland |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6076 | 2022-05-15 | 345 | Tier 3 |  |  |  | 3319, 3321, 3322 | Y | 13170 | 5466
5467 | Nacogdoches Southeast_Redland 345kV Line | Establish a new 345kV Line between Nacogdoches Southeast Switch and Redland Switch | Nacogdoches Southeast | Redland |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 2022-05-15 | 345 | Tier 2 |  |  |  | 3119, 3321 | Y | 13171 | 5467
56350A | Burnett-Ringgold Magnolia Tap 69 kV Line |  | Burnett | Ringgold Magnolia Tap |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4015 | 2022-05-15 | 69 | Tier 3 |  |  |  | 1452, 1523, 1543, 1544, 1426, 1491, 1545 | Y | 56861 | 56350
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 2023-05-15 | 138 | Tier 2 |  |  |  | 1881, 2202 | Y | 12436 | 4834
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 2023-05-15 | 138 | Tier 3 |  |  |  | 1032, 1333 | Y | 13139 | 5436
5475 | Lufkin Switch - Redland Switch 345 kV Line | Construct a new 345 kV Line from Lufkin Switch to Redland Switch | Lufkin Switch | Redland Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 2023-05-15 | 345 | Tier 2 |  |  |  | 3117, 3321 | Y | 13180 | 5475
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line | Forney | Lake Hubbard |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4233 | 2023-05-15 | 345 | Tier 2 |  |  |  | 2455, 2467 | Y | 13252 | 5525
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station | Forney |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 2023-05-15 | 345 | Tier 3 |  |  |  | 2467, 2433, 2437, 2470, 2478, 150189, 2438, 12438 | Y | 49916 | 5526
5624 | Killeen Sw. Sta. 345/138 kV Autotransformer Replacement | Replace existing autotransformer | Killeen Sw. Sta. | Killeen Sw. Sta |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R797 | 2023-05-15 | 345 | Tier 3 |  |  |  | 3422, 3423, 13423 | Y | 13354 | 5624
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North | Shamburger North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 2023-05-15 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2478, 3103, 3201, 3206 | Y | 13696 | 5981
7023 | Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Upgrade existing Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Hicks Sw. Sta. | Roanoke Sw. Sta. |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5256 | 2023-05-15 | 345 | Tier 3 |  |  |  | 1855, 2081, 1845, 1851 | Y | 52815 | 7023
12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer | Forney Sw. Sta. |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4037 | 2023-05-15 | 345 | Tier 3 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | 9769 | 2489
56350B | Burnett-Ringgold Magnolia Tap 69 kV Line |  | Bowie | Ringgold Magnolia Tap |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4015 | 2023-05-15 | 69 | Tier 3 |  |  |  | 1540, 1545, 1547, 1548, 1550, 33770 | Y | 56862 | 56350
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station | Lake Hubbard |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4139 | 2023-05-17 | 345 | Tier 3 |  |  |  | 12455, 12456, 2401, 2402, 2455 | Y | 13249 | 5522
52070 | Carver - Maxwell: Line Rebuild | Carver - Maxwell: Line Rebuild | Carver | Maxwell | 1079 - 1252 | AEP | Charity Kreher bcogan@aep.com 918-599-2853 | 3804 | 2024-10-31 | 138 | Tier 3 |  |  |  | 8259, 8261, 60412, 8991, 8998, 60440 | Y | 52071 | 52070
54892 | Eden to North Brady: Rebuild 69 kV line | Rehab Eden to North Brady 69 kV line | Eden | North Brady | 1039 - 1266 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 1856 | 2024-04-30 | 69 | Tier 3 |  |  |  | 6384, 60797, 6006, 6372, 6380, 6385 | Y | 54893 | 54892
55299 | Munday to Throckmorton: Rebuild 69 kV line | Rehab 69 kV line from Munday to Throckmorton | Munday | Throckmorton | 1094 - 1272 | AEP TNC | Charity Kreher mlforcum@aep.com 918-599-2857 | 1862 | 2023-11-30 | 69 | Tier 3 |  |  |  | 6107, 6204, 6205 | Y | 55300 | 55299
54523 | BEPC_20TPIT54523_Moffat_Hasse | At some later point, this will be broken up into phases. The submission to RPG is being prepared and will be submitted in April 2020. | Moffat | Hasse |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2024-02-05 | 138 | Tier 2 |  |  |  | 142, 145, 149, 152, 153, 157, 158, 159, 250, 254, 258, 262, 265, 268, 269, 273, 277, 126, 141, 3583, 1649, 3586, 37580 | Y | 54524 | 54523
55603 | Big Foot to Pearsall: Rebuild 69 kV line | Rebuild 69 kV line from Big Foot to Dilley | Big Foot | Pearsall | 1104 - 1282 | AEP | Bill Roberts bcogan@aep.com 918-599-2857 | 3821 | 2022-11-30 | 69 | Tier 3 |  |  |  | 8218, 8216 | Y | 55604 | 55603
55605 | New Barksdale to Rocksprings: Rebuild 69 kV line | Rebuild 69 kV line from Campwood to Rocksprings | New Barksdale | Rocksprings | 1102 - 1280 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3819 | 2023-11-01 | 69 | Tier 3 |  |  |  | 8365, 8238 | Y | 55606 | 55605
55617 | Campwood to New Barksdale: Rebuild 69 kV line | Rebuild 69 kV line from Campwood to Rocksprings | New Barksdale | Campwood | 1102 - 1280 | AEP | Glen Reed gareed@aep.com 918-599-2664 | 3820 | 2024-11-01 | 69 | Tier 3 |  |  |  | 8633, 8365 | Y | 55618 | 55617
5496 | Forney - Royse 345 kV Line | Upgrade existing Royse - Forney 345 kV Line | Royse | Forney |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4235 | 2024-05-10 | 345 | Tier 3 |  |  |  | 2437, 2467, 2470, 2474, 2478 | Y | 49917 | 5496
5479 | Trinidad_TriC_Watermill_345kV_DCKT | Upgrade existing DCKT line | Trinidad Sw. Sta | TriCorner/Watermill |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4045 | 2024-05-15 | 345 | Tier 3 |  |  |  | 2432, 3123, 3124 | Y | 13184 | 5479
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer | Elkton | Elkton |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6032-E | 2024-05-15 | 345 | Tier 3 |  |  |  | 3105, 3106, 29150 | Y | 10501 | 3155
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | Royse | Forney |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 2024-05-15 12:00 | 345 | Tier 3 |  |  |  | 2469, 2470, 12471, 2437, 2467, 2471, 2478, 2702, 2474, 2710, 3223, 12702 | Y | 49918 | 5524
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Shamburger North | Shamburger |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6085 | 2024-05-28 | 345 | Tier 3 |  |  |  | 3103, 3223 | Y | 14033 | 6304
55622 | Dilley to Pearsall: Rebuild 69 kV line | Rebuild 69 kV line from Big Foot to Dilley | Dilley | Pearsal | 1104 - 1282 | AEP TCC | Brandon Cogan bcogan@aep.com 918-599-2857 | 3822 | 2023-05-01 | 69 | Tier 3 |  |  |  | 8216, 8208 | Y | 55623 | 55622
55626 | Ganso to Hamilton Road: Rebuild 138 kV line | Rebuild 138 kV line from Ganso to Hamilton Road | Maverick | Hamilton Road | 1105 - 1283 | AEP | Bill Roberts bcogan@aep.com 918-599-2857 | 3824 | 2024-05-30 | 138 | Tier 3 |  |  |  | 8267, 8692, 8255 | Y | 55627 | 55626
5492 | Venus - Webb/Cedar Hill Sw. Sta. 345 kV DCKT Line | Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line | Ellis | Tarrant |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4230 | 2022-12-15 | 345 | Tier 4; This project was reclassified as Tier 3 after the creation of this TPIT |  |  |  | 1904, 1906, 2420, 11901 | Y | 13230 | 5492
4804 | Wichita Falls South 345/138 kV autotransformer | Install autotransformer | Wichita Falls South |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R4010 | 2023-05-15 | 345 | Tier 4; This project was reclassified as Tier 3 after the creation of this TPIT |  |  |  | 11464, 11465, 1422, 1425, 1464 | Y | 12410 | 4804
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade the existing 345 kV Line | Sherry | Webb/Kennedale |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4252 | 2025-05-15 | 345 | Tier 4; This project was reclassified as Tier 3 after the creation of this TPIT |  |  |  | 1911, 1918, 1930, 1929, 1932, 1934 | Y | 14016 | 6287
RPG Projects With ISD Changes
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Original Projected In-Service Date (Month/Yr) | New Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
45399 | Bearkat Loop - Bearkat to Longshore | Adds 345 KV line from Bearkat to Longshore. | Bearkat | Longshore |  | WETT/ONCOR | Christina Minchew christina.minchew@windene 512-436-9469 |  | 2022-03-31 | 2022-09-01 | 345 | Tier 1 | 2017-08-15 | 2018-09-19 | 2018-10-09 | 1058, 59903 | Y | 45473 | 45399
45501 | Eldorado Live Oak to Sonora: Rebuild 69 kV line | Rehab Eldorado Live Oak to Sonora 69 kV line | Eldorado Live Oak | Sonora | 982 - 1160 | AEP TNC | Dave Baker mlforcum@aep.com 918-599-2674 | 2769 | 2023-03-31 01:00 | 2024-05-01 | 69 | Tier 3 | 2018-12-18 | 2019-01-17 |  | 6498, 6505, 6509, 6510, 6513 | Y | 45502 | 45501
50900 | Mason to North Brady: Rebuild 69 kV line | Rehab Mason to North Brady 69 kV line | Mason | North Brady | 1046 - 1219 | AEP TNC | David Baker mlforcum@aep.com 918-599-2674 | 2794 | 2022-03-31 | 2024-03-01 | 69 | Tier 3 | 2019-10-01 | 2019-11-01 |  | 6006, 6381, 6393, 6406, 60386 | Y | 50901 | 50900
52523A | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Hayes to Alief as a Clearance upgrade | Hayes | Alief |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 | 2021-12-01 | 138 | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44020, 44120, 44310 | Y | 57335 | 52523
52523B | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Alief to Stafford as a Clearance upgrade | Alief | Stafford |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 | 2021-12-01 | 138 | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44020, 44671 | Y | 57336 | 52523
52523C | Hayes to WA Parish Ckt.09A Upgrades | Upgrade Ckt.09A Stafford to WA Parish as a Clearance upgrade | Stafford | WA Parish |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2022-12-31 | 2021-12-01 | 138 | Tier 3 | 2019-12-18 | 2020-01-16 |  | 44015, 44671 | Y | 57337 | 52523
51001 | Friess Ranch to Sonora: Rebuild 69 kV line | Rebuild Rocksprings to Sonora 69 kV line | Friess Ranch | Sonora | 1044 - 1217 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2791 | 2022-04-30 12:00 | 2023-03-01 | 69 | Tier 3 |  |  |  | 8238, 8239, 60438, 6513, 6570 | Y | 51002 | 51001
51005 | Rocksprings to Friess Ranch: Rebuild 69 kV line | Rebuild Rocksprings to Sonora 69 kV line | Rocksprings | Friess Ranch | 1044 - 1217 | AEP TNC | Nathan Cowan mlforcum@aep.com 918-599-2674 | 2792 | 2022-04-30 | 2023-03-01 | 69 | Tier 3 |  |  |  | 8238, 8239 | Y | 51006 | 51005

## Recently Approved RPG Projects
Date Last Updated: | 2021-10-25 |  | Back
Status | Final
Project Name | TDSP | Approve Date
Texas City Transmission Improvement Project | TNMP | 2020-09-22
AEPSC Lake Pauline Area Improvement Project | AEP | 2020-11-09
AEPSC Hamilton Road to Maxwell 138 kV line Rebuild Project | AEP | 2021-01-19
AEPSC Coleto Creek to Kenedy SS 138 kV Transmission Project | AEP | 2020-09-11
AEPSC Port Lavaca Area Improvement Project | AEP | 2021-10-22
Oncor Burnett - Bowie 69 kV Line Upgrade Project | Oncor | 2021-06-22
Oncor Midland East Area Project | Oncor | 2021-03-30
STEC LCRA TSC Second Circuit Bakersfield to Big Hill Project | STEC LCRA TSC | 2021-06-11

## Model Updates & Corrections
Date Last Updated: | 2021-11-13 | Back
Status | Final
Model Corrections/Updates Made to the 2021 RTP Cases
Transmission Changes | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Corrected impedance values for the Forney (2437) to Royse (2478) 345-kV line | Oncor | X |  |  |  |  | Based on the March 2021 SSWG cases
Corrected impedance values at Collins series reactor (29555) to (2370) | Oncor | X | X | X | X | X | Based on the March 2021 SSWG cases
Updated ratings for the following lines: 38650-39400, 39400-39435, 39345-39400, 39340-39345, 39340-39360, 38850-38920, 38930-38950, 38530-38575, 39530-39560 | TNMP | X | X | X | X | X | Based on TNMP feedback
Corrected modeling of the Oncor Eagle Mountain-Saginaw Switch Recently Approved RPG project | Oncor | X | X | X | X | X | Based on Oncor feedback
Added the last phase of the CNP Wallis-Peters recently approved RPG project (22TPIT59322) | CNP | X | X | X | X | X | Based on CNP feedback
Interconnected the Mirage unit (111161) so that it is no longer islanded | CNP |  | X | X | X | X | Based on CNP feedback
Updated the modeling of the AEP Alamito to Alpine rehab project | AEP |  | X | X | X | X | Based on AEP feedback
Removed the AEP Alamito to Alpine rehab project | AEP | X |  |  |  |  | Based on AEP feedback
Applied CNP Tier 4 Project 20TPIT48281 (MOD 48281) Angleton Upgrade | CNP | X | X | X | X | X
Removed all MSL definitons from the cases | CNP | X | X | X | X | X
Added the CNP Tier 4 Project (MOD 59346) to upgrade the Dunvale to Hilcroft line (47072-47191) | CNP | X | X | X | X | X | Based on TSP feedback
Added Tier 4 MOD project 59099 | AEP | X | X | X | X | X | Based on AEP feedback
Added Tier 4 MOD project 62305 | AEP | X | X | X | X | X | Based on information from MOD
Added Tier 4 MOD project 59319 | CNP | X | X | X | X | X | Based on information from MOD
Corrected NW Carrollton xfmr reg bus | Oncor | X | X | X | X | X | Based on TSP feedback
Updated West Denton Xfmr ratings | Denton | X | X | X | X | X | Based on TSP feedback
Added Tier 4 MOD project 59265 | Oncor | X | X | X | X | X | Based on information from MOD
Corrected the line rating for the Blackfork-TylerNW 138 kV line (3137-3141) | Oncor | X | X | X | X | X | Based on Oncor feedback
Kiamichi Bus Reg Fix | Oncor | X | X | X | X | X
Venus_MOD5492-ModelUpdate-AllYears | Oncor | X | X | X | X | X | Based on information from MOD
Houston School Re-Model | Oncor | X | X | X | X | X | Based on Oncor feedback
McCree-Centrval-Oates FY2023 | Oncor | X | X | X | X | X | Based on information from MOD
Added tier 4 MOD project: Desoto Switch-Glen Heights line upgrade | Oncor | X | X | X | X | X | MOD 59518
Updated AEP Live Oak to Sonoma MOD 4551 | AEP | X | X | X | X | X | Based on AEP feedback
Updated AEP Mason to North Brady MOD 50900 | AEP | X | X | X | X | X | Based on AEP feedback
Deleted a redundant modeled transformer at Bluff Creek | AEP | X | X | X | X | X | Based on Grid Geo and newer SSWG case modeling information
Updated parameters for line from 38410 to 38411 | AEP | X | X | X | X | X | Based on newer SSWG case modeling information
Updated parameters for Lynx 60400 lines to RioPecos and Tombstone | AEP | X | X | X | X | X | Based on MOD 5533 which is already committed
Upgraded 69-kV line from 6225 Abiline Northwest to 6253 Elm Creek | AEP | X | X | X | X | X | Based on Grid Geo and June 2021 SSWG case
Applied various AEN model updates including closing the McNel tie between Austin Energy and LCRA, Big start solar model correction, Patton Lane substation circuit relocation, some transformers model change, switch shunt voltage level change and some bus voltage level change | AEN | x | X | X | X | X | Based on AEN feedback
Added TPIT project 59088 | AEP | x | X | X | X | X | Based on TSP feedback and newer SSWG case modeling information
Corrected line rating for Elmcreek-STP | CPS | x | X | X | X | X | Based on SSWG, NMMS information
Corrected line rating for Barney Davis-Naval Base | AEP | x | X | X | X | X | Based on SSWG, NMMS information
Added tier 4 MOD project (#52068): Pleasanton to Three Rivers: Rebuild 69 kV line | AEP | x | X | X | X | X | Based on information from MOD
Generation Changes | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Corrected coal and nuclear unit max/min Mvar values to account for auxiliary loads | Multiple | X | X | X | X | X | Based on RARF data
Corrected generator IDs from W1/W2 to S1/S2 at units 135271 and 135321 | AEP | X | X | X | X | X | Based on updated modeling information
Updated generator MW and Mvar limits for the following generators: 162451, 162452, 182771, 182772, 182773, 182774, 183021 | AEP, LCRA, Oncor | X | X | X | X | X | Based on updated modeling information
Removed extraordinary dispatch unit at bus 199973 | Sharyland | X | X | X | X | X | Based on updated modeling information
Removed Upton Solar 16INR0114 (bus 132581) due to the project being canceled | LCRA | X | X | X | X | X | Based on updated GINR information
Corrected the regulated bus for the units at busses 111341, 111342, 112311 to regulate their POI | AEP | X | X | X | X | X | Based on updated modeling information
Turn AVR off for the Brandon unit (142761) since it is a DG unit | LPL | X | X | X | X | X | Based on updated modeling information
Corrected the regulated bus for the unit at bus 134291 | Oncor | X | X | X | X | X | Based on updated voltage profile information
Load Changes | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Changed the AGC flag from Yes to No for the self serve load on bus 32794 | Bryan Utilities | X | X | X | X | X | Based on BTU feedback
Adjusted load value associated with Texas City Transmission Improvement Project | TNMP | X | X | X | X | X | Based on modeling information
Corrected ALDR city load value (previously 0 MW) at bus 601 | BEPC | X | X | X | X | X | Based on historical data and models
Corrected ALDR City load values (previously 0 MW) at busses 31, 118, 480, 495, 499, 505, 512, 718 | BEPC, AEP TNC | X | X | X | X | X | Based on historical data and models
Corrected LCRA reactive load modeling at bus 7078 | LCRA | X | X | X | X | X | Based on LCRA feedback
Applied various load updates based on TSP feedback | Multiple | X | X | X | X | X | Based on TSP feedback
Correct the Formosa PUN load vlues in the cases | AEP | X | X | X | X | X | Based on AEP and Formosa feedback
Correct bus 2020 load values in 2023 case | Oncor | X | - | - | - | - | Based on historical data and models
Moved load from Stanton 1229 69-kV bus to 11229 138-kV bus | Oncor | X | X | X | X | X | Part of Oncor Midland East Area Project
Changed load value for Persimmon Gap load at bus 76669 | LCRA | X | X | X | X | X | Based on LCRA feedback
Disconnected S Carbide load at bus 8337 | AEP | X | X | X | X | X | Based on historical data and models
Bus Voltage Changes | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Capacitor Bank Changes | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Corrected the regulated bus for the shunt on bus 80220 from bus 1 to it's own bus (80220) | AEP |  | X |  |  |  | Based on updated SSWG cases
Added Oncor Culberson Loop Capacitor Bank at McLIvain bus 11182 |  | X | X | X | X | X | Based on MOD 59421; Same as project identified in 2020-RTP (FW7)
Made correction to add cap bank on Hutto 138kV bus(3666) | ONCOR | x | X | X | X | X | Based on historical data and models
Phase Shifters | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Synchronous Condensers | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
FACTs, STATCOMs, SVCs | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Batteries | TO | [5 empty] | Comments
|  | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM
Corrected modeling of the Madero battery (21INR0244) | Sharyland | X | X | X | X | X | Based on updated modeling information
Added separate modeling for the Ignatio Battery (21INR0522) | Sharyland | X | X | X | X | X | Based on updated modeling information
Removed inaccurate Lily Solar Battery modeling at bus 151471 and updated modeling of battery at bus 151371 | Rayburn | X | X | X | X | X | Based on updated modeling information

## Transmission & Gen Outages
Date Last Updated: | 2021-09-13 |  | Back
Status | Final
Case
Outaged Elements | Outage Description | Associated TO/RE | 2023 SUM | 2024 SUM | 2024 MIN | 2026 SUM | 2027 SUM | Notes
Some outages collected by ERCOT Market Notice "M-A120220-01 Request for known outage(s) with a duration of at least six months to address NERC Reliability Standard TPL-001-4" were also incorporated in applicable cases.

## Temp. for Dynamic Ratings
Date Last Updated: | 2021-07-14 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 100
East | 105
Far West | 110
North Central | 110
North | 110
South Central | 105
South | 105
West | 110

## Gen Add. Ret. and Mothball
Date Last Updated: | 2021-07-14 |  | Back
Status | Final
Based on generators met PG Section 6.9 requirements (1)9b) through 1(d) by 4/1/2021
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2023 SUM | 2024 MIN | 2024 SUM | 2026 SUM | 2027 SUM | Comments
18INR0079 | Woodward I repower | Pecos | 2021-05-31 | WIN | 0 | 10/30/2020 | X | X | X | X | X | Repower
19INR0117 | Roadrunner Crossing Wind | Eastland | 2021-12-15 | WIN | 200.2 | 09/17/2020 | X | X | X | X | X
19INR0176 | Roughneck Storage | Brazoria | 2021-07-01 | OTH | 50 | 10/28/2020 | X | X | X | X | X
20INR0082 | Vision Solar 1 | Navarro | 2021-11-07 | SOL | 129.24 | 10/27/2020 | X | X | X | X | X
20INR0130 | Ramsey Solar | Wharton | 2021-07-15 | SOL | 514 | 10/07/2020 | X | X | X | X | X
20INR0266 | Tres Bahias Solar | Calhoun | 2022-05-21 | SOL | 195 | 10/07/2020 | X | X | X | X | X
21INR0201 | Brandon | Lubbock | 2021-06-03 | GAS | 21 | 10/30/2020 | X | X | X | X | X
21INR0202 | R Massengale | Lubbock | 2021-06-03 | GAS | 58 | 10/30/2020 | X | X | X | X | X
21INR0365 | Bat Cave Energy Storage | Mason | 2021-06-01 | OTH | 100.49 | 10/29/2020 | X | X | X | X | X
21INR0506 | Ty Cooke | Lubbock | 2021-07-31 | GAS | 33 | 10/30/2020 | X | X | X | X | X
22INR0205 | Sbranch Solar | Wharton | 2022-04-01 | SOL | 154 | 10/07/2020 | X | X | X | X | X
20INR0098 | Danciger Solar | Brazoria | 2022-06-01 | SOL | 203.2 | 11/09/2020 | X | X | X | X | X
20INR0216 | Starr Solar Ranch | Starr | 2022-12-30 | SOL | 135.99 | 11/19/2020 | X | X | X | X | X
21INR0522 | Ignacio Grid | Hidalgo | 2022-03-03 | OTH | 101.52 | 10/30/2020 | X | X | X | X | X
22INR0371 | PES 2 Power Station | Harris | 2021-07-01 | GAS | 102 | 10/30/2020 | X | X | X | X | X
19INR0085 | Blue Jay Solar | Grimes | 2021-12-30 | SOL | 210 | 12/02/2020 | X | X | X | X | X
21INR0387 | Anchor Wind | Eastland | 2021-12-24 | WIN | 300 | 12/02/2020 | X | X | X | X | X
21INR0413 | Big Star Solar | Bastrop | 2022-03-31 | SOL | 220.61 | 12/04/2020 | X | X | X | X | X
21INR0460 | Republic Road Storage | Robertson | 2021-10-29 | OTH | 51.75 | 12/02/2020 | X | X | X | X | X
21INR0323 | Spanish Crown | Falls | 2022-07-15 | SOL | 103.1 | 2021-01-28 | X | X | X | X | X
21INR0341 | Space City Solar | Wharton | 2022-05-06 | SOL | 609.74 | 2021-01-11 | X | X | X | X | X
21INR0357 | SP TX-12B BESS | Upton | 2021-09-01 | OTH | 25.12 | 2021-01-31 | X | X | X | X | X
21INR0496 | Flower Valley II Batt | Reeves | 2021-08-01 | OTH | 100.98 | 2021-01-29 | X | X | X | X | X
21INR0497 | Swoose II | Ward | 2021-08-01 | OTH | 100.98 | 2021-01-29 | X | X | X | X | X
22INR0325 | BRP Dickens BESS | Dickens | 2022-09-30 | OTH | 202.41 | 2021-01-14 | X | X | X | X | X
19INR0056 | Chamon 2 | Harris | 2021-10-01 | GAS | 100 | 2021-02-01 | X | X | X | X | X
19INR0057 | Old Bloomington Road | Victoria | 2021-07-15 | GAS | 100 | 2021-02-01 | X | X | X | X | X
20INR0097 | El Suaz Ranch | Willacy | 2022-09-30 | WIN | 301.74 | 2021-02-03 | X | X | X | X | X
21INR0205 | Radian Solar | Brown | 2022-11-30 | SOL | 374.4 | 2021-02-02 | X | X | X | X | X
21INR0510 | Crossett Power Batt | Crane | 2021-08-01 | OTH | 206.97 | 2021-02-01 | X | X | X | X | X
21INR0521 | White Mesa 2 Wind | Coke | 2021-11-30 | WIN | 348 | 2021-02-01 | X | X | X | X | X
22INR0322 | BRP Paleo BESS | Hale | 2022-09-30 | OTH | 202.4 | 2021-02-05 | X | X | X | X | X
16INR0085 | Priddy Wind | Mills | 2021-11-30 | WIN | 300 | 2021-03-29 | X | X | X | X | X
19INR0103 | Rodeo Solar | Andrews | 2022-01-30 | SOL | 200 | 2021-03-10 | X | X | X | X | X
20INR0120 | Vortex Wind | Throckmorton | 2021-12-31 | WIN | 350.15 | 2021-03-25 | X | X | X | X | X
20INR0142 | Ajax Wind | Wilbarger | 2021-12-01 | WIN | 366.6 | 2020-08-03 | X | X | X | X | X
21INR0012 | Air Products GCA | Galveston | 2022-05-15 | GAS | 14 | 2020-08-21 | X | X | X | X | X
21INR0221 | Samson Solar 1 | Lamar | 2021-12-31 | SOL | 250 | 2020-08-26 | X | X | X | X | X
21INR0389 | Red-tailed Hawk Solar | Wharton | 2022-05-31 | SOL | 355.27 | 2020-08-28 | X | X | X | X | X
21INR0449 | Panther Creek III Repower | Howard | 2021-03-30 | WIN | 15.96 | 2020-08-03 | X | X | X | X | X | Repower
21INR0491 | Samson Solar 3 | Lamar | 2021-12-31 | SOL | 250 | 2020-08-27 | X | X | X | X | X
22INR0202 | Delilah Solar 1 | Lamar | 2022-06-01 | SOL | 300 | 2021-03-23 | X | X | X | X | X
22INR0203 | Delilah Solar 2 | Lamar | 2023-06-30 | SOL | 310 | 2021-03-23 | X | X | X | X | X
22INR0242 | Bright Arrow Solar | Hopkins | 2022-12-15 | SOL | 324.72 | 2021-03-01 | X | X | X | X | X
22INR0352 | Sparta Solar | Bee | 2022-05-02 | SOL | 256 | 2020-08-17 | X | X | X | X | X
23INR0042 | Delilah Solar 3 | Lamar | 2023-06-30 | SOL | 200 | 2021-03-23 | X | X | X | X | X
23INR0060 | Delilah Solar 4 | Lamar | 2023-06-30 | SOL | 90 | 2021-03-23 | X | X | X | X | X
20INR0221. | Braes Power Plant | Fort Bend | 2022-03-07 | GAS | 408 | 2021-04-01 | X | X | X | X | X
Retired Units
Unit Name | MW For Grid | 2023 | 2024MIN | 2024 | 2026 | 2027 | Comments
TGF_TGFGT_1 | 69 | X | X | X | X | X | Per NSO Submitted 11/30/2020
RAYBURN_RAYBURG1 | 11 | X | X | X | X | X | Per NSO Submitted 10/1/2020
RAYBURN_RAYBURG2 | 11 | X | X | X | X | X | Per NSO Submitted 10/1/2020
KEO_KEO_SM1 | 150 | X | X | X | X | X | Per NSO Submitted 1/20/2021
ENAS_ENA1 | 63 | X | X | X | X | X | Per NSO Submitted 5/26/2021
Generation Resources Unavailable in Planning Studies Prior to NSO
Unit Name | MW For Grid | 2023 | 2024MIN | 2024 | 2026 | 2027 | Comments
DECKER_DPG2 | 420 | X | X | X | X | X | Public Announcement: https://www.austintexas.gov/edims/document.cfm?id=317748
COLETO_COLETOG1 | 655 |  |  |  |  | X | Vistra notified the U.S. Environmental Protection Agency on November 20, 2020 that Coleto Creek's Primary Ash Pond will be closed to meet requirements of EPA’s coal combustion residual (CCR) rule, and that boiler operations will cease no later than July 17, 2027. The notification is available on Vistra’s public website, https://www.luminant.com/ccr/.
BRAUNIG_VHB1 | 217 |  |  |  | X | X | Public Announcement: https://www.cpsenergy.com/content/dam/corporate/en/Documents/Trustees/COO_Flexible%20Path%20Resource%20Plan_Jan%20BoT%20Final_01242021_V3.pdf
BRAUNIG_VHB2 | 230 |  |  |  | X | X | Public Announcement: https://www.cpsenergy.com/content/dam/corporate/en/Documents/Trustees/COO_Flexible%20Path%20Resource%20Plan_Jan%20BoT%20Final_01242021_V3.pdf
BRAUNIG_VHB3 | 412 |  |  |  | X | X | Public Announcement: https://www.cpsenergy.com/content/dam/corporate/en/Documents/Trustees/COO_Flexible%20Path%20Resource%20Plan_Jan%20BoT%20Final_01242021_V3.pdf
CALAVER_OWS1 | 420 |  |  |  |  | X | Public Announcement: https://www.cpsenergy.com/content/dam/corporate/en/Documents/Trustees/COO_Flexible%20Path%20Resource%20Plan_Jan%20BoT%20Final_01242021_V3.pdf
Mothballed Units
Unit Name | MW For Grid | 2023 | 2024MIN | 2024 | 2026 | 2027 | Comments
CALAVERS_JTD1 | 420 | X | X | X | X | X | Per NSO Submitted 10/25/2013
CALAVERS_JTD2 | 420 | X | X | X | X | X | Per NSO Submitted 10/25/2013
PNPI_GT2 | 71 | X | X | X | X | X | Per NSO Submitted 1/27/2021
AMOCOOIL_AMOCO_5 | 32 | X | X | X | X | X | Per NSO Submitted 1/13/2014
AMOCOOIL _AMOCO_S2 | 75 | X | X | X | X | X | Per NSO Submitted 1/27/2021
Seasonal Mothballed Units (Offline in the 2024 Min case only)
Unit Name | MW For Grid | 2023 | 2024MIN | 2024 | 2026 | 2027 | Comments
LGE_LGE_GT1 | 145 |  | X |  |  |  | Per NSO Submitted 7/19/2019
LGE_LGE_GT2 | 145 |  | X |  |  |  | Per NSO Submitted 7/19/2019
LGE_LGE_STG | 75 |  | X |  |  |  | Per NSO Submitted 7/19/2019
SPNCER_SPNCE_4 | 57 |  | X |  |  |  | Per NSO Submitted 6/8/2018
SPNCER_SPNCE_5 | 61 |  | X |  |  |  | Per NSO Submitted 6/8/2018
NACPW_UNIT1 | 105 |  | X |  |  |  | Per NSO Submitted 5/19/2020
Planned Units Removed Due to Project Cancellation
Unit Name | MW For Grid | 2023 | 2024MIN | 2024 | 2026 | 2027 | Comments
LGE_LGE_GT1 | 104.56 | X | X | X | X | X | Project 16INR0114 was canceled per the Generation Interconnection database.
NOTES: Simple model Settlement Only Distributed Generators (SODGs) were added to reflect those currently operational. Battery models were also added to reflect those currently in the Operations model.

## Renewable Generation Dispatch
Date Last Updated: | 2021-07-14 |  | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR_Summer_PeakAveSolarCapacityPercentages_11-23-2020" posted on the ERCOT website under Resource Adequacy. Note: Solar units are offline in the Min case.
* SOLARPEAKPCT Values | 79.59%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Wind
Information obtained from the spreadsheet "CDR_Summer_PeakAveWindCapacityPercentages_11_23-2020" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Coastal | Summer, Panhandle | Summer, Other
60.52% | 28.86% | 18.69%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Inside Study Region
Summer, Coastal | Summer, Panhandle | Summer, Other
40.68% | 12.95% | 9.555%
Inside and Outside Study Region
Min Case, Coastal | Min Case, Panhandle | Min Case, Other
22.04% | 49.09% | 36.76%
Hydro
Unit specific generation MW dispatch modeled using CDR methodology which is based on historical Settlements HSL dispatch levels during the top 20 load hours of the last three years. Note: All Hydro units are offline in the Min case.
AMI_AMISTAG1 (H1) | 28.6
AMI_AMISTAG2 (H2) | 28.91
AUS_AUSTING1 (H2) | 8.1
AUS_AUSTING1 (H1) | 8
BUC_BUCHANG1 (H1) | 16
BUC_BUCHANG2 (H2) | 16
BUC_BUCHANG3 (H3) | 17
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 14.67
DND_DENISOG2 (H2) | 40
EA_EAGLE_HY1 (H3) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H1) | 0
FAL_FALCONG1 (H1) | 6.86
FAL_FALCONG2 (H2) | 6.8
FAL_FALCONG3 (H3) | 6.57
INKS_INKS_G1 (H1) | 13.42
MAR_MARBFAG1 (H1) | 20.24
MAR_MARBFAG2 (H2) | 19.87
MAR_MARSFOG1 (H1) | 34.27
MAR_MARSFOG2 (H2) | 35.8
MAR_MARSFOG3 (H3) | 35.07
WIR_WIRTZ_G1 (H1) | 28.69
WIR_WIRTZ_G2 (H2) | 29
WND_WHITNEY1 (H1) | 20.04
WND_WHITNEY2 (H2) | 20.04

## Switchable Generation
Date Last Updated: | 2021-07-13 |  | Back
Status | Final
Operational Resources Unavailable to ERCOT (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | North | 2017 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | North | 2017 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | North | 2017 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | North | 2017 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | North | 2017 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  |  |  |  | 542 | 542 | 542 | 542 | 542 | 542 | 542 | 542 | 542 | 542

## DC Tie Modeling & Dispatch
Date Last Updated: | 2021-07-13 |  | Back
Status | Final
Reliability Analysis
DC Tie Dispatch - Summer Peak Conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 0
DC_R* | 0
DC_S* | 0
DC Tie Dispatch - Minimum Load Conditions (MW)
DC_E | 0
DC_N | 0
DC_L* | 0
DC_R* | 0
DC_S* | 0
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.

## Reserve Requirement
Date Last Updated: | 2021-07-13 | Back
Status | Final
Reliabity Cases | 3000 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.

## Fuel Price Assumptions
Date Last Updated: | Tuesday, July 6, 2021 |  | Back
Status | Final
Source
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2021 | 3.35 | 3.1192 | 2.9872 | 3.0442 | 3.0926 | 3.1462 | 3.035 | 3.0441 | 3.0214 | 3.1723 | 3.1912 | 3.3977 | 3.1334
2022 | 3.5259 | 3.2829 | 3.1439 | 3.204 | 3.2549 | 3.3113 | 3.1943 | 3.2038 | 3.18 | 3.3388 | 3.3587 | 3.5761 | 3.2979
2023 | 3.3152 | 3.0868 | 2.9561 | 3.0125 | 3.0605 | 3.1135 | 3.0034 | 3.0124 | 2.99 | 3.1393 | 3.158 | 3.3624 | 3.1009
2024 | 3.1563 | 2.9388 | 2.8144 | 2.8681 | 2.9137 | 2.9642 | 2.8595 | 2.868 | 2.8467 | 2.9888 | 3.0066 | 3.2012 | 2.9522
2025 | 3.3123 | 3.0841 | 2.9536 | 3.0099 | 3.0578 | 3.1108 | 3.0008 | 3.0098 | 2.9874 | 3.1366 | 3.1553 | 3.3595 | 3.0982
2026 | 3.5137 | 3.2715 | 3.1331 | 3.1929 | 3.2437 | 3.2999 | 3.1832 | 3.1927 | 3.169 | 3.3273 | 3.3471 | 3.5637 | 3.2865
2027 | 3.5137 | 3.2715 | 3.1331 | 3.1929 | 3.2437 | 3.2999 | 3.1832 | 3.1927 | 3.169 | 3.3273 | 3.3471 | 3.5637 | 3.2865

## Reliability Case-Load Forecast
Date Last Updated | 2021-11-19 | Back
Status | Final
SSWG Load– Based on 20 SSWG cases posted on 10/08/2020 less self-served load (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2023 | 24782.89 | 3230.58 | 8239.53 | 2231.43 | 28498.23 | 14755.59 | 7235.15 | 2352.89 | 91326.29
2024 | 24902.54 | 3273.52 | 8500.68 | 2250.32 | 29077.74 | 15003.44 | 7602.02 | 2372.24 | 92982.5
2026 | 25052.61 | 3353.88 | 8817.51 | 2304.51 | 30304.75 | 15521.54 | 8035.47 | 2411.56 | 95801.83
2027 | 25152.09 | 3392.66 | 8963.91 | 2330.89 | 31013.5 | 15757.17 | 8140.17 | 2427.66 | 97178.05
ERCOT 90th percentile Load Forecast– less losses for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2023 | 22775.3561 | 2896.5351 | 5737.1764 | 2103.3871 | 27201.6817 | 13986.312 | 7106.5439 | 2343.1797 | 84150.1721
2024 | 22990.6246 | 2940.1404 | 5961.6213 | 2104.7399 | 27431.4604 | 14060.938 | 7320.3603 | 2371.5132 | 85181.3981
2026 | 23368.1402 | 3023.0867 | 6417.6312 | 2107.6615 | 27870.6831 | 14200.0321 | 7432.9494 | 2432.864 | 86853.0482
2027 | 23555.7014 | 3062.1184 | 6647.8939 | 2109.2248 | 28078.867 | 14265.8399 | 7488.3623 | 2466.8283 | 87674.8359
2021 RTP load level with self-served load (MW) (based on on 5% boundary threshold, ERCOT load review results, and the incorporation of the IHS Markit study Permian Basin load forecast)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2023 | 28206.3 | 3090.86 | 6907.87 | 2188.58 | 28771.01 | 14685.59 | 7599.37 | 2505.88 | 93955.46
2024 | 28433.86 | 3136.65 | 7509.17 | 2191.76 | 29142.32 | 14763.98 | 7890.72 | 2544.54 | 95613
2026 | 28831.24 | 3223.74 | 8287.86 | 2201.78 | 29660.11 | 14910.04 | 8243.84 | 2611.78 | 97970.39
2027 | 29028.87 | 3264.73 | 8714.07 | 2207.36 | 29887.33 | 14981.1 | 8315.72 | 2659.35 | 99058.53
2021 RTP load level with self-served load for Off-Peak Case (MW) (based on 2024 SSWG Min Case and adjusted with ERCOT load review results)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2024 | 15074.45 | 1285.09 | 4304.77 | 980.27 | 10603.24 | 5357.5 | 4078.91 | 1230.18 | 42914.41

## Sensitivity Analysis
Date Last Updated: | 2021-11-29 | Back
Status | Final
For Sensitivity 1 nuclear, coal, natural gas, and energy storage resources with at least four hours of duration at their maximum discharge capability were assumed to generate at maximum capacity. The wind and solar output values below reflect their assumed output prior to any redispatch to alleviate transmission constraints.
Sensitivity 1: | Deliverability Assessment Under ERCOT Coincident Summer Peak Load Conditions
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | Coastal | Panhandle | Other
2023 | 85300 | -820 | 3329 | 1278 | 5235 | 13905 | 23747
2026 | 88536 | -820 | 3329 | 1278 | 5235 | 13905 | 23747
Sensitivity 2: | Stressed Resource Availability Under ERCOT Off-Peak Load Condition
Case | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  | Solar Output (MW) | Total Renewable Output (MW) | Generation Resource Capabity Unavailable due to Planned Outages (MW)
|  |  | Coastal | Panhandle | Other
2024 | 58290 | 0 | 0 | 0 | 0 | 0 | 0 | 14043
* negative sign indicating DC tie import.