## Slide 1
Oncor Wilmer 345/138-kV Switch Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
January 22, 2025

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Wilmer 345/138-kV Switch Project for Regional Planning Group (RPG) review in July 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $158.2 million and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in the Dallas, Kaufman, and Ellis Counties in the North Central Weather Zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Dallas, Kaufman, and Ellis Counties in the North Central Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category | Thermal Overloads | Voltage Violations | Unsolved Power Flows
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | 8 | 6 | None
P3: G-1+N-1 | None | None | None
P6-2: X-1+N-1 | 3 | 11 | 2

## Slide 5: Comparison of Project Options
ERCOT analyzed four options and short-listed two options
Among the two short-listed options, Option 1 addresses the reliability violations, and is the least expensive option. Option 1 also improves long-term load-serving capability and requires the least amount of CCN mileages.
Option 1 is the preferred option
* Cost estimates and CCN mileage were provided by TSPs
 | Option 1 | Option 4
Addresses the project needs | Yes | Yes
Meets ERCOT and NERC Reliability Criteria | Yes | Yes
Improves Long-Term Load-Serving Capability | Yes | Yes
CCN Required (~miles) | Yes (3.8) | Yes (14.6)
Construction Feasibility (Based on TSP assessment) | Yes | Yes
Capital Cost Estimates* (~$M) | 158.2 | 198.6

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause a new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability needs in the Dallas, Kaufman, and Ellis Counties in the North Central Weather Zone
TSPs expect to implement the upgrades by May 2026
Estimated Capital Cost: $158.2 million

## Slide 9: ERCOT Recommendation
Expand the existing Wilmer 138-kV substation to establish the new Wilmer 345/138-kV switchyard by installing eight 345-kV, 5000 A breakers and fifteen 138-kV, 3200 A breakers in breaker-and-a-half bus arrangements;
  Install two 345/138-kV autotransformers with normal and emergency ratings of at least 700 MVA and 750 MVA each
  Install two 110.4 MVAr (in three 36.8 MVAr stages) 138-kV capacitor banks
Rebuild portion of the existing Watermill Switch to Tri Corner Switch 345-kV double-circuit transmission line with two separate double-circuit structures starting from Watermill Switch to structure number 102/3, utilizing the existing ROW using a conductor with a normal and emergency rating of at least 2988 MVA, approximately 2.4-mile;
Install two new 345-kV circuits from Watermill Switch to Wilmer Switch on each of the existing Watermill Switch to Tri Corner Switch 345-kV double-circuit structures using a conductor with a normal and emergency rating of at least 2988 MVA, 1.4-mile of the approximately 3.8-mile circuits will require new ROW;
Terminate the existing Lavender Switch to Parkdale Switch 138-kV transmission line to the Wilmer 138-kV switch;
Rebuild the existing Watermill Switch to Lavender Switch 138-kV transmission line using a conductor with a normal and emergency rating of at least 764 MVA, approximately 3.1-mile;

## Slide 10: ERCOT Recommendation (continued)
Rebuild the existing Lavender Switch to Wilmer Switch 138-kV transmission line using a conductor with a normal and emergency rating of at least 764 MVA, approximately 1.2-mile;
Convert the existing Wilmer Switch to Ferris Switch 69-kV transmission line to 138-kV operation with a normal and emergency rating of at least 764 MVA, approximately 4.0-mile;
Relocate the existing Wilmer 138/69-kV autotransformer to the existing Ferris 69-kV switch; and
Ensure all transmission line terminal and associated equipment elements are rated to meet or exceed 5000 A for 345-kV and 3200 A for 138-kV.

## Slide 11: ERCOT Recommendation