## Slide 1
Oncor Venus Switch to Sam Switch 345-kV Line Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
January 22, 2025

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Venus Switch to Sam Switch 345-kV Line Project for Regional Planning Group (RPG) review in June 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $118.9 million and will not require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in the Ellis and Hill Counties in the North Central Weather Zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Ellis and Hill Counties in the North Central Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category | Thermal Overloads | Voltage Violations | Unsolved Power Flows
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | 4 | None | None
P3: G-1+N-1 | 5* | None | None
P6-2: X-1+N-1 | 4* | None | None
* Violations under P1 (N-1) events were also observed under P3 (G-1+N-1) and P6-2 (X-1+N-1) events

## Slide 5: Comparison of Project Options
ERCOT analyzed three options and short-listed two options
Among the two short-listed options, Option 1 addresses the reliability violations, is the least expensive option, and improves long-term load-serving capability.
Option 1 is the preferred option
* Cost estimates were provided by TSPs
 | Option 1 | Option 2
Met ERCOT and NERC Reliability Criteria | Yes | Yes
Improved Operational Flexibility (Planned Maintenance Outages) | Yes | Yes
Improved Long-Term Load-Serving Capability | Yes | Yes
CCN Needed | No | No
Capital Cost Estimates* (~M) | $118.9 | $253.5

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did cause an increase on existing congestion within the study area
    Upgrading the congested line did not yield any economic benefit and therefore will not be recommended for upgrade as part of this project
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability needs in the Ellis and Hill Counties in the North Central Weather Zone
TSPs expect to implement the upgrades by May 2026
Estimated Capital Cost: $118.9 million

## Slide 9: ERCOT Recommendation
Rebuild the existing Venus Switch to Fort Smith Switch 345-kV transmission line with normal and emergency ratings of 1912 MVA or greater, approximately 17.80-mile;
Rebuild the existing Venus Switch to Sam Switch 345-kV transmission line with normal and emergency ratings of 1792 MVA or greater, approximately 38.0-mile;
Rebuild the existing Fort Smith Switch to Files Valley 345-kV transmission line with normal and emergency ratings of 1912 MVA or greater, approximately 3.30-mile; and
Rebuild the existing Sam Switch to Files Valley 345-kV transmission line with normal and emergency ratings of 1792 MVA or greater, approximately 16.90-mile.

## Slide 10: ERCOT Recommendation