## Slide 1
Oncor Forney 345/138-kV Switch Rebuild Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
January 22, 2025

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Forney 345/138-kV Switch Rebuild Project for Regional Planning Group (RPG) review in July 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $103.5 million and will not require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in the Kaufman County in the North Central Weather Zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violation in the Kaufman County in the North Central Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category | Thermal Overloads | Voltage Violations | Unsolved Power Flows
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | None | None | None
P3: G-1+N-1 | None | None | None
P6-2: X-1+N-1 | 1 | None | None

## Slide 5: Comparison of Project Options
ERCOT analyzed five options and short-listed four options
Among the three feasible short-listed options, Option 1A addresses the reliability violation, is the least expensive option that addresses the aging infrastructure issues. Option 1A also improves long-term load-serving capability, is feasible and does not require new right-of-way.
Option 1A is the preferred option
*Cost estimates were provided by TSPs
**Cost estimate does not include ROW costs
 | Option 1 | Option 1A | Option 3
Met ERCOT and NERC Reliability Criteria | Yes | Yes | Yes
Feasibility | Yes | Yes | Yes
Improved Operational Flexibility (Planned Maintenance Outages) | Yes | Yes | Yes
Improved Long-Term Load-Serving Capability | Yes | Yes | Yes
Replaces Aging Infrastructure | Yes | Yes | No
New Right of Way (ROW) required | No | No | Yes
Capital Cost Estimates* (~M) | $103.5 | $100.4 | $76.68**

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1A and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1A did not cause a new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1A to address the reliability need in the Kaufman County in the North Central Weather Zone
TSPs expect to implement the upgrades by December 2025
Estimated Capital Cost: $100.4 million

## Slide 9: ERCOT Recommendation
Rebuild Forney 345/138-kV Switch by installing fifteen 345-kV, 5000 A breakers and ten 138-kV, 3200 A breakers in breaker-and-a-half bus arrangement;
Install a second 345/138-kV autotransformer at Forney Switch with normal and emergency ratings of 700 MVA and 750 MVA respectively;
Connect the Forney substation transformers to the Forney Switch to Mesquite East Switch 138-kV double-circuit transmission line; and
Ensure all line terminal and associated equipment are rated to meet or exceed 5000 A for 345-kV and 3200 A for 138-kV.

## Slide 10: ERCOT Recommendation