## QSE_TSP Info
ERCOT ICCP Change Request - MP Information
Instructions: | Please provide the contact information for the technical contact(s) submitting these changes. This person will be contacted if there are any questions regarding the changes.
Market Participant Name:
Primary Contact Person:
Contact Number:
Contact Number 2:
Contact Email:
Secondary Contact Person:
Contact Number:
Contact Number 2:
Contact Email:

## Conventional Resource
RealQ
StateQ
ERCOT ICCP Change Request Form | [10 empty] | DiscreteQ
Existing point from QSE for both Current and RTC
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way. | [8 empty] | Existing ICCP From QSE in Current System, going away in RTC
Current System only need if providing service, gone in RTC
RED RTC ONLY ICCP from QSE
[8 empty] | Add (-1) Delete (-2) |  | Existing Point FROM ERCOT, exist in both
New RTC ICCP FROM ERCOT
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Up Ramp Rate | ACMQUN_SUBSTN_NURRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Down Ramp Rate | ACMQUN_SUBSTN_NDRRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Up Ramp Rate | ACMQUN_SUBSTN_EURRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Down Ramp Rate | ACMQUN_SUBSTN_EDRRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | High Emergency Limit | ACMQUN_SUBSTN_HEL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Low Emergency Limit | ACMQUN_SUBSTN_LEL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | High Sustained Limit | ACMQUN_SUBSTN_HSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Low Sustained Limit | ACMQUN_SUBSTN_LSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Responsibility | ACMQUN_SUBSTN_RURSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Responsibility | ACMQUN_SUBSTN_RDRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Responsibility | ACMQUN_SUBSTN_RRRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Responsibility | ACMQUN_SUBSTN_NSRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RST_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Schedule | ACMQUN_SUBSTN_RRSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Schedule | ACMQUN_SUBSTN_NSSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Participation Factor | ACMQUN_SUBSTN_RUPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Participation Factor | ACMQUN_SUBSTN_RDPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | FRRS Down Participation Factor | ACMQUN_SUBSTN_FDPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | FRRS Up Participation Factor | ACMQUN_SUBSTN_FUPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | FRRS Down Responsibility | ACMQUN_SUBSTN_FDRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | FRRS Up Responsibility | ACMQUN_SUBSTN_FURSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS responsibility | ACMQUN_SUBSTN_ECRSUNIT1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS schedule | ACMQUN_SUBSTN_ECSCUNIT1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megawatts | ACMQUN_SUBSTN_NPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Combine Cycle Configuration | ACMQUN_SUBSTN_CCC_CCC1_INDX | DiscreteQ | -1 | ACMQ | Combined Cycle Only
ACMQ | SUBSTN |  | Generation Unit | UN | Total Combine cycle Net Power | ACMQUN_SUBSTN_NPF_CCC1_MW | RealQ | -1 | ACMQ | Combined Cycle Only
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RSTR_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up (5 min) Ramp Rate | ACMQUN_SUBSTN_RURR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down (5 min) Ramp Rate | ACMQUN_SUBSTN_RDRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS (10 min) Ramp Rate | ACMQUN_SUBSTN_ECRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin (30 min) Ramp Rate | ACMQUN_SUBSTN_NSRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide PFR | ACMQUN_SUBSTN_PFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide FFR | ACMQUN_SUBSTN_FFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Frequency Responsive Capacity Factor (0 to 1) | ACMQUN_SUBSTN_FRQF_GEN1_MW | RealQ | -1 | ACMQ | only for resouces capable of power augmentation
ACMQ | SUBSTN |  | Generation Unit | UN | High Frequency Responsive Capacity Limit | ACMQUN_SUBSTN_HFRL_GEN1_MW | RealQ | -1 | ACMQ | only for resouces capable of power augmentation
ACMQ | SUBSTN |  | Generation Unit | UN | Low Frequency Responsive Capacity Limit | ACMQUN_SUBSTN_LFRL_GEN1_MW | RealQ | -1 | ACMQ | only for resouces capable of power augmentation
ACMQ | SUBSTN |  | Generation Unit | UN | Power Augmentatin Capacity | ACMQUN_SUBSTN_PAUG_GEN1_MW | RealQ | -1 | ACMQ | only for resouces capable of power augmentation
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Desired Generation | ACMQUN_SUBSTN_UDBP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Base Point | ACMQUN_SUBSTN_BP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Locational Marginal Price | ERCTUN_SUBSTN_LMP_GEN1_USD | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Non-spin Deployed flag | ACMQUN_SUBSTN_NDPLGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Curtailment flag | ACMQUN_SUBSTN_SBBHGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | SCCT SCED Mitigation flag | ACMQUN_SUBSTN_SCCTGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Set Point RTC | ACMQUN_SUBSTN_UDSP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Award | ACMQUN_SUBSTN_REGU_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Award | ACMQUN_SUBSTN_REGD_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS PFR AS Award | ACMQUN_SUBSTN_PFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS FFR AS Award | ACMQUN_SUBSTN_FFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS AS Award | ACMQUN_SUBSTN_ECRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | NSRS AS Award | ACMQUN_SUBSTN_NSRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Deployment | ACMQUN_SUBSTN_RURQ_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Deployment | ACMQUN_SUBSTN_RDRQ_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | ONSC RRS Active | ACMQUN_SUBSTN_ORRA_GEN1_MW | StateQ | -1 | ERCT | for synchronous condenser only
ACMQ | SUBSTN |  | Generation Unit | UN | ONSC ECRS Active | ACMQUN_SUBSTN_OECA_GEN1_MW | StateQ | -1 | ERCT | for synchronous condenser only
Any additional telemetry needed for subtation
Based off physical equipment at the substation.
ACMQ | SUBSTN |  | Generation Unit | UN | Switches | ACMQUN_SUBSTN_SWITCHNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Breaker Status | ACMQUN_SUBSTN_BRKRNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Capbanks | ACMQCP_SUBSTN_CAPNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | High Side Voltage | ACMQBS_SUBSTN_1380GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | Low Side Voltage | ACMQBS_SUBSTN_0240GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MV | RealQ | -1 | ACMQ

## Energy Storage(ESR)
RealQ
StateQ
ERCOT ICCP Change Request Form | [10 empty] | DiscreteQ
Existing point from QSE for both Current and RTC
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way. | [8 empty] | Existing ICCP From QSE in Current System, going away in RTC
Current System only need if providing service, gone in RTC
RED RTC ONLY ICCP from QSE
Existing Point FROM ERCOT, exist in both
[8 empty] | Add (-1) Delete (-2) |  | New RTC ICCP FROM ERCOT
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Generation Unit | ESR | Normal Up Ramp Rate | ACMQESR_SUBSTN_NURRESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Normal Down Ramp Rate | ACMQESR_SUBSTN_NDRRESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Emergency Up Ramp Rate | ACMQESR_SUBSTN_EURRESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Emergency Down Ramp Rate | ACMQESR_SUBSTN_EDRRESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | High Emergency Limit | ACMQESR_SUBSTN_HEL_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Low Emergency Limit | ACMQESR_SUBSTN_LEL_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | High Sustained Limit | ACMQESR_SUBSTN_HSL_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Low Sustained Limit | ACMQESR_SUBSTN_LSL_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | NET Megawatts | ACMQESR_SUBSTN_NPF_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | NET Megavars | ACMQESR_SUBSTN_NPF_ESR1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Gross Megawatts | ACMQESR_SUBSTN_GPF_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Gross Megavars | ACMQESR_SUBSTN_GPF_ESR1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Raise block status | ACMQESR_SUBSTN_RBSTESR1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Lower Block Status | ACMQESR_SUBSTN_LBSTESR1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Voltage Regulator | ACMQESR_SUBSTN_AVR_ESR1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Power System Stabilizer | ACMQESR_SUBSTN_PSS_ESR1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Maximum Operating State of Charge | ACMQESR_SUBSTN_MXOSESR1_MWH | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Minimum Operating State of Charge | ACMQESR_SUBSTN_MNOSESR1_MWH | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | State of Charge | ACMQESR_SUBSTN_SOC_ESR1_MWH | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Maximum Operating Discharge Power Limit | ACMQESR_SUBSTN_MXDPESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Maximum Operating Charge Power Limit | ACMQESR_SUBSTN_MXCPESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Resource Status RTC | ACMQESR_SUBSTN_RSTR_ESR1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Up (5 min) Ramp Rate | ACMQESR_SUBSTN_RURR_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Down (5 min) Ramp Rate | ACMQESR_SUBSTN_RDRR_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | ECRS (10 min) Ramp Rate | ACMQESR_SUBSTN_ECRR_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Non-Spin (30 min) Ramp Rate | ACMQESR_SUBSTN_NSRR_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Current Capability to provide PFR | ACMQESR_SUBSTN_PFRC_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Current Capability to provide FFR | ACMQESR_SUBSTN_FFRC_ESR1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | ESR | Base Point | ACMQESR_SUBSTN_BP_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Locational Marginal Price | ERCTESR_SUBSTN_LMP_ESR1_USD | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Non-spin Deployed flag | ACMQESR_SUBSTN_NDPLESR1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Curtailment flag | ACMQESR_SUBSTN_SBBHESR1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | SCCT SCED Mitigation flag | ACMQESR_SUBSTN_SCCTESR1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Voltage KV at POI Meter | ACMQESR_SUBSTN_KVM_ESR1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Desired Voltage Setpoint from TDSP | ACMQESR_SUBSTN_KVT_ESR1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Updated Set Point RTC | ACMQESR_SUBSTN_UDSP_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Up Award | ACMQESR_SUBSTN_REGU_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Down Award | ACMQESR_SUBSTN_REGD_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | RRS PFR AS Award | ACMQESR_SUBSTN_PFRA_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | RRS FFR AS Award | ACMQESR_SUBSTN_FFRA_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | ECRS AS Award | ACMQESR_SUBSTN_ECRA_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | NSRS AS Award | ACMQESR_SUBSTN_NSRA_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Up Deployment | ACMQESR_SUBSTN_RURQ_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | Regulation Down Deployment | ACMQESR_SUBSTN_RDRQ_ESR1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | ESR | FFR Active (for ESR only) | ACMQESR_SUBSTN_FFAC_ESR1_ST | StateQ | -1 | ERCT
Any additional telemetry needed for subtation
Based off physical equipment at the substation.
ACMQ | SUBSTN |  | Generation Unit | UN | Switches | ACMQUN_SUBSTN_SWITCHNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Breaker Status | ACMQUN_SUBSTN_BRKRNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Capbanks | ACMQCP_SUBSTN_CAPNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | High Side Voltage | ACMQBS_SUBSTN_1380BS_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | Low Side Voltage | ACMQBS_SUBSTN_0240BS_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load MW | ACMQGP_SUBSTN_LOAD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load MVAR | ACMQGP_SUBSTN_LOAD1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Charging Load MW | ACMQGP_SUBSTN_CHARGE1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Charging Load MVAR | ACMQGP_SUBSTN_CHARGE1_MV | RealQ | -1 | ACMQ

## NCLR
RealQ
StateQ
ERCOT ICCP Change Request Form | [10 empty] | DiscreteQ
Existing point from QSE for both Current and RTC
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way. | [8 empty] | Existing ICCP From QSE in Current System, going away in RTC
Current System only need if providing service, gone in RTC
[8 empty] | Add (-1) Delete (-2) |  | RED RTC ONLY ICCP from QSE
Existing Point FROM ERCOT, exist in both
New RTC ICCP FROM ERCOT
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Net Load MW | ACMQLR_SUBSTN_NPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | High-set Under-frequency Relay Status | ACMQLR_SUBSTN_HSUF_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Load Resource Breaker Status | ACMQLR_SUBSTN_LRCB_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Resource Status | ACMQLR_SUBSTN_RST_LD1_ST | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Load Resource Low Power Consumption | ACMQLR_SUBSTN_LPC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Load Resource Maximum Power Consumption | ACMQLR_SUBSTN_MPC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Responsive Reserve Responsibility | ACMQLR_SUBSTN_RRRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Responsive Reserve Schedule | ACMQLR_SUBSTN_RRSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Non-Spin Responsibility | ACMQLR_SUBSTN_NSRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Non-spin Schedule | ACMQLR_SUBSTN_NSSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | ECRS Responsibility | ACMQLR_SUBSTN_ECRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | ECRS Schedule | ACMQLR_SUBSTN_ECSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Resource Status RTC | ACMQLR_SUBSTN_RSTR_LD1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Current Capability to provide FFR | ACMQLR_SUBSTN_FFRC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Current Capability to Provide UFR | ACMQLR_SUBSTN_UFRC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Non-Spin Ramp Rate | ACMQLR_SUBSTN_NSRR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | ECRS Ramp Rate | ACMQLR_SUBSTN_ESRR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Self Provided RRS UFR | ACMQLR_SUBSTN_SPUF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Self Provided RRS FFR | ACMQLR_SUBSTN_SPFF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Self Provided RRS ECRS | ACMQLR_SUBSTN_SPEC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | RRS UFR AS Award | ACMQLR_SUBSTN_UFRA_LD1_MW | RealQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | ECRS AS Award | ACMQLR_SUBSTN_ECRA_LD1_MW | RealQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | NSRS AS Award | ACMQLR_SUBSTN_NSRA_LD1_MW | RealQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | FFRS AS Award | ACMQLR_SUBSTN_NSRA_LD1_MW | RealQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Non-spin Deployed | ACMQLR_SUBSTN_NDPL_LD1_ST | StateQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | Resonspive Deployed | ACMQLR_SUBSTN_RDPL_LD1_ST | StateQ | -1 | ERCOT
ACMQ | SUBSTN |  | Non-Controllable Load Resource | LR | ECRS Deployed flag | ACMQLR_SUBSTN_MMEC_LD1_ST | StateQ | -1 | ERCOT

## CLR
RealQ
StateQ
ERCOT ICCP Change Request Form | [11 empty] | DiscreteQ
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way.
Add (-1) Delete (-2)
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Normal Up Ramp Rate | ACMQCLR_SUBSTN_NURR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Normal Down Ramp Rate | ACMQCLR_SUBSTN_NDRR_LD1_MW | RealQ | -1 | ACMQ |  | Current System, going away in RTC
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Emergency Up Ramp Rate | ACMQCLR_SUBSTN_EURR_LD1_MW | RealQ | -1 | ACMQ |  | Current System only need if providing service, gone in RTC
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Emergency Down Ramp Rate | ACMQCLR_SUBSTN_EDRR_LD1_MW | RealQ | -1 | ACMQ |  | RED RTC ONLY ICCP from QSE
ACMQ | SUBSTN |  | Controllable Load Resource | LR | High Emergency Limit | ACMQCLR_SUBSTN_HEL_LD1_MW | RealQ | -1 | ACMQ |  | Existing Point FROM ERCOT, exist in both
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Low Emergency Limit | ACMQCLR_SUBSTN_LEL_LD1_MW | RealQ | -1 | ACMQ |  | New RTC ICCP FROM ERCOT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | High Sustained Limit | ACMQCLR_SUBSTN_HSL_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Low Sustained Limit | ACMQCLR_SUBSTN_LSL_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Maximum Power Consumption | ACMQCLR_SUBSTN_MPC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Low Power Consumption | ACMQCLR_SUBSTN_LPC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Scheduled Power Consumption | ACMQCLR_SUBSTN_SPC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Scheduled Power Consumption +2 hours | ACMQCLR_SUBSTN_SPC2_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Up Responsibility | ACMQCLR_SUBSTN_RURS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Down Responsibility | ACMQCLR_SUBSTN_RDRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Responsive Reserve Responsibility | ACMQCLR_SUBSTN_RRRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Non-Spin Responsibility | ACMQCLR_SUBSTN_NSRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Resource Status RTC | ACMQCLR_SUBSTN_RST_LD1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Responsive Reserve Schedule | ACMQCLR_SUBSTN_RRSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Non-Spin Schedule | ACMQCLR_SUBSTN_NSSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Up Participation Factor | ACMQCLR_SUBSTN_RUPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Down Participation Factor | ACMQCLR_SUBSTN_RDPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FRRS Down Participation Factor | ACMQCLR_SUBSTN_FDPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FRRS Up Participation Factor | ACMQCLR_SUBSTN_FUPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FRRS Down Responsibility | ACMQCLR_SUBSTN_FDRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FRRS Up Responsibility | ACMQCLR_SUBSTN_FURS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FFR Responsibility | ACMQCLR_SUBSTN_FFRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | FFR Schedule | ACMQCLR_SUBSTN_FFSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | ECRS responsibility | ACMQCLR_SUBSTN_ECRS_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | ECRS schedule | ACMQCLR_SUBSTN_ECSC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | NET Megawatts | ACMQCLR_SUBSTN_NPF_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Raise block status | ACMQCLR_SUBSTN_RBST_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Lower Block Status | ACMQCLR_SUBSTN_LBST_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Voltage Regulator | ACMQCLR_SUBSTN_AVR_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Power System Stabilizer | ACMQCLR_SUBSTN_PSS_LD1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Resource Status RTC | ACMQCLR_SUBSTN_RSTR_LD1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Up (5 min) Ramp Rate | ACMQCLR_SUBSTN_RURR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Down (5 min) Ramp Rate | ACMQCLR_SUBSTN_RDRR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | ECRS (10 min) Ramp Rate | ACMQCLR_SUBSTN_ECRR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Non-Spin (30 min) Ramp Rate | ACMQCLR_SUBSTN_NSRR_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Capability to provide PFR | ACMQCLR_SUBSTN_PFRC_LD1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Updated Desired Generation | ACMQCLR_SUBSTN_UDBP_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Base Point | ACMQCLR_SUBSTN_BP_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Locational Marginal Price | ERCTUN_SUBSTN_LMP_LD1_USD | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Non-spin Deployed flag | ACMQCLR_SUBSTN_NDPL_LD1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Resonsive Reserve Deployed flag | ACMQCLR_SUBSTN_RDPL_LD1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | SCCT SCED Mitigation flag | ACMQCLR_SUBSTN_SCCT_LD1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Updated Set Point RTC | ACMQCLR_SUBSTN_UDSP_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Up Award | ACMQCLR_SUBSTN_REGU_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Down Award | ACMQCLR_SUBSTN_REGD_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | RRS PFR AS Award | ACMQCLR_SUBSTN_PFRA_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | ECRS AS Award | ACMQCLR_SUBSTN_ECRA_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | NSRS AS Award | ACMQCLR_SUBSTN_NSRA_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Up Deployment | ACMQCLR_SUBSTN_RURQ_LD1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Controllable Load Resource | LR | Regulation Down Deployment | ACMQCLR_SUBSTN_RDRQ_LD1_MW | RealQ | -1 | ERCT

## Wind
RealQ
StateQ
ERCOT ICCP Change Request Form | [11 empty] | DiscreteQ
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way.
Add (-1) Delete (-2)
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Up Ramp Rate | ACMQUN_SUBSTN_NURRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Down Ramp Rate | ACMQUN_SUBSTN_NDRRGEN1_MW | RealQ | -1 | ACMQ |  | Current System, going away in RTC
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Up Ramp Rate | ACMQUN_SUBSTN_EURRGEN1_MW | RealQ | -1 | ACMQ |  | RED RTC ONLY ICCP from QSE
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Down Ramp Rate | ACMQUN_SUBSTN_EDRRGEN1_MW | RealQ | -1 | ACMQ |  | Existing Point FROM ERCOT, exist in both
ACMQ | SUBSTN |  | Generation Unit | UN | High Emergency Limit | ACMQUN_SUBSTN_HEL_GEN1_MW | RealQ | -1 | ACMQ |  | New RTC ICCP FROM ERCOT
ACMQ | SUBSTN |  | Generation Unit | UN | Low Emergency Limit | ACMQUN_SUBSTN_LEL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | High Sustained Limit | ACMQUN_SUBSTN_HSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Low Sustained Limit | ACMQUN_SUBSTN_LSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Responsibility | ACMQUN_SUBSTN_RURSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Responsibility | ACMQUN_SUBSTN_RDRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Responsibility | ACMQUN_SUBSTN_RRRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Responsibility | ACMQUN_SUBSTN_NSRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RST_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Schedule | ACMQUN_SUBSTN_RRSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Schedule | ACMQUN_SUBSTN_NSSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Participation Factor | ACMQUN_SUBSTN_RUPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Participation Factor | ACMQUN_SUBSTN_RDPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megawatts | ACMQUN_SUBSTN_NPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RSTR_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up (5 min) Ramp Rate | ACMQUN_SUBSTN_RURR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down (5 min) Ramp Rate | ACMQUN_SUBSTN_RDRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS (10 min) Ramp Rate | ACMQUN_SUBSTN_ECRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin (30 min) Ramp Rate | ACMQUN_SUBSTN_NSRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide PFR | ACMQUN_SUBSTN_PFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide FFR | ACMQUN_SUBSTN_FFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Desired Generation | ACMQUN_SUBSTN_UDBP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Base Point | ACMQUN_SUBSTN_BP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Locational Marginal Price | ERCTUN_SUBSTN_LMP_GEN1_USD | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Non-spin Deployed flag | ACMQUN_SUBSTN_NDPLGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Curtailment flag | ACMQUN_SUBSTN_SBBHGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | SCCT SCED Mitigation flag | ACMQUN_SUBSTN_SCCTGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Set Point RTC | ACMQUN_SUBSTN_UDSP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Award | ACMQUN_SUBSTN_REGU_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Award | ACMQUN_SUBSTN_REGD_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS PFR AS Award | ACMQUN_SUBSTN_PFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS FFR AS Award | ACMQUN_SUBSTN_FFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS AS Award | ACMQUN_SUBSTN_ECRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | NSRS AS Award | ACMQUN_SUBSTN_NSRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Deployment | ACMQUN_SUBSTN_RURQ_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Deployment | ACMQUN_SUBSTN_RDRQ_GEN1_MW | RealQ | -1 | ERCT
Additional telemetry for Wind resources
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Turbines Online | ACMQUN_SUBSTN_NTONUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Turbines Offline | ACMQUN_SUBSTN_NTOFUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Turbines Unknown | ACMQUN_SUBSTN_NTUNUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Barometric Pressure | ACMEWS_SUBSTN_0180BAROM1_MILB | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Wind Direction | ACMEWS_SUBSTN_0180ANAMOM1_DEG | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Wind Speed | ACMEWS_SUBSTN_0180ANAMOM1_MPH | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Temperature | ACMEWS_SUBSTN_0180THERMO1_DEGC | RealQ | -1 | ACMQ
Any additional telemetry needed for subtation
Based off physical equipment at the substation.
ACMQ | SUBSTN |  | Generation Unit | UN | Switches | ACMQUN_SUBSTN_SWITCHNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Breaker Status | ACMQUN_SUBSTN_BRKRNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Capbanks | ACMQCP_SUBSTN_CAPNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | High Side Voltage | ACMQBS_SUBSTN_1380GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | Low Side Voltage | ACMQBS_SUBSTN_0240GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MV | RealQ | -1 | ACMQ

## Solar
RealQ
StateQ
ERCOT ICCP Change Request Form | [11 empty] | DiscreteQ
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way.
Add (-1) Delete (-2)
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Up Ramp Rate | ACMQUN_SUBSTN_NURRGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Normal Down Ramp Rate | ACMQUN_SUBSTN_NDRRGEN1_MW | RealQ | -1 | ACMQ |  | Current System, going away in RTC
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Up Ramp Rate | ACMQUN_SUBSTN_EURRGEN1_MW | RealQ | -1 | ACMQ |  | RED RTC ONLY ICCP from QSE
ACMQ | SUBSTN |  | Generation Unit | UN | Emergency Down Ramp Rate | ACMQUN_SUBSTN_EDRRGEN1_MW | RealQ | -1 | ACMQ |  | Existing Point FROM ERCOT, exist in both
ACMQ | SUBSTN |  | Generation Unit | UN | High Emergency Limit | ACMQUN_SUBSTN_HEL_GEN1_MW | RealQ | -1 | ACMQ |  | New RTC ICCP FROM ERCOT
ACMQ | SUBSTN |  | Generation Unit | UN | Low Emergency Limit | ACMQUN_SUBSTN_LEL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | High Sustained Limit | ACMQUN_SUBSTN_HSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Low Sustained Limit | ACMQUN_SUBSTN_LSL_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Responsibility | ACMQUN_SUBSTN_RURSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Responsibility | ACMQUN_SUBSTN_RDRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Responsibility | ACMQUN_SUBSTN_RRRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Responsibility | ACMQUN_SUBSTN_NSRSGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RST_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Responsive Reserve Schedule | ACMQUN_SUBSTN_RRSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin Schedule | ACMQUN_SUBSTN_NSSCGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Participation Factor | ACMQUN_SUBSTN_RUPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Participation Factor | ACMQUN_SUBSTN_RDPFGEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megawatts | ACMQUN_SUBSTN_NPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_GEN1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_GEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Resource Status RTC | ACMQUN_SUBSTN_RSTR_GEN1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up (5 min) Ramp Rate | ACMQUN_SUBSTN_RURR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down (5 min) Ramp Rate | ACMQUN_SUBSTN_RDRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS (10 min) Ramp Rate | ACMQUN_SUBSTN_ECRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Non-Spin (30 min) Ramp Rate | ACMQUN_SUBSTN_NSRR_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide PFR | ACMQUN_SUBSTN_PFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Current Capability to provide FFR | ACMQUN_SUBSTN_FFRC_GEN1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Desired Generation | ACMQUN_SUBSTN_UDBP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Base Point | ACMQUN_SUBSTN_BP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Locational Marginal Price | ERCTUN_SUBSTN_LMP_GEN1_USD | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Non-spin Deployed flag | ACMQUN_SUBSTN_NDPLGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Curtailment flag | ACMQUN_SUBSTN_SBBHGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | SCCT SCED Mitigation flag | ACMQUN_SUBSTN_SCCTGEN1_ST | StateQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_GEN1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Updated Set Point RTC | ACMQUN_SUBSTN_UDSP_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Award | ACMQUN_SUBSTN_REGU_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Award | ACMQUN_SUBSTN_REGD_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS PFR AS Award | ACMQUN_SUBSTN_PFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | RRS FFR AS Award | ACMQUN_SUBSTN_FFRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | ECRS AS Award | ACMQUN_SUBSTN_ECRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | NSRS AS Award | ACMQUN_SUBSTN_NSRA_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Up Deployment | ACMQUN_SUBSTN_RURQ_GEN1_MW | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Regulation Down Deployment | ACMQUN_SUBSTN_RDRQ_GEN1_MW | RealQ | -1 | ERCT
Additional telemetry for PV resources
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Inverters Online | ACMQUN_SUBSTN_NIONUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Inverters Offline | ACMQUN_SUBSTN_NIOFUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Number of Inverters Unknown | ACMQUN_SUBSTN_NIUNUNIT1_INDX | DiscreteQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Barometric Pressure | ACMEWS_SUBSTN_0180BAROM1_MILB | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Wind Direction | ACMEWS_SUBSTN_0180ANAMOM1_DEG | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Wind Speed | ACMEWS_SUBSTN_0180ANAMOM1_MPH | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Temperature, in degrees C | ACMEWS_SUBSTN_0180THERMO1_DEGC | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Back Panel Temp, in degrees C | ACMEWS_SUBSTN_PTMPUNIT1_DEGC | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Meteorological Device | UN | Plane of Array Irradiance, w/m2 | ACMEWS_SUBSTN_IRADUNIT1_IRAD | RealQ | -1 | ACMQ
Any additional telemetry needed for subtation
Based off physical equipment at the substation.
ACMQ | SUBSTN |  | Generation Unit | UN | Switches | ACMQUN_SUBSTN_SWITCHNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Breaker Status | ACMQUN_SUBSTN_BRKRNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Capbanks | ACMQCP_SUBSTN_CAPNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | High Side Voltage | ACMQBS_SUBSTN_1380GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | Low Side Voltage | ACMQBS_SUBSTN_0240GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOADGEN_MV | RealQ | -1 | ACMQ

## Combine Cycle Physical Unit
RealQ
StateQ
ERCOT ICCP Change Request Form | [11 empty] | DiscreteQ
Instructions: | Please fill out the form (paste data) based on the data requested information in each column. An example is provided. If you have any questions regarding the form, please contact ERCOT's ICCP team. Please do not ALTER this form in any way.
Add (-1) Delete (-2)
Physical Unit
Remote | Station Shortname | Voltage | Device | Device Type | Description | New ICCP Object Name | ICCP Data Type | Add or Remove | Owner | Comment
ACMQ | SUBSTN |  | Generation Unit | UN | Total Combine cycle Net Power | ACMQUN_SUBSTN_NPF_CT1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_CT1_MV | RealQ | -1 | ACMQ |  | Current System, going away in RTC
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_CT1_MW | RealQ | -1 | ACMQ |  | Current System only need if providing service, gone in RTC
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_CT1_MV | RealQ | -1 | ACMQ |  | RED RTC ONLY ICCP from QSE
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTCT1_ST | StateQ | -1 | ACMQ |  | Existing Point FROM ERCOT, exist in both
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTCT1_ST | StateQ | -1 | ACMQ |  | New RTC ICCP FROM ERCOT
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_CT1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_CT1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_CT1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_CT1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Total Combine cycle Net Power | ACMQUN_SUBSTN_NPF_CT2_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_CT2_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_CT2_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_CT2_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTCT2_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTCT2_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_CT2_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_CT2_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_CT2_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_CT2_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Total Combine cycle Net Power | ACMQUN_SUBSTN_NPF_ST1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | NET Megavars | ACMQUN_SUBSTN_NPF_ST1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megawatts | ACMQUN_SUBSTN_GPF_ST1_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Gross Megavars | ACMQUN_SUBSTN_GPF_ST1_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Raise block status | ACMQUN_SUBSTN_RBSTST1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Lower Block Status | ACMQUN_SUBSTN_LBSTST1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage Regulator | ACMQUN_SUBSTN_AVR_ST1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Power System Stabilizer | ACMQUN_SUBSTN_PSS_ST1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Voltage KV at POI Meter | ACMQUN_SUBSTN_KVM_ST1_KV | RealQ | -1 | ERCT
ACMQ | SUBSTN |  | Generation Unit | UN | Desired Voltage Setpoint from TDSP | ACMQUN_SUBSTN_KVT_ST1_KV | RealQ | -1 | ERCT
Any additional telemetry needed for subtation
Based off physical equipment at the substation.
ACMQ | SUBSTN |  | Generation Unit | UN | Switches | ACMQUN_SUBSTN_SWITCHNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Breaker Status | ACMQUN_SUBSTN_BRKRGEN1_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Capbanks | ACMQCP_SUBSTN_CAPNAME_ST | StateQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Line flows | ACMQLN_SUBSTN_LINENAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Unit | UN | Transformer flows | ACMQXF_SUBSTN_XFNAME_MV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | High Side Voltage | ACMQBS_SUBSTN_1380GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Buss | BS | Low Side Voltage | ACMQBS_SUBSTN_0240GEN1_KV | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOAD_MW | RealQ | -1 | ACMQ
ACMQ | SUBSTN |  | Generation Plant | GP | Plant Auxiliary Load | ACMQGP_SUBSTN_LOAD_MV | RealQ | -1 | ACMQ