## TitlePage
Report on the Capacity, Demand and Reserves
(CDR) in the ERCOT Region, 2025-2029
February 13, 2025

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read
MAIN REPORT
Findings & Discussion | Overview and highlights of the CDR
Load-Resource Scenarios | Presents condensed demand-resource summaries for the summer and winter seasons based on alternative peak demand and/or resource scenarios
Summer Summary | Shows load forecasts, resource capacities and reserve margins for the next five summer seasons, for both the expected Peak Load hour and Peak Net Load Hour
Winter Summary | Shows load forecasts, resource capacities and reserve margins for the next five winter seasons, for both the expected Peak Load hour and Peak Net Load Hour
DATA TABLES
Unit Details | List of registered resources and capabilities used in determining the capacity contributions by Season
Capacity by Resource Type | A table that lists installed capacities by fuel/technology type categories
ELCCs | Background on Effective Load Carrying Capabilities (ELCCs) for Inverter Based Resources, along with table that lists the ELCC values used for Planning Reserve Margin calculation
New CDR-Eligible Resources | A table listing those planned resources that have meet the criteria to be included in the CDR since the last CDR release
DOCUMENTATION
Acronyms | List of acroynms used in the CDR data tables
Definitions | Definitions of terms used in the CDR
Wind-Solar Region Mapping | Tables that list the counties in the ERCOT region assigned to the CDR Wind and Solar Regions
Background | An overview of the CDR's purpose and key concepts needed to interpret results

## Disclaimer
Disclaimer
FOR PLANNING PURPOSES ONLY
This CDR report has been prepared using data provided by ERCOT and Market Participants. The data may contain errors or become obsolete and thereby affect the accuracy of report results. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the CDR report and its accuracy should be confirmed by each ERCOT Market Participant that contributed data.

## Findings & Discussion
CDR - Findings & Discussion
Overview
| ● | This CDR reflects a December 2024 snapshot of expected resource availability and peak Load and peak net Load hours based on prescriptive rules (ERCOT Protocols) and information from resource developers/owners and transmission companies. While the CDR provides a deterministic view of resource adequacy, this is forecasted information, and it will change over time. For example, state/federal policy changes, economic developments, market design initiatives, evolving grid management practices, and technology improvements, can significantly alter the long-term resource adequacy outcome in this CDR. Nevertheless, the CDR signals an indicative trend of eroding resource adequacy (planning reserve margins) in the absence of major mitigating factors.
A description of the most significant load and resource uncertainties, and how they are addressed through supplementary deterministic scenarios, is provided in the Load/Resource Forecast Uncertainty section below.
| ● | One scenario in this CDR indicates that Planning Reserve Margins for 2025 through 2029 decrease significantly from year to year, and cross over to negative values in 2026 or 2027 depending on the season. The summer Margins for the peak Net Load hours are lower than for the peak Load hours due mainly to decreasing solar generation availability in the early evening when loads are still high. The decreases are mainly due to:
|  | ‒ | The addition of new forecasted loads reported by Transmission Service Providers (TSPs), dominated by large consumers such as data centers, industrial/oil & gas production facilities, and cryptocurrency mining operations.
|  | ‒ | A change to the methodology for characterizing the availability of Inverter Based Resources (wind and solar) to reflect their anticipated reliability benefits during the hours with the greatest risk of capacity reserve shortages. (Some of the decreased wind and solar availability is offset by battery energy storage availability that is included in the Reserve Margin calculations for the first time.)
|  | ‒ | Including new eligibility criteria for including planned resources in the Planning Reserve Margin to more accurately account for project delay trends.
CDR Methodology Changes
| ● | This CDR reflects significant modifications to resource capacity availability and load forecast reporting methodologies used for Planning Reserve Margin calculation.
|  | These changes are summarized in the |  |  | Background tab.
CDR Load Forecast
| ● | This CDR is based on the peak load forecast developed as a mid-year 2024 update. The mid-year update includes new Loads associated with a signed interconnection agreement and "officer letter" Loads reported by Transmission Service Providers. The 2024 mid-year forecast retains the base peak load forecast originally prepared in November 2023 since there is not enough of a change to the forecast modeling results to warrant a switch. The mid-year forecast update is available on ercot.com at:
https://www.ercot.com/gridinfo/load/forecast
| ● | The peak load forecast is the sum of the forecast components in the following formula:
Peak Load Forecast = Base Load Forecast + Electric Vehicle Forecast - Rooftop PV Forecast + Existing LFL Forecast + New Contracted Loads + New TSP Officer Letter Loads
where, Existing Large Flexible Load forecast is the expected load from interconnected facilities that can come online quickly and are responsive to real time prices (nearly all the load comprises crypto-currency mining), New Contracted Loads are all planned loads with signed interconnection agreements reported to ERCOT by the loads' Transmission Service Providers as of March 2024, New TSP Officer Letter Loads are all planned loads documented in a TSP officer letter as of March 2024. (An officer letter is an attestation indicating confidence that loads are expected to be interconnected even though the interconnection agreement has not been signed yet.)
| ● | ERCOT assumes all Loads other than Large Flexible Loads (i.e., crypto-currency mining) are considered firm Loads. Firm Loads are Loads that will remain on when entering emergency conditions. On the other hand, Large Flexible Loads are responsive to real time prices and can reduce consumption or turn off quickly before emergency conditions. With an expectation of increasing Large Loads (75 MW or more), like data centers, connecting to the ERCOT grid, there is discussion among policymakers and the industry regarding requirements for Large Loads to be demand-flexible during periods of grid scarcity. A demand flexibility requirement would change the assumption for Large Loads to align more similarly to Large Flexible Loads and would improve planning reserve margins in the future. This outcome is represented in the Load-Resource Scenarios tab where 50% or no TSP Officer Letter Load is assumed across the years.
| ● | The following table shows the amount of new planned loads, by type, included in the mid-year load forecast update for summer 2025-2029. The last column indicates the average annual growth rate.
New Loads Added to the November 2023 Load Forecast Cumulative MW
|  |  | Large Load Type* | Summer 2025 | Summer 2026 | Summer 2027 | Summer 2028 | Summer 2029 | Ave. Annual Growth Rate (%)
|  |  | Contracted Loads (non-LFL) | 4017 | 8105.675 | 12900.667 | 16532.833 | 17493.433 | 44.46%
|  |  | Contracted LFLs | 1565 | 3443 | 3543 | 3543 | 3543 | 22.66%
|  |  | TSP Officer Letter Loads (non-LFL) | 899.5 | 8349.656 | 17399.776 | 28284.48 | 29359.48 | 139%
|  |  | TSP Officer Letter LFLs | 700 | 2335 | 2335 | 2335 | 2335 | 35.14%
|  |  | Total | 7181.5 | 22233.331 | 36178.443 | 50695.313 | 52730.913 | 64.61%
* See the definitions in the previous bullet.
| ● | The following table shows the summer peak Load and peak Net Load forecasts for 2025-2029, along with the associated peak load hours:
[5 empty] | Load for the peak Load hour |  | Load for the peak Net Load hour (Load minus wind and solar generation)
|  |  |  | Year | Summer Forecast | Summer Peak Load Hour (Hour Ending) | Summer Forecast | Summer Peak Net Load Hour (Hour Ending)
|  |  |  | 2025 | 90472.0122 | 5:00 p.m. | 86699.069 | 9:00 p.m.
|  |  |  | 2026 | 106405.0656 | 5:00 p.m. | 104593.6727 | 10:00 p.m.
|  |  |  | 2027 | 121140.3275 | 5:00 p.m. | 121140.3275 | 10:00 p.m.
|  |  |  | 2028 | 137318.7238 | 10:00 p.m. | 137318.7238 | 10:00 p.m.
|  |  |  | 2029 | 140872.3192 | 10:00 p.m. | 140872.3192 | 10:00 p.m.
The shift in the peak load hour to 10:00 p.m. beginning in summer 2028 is mainly due to the growth in price-driven demand response. Price-responsive Loads, such as crypto-currency miners, are expected to interconnect at roughly the same time prior to summer 2028. These price-responsive loads are anticipated to curtail their consumption through the early evening hours when net loads are typically at their highest and then ramp back up thereafter. This causes the peak load hour and peak net load hour to converge in 2028. The growth in rooftop solar also contributes to the peak hour shift.
Planning Reserve Margins for the Peak Load and Peak Net Load Hours
| ● | The following charts show the trends in one scenario of summer and winter Planning Reserve Margins for the next five years. Trends are shown for the peak Load and peak Net Load hours. The summer peak Net Load hour Margin enters negative territory beginning summer 2026, while the peak Load hour Margin enters negative territory beginning summer 2027. The lower Margins for the peak Net Load hour relative to those for the peak Load hour mainly reflect the lower reliability contribution of solar generation during the evening hours when the peak Net Load occurs. For winter 2027/28, both peak Load and peak Net Load Margins enter negative territory beginning winter 2027/28. Unlike summer, the peak Net Load hour Margins are higher than the peak Load hour Margins. This flip stems from a larger drop-off in early evening loads relative to those experienced during the summer. The lower and sharply downward trajectory of the Margins is due to (1) high load growth largely driven by new Loads reported by Transmission Service Providers, (2) a lower capacity contribution from wind and solar resources due to the switch to Effective Load Carrying Capabilities, (3) fewer planned resources that result from applying additional eligibility criteria to be included in Planning Reserve Margins, and (4) inclusion of planned unit retirements publicly announced but not officially reported as a planned retirement to ERCOT ("Unconfirmed Retirements"). The impact of these changes and others are described below.
| ● | The following three waterfall charts show the Reserve Margin capacity components for summer 2025 through 2027 that contribute to the differences in Planning Reserve Margins reported in the May 2024 CDR versus the December 2024 CDR. (Red bars signify components that reduce Reserve Margin capacity whereas green bars signify components that increase Reserve Margin capacity.)
Notes: ELCC is Effective Load Carrying Capability. COD is Commercial Operations Date. Miscellaneous resource changes include rating changes to operational and planned resources, updates to unavailable Switchable Generation Resource (SWGR) capacity, and changes to Private-Use Network (PUN) Capacity Contributions. Miscellaneous load changes include updates to Load Resource categories shown in the Summer Summary tab (LRs providing Responsive Reserve Service, Non-spin Reserve Service, and ERCOT Contingency Reserve Service; Controllable Load Resources; Emergency Responsive Service; and TDSP load management programs).
Resource Impacts due to new ERCOT Protocol Changes for the CDR
| ● | The CDR now uses Effective Load Carrying Capabilities (ELCCs) for wind and solar instead of using peak average capacity contributions, the prior method. ELCCs reflect the expected future reliability value of resources during those hours with the highest risk of capacity reserve shortages. In contrast, the peak average capacity contribution captures the historical generation during peak load hours, which is often no longer when the risk of capacity shortfalls is at its highest. For a summer afternoon in 2025, the aggregate ELCC of wind and solar resources is 17,732 MW, reflecting the resource reliability benefit during the hours with the highest loads. In contrast, the value based on the peak average capacity contribution method is higher at 35,995 MW. The aggregate ELCC drops to 6,189 MW for the evening hours, largely reflecting the decrease in solar generation and continued high loads (i.e., hours with the highest Net Loads). Note that ELCCs are estimated by all other Regional Transmission Organizations (RTO) and Independent System Operators (ISOs) in the U.S.(PJM Interconnection, Midcontinent Independent System Operator, Southwest Power Pool, California ISO, ISO New England, and New York ISO).
|  | More ELCC information is available on the |  |  | ELCCs tab.
| ● | Capacity contributions for Energy Storage Resources are now included in the Reserve Margin calculations. Relative to the May 2024 CDR, this results in 11,597 MW of additional summer 2025 capacity availability for the Peak Load and Net Peak load hours.
| ● | The Protocol changes include two additional criteria that planned projects must meet to be included in the CDR report: proof that the required financial security for interconnection construction has been received, and that a notice to proceed with construction has been received by the Transmission/Distribution Service Provider. These additional criteria resulted in a 1,054 MW decrease in planned capacity for summer 2025 (1,054 MW of solar, and 50 MW of battery energy storage).
| ● | The CDR now accounts for "Unconfirmed Retirements" in the Reserve Margin calculations. An Unconfirmed Retirement is a generating unit associated with a publicly announced retirement plan, but its owner hasn't yet submitted a formal Notification of Suspension of Operations (NSO) to ERCOT. This CDR reflects 1,100 MW of installed capacity planned for retirement by summer 2027, and an additional 1,917 MW planned for retirement by summer 2029. The five units include Spruce U1/U2 (CPS Energy), Coletto Creek (Vistra Energy), and O W Sommers STG1/STG2 (CPS Energy). CPS Energy is expecting to convert Spruce U2 from coal-fired to natural gas-fired based on their current Resource Plan.
Planned Resource Trends
| ● | The addition of six newly CDR-eligible natural gas projects and three diesel projects has doubled the Summer 2029 planned thermal capacity forecast relative to the May 2024 CDR forecast (from 972 MW to 1,909 MW). Note that the CDR eligibility criteria for this scenario does not allow including most new planned TEF generation resources. Those resources are included in subsequent scenarios on the Load-Resource Scenario Tab. Note that CDR-eligible TEF projects in the Unit Details tab have "TEF" as a suffix in the project name.
| ● | The table below shows the changes in resource capacity additions for summer 2025-2029 by resource category. Only those projects that have met the CDR eligibility criteria are included. Solar is expected to continue out-pacing the other resource types in terms of installed capacity growth, followed by Energy Storage Resources (battery energy storage).
Planned Generation Installed Capacity Additions by Summer Season (Projects that meet CDR-Eligibility Criteria)
|  |  |  | Summer 2025 | Summer 2026 | Summer 2027 | Summer 2028 | Summer 2029 | Trend
|  |  | Thermal (Natural Gas and Diesel) | 267.2 | 1472.5 | 1472.5 | 2146.5 | 2146.5
|  |  | Battery Energy Storage | 4235.51 | 11672.36 | 14911.56 | 17002.56 | 17558.66
|  |  | Dispatchable Total | 4502.71 | 13144.86 | 16384.06 | 19149.06 | 19705.16
|  |  | Solar | 5176.4 | 17258.9 | 24870.5 | 28157.4 | 29543
|  |  | Wind | 241.51 | 1980.31 | 3267.91 | 3493.51 | 3493.2
|  |  | Non-Dispatchable Total | 5417.91 | 19239.21 | 28138.41 | 31650.91 | 33036.2
|  |  | Total | 9920.62 | 32384.07 | 44522.47 | 50799.97 | 52741.36
Significant Resource Status Changes
| ● | On December 3, 2024, the ERCOT Board of Directors approved moving forward with a Reliability Must Run (RMR) contract for CPS Energy's Braunig 3 unit. ERCOT assumes that an RMR contract is executed, and the unit provides RMR service for summer 2025 through winter 2026-2027 and then is retired. RMR decisions on Braunig units 1 and 2 have been deferred to February 2025 to consider CenterPoint Energy's Mobile Generation Solution. More information is available at:
https://www.ercot.com/files/docs/2024/11/27/9-ercot-staff-recommendation-regarding-ercot-board-approval-of-reliability-must-run-rmr-and-must-run-alternative-mra-agreements-related-to-cps-energy-braunig-resources-revised.pdf
Load/Resource Forecast Uncertainty
| ● | Peak Load Forecast: In addition to the typical sources of peak load forecast uncertainty (weather, demand response, economic growth changes, electrification trends), the forecast used for this CDR presumes that the Loads seeking interconnection with the ERCOT grid materialize as currently forecasted by their TSPs. The size and ramp rates of Loads may deviate significantly from current TSP expectations. To provide an alternate view of load growth, this CDR includes a load/resource scenario that assumes that load growth is capped at levels and ramp rates associated with just the new contracted Loads identified by the TSPs. (i.e., exclusion of TSP officer letter Loads). This assumption serves as a proxy for a future with slower load growth growth, significant mitigation of the reliability risks for Loads, or both conditions.
| ● | Planned Resource Forecast: CDR planned resource accounting has become more conservative than for past CDRs due to the inclusion of additional eligibility criteria via NPRR1219. In recognition of the impact of Texas Energy Fund (TEF) financial incentives, ERCOT has developed summer and winter planned resource scenarios that include TEF project capacity that is in ERCOT's interconnection queue but does not currently meet all the CDR eligibility criteria. Crucially, the scenario assumes that the TEF capacity experiences no Commercial Operations Date delays as is typical of many other planned projects.
|  | The load and scenarios are provided in the |  |  | "Load-Resource Scenarios" tab.

## Load-Resource Scenarios
The summer and winter peak-load-hour scenarios below (Tables 1 and 2, respectively) show the Planning Reserve Margin impacts of making the following two changes to the original Firm Peak Load and Total Capacity estimates: (1) Remove portions of the TSP Officer Letter Loads from the Firm Peak Load forecast. (2) Add Texas Energy Fund project capacity to the Total Capacity estimates for those projects that are currently in the ERCOT interconnection queue but not yet eligible to be included as planned resources in the CDR. (Note that there is 915 MW of TEF project capacity already reflected in the resource forecast.)
Peak Load Hour Scenarios: Summer and Winter | [5 empty] | Net Peak Load Hour Scenarios: Summer and Winter
| Peak Load Hour | [5 empty] | Peak Net Load Hour
Table 1: Summer Load and Resource Scenarios | 2025 | 2026 | 2027 | 2028 | 2029 | Table 1: Summer Load and Resource Scenarios | 2025 | 2026 | 2027 | 2028 | 2029
Original Firm Peak Load, MW | 86716.9122 | 102623.9656 | 117359.2275 | 133557.6238 | 137111.2192 | Original Firm Peak Load, MW | 82963.969 | 100832.5727 | 117024.9374 | 133557.6238 | 137111.2192
TSP Officer Letter Loads Reported by Transmission Service Providers | -1600 | -10685 | -19735 | -30619 | -31694 | TSP Officer Letter Loads Reported by Transmission Service Providers | -1600 | -10685 | -19735 | -30619 | -31694
50% of TSP Officer Letter Loads Reported by Transmission Service Providers | -800 | -5342.5 | -9867.5 | -15309.5 | -15847 | 50% of TSP Officer Letter Loads Reported by Transmission Service Providers | -800 | -5342.5 | -9867.5 | -15309.5 | -15847
Firm Peak Load, excluding 50% of TSP Officer Letter Loads, MW | 85916.9122 | 97281.4656 | 107491.7275 | 118248.1238 | 121264.2192 | Firm Peak Load, excluding 50% of TSP Officer Letter Loads, MW | 82163.969 | 95490.0727 | 107157.4374 | 118248.1238 | 121264.2192
Firm Peak Load, excluding TSP Officer Letter Loads, MW | 85116.9122 | 91938.9656 | 97624.2275 | 102938.6238 | 105417.2192 | Firm Peak Load, excluding TSP Officer Letter Loads, MW | 81363.969 | 90147.5727 | 97289.9374 | 102938.6238 | 105417.2192
Total Capacity, MW | 103105.4811 | 107920.8977 | 107628.2932 | 93370.1217 | 92623.0472 | Total Capacity, MW | 91651.7982 | 94583.5317 | 92484.9226 | 93370.1217 | 92623.0472
Texas Energy Fund (TEF) Projects not already included in the CDR | 0 | 1920.32 | 2667.72 | 7739.72 | 8669.72 | Texas Energy Fund (TEF) Projects not already included in the CDR | 0 | 1920.32 | 2667.72 | 7739.72 | 8669.72
Total Capacity with TEF Projects, MW | 103105.4811 | 109841.2177 | 112508.9377 | 120248.6577 | 128918.3777 | Total Capacity with TEF Projects, MW | 91651.7982 | 96503.8517 | 99171.5717 | 106911.2917 | 115581.0117
Protocol-prescribed Planning Reserve Margins (%) | 18.9% | 5.161% | -8.292% | -30.09% | -32.45% | Protocol-prescribed Planning Reserve Margins (%) | 10.47% | -6.197% | -20.97% | -30.09% | -32.45%
Reserve Margins without 50% of TSP Officer Letter Loads (%) | 20.01% | 10.94% | 0.127% | -21.04% | -23.62% | Reserve Margins without 50% of TSP Officer Letter Loads (%) | 11.55% | -0.9494% | -13.69% | -21.04% | -23.62%
Reserve Margins without 50% of TSP Officer Letter Loads plus Additional TEF Projects (%) | 20.01% | 12.91% | 4.668% | 1.692% | 6.312% | Reserve Margins without 50% of TSP Officer Letter Loads plus Additional TEF Projects (%) | 11.55% | 1.062% | -7.452% | -9.587% | -4.687%
Reserve Margins without TSP Officer Letter Loads plus Additional TEF Projects (%) | 21.13% | 19.47% | 15.25% | 16.82% | 22.29% | Reserve Margins without TSP Officer Letter Loads plus Additional TEF Projects (%) | 12.64% | 7.051% | 1.934% | 3.859% | 9.641%
Table 2: Winter Load and Resource Scenario | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | Table 2: Winter Load and Resource Scenario | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30
Original Firm Peak Load, MW | 78607.892 | 94350.892 | 110082.892 | 126284.892 | 131997.892 | Original Firm Peak Load, MW | 72843.4218 | 88549.8316 | 104870.1062 | 121368.3685 | 126885.6629
TSP Officer Letter Loads Reported by Transmission Service Providers | -3707 | -11390 | -20316 | -31094 | -33660 | TSP Officer Letter Loads Reported by Transmission Service Providers | -3707 | -11390 | -20316 | -31094 | -33660
50% of TSP Officer Letter Loads Reported by Transmission Service Providers | -1853.5 | -5695 | -10158 | -15547 | -16830 | 50% of TSP Officer Letter Loads Reported by Transmission Service Providers | -1853.5 | -5695 | -10158 | -15547 | -16830
Firm Peak Load, excluding 50% of TSP Officer Letter Loads, MW | 76754.392 | 88655.892 | 99924.892 | 110737.892 | 115167.892 | Firm Peak Load, excluding 50% of TSP Officer Letter Loads, MW | 70989.9218 | 82854.8316 | 94712.1062 | 105821.3685 | 110055.6629
Firm Peak Load, excluding TSP Officer Letter Loads, MW | 74900.892 | 82960.892 | 89766.892 | 95190.892 | 98337.892 | Firm Peak Load, excluding TSP Officer Letter Loads, MW | 69136.4218 | 77159.8316 | 84554.1062 | 90274.3685 | 93225.6629
Total Capacity, MW | 97254.7273 | 98589.978 | 96719.0474 | 97011.8082 | 96652.4893 | Total Capacity, MW | 96438.1479 | 97655.8982 | 95895.2373 | 96119.1134 | 95748.4851
Texas Energy Fund (TEF) Projects not already included in the CDR | 0 | 1920.32 | 3661.72 | 7739.72 | 8669.72 | Texas Energy Fund (TEF) Projects not already included in the CDR | 0 | 1920.32 | 3661.72 | 7739.72 | 8669.72
Total Capacity with TEF Projects, MW | 97254.7273 | 100510.298 | 104172.018 | 111911.738 | 120581.458 | Total Capacity with TEF Projects, MW | 96438.1479 | 99576.2182 | 103237.9382 | 110977.6582 | 119647.3782
Protocol-prescribed Planning Reserve Margins (%) | 23.72% | 4.493% | -12.14% | -23.18% | -26.78% | Protocol-prescribed Planning Reserve Margins (%) | 32.39% | 10.28% | -8.558% | -20.8% | -24.54%
Reserve Margins without 50% of TSP Officer Letter Loads (%) | 26.71% | 11.21% | -3.208% | -12.4% | -16.08% | Reserve Margins without 50% of TSP Officer Letter Loads (%) | 35.85% | 17.86% | 1.249% | -9.169% | -13%
Reserve Margins without 50% of TSP Officer Letter Loads plus Additional TEF Projects (%) | 26.71% | 13.37% | 4.25% | 1.06% | 4.701% | Reserve Margins without 50% of TSP Officer Letter Loads plus Additional TEF Projects (%) | 35.85% | 20.18% | 9.002% | 4.873% | 8.715%
Reserve Margins without TSP Officer Letter Loads plus Additional TEF Projects (%) | 29.84% | 21.15% | 16.05% | 17.57% | 22.62% | Reserve Margins without TSP Officer Letter Loads plus Additional TEF Projects (%) | 39.49% | 29.05% | 22.1% | 22.93% | 28.34%

## Summer Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Summer Summary: 2025-2029
|  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029
|  | Peak Load Hour: | Peak Net Load Hour: | Difference [1] less [2] | Peak Load Hour: | Peak Net Load Hour: | Difference [4] less [5] | Peak Load Hour: | Peak Net Load Hour: | Difference [7] less [8] | Peak Load Hour: | Peak Net Load Hour: | Difference [10] less [11] | Peak Load Hour: | Peak Net Load Hour: | Difference [13] less [14]
|  | 17 | 21 |  | 17 | 22 |  | 17 | 22 |  | 22 | 22 |  | 22 | 22
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
| Total Summer Load based on normal weather conditions* | 91935.2452 | 86847.4867 | 5087.7585 | 108391.1836 | 104593.6727 | 3797.5109 | 123788.8864 | 120786.0374 | 3002.849 | 137318.7238 | 137318.7238 | 0 | 140872.3192 | 140872.3192 | 0
| less: Incremental Rooftop PV Forecast | -1463.233 | -148.4177 | -1314.8153 | -1986.118 | 0 | -1986.118 | -2648.5589 | 0 | -2648.5589 | 0 | 0 | 0 | 0 | 0 | 0
| less: Load Resources providing Responsive Reserves | -985 | -965 | -20 | -985 | -965 | -20 | -985 | -965 | -20 | -965 | -965 | 0 | -965 | -965 | 0
| less: Load Resources providing Non-Spinning Reserves | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0
| less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | -216.2 | -216.2 | 0 | -216.2 | -216.2 | 0 | -216.2 | -216.2 | 0 | -216.2 | -216.2 | 0 | -216.2 | -216.2 | 0
| less: Controllable Load Resources not included in other adjustments | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -1269 | -1269 | 0 | -1295 | -1295 | 0 | -1295 | -1295 | 0 | -1295 | -1295 | 0 | -1295 | -1295 | 0
| less: TDSP Standard Offer Load Management Programs | -372.3 | -372.3 | 0 | -372.3 | -372.3 | 0 | -372.3 | -372.3 | 0 | -372.3 | -372.3 | 0 | -372.3 | -372.3 | 0
| less: Distribution Voltage Reduction | -678 | -678 | 0 | -678 | -678 | 0 | -678 | -678 | 0 | -678 | -678 | 0 | -678 | -678 | 0
| Firm Peak Load, MW | 86716.9122 | 82963.969 | 3752.9432 | 102623.9656 | 100832.5727 | 1791.3929 | 117359.2275 | 117024.9374 | 334.2901 | 133557.6238 | 133557.6238 | 0 | 137111.2192 | 137111.2192 | 0
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
| Installed Summer-rated Capacity, Thermal | 66138 | 66138 | 0 | 66138 | 66138 | 0 | 66138 | 66138 | 0 | 65353 | 65353 | 0 | 65353 | 65353 | 0
| Hydroelectric, Peak Average Capacity Contribution | 543.685 | 543.685 | 0 | 543.685 | 543.685 | 0 | 543.685 | 543.685 | 0 | 543.685 | 543.685 | 0 | 543.685 | 543.685 | 0
| Switchable Capacity | 3680 | 3680 | 0 | 3680 | 3680 | 0 | 3680 | 3680 | 0 | 3680 | 3680 | 0 | 3680 | 3680 | 0
| less: Switchable Capacity Unavailable to ERCOT | -1480 | -1480 | 0 | -1631 | -1631 | 0 | -1633 | -1633 | 0 | -1020 | -1020 | 0 | -1020 | -1020 | 0
| Available Mothballed Capacity (Units with reported return probabilities ≥ 75%) | 135.5 | 135.5 | 0 | 135.5 | 135.5 | 0 | 135.5 | 135.5 | 0 | 135.5 | 135.5 | 0 | 135.5 | 135.5 | 0
| Capacity from Private Use Networks | 3265 | 3354.1345 | -89.1345 | 3155 | 3096.0015 | 58.9985 | 3362 | 3299.1306 | 62.8694 | 3301 | 3301 | 0 | 3551 | 3551 | 0
| Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs) | [3]: 0; [6]: 0; [9]: 0; [12]: 0; [15]: 0
| Coastal Wind | 1674.2552 | 889.0907 | 785.1645 | 1713.5387 | 922.9988 | 790.5399 | 1727.232 | 894.0771 | 833.1549 | 894.0771 | 894.0771 | 0 | 894.0771 | 894.0771 | 0
| Panhandle Wind | 1566.5817 | 831.9121 | 734.6696 | 1603.3389 | 863.6396 | 739.6993 | 1616.1516 | 836.5779 | 779.5737 | 836.5779 | 836.5779 | 0 | 836.5779 | 836.5779 | 0
| Other Wind | 4592.2819 | 2438.6695 | 2153.6124 | 4700.032 | 2531.6754 | 2168.3566 | 4737.5911 | 2452.3468 | 2285.2443 | 2452.3468 | 2452.3468 | 0 | 2452.3468 | 2452.3468 | 0
| Far West Solar Utility-Scale | 1893.4658 | 383.5094 | 1509.9564 | 1491.3342 | 178.1328 | 1313.2014 | 1407.7035 | 99.5448 | 1308.1587 | 46.105 | 46.105 | 0 | 33.007 | 33.007 | 0
| West Solar Utility-Scale | 1571.8166 | 318.3614 | 1253.4551 | 1237.9964 | 147.8728 | 1090.1236 | 1168.5724 | 82.6348 | 1085.9376 | 38.273 | 38.273 | 0 | 27.4 | 27.4 | 0
| Other Solar Utility-Scale | 4859.8013 | 984.3218 | 3875.4795 | 3827.6835 | 457.1987 | 3370.4848 | 3613.0357 | 255.4934 | 3357.5424 | 118.3338 | 118.3338 | 0 | 84.7162 | 84.7162 | 0
| Energy Storage | 7902.8627 | 7902.8627 | 0 | 5893.1454 | 5893.1454 | 0 | 4912.1886 | 4912.1886 | 0 | 4689.7126 | 4689.7126 | 0 | 4639.7811 | 4639.7811 | 0
| RMR Capacity to be under Contract | 412 | 412 | 0 | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, Total | 96755.2502 | 86532.0472 | 10223.203 | 92900.254 | 83368.8499 | 9531.4041 | 91408.66 | 81696.1791 | 9712.4809 | 81068.6112 | 81068.6112 | 0 | 81211.0912 | 81211.0912 | 0
Non-Synchronous Ties (Based on average net import contribution during the summer 2023 EEA event) |  | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
| Thermal Resources | 267.2 | 267.2 | 0 | 1472.5 | 1472.5 | 0 | 1472.5 | 1472.5 | 0 | 2146.5 | 2146.5 | 0 | 2146.5 | 2146.5 | 0
| Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs) | [3]: 0; [6]: 0; [9]: 0; [12]: 0; [15]: 0
| Coastal Wind | 74.3675 | 39.4919 | 34.8756 | 76.1124 | 40.998 | 35.1144 | 219.6653 | 113.7066 | 105.9587 | 113.7066 | 113.7066 | 0 | 113.7066 | 113.7066 | 0
| Panhandle Wind | 0 | 0 | 0 | 203.0891 | 109.3941 | 93.695 | 204.7121 | 105.9663 | 98.7458 | 105.9663 | 105.9663 | 0 | 105.9663 | 105.9663 | 0
| Other Wind | 0 | 0 | 0 | 184.1677 | 99.2021 | 84.9657 | 321.2058 | 166.2676 | 154.9382 | 185.1548 | 185.1548 | 0 | 185.1548 | 185.1548 | 0
| Far West Solar Utility-Scale | 52.9456 | 10.7238 | 42.2218 | 276.1951 | 32.9902 | 243.2049 | 260.7067 | 18.4357 | 242.271 | 8.5386 | 8.5386 | 0 | 8.0224 | 8.0224 | 0
| West Solar Utility-Scale | 314.4211 | 63.684 | 250.7371 | 1264.3833 | 151.0246 | 1113.3587 | 1463.3217 | 103.4778 | 1359.8439 | 58.6555 | 58.6555 | 0 | 48.8118 | 48.8118 | 0
| Other Solar Utility-Scale | 1131.9056 | 229.2603 | 902.6454 | 2538.8803 | 303.2572 | 2235.6231 | 3733.1169 | 263.9848 | 3469.1321 | 135.9662 | 135.9662 | 0 | 97.3394 | 97.3394 | 0
| Energy Storage | 3691.991 | 3691.991 | 0 | 8187.9156 | 8187.9156 | 0 | 8802.0046 | 8802.0046 | 0 | 9804.6225 | 9804.6225 | 0 | 9934.0547 | 9934.0547 | 0
| Unconfirmed Planned Retirements | 0 | 0 | 0 | 0 | 0 | 0 | -1075 | -1075 | 0 | -1075 | -1075 | 0 | -2045 | -2045 | 0
| Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements | 5532.8309 | 4302.351 | 1230.48 | 14203.2437 | 10397.2818 | 3805.9618 | 15402.2331 | 9971.3435 | 5430.8896 | 11484.1106 | 11484.1106 | 0 | 10594.556 | 10594.556 | 0
Total Capacity |  | 103105.4811 | 91651.7982 | 11453.683 | 107920.8977 | 94583.5317 | 13337.366 | 107628.2932 | 92484.9226 | 15143.3706 | 93370.1217 | 93370.1217 | 0 | 92623.0472 | 92623.0472 | 0
| Reserve Margin | 18.9% | 10.47% | 8.427% | 5.161% | -6.197% | 11.36% | -8.292% | -20.97% | 12.68% | -30.09% | -30.09% | 0% | -32.45% | -32.45% | 0%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
*Total Load consists of the following forecast components: Base Economic, Electric Vehicle Forecast, Large Flexible Loads forecast (with 15% curtailment assumption for Summer months from HE14 to HE21), Total Contracts, and Total Officer Letters. The rooftop PV forecast is shown as a separate adjustment to indicate the magnitude of this Distributed Generation resource. https://www.ercot.com/gridinfo/load/forecast

## Winter Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Winter Summary: 2025/26 - 2029/30
|  | 2025/26 |  |  | 2026/27 |  |  | 2027/28 |  |  | 2028/29 |  |  | 2029/30
|  | Peak Load Hour: | Peak Net Load Hour: | Difference [1] less [2] | Peak Load Hour: | Peak Net Load Hour: | Difference [4] less [5] | Peak Load Hour: | Peak Net Load Hour: | Difference [7] less [8] | Peak Load Hour: | Peak Net Load Hour: | Difference [10] less [11] | Peak Load Hour: | Peak Net Load Hour: | Difference [13] less [14]
|  | 8 | 19 |  | 8 | 19 |  | 8 | 19 |  | 8 | 19 |  | 8 | 19
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
| Total Winter Load based on normal weather conditions* | 82971 | 77095.8637 | 5875.1363 | 98807 | 92888.582 | 5918.418 | 114559 | 109220.3401 | 5338.6599 | 130786 | 125732.4332 | 5053.5668 | 136528 | 131265.8288 | 5262.1712
| less: Incremental Rooftop PV Forecast | -47 | -29.3339 | -17.6661 | -63 | -38.6424 | -24.3576 | -83 | -50.1259 | -32.8741 | -108 | -63.9568 | -44.0432 | -137 | -80.0579 | -56.9421
| less: Load Resources providing Responsive Reserves | -1633 | -1540 | -93 | -1633 | -1540 | -93 | -1633 | -1540 | -93 | -1633 | -1540 | -93 | -1633 | -1540 | -93
| less: Load Resources providing Non-Spinning Reserves | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0 | -234.6 | -234.6 | 0
| less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | -167.3 | -167.3 | 0 | -167.3 | -167.3 | 0 | -167.3 | -167.3 | 0 | -167.3 | -167.3 | 0 | -167.3 | -167.3 | 0
| less: Controllable Load Resources not included in other adjustments | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -1553 | -1553 | 0 | -1630 | -1630 | 0 | -1630 | -1630 | 0 | -1630 | -1630 | 0 | -1630 | -1630 | 0
| less: TDSP Standard Offer Load Management Programs | -41.208 | -41.208 | 0 | -41.208 | -41.208 | 0 | -41.208 | -41.208 | 0 | -41.208 | -41.208 | 0 | -41.208 | -41.208 | 0
| less: Distribution Voltage Reduction | -687 | -687 | 0 | -687 | -687 | 0 | -687 | -687 | 0 | -687 | -687 | 0 | -687 | -687 | 0
| Firm Peak Load, MW | 78607.892 | 72843.4218 | 5764.4702 | 94350.892 | 88549.8316 | 5801.0604 | 110082.892 | 104870.1062 | 5212.7858 | 126284.892 | 121368.3685 | 4916.5235 | 131997.892 | 126885.6629 | 5112.2291
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
| Installed Winter-rated Capacity, Thermal | 69869.1 | 69869.1 | 0 | 69869.1 | 69869.1 | 0 | 69869.1 | 69869.1 | 0 | 69084.1 | 69084.1 | 0 | 69084.1 | 69084.1 | 0
| Hydroelectric, Peak Average Capacity Contribution | 515.07 | 520.793 | -5.723 | 515.07 | 520.793 | -5.723 | 515.07 | 520.793 | -5.723 | 515.07 | 520.793 | -5.723 | 515.07 | 520.793 | -5.723
| Switchable Capacity | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0
| less: Switchable Capacity Unavailable to ERCOT | -364 | -364 | 0 | -364 | -364 | 0 | -542 | -542 | 0 | -357 | -357 | 0 | 0 | 0 | 0
| Available Mothballed Capacity (Units with reported return probabilities ≥ 75%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity from Private Use Networks | 4049 | 3851.8137 | 197.1863 | 3939 | 3747.1707 | 191.8293 | 4146 | 3944.0898 | 201.9102 | 4146 | 3944.0898 | 201.9102 | 4396 | 4181.9148 | 214.0852
| Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs) | [3]: 0; [6]: 0; [9]: 0; [12]: 0; [15]: 0
| Coastal Wind | 1623.5088 | 1623.5088 | 0 | 1615.592 | 1615.592 | 0 | 1582.2166 | 1582.2166 | 0 | 1582.3205 | 1582.3205 | 0 | 1582.3686 | 1582.3686 | 0
| Panhandle Wind | 1519.0989 | 1519.0989 | 0 | 1511.6913 | 1511.6913 | 0 | 1480.4623 | 1480.4623 | 0 | 1480.5595 | 1480.5595 | 0 | 1480.6046 | 1480.6046 | 0
| Other Wind | 4458.5786 | 4458.5786 | 0 | 4436.8372 | 4436.8372 | 0 | 4345.1794 | 4345.1794 | 0 | 4345.4648 | 4345.4648 | 0 | 4345.5971 | 4345.5971 | 0
| Far West Solar Utility-Scale | 135.8787 | 135.8787 | 0 | 103.0881 | 103.0881 | 0 | 95.5198 | 95.5198 | 0 | 91.7064 | 91.7064 | 0 | 92.1328 | 92.1328 | 0
| West Solar Utility-Scale | 112.7966 | 112.7966 | 0 | 85.5762 | 85.5762 | 0 | 79.2936 | 79.2936 | 0 | 76.1279 | 76.1279 | 0 | 76.4819 | 76.4819 | 0
| Other Solar Utility-Scale | 348.1433 | 348.1433 | 0 | 264.1284 | 264.1284 | 0 | 244.7373 | 244.7373 | 0 | 234.9666 | 234.9666 | 0 | 236.0592 | 236.0592 | 0
| Energy Storage | 4322.94 | 4024.0655 | 298.8745 | 3424.5598 | 3139.2857 | 285.2741 | 2911.8988 | 2688.4619 | 223.4369 | 2839.1888 | 2600.2587 | 238.93 | 2807.1247 | 2571.0686 | 236.0561
| RMR Capacity to be under Contract | 412 | 412 | 0 | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, Total | 91018.1148 | 90527.7771 | 490.3378 | 89828.6431 | 89357.2627 | 471.3804 | 88743.4777 | 88323.8537 | 419.6241 | 88054.5044 | 87619.3872 | 435.1172 | 88631.539 | 88187.1206 | 444.4183
Non-Synchronous Ties (Based on average net import contribution during winter 2020/2021 EEA events) |  | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
| Thermal Resources | 487.5 | 487.5 | 0 | 1399.5 | 1399.5 | 0 | 1399.5 | 1399.5 | 0 | 2096.5 | 2096.5 | 0 | 2096.5 | 2096.5 | 0
| Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs) | [3]: 0; [6]: 0; [9]: 0; [12]: 0; [15]: 0
| Coastal Wind | 72.1134 | 72.1134 | 0 | 205.4672 | 205.4672 | 0 | 201.2226 | 201.2226 | 0 | 201.2358 | 201.2358 | 0 | 201.2419 | 201.2419 | 0
| Panhandle Wind | 54.1768 | 54.1768 | 0 | 191.4805 | 191.4805 | 0 | 187.5248 | 187.5248 | 0 | 187.5371 | 187.5371 | 0 | 187.5428 | 187.5428 | 0
| Other Wind | 128.8847 | 128.8847 | 0 | 230.3862 | 230.3862 | 0 | 327.6619 | 327.6619 | 0 | 327.6834 | 327.6834 | 0 | 327.6934 | 327.6934 | 0
| Far West Solar Utility-Scale | 3.7995 | 3.7995 | 0 | 19.0919 | 19.0919 | 0 | 17.6903 | 17.6903 | 0 | 22.2895 | 22.2895 | 0 | 22.3931 | 22.3931 | 0
| West Solar Utility-Scale | 46.7894 | 46.7894 | 0 | 95.3101 | 95.3101 | 0 | 121.522 | 121.522 | 0 | 124.6784 | 124.6784 | 0 | 136.249 | 136.249 | 0
| Other Solar Utility-Scale | 133.7263 | 133.7263 | 0 | 209.8714 | 209.8714 | 0 | 263.7555 | 263.7555 | 0 | 270.4473 | 270.4473 | 0 | 271.705 | 271.705 | 0
| Energy Storage | 4589.8224 | 4263.5807 | 326.2417 | 5690.4278 | 5227.7283 | 462.6995 | 5811.8927 | 5407.7066 | 404.1861 | 6082.1323 | 5624.5547 | 457.5775 | 6102.8251 | 5643.2393 | 459.5858
| Unconfirmed Planned Retirements | 0 | 0 | 0 | 0 | 0 | 0 | -1075 | -1075 | 0 | -1075 | -1075 | 0 | -2045 | -2045 | 0
| Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements | 5516.8125 | 5190.5708 | 326.2417 | 8041.535 | 7578.8355 | 462.6995 | 7255.7697 | 6851.5836 | 404.1861 | 8237.5038 | 7779.9262 | 457.5775 | 7301.1503 | 6841.5645 | 459.5858
Total Capacity |  | 97254.7273 | 96438.1479 | 816.5795 | 98589.978 | 97655.8982 | 934.0799 | 96719.0474 | 95895.2373 | 823.8101 | 97011.8082 | 96119.1134 | 892.6948 | 96652.4893 | 95748.4851 | 904.0041
| Reserve Margin | 23.72% | 32.39% | -8.67% | 4.493% | 10.28% | -5.791% | -12.14% | -8.558% | -3.582% | -23.18% | -20.8% | -2.376% | -26.78% | -24.54% | -2.238%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
*Total Load consists of the following forecast components: Base Economic, Electric Vehicle Forecast, Large Flexible Loads forecast, Total Contracts, and Total Officer Letters. The rooftop PV forecast is shown as a separate adjustment to indicate the magnitude of this Distributed Generation resource. https://www.ercot.com/gridinfo/load/forecast

## Unit Details
NOTES
See the Acronym tab for terms associated with the Technology, Fuel, Status and CDR Resource Attribute columns below.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Resources Services (RIOO-RS) system.
Seasonal Capabilities are based on the reported Seasonal Net Sustained Capabilities in RIOO-RS. For planned projects, if Net Sustained Capabilities are not available, then the maximum capacities reported in the RIOO-Information Services (RIOO-RS) system are used.
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
[11 empty] | Summer Capabilities, MW (As of the Season Start Date, June 1) |  |  |  |  | Winter Capabilities, MW (As of the Season Start Date, December 1)
UNIT NAME | INTERCONNECTION REQUEST NUMBER (INR) | UNIT CODE | TECHNOLOGY | FUEL | CDR STATUS | CDR RESOURCE ATTRIBUTE | COUNTY | ZONE | IN-SERVICE DATE | INSTALLED CAPACITY (MW) | 2025 | 2026 | 2027 | 2028 | 2029 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30
COMANCHE PEAK U1 |  | CPSES_UNIT1 | ST | NUCLEAR | OPER | CONV | SOMERVELL | NORTH | 1990-08-13 | 1269 | 1205 | 1205 | 1205 | 1205 | 1205 | 1235 | 1235 | 1235 | 1235 | 1235
COMANCHE PEAK U2 |  | CPSES_UNIT2 | ST | NUCLEAR | OPER | CONV | SOMERVELL | NORTH | 1993-08-03 | 1269 | 1195 | 1195 | 1195 | 1195 | 1195 | 1225 | 1225 | 1225 | 1225 | 1225
SOUTH TEXAS U1 |  | STP_STP_G1 | ST | NUCLEAR | OPER | CONV | MATAGORDA | COASTAL | 1988-03-22 | 1365 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2
SOUTH TEXAS U2 |  | STP_STP_G2 | ST | NUCLEAR | OPER | CONV | MATAGORDA | COASTAL | 1989-03-28 | 1365 | 1280 | 1280 | 1280 | 1280 | 1280 | 1340 | 1340 | 1340 | 1340 | 1340
COLETO CREEK |  | COLETO_COLETOG1 | ST | COAL | OPER-UNR | CONV | GOLIAD | SOUTH | 1980-01-01 | 655 | 655 | 655 | 0 | 0 | 0 | 655 | 655 | 0 | 0 | 0
FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1979-06-16 | 615 | 604 | 604 | 604 | 604 | 604 | 603 | 603 | 603 | 603 | 603
FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1980-05-20 | 615 | 599 | 599 | 599 | 599 | 599 | 605 | 605 | 605 | 605 | 605
FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1988-04-29 | 460 | 437 | 437 | 437 | 437 | 437 | 449 | 449 | 449 | 449 | 449
J K SPRUCE U1 |  | CALAVERS_JKS1 | ST | COAL | OPER-UNR | CONV | BEXAR | SOUTH | 1992-11-01 | 560 | 560 | 560 | 560 | 560 | 0 | 560 | 560 | 560 | 560 | 0
J K SPRUCE U2 |  | CALAVERS_JKS2 | ST | COAL | OPER-UNR | CONV | BEXAR | SOUTH | 2010-05-28 | 922 | 785 | 785 | 785 | 0 | 0 | 785 | 785 | 785 | 0 | 0
LIMESTONE U1 |  | LEG_LEG_G1 | ST | COAL | OPER | CONV | LIMESTONE | NORTH | 1985-12-01 | 893 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824
LIMESTONE U2 |  | LEG_LEG_G2 | ST | COAL | OPER | CONV | LIMESTONE | NORTH | 1986-12-01 | 956.8 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836
MARTIN LAKE U1 |  | MLSES_UNIT1 | ST | COAL | OPER | CONV | RUSK | NORTH | 1977-05-16 | 893 | 800 | 800 | 800 | 800 | 800 | 815 | 815 | 815 | 815 | 815
MARTIN LAKE U2 |  | MLSES_UNIT2 | ST | COAL | OPER | CONV | RUSK | NORTH | 1978-05-23 | 893 | 805 | 805 | 805 | 805 | 805 | 820 | 820 | 820 | 820 | 820
MARTIN LAKE U3 |  | MLSES_UNIT3 | ST | COAL | OPER | CONV | RUSK | NORTH | 1979-04-01 | 893 | 805 | 805 | 805 | 805 | 805 | 820 | 820 | 820 | 820 | 820
OAK GROVE SES U1 |  | OGSES_UNIT1A | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 2010-04-14 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
OAK GROVE SES U2 |  | OGSES_UNIT2 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 2011-04-19 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
SAN MIGUEL U1 |  | SANMIGL_G1 | ST | COAL | OPER | CONV | ATASCOSA | SOUTH | 1982-02-07 | 430 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDY CREEK U1 |  | SCES_UNIT1 | ST | COAL | OPER | CONV | MCLENNAN | NORTH | 2013-07-17 | 1008 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6
TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 1990-06-08 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 1991-05-31 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
W A PARISH U5 |  | WAP_WAP_G5 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1977-12-27 | 734.1 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
W A PARISH U6 |  | WAP_WAP_G6 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1978-12-27 | 734.1 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
W A PARISH U7 |  | WAP_WAP_G7 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1980-06-02 | 614.6 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH U8 |  | WAP_WAP_G8 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1982-12-01 | 653.99 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 189 | 178.2 | 178.2 | 178.2 | 178.2 | 178.2 | 176 | 176 | 176 | 176 | 176
ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 195 | 164 | 164 | 164 | 164 | 164 | 176 | 176 | 176 | 176 | 176
ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 222 | 197.5 | 197.5 | 197.5 | 197.5 | 197.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
ATKINS CTG 7 |  | ATKINS_ATKINSG7 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 1973-01-01 | 21 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20
BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-26 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165
BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-26 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165
BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | ST | GAS | OPER | CONV | NUECES | COASTAL | 1974-04-15 | 352.8 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | CC | GAS | OPER | CONV | NUECES | COASTAL | 1976-03-01 | 351 | 319 | 319 | 319 | 319 | 319 | 325 | 325 | 325 | 325 | 325
BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 188 | 171 | 171 | 171 | 171 | 171 | 188 | 188 | 188 | 188 | 188
BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 188 | 171 | 171 | 171 | 171 | 171 | 188 | 188 | 188 | 188 | 188
BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 242 | 233 | 233 | 233 | 233 | 233 | 234 | 234 | 234 | 234 | 234
BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2000-06-01 | 188.7 | 143 | 143 | 143 | 143 | 143 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2000-06-01 | 188.7 | 143 | 143 | 143 | 143 | 143 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2001-06-01 | 188.7 | 145 | 145 | 145 | 145 | 145 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5
BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2001-06-01 | 94.95 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2
BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2009-03-01 | 254.15 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7
BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 275.57 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 270 | 270 | 270 | 270 | 270
BROTMAN POWER STATION U1 |  | BTM_UNIT1 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U2 |  | BTM_UNIT2 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U3 |  | BTM_UNIT3 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U4 |  | BTM_UNIT4 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U5 |  | BTM_UNIT5 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U6 |  | BTM_UNIT6 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BROTMAN POWER STATION U7 |  | BTM_UNIT7 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-10-23 | 60.5 | 41.3 | 41.3 | 41.3 | 41.3 | 41.3 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
BROTMAN POWER STATION U8 |  | BTM_UNIT8 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-10-23 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | GT | GAS | OPER | CONV | HOWARD | WEST | 1987-07-20 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | GT | GAS | OPER | CONV | HOWARD | WEST | 1987-07-21 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | GT | GAS | OPER | CONV | CALHOUN | COASTAL | 2017-10-03 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | GT | GAS | OPER | CONV | CALHOUN | COASTAL | 2017-10-03 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2017-10-24 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2017-10-24 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 163 | 163 | 163 | 163 | 163 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 163 | 163 | 163 | 163 | 163 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU 4 STG |  | CBY4_ST04 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 178 | 178 | 178 | 178 | 178 | 186 | 186 | 186 | 186 | 186
CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | ST | GAS | OPER | CONV | CHAMBERS | HOUSTON | 1970-12-11 | 765 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | ST | GAS | OPER | CONV | CHAMBERS | HOUSTON | 1972-03-15 | 765 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 86.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 87 | 87 | 87 | 87 | 87
COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 86.5 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6
COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 86.5 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7
COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 86.5 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9
COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 107.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2
COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 110.7 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7
COLORADO BEND II CTG 7 |  | CBECII_CT7 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 360.9 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2
COLORADO BEND II CTG 8 |  | CBECII_CT8 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 360.9 | 335 | 335 | 335 | 335 | 335 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6
COLORADO BEND II STG 9 |  | CBECII_STG9 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 508.5 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5
COLORADO BEND ENERGY CENTER CTG 11 |  | CBEC_GT11 | GT | GAS | OPER | CONV | WHARTON | HOUSTON | 2023-05-31 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
COLORADO BEND ENERGY CENTER CTG 12 |  | CBEC_GT12 | GT | GAS | OPER | CONV | WHARTON | HOUSTON | 2023-05-31 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 169 | 169 | 169 | 169 | 169 | 185 | 185 | 185 | 185 | 185
CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 165 | 165 | 165 | 165 | 165 | 182 | 182 | 182 | 182 | 182
CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 165 | 165 | 165 | 165 | 165 | 181 | 181 | 181 | 181 | 181
CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 150 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
DANSBY CTG 2 |  | DANSBY_DANSBYG2 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 2004-02-01 | 48 | 45 | 45 | 45 | 45 | 45 | 48 | 48 | 48 | 48 | 48
DANSBY CTG 3 |  | DANSBY_DANSBYG3 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 2010-01-11 | 50 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50
DANSBY STG 1 |  | DANSBY_DANSBYG1 | ST | GAS | OPER | CONV | BRAZOS | NORTH | 1978-09-01 | 120 | 107 | 107 | 107 | 107 | 107 | 110 | 110 | 110 | 110 | 110
DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54
DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54
DECORDOVA CTG 1 |  | DCSES_CT10 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 88 | 88 | 88 | 88 | 88
DECORDOVA CTG 2 |  | DCSES_CT20 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 87 | 87 | 87 | 87 | 87
DECORDOVA CTG 3 |  | DCSES_CT30 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 68 | 68 | 68 | 68 | 68 | 86 | 86 | 86 | 86 | 86
DECORDOVA CTG 4 |  | DCSES_CT40 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 86 | 86 | 86 | 86 | 86
DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 203 | 172 | 172 | 172 | 172 | 172 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 215 | 182 | 182 | 182 | 182 | 182 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 203 | 172 | 172 | 172 | 172 | 172 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 215 | 182 | 182 | 182 | 182 | 182 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2014-06-11 | 199 | 156 | 156 | 156 | 156 | 156 | 190 | 190 | 190 | 190 | 190
DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 290 | 287 | 287 | 287 | 287 | 287 | 290 | 290 | 290 | 290 | 290
DENTON ENERGY CENTER IC A |  | DEC_AGR_A | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC B |  | DEC_AGR_B | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC C |  | DEC_AGR_C | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC D |  | DEC_AGR_D | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | GT | GAS | OPER | CONV | ECTOR | WEST | 2015-07-25 | 181 | 181 | 181 | 181 | 181 | 181 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | GT | GAS | OPER | CONV | ECTOR | WEST | 2015-07-25 | 181 | 181 | 181 | 181 | 181 | 181 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-01-01 | 260 | 204 | 204 | 204 | 204 | 204 | 245 | 245 | 245 | 245 | 245
ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-01-01 | 140 | 115 | 115 | 115 | 115 | 115 | 116 | 116 | 116 | 116 | 116
EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40
EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40
EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40
EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40
FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 185.3 | 169 | 169 | 169 | 169 | 169 | 180 | 180 | 180 | 180 | 180
FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 185.3 | 169 | 169 | 169 | 169 | 169 | 180 | 180 | 180 | 180 | 180
FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 204 | 182 | 182 | 182 | 182 | 182 | 194 | 194 | 194 | 194 | 194
FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 165 | 165 | 165 | 165 | 165 | 195 | 195 | 195 | 195 | 195
FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185
FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185
FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 165 | 165 | 165 | 165 | 165 | 195 | 195 | 195 | 195 | 195
FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185
FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185
FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 422 | 406 | 406 | 406 | 406 | 406 | 418 | 418 | 418 | 418 | 418
FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 422 | 406 | 406 | 406 | 406 | 406 | 418 | 418 | 418 | 418 | 418
FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 179.35 | 147 | 147 | 147 | 147 | 147 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 179.35 | 147 | 147 | 147 | 147 | 147 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 179.35 | 145 | 145 | 145 | 145 | 145 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 179.35 | 145 | 145 | 145 | 145 | 145 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 190.74 | 169 | 169 | 169 | 169 | 169 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 190.74 | 168 | 168 | 168 | 168 | 168 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7
FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2018-11-08 | 129 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
FRONTERA ENERGY CENTER CTG 1 |  | FRONT_EC_CT1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
FRONTERA ENERGY CENTER CTG 2 |  | FRONT_EC_CT2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
FRONTERA ENERGY CENTER STG |  | FRONT_EC_ST | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5
GRAHAM STG 1 |  | GRSES_UNIT1 | ST | GAS | OPER | CONV | YOUNG | WEST | 1960-12-19 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
GRAHAM STG 2 |  | GRSES_UNIT2 | ST | GAS | OPER | CONV | YOUNG | WEST | 1969-06-05 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 57 | 57 | 57 | 57 | 57 | 67 | 67 | 67 | 67 | 67
GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 53 | 53 | 53 | 53 | 53 | 68 | 68 | 68 | 68 | 68
GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 53 | 53 | 53 | 53 | 53 | 69 | 69 | 69 | 69 | 69
GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 47 | 47 | 47 | 47 | 47 | 53 | 53 | 53 | 53 | 53
GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 61 | 61 | 61 | 61 | 61 | 72 | 72 | 72 | 72 | 72
GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 56 | 56 | 56 | 56 | 56 | 67 | 67 | 67 | 67 | 67
GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 185 | 145 | 145 | 145 | 145 | 145 | 165 | 165 | 165 | 165 | 165
GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 185 | 145 | 145 | 145 | 145 | 145 | 165 | 165 | 165 | 165 | 165
GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 100 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 143 | 143 | 143 | 143 | 143 | 167 | 167 | 167 | 167 | 167
GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 143 | 143 | 143 | 143 | 143 | 167 | 167 | 167 | 167 | 167
GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 141 | 141 | 141 | 141 | 141 | 167 | 167 | 167 | 167 | 167
GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 141 | 141 | 141 | 141 | 141 | 167 | 167 | 167 | 167 | 167
GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 204 | 198 | 198 | 198 | 198 | 198 | 203 | 203 | 203 | 203 | 203
GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 204 | 198 | 198 | 198 | 198 | 198 | 203 | 203 | 203 | 203 | 203
HANDLEY STG 3 |  | HLSES_UNIT3 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1963-01-01 | 395 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
HANDLEY STG 4 |  | HLSES_UNIT4 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1976-01-01 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY STG 5 |  | HLSES_UNIT5 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1977-01-01 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-05-28 | 242 | 210 | 210 | 210 | 210 | 210 | 239 | 239 | 239 | 239 | 239
HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-04-19 | 242 | 211 | 211 | 211 | 211 | 211 | 240 | 240 | 240 | 240 | 240
HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-08-16 | 252 | 210 | 210 | 210 | 210 | 210 | 242 | 242 | 242 | 242 | 242
HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-08-15 | 252 | 213 | 213 | 213 | 213 | 213 | 243 | 243 | 243 | 243 | 243
HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 176.63 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150
HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 176.63 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150
HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 198.05 | 168 | 168 | 168 | 168 | 168 | 176 | 176 | 176 | 176 | 176
JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 198.9 | 150 | 150 | 150 | 150 | 150 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 198.9 | 150 | 150 | 150 | 150 | 150 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 198.9 | 158 | 158 | 158 | 158 | 158 | 182 | 182 | 182 | 182 | 182
JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 198.9 | 158 | 158 | 158 | 158 | 158 | 182 | 182 | 182 | 182 | 182
JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 320.6 | 289 | 289 | 289 | 289 | 289 | 300 | 300 | 300 | 300 | 300
JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 320.6 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | CC | GAS | OPER | CONV | JOHNSON | NORTH | 1997-01-02 | 185 | 163 | 163 | 163 | 163 | 163 | 177 | 177 | 177 | 177 | 177
JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | CC | GAS | OPER | CONV | JOHNSON | NORTH | 1997-01-02 | 107 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1970-06-18 | 397 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | ST | GAS | OPER | CONV | DALLAS | NORTH | 1973-11-20 | 531 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 153 | 153 | 153 | 153 | 153 | 186 | 186 | 186 | 186 | 186
LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 145 | 145 | 145 | 145 | 145 | 178 | 178 | 178 | 178 | 178
LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 145 | 145 | 145 | 145 | 145 | 178 | 178 | 178 | 178 | 178
LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 153 | 153 | 153 | 153 | 153 | 186 | 186 | 186 | 186 | 186
LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAREDO CTG 4 |  | LARDVFTN_G4 | GT | GAS | OPER | CONV | WEBB | SOUTH | 2008-07-27 | 98.5 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4
LAREDO CTG 5 |  | LARDVFTN_G5 | GT | GAS | OPER | CONV | WEBB | SOUTH | 2008-08-20 | 98.5 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4
LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-03-26 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-08 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-15 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-22 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2022-06-20 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 44 | 44 | 44 | 44 | 44
LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2022-06-20 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 44 | 44 | 44 | 44 | 44
LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 202.5 | 170 | 170 | 170 | 170 | 170 | 183 | 183 | 183 | 183 | 183
LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 202.5 | 170 | 170 | 170 | 170 | 170 | 183 | 183 | 183 | 183 | 183
LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 204 | 188 | 188 | 188 | 188 | 188 | 192 | 192 | 192 | 192 | 192
MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 266.9 | 215 | 215 | 215 | 215 | 215 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 266.9 | 215 | 215 | 215 | 215 | 215 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 258.4 | 236 | 236 | 236 | 236 | 236 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9
MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-03-18 | 258 | 229 | 229 | 229 | 229 | 229 | 258 | 258 | 258 | 258 | 258
MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-03-15 | 256 | 227 | 227 | 227 | 227 | 227 | 256 | 256 | 256 | 256 | 256
MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-01-22 | 255 | 227 | 227 | 227 | 227 | 227 | 255 | 255 | 255 | 255 | 255
MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-02-08 | 258 | 227 | 227 | 227 | 227 | 227 | 258 | 258 | 258 | 258 | 258
MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-06-28 | 276 | 241 | 241 | 241 | 241 | 241 | 276 | 276 | 276 | 276 | 276
MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-06-07 | 278 | 243 | 243 | 243 | 243 | 243 | 278 | 278 | 278 | 278 | 278
MORGAN CREEK CTG 1 |  | MGSES_CT1 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 66 | 66 | 66 | 66 | 66 | 82 | 82 | 82 | 82 | 82
MORGAN CREEK CTG 2 |  | MGSES_CT2 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 80 | 80 | 80 | 80 | 80
MORGAN CREEK CTG 3 |  | MGSES_CT3 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 80 | 80 | 80 | 80 | 80
MORGAN CREEK CTG 4 |  | MGSES_CT4 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK CTG 5 |  | MGSES_CT5 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 80 | 80 | 80 | 80 | 80
MORGAN CREEK CTG 6 |  | MGSES_CT6 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 82 | 82 | 82 | 82 | 82
MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1956-01-01 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1958-01-01 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1967-01-01 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-20 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165
NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-20 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165
NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | CC | GAS | OPER | CONV | NUECES | COASTAL | 1972-01-01 | 351 | 319 | 319 | 319 | 319 | 319 | 325 | 325 | 325 | 325 | 325
O W SOMMERS STG 1 |  | CALAVERS_OWS1 | ST | GAS | OPER-UNR | CONV | BEXAR | SOUTH | 1972-06-06 | 445 | 420 | 420 | 0 | 0 | 0 | 420 | 420 | 0 | 0 | 0
O W SOMMERS STG 2 |  | CALAVERS_OWS2 | ST | GAS | OPER-UNR | CONV | BEXAR | SOUTH | 1974-03-20 | 435 | 410 | 410 | 410 | 410 | 0 | 410 | 410 | 410 | 410 | 0
ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 195.2 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2
ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 189.1 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1
ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 195.2 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2
ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 189.1 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1
ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 224 | 206 | 206 | 206 | 206 | 206 | 217 | 217 | 217 | 217 | 217
ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 224 | 206 | 206 | 206 | 206 | 206 | 217 | 217 | 217 | 217 | 217
OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2022-01-12 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2022-01-12 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 232 | 199 | 199 | 199 | 199 | 199 | 224 | 224 | 224 | 224 | 224
PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 232 | 199 | 199 | 199 | 199 | 199 | 224 | 224 | 224 | 224 | 224
PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 353.1 | 287 | 287 | 287 | 287 | 287 | 316 | 316 | 316 | 316 | 316
PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 232 | 223 | 223 | 223 | 223 | 223 | 222 | 222 | 222 | 222 | 222
PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 232 | 220 | 220 | 220 | 220 | 220 | 209 | 209 | 209 | 209 | 209
PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 353.1 | 326 | 326 | 326 | 326 | 326 | 325 | 325 | 325 | 325 | 325
PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 353.1 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | CC | GAS | OPER | CONV | LAMAR | NORTH | 1989-06-01 | 90.88 | 76 | 76 | 76 | 76 | 76 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | CC | GAS | OPER | CONV | LAMAR | NORTH | 1989-06-01 | 90.88 | 76 | 76 | 76 | 76 | 76 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | CC | GAS | OPER | CONV | LAMAR | NORTH | 1990-02-01 | 90 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 176 | 176 | 176 | 176 | 176
PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 176 | 176 | 176 | 176 | 176
PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 195.5 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 169 | 169 | 169 | 169 | 169
PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 63 | 63 | 63 | 63 | 63 | 79 | 79 | 79 | 79 | 79
PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 76 | 76 | 76 | 76 | 76
PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 78 | 78 | 78 | 78 | 78
PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | GT | GAS | OPER | CONV | WARD | WEST | 1990-02-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 75 | 75 | 75 | 75 | 75
PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | GT | GAS | OPER | CONV | WARD | WEST | 1990-02-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 79 | 79 | 79 | 79 | 79
PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-11-11 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-11-11 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 59 | 59 | 59 | 59 | 59 | 65 | 65 | 65 | 65 | 65
PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 61 | 61 | 61 | 61 | 61 | 65 | 65 | 65 | 65 | 65
PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 49 | 49 | 49 | 49 | 49 | 65 | 65 | 65 | 65 | 65
PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 54 | 54 | 54 | 54 | 54 | 65 | 65 | 65 | 65 | 65
PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 54 | 54 | 54 | 54 | 54 | 64 | 64 | 64 | 64 | 64
PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 52 | 52 | 52 | 52 | 52 | 65 | 65 | 65 | 65 | 65
POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | ST | GAS | OPER | CONV | HUNT | NORTH | 1967-01-01 | 25 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | ST | GAS | OPER | CONV | HUNT | NORTH | 1978-01-01 | 43.2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 90.6 | 74 | 74 | 74 | 74 | 74 | 84 | 84 | 84 | 84 | 84
QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 90.6 | 74 | 74 | 74 | 74 | 74 | 86 | 86 | 86 | 86 | 86
QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 90.6 | 72 | 72 | 72 | 72 | 72 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 90.6 | 72 | 72 | 72 | 72 | 72 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
R W MILLER CTG 4 |  | MIL_MILLERG4 | GT | GAS | OPER | CONV | PALO PINTO | NORTH | 1994-07-01 | 115.25 | 100 | 100 | 100 | 100 | 100 | 116 | 116 | 116 | 116 | 116
R W MILLER CTG 5 |  | MIL_MILLERG5 | GT | GAS | OPER | CONV | PALO PINTO | NORTH | 1994-07-01 | 115.25 | 100 | 100 | 100 | 100 | 100 | 116 | 116 | 116 | 116 | 116
R W MILLER STG 1 |  | MIL_MILLERG1 | ST | GAS | OPER | CONV | PALO PINTO | NORTH | 1968-10-01 | 74.98 | 70 | 70 | 70 | 70 | 70 | 75 | 75 | 75 | 75 | 75
R W MILLER STG 2 |  | MIL_MILLERG2 | ST | GAS | OPER | CONV | PALO PINTO | NORTH | 1972-07-01 | 120 | 118 | 118 | 118 | 118 | 118 | 120 | 120 | 120 | 120 | 120
R W MILLER STG 3 |  | MIL_MILLERG3 | ST | GAS | OPER | CONV | PALO PINTO | NORTH | 1975-08-01 | 216.01 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | GT | GAS | OPER | CONV | COLLIN | NORTH | 2001-06-01 | 95 | 80 | 80 | 80 | 80 | 80 | 95 | 95 | 95 | 95 | 95
RAY OLINGER STG 2 |  | OLINGR_OLING_2 | ST | GAS | OPER | CONV | COLLIN | NORTH | 1971-05-01 | 113.64 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER STG 3 |  | OLINGR_OLING_3 | ST | GAS | OPER | CONV | COLLIN | NORTH | 1975-12-01 | 156.6 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
RABBS POWER STATION U1 |  | RAB_UNIT1 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-09-12 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U2 |  | RAB_UNIT2 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-07-12 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U3 |  | RAB_UNIT3 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U4 |  | RAB_UNIT4 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U5 |  | RAB_UNIT5 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U6 |  | RAB_UNIT6 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U7 |  | RAB_UNIT7 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RABBS POWER STATION U8 |  | RAB_UNIT8 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REDGATE IC A |  | REDGATE_AGR_A | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC B |  | REDGATE_AGR_B | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC C |  | REDGATE_AGR_C | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC D |  | REDGATE_AGR_D | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REMY JADE POWER STATION U1 |  | JAD_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U2 |  | JAD_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U3 |  | JAD_UNIT3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U4 |  | JAD_UNIT4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U5 |  | JAD_UNIT5 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U6 |  | JAD_UNIT6 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 203 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 203 | 203 | 203 | 203 | 203
RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 193 | 158 | 158 | 158 | 158 | 158 | 193 | 193 | 193 | 193 | 193
RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 203 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 203 | 203 | 203 | 203 | 203
RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 373.16 | 303 | 303 | 303 | 303 | 303 | 319 | 319 | 319 | 319 | 319
SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-24 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 60.5 | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 51
SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 41.98 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1995-04-21 | 88.23 | 80 | 80 | 80 | 80 | 80 | 87 | 87 | 87 | 87 | 87
SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1995-04-21 | 88.23 | 80 | 80 | 80 | 80 | 80 | 87 | 87 | 87 | 87 | 87
SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | CC | GAS | OPER | CONV | TRAVIS | SOUTH | 2004-09-01 | 198.9 | 142 | 142 | 142 | 142 | 142 | 175 | 175 | 175 | 175 | 175
SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2010-03-22 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2010-04-09 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | CC | GAS | OPER | CONV | TRAVIS | SOUTH | 2004-09-01 | 191 | 139 | 139 | 139 | 139 | 139 | 150 | 150 | 150 | 150 | 150
SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | GT | GAS | OPER | CONV | CAMERON | COASTAL | 2004-01-01 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CC | GAS | OPER | CONV | CAMERON | COASTAL | 1996-01-01 | 50 | 38 | 38 | 38 | 38 | 38 | 49 | 49 | 49 | 49 | 49
SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CC | GAS | OPER | CONV | CAMERON | COASTAL | 1962-03-02 | 25 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21
SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1965-05-15 | 136 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1968-03-01 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1972-05-01 | 351 | 336 | 336 | 336 | 336 | 336 | 340 | 340 | 340 | 340 | 340
SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | IC | GAS | OPER | CONV | COLORADO | SOUTH | 2016-02-10 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | IC | GAS | OPER | CONV | COLORADO | SOUTH | 2016-02-10 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
STRYKER CREEK STG 1 |  | SCSES_UNIT1A | ST | GAS | OPER | CONV | CHEROKEE | NORTH | 1958-06-26 | 177 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK STG 2 |  | SCSES_UNIT2 | ST | GAS | OPER | CONV | CHEROKEE | NORTH | 1965-12-21 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
T H WHARTON CTG 1 |  | THW_THWGT_1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1967-07-31 | 16.32 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16
T H WHARTON POWER CTG 31 |  | THW_THWGT31 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 32 |  | THW_THWGT32 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 33 |  | THW_THWGT33 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 34 |  | THW_THWGT34 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 41 |  | THW_THWGT41 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 42 |  | THW_THWGT42 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 43 |  | THW_THWGT43 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 44 |  | THW_THWGT44 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 69 | 54 | 54 | 54 | 54 | 54 | 69 | 69 | 69 | 69 | 69
T H WHARTON POWER CTG 51 |  | THW_THWGT51 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER CTG 52 |  | THW_THWGT52 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER CTG 53 |  | THW_THWGT53 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER CTG 54 |  | THW_THWGT54 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER CTG 55 |  | THW_THWGT55 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER CTG 56 |  | THW_THWGT56 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65
T H WHARTON POWER STG 3 |  | THW_THWST_3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
T H WHARTON POWER STG 4 |  | THW_THWST_4 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
TEXAS CITY POWER CTG A |  | TXCTY_CTA | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY POWER CTG B |  | TXCTY_CTB | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY POWER CTG C |  | TXCTY_CTC | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
TEXAS CITY POWER STG |  | TXCTY_ST | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 143.65 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5
TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | GT | GAS | OPER | CONV | WHARTON | SOUTH | 1985-04-25 | 94 | 90 | 90 | 90 | 90 | 90 | 94 | 94 | 94 | 94 | 94
TRINIDAD STG 6 |  | TRSES_UNIT6 | ST | GAS | OPER | CONV | HENDERSON | NORTH | 1965-05-26 | 239 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | ST | GAS | OPER | CONV | BEXAR | SOUTH | 1966-05-03 | 225 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | ST | GAS | OPER | CONV | BEXAR | SOUTH | 1968-05-15 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | ST | GAS | RMR | CONV | BEXAR | SOUTH | 1970-08-01 | 420 | 412 | 412 | 0 | 0 | 0 | 412 | 412 | 0 | 0 | 0
VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2020-02-06 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2020-02-06 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2019-09-30 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2019-09-30 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2009-10-15 | 196.86 | 160 | 160 | 160 | 160 | 160 | 171 | 171 | 171 | 171 | 171
VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2009-10-15 | 180.2 | 125 | 125 | 125 | 125 | 125 | 132 | 132 | 132 | 132 | 132
W A PARISH CTG 1 |  | WAP_WAPGT_1 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 1967-07-31 | 16.32 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
W A PARISH STG 1 |  | WAP_WAP_G1 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1958-06-01 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG 2 |  | WAP_WAP_G2 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1958-12-20 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG 3 |  | WAP_WAP_G3 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1961-03-15 | 299.2 | 240 | 240 | 240 | 240 | 240 | 258 | 258 | 258 | 258 | 258
W A PARISH STG 4 |  | WAP_WAP_G4 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1968-06-01 | 580.5 | 527 | 527 | 527 | 527 | 527 | 552 | 552 | 552 | 552 | 552
WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46
WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8
WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8
WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 264.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4
WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 264.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4
WOLF HOLLOW POWER STG |  | WHCCS_STG | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 300 | 268 | 268 | 268 | 268 | 268 | 269 | 269 | 269 | 269 | 269
WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 360 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3
WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 360 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6
WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 511.2 | 446.3 | 446.3 | 446.3 | 446.3 | 446.3 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1
NACOGDOCHES POWER |  | NACPW_UNIT1 | ST | BIOMASS | OPER | CONV | NACOGDOCHES | NORTH | 2012-06-22 | 116.45 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | ST | BIOMASS | OPER | CONV-SODG | DENTON | NORTH | 2011-08-01 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | ST | BIOMASS | OPER | CONV-SODG | DALLAS | NORTH | 2015-03-20 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
NELSON GARDENS LFG |  | DG_78252_4UNITS | ST | BIOMASS | OPER | CONV-SODG | BEXAR | SOUTH | 2013-12-31 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | ST | BIOMASS | OPER | CONV-SODG | TRAVIS | SOUTH | 2007-11-21 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | ST | BIOMASS | OPER | CONV-SODG | COMAL | SOUTH | 2011-08-01 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | ST | BIOMASS | OPER | CONV-SODG | PARKER | NORTH | 2010-02-05 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
REMY JADE POWER STATION U7 | 24INR0736 | JAD_UNIT7 | GT | GAS | OPER-SYN | CONV | HARRIS | HOUSTON | 2024-09-12 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
REMY JADE POWER STATION U8 | 24INR0736 | JAD_UNIT8 | GT | GAS | OPER-SYN | CONV | HARRIS | HOUSTON | 2024-09-12 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD II POWER STATION U7 | 23INR0506 | BCH_UNIT7 | GT | GAS | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-11-15 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
BEACHWOOD II POWER STATION U8 | 23INR0506 | BCH_UNIT8 | GT | GAS | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-11-15 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | HY | HYDRO | OPER | CONV | VAL VERDE | WEST | 1983-06-01 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | HY | HYDRO | OPER | CONV | VAL VERDE | WEST | 1983-10-01 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1940-04-01 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1940-04-01 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1950-05-19 | 18.3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | HY | HYDRO | OPER | CONV | GRAYSON | NORTH | 1944-03-01 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
DENISON DAM 2 |  | DNDAM_DENISOG2 | HY | HYDRO | OPER | CONV | GRAYSON | NORTH | 1948-03-04 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | HY | HYDRO | OPER | CONV-TGR | MAVERICK | SOUTH | 1928-01-01 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
FALCON HYDRO 1 |  | FALCON_FALCONG1 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-06-28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-08-03 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | HY | HYDRO | OPER | CONV-TGR | COMAL | SOUTH | 1928-01-01 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
INKS HYDRO 1 |  | INKSDA_INKS_G1 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-10-10 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-09-25 | 19.8 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
WHITNEY DAM HYDRO |  | WND_WHITNEY1 | HY | HYDRO | OPER | CONV | BOSQUE | NORTH | 1953-01-01 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | HY | HYDRO | OPER | CONV | BOSQUE | NORTH | 1953-01-01 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | HY | HYDRO | OPER | CONV-SODG | TARRANT | NORTH | 1928-01-01 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | HY | HYDRO | OPER | CONV-SODG | GUADALUPE | SOUTH | 1928-01-01 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | HY | HYDRO | OPER | CONV-SODG | GUADALUPE | SOUTH | 1928-01-01 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | HY | HYDRO | OPER | CONV-SODG | DENTON | NORTH | 1991-01-01 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
ANTELOPE IC 1 |  | AEEC_ANTLP_1 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56
ANTELOPE IC 2 |  | AEEC_ANTLP_2 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56
ANTELOPE IC 3 |  | AEEC_ANTLP_3 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56
ELK STATION CTG 1 |  | AEEC_ELK_1 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200
ELK STATION CTG 2 |  | AEEC_ELK_2 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200
ELK STATION CTG 3 |  | AEEC_ELK_3 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200
TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 156 | 156 | 156 | 156 | 156 | 162 | 162 | 162 | 162 | 162
TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 135 | 135 | 135 | 135 | 135 | 179 | 179 | 179 | 179 | 179
TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 153 | 153 | 153 | 153 | 153 | 178 | 178 | 178 | 178 | 178
TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 402 | 402 | 402 | 402 | 402 | 402 | 389 | 389 | 389 | 389 | 389
TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 151 | 151 | 151 | 151 | 151 | 185 | 185 | 185 | 185 | 185
TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 148 | 148 | 148 | 148 | 148 | 185 | 185 | 185 | 185 | 185
TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 330 | 310 | 310 | 310 | 310 | 310 | 330 | 330 | 330 | 330 | 330
TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 150 | 150 | 150 | 150 | 150 | 185 | 185 | 185 | 185 | 185
TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 152 | 152 | 152 | 152 | 152 | 185 | 185 | 185 | 185 | 185
TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 330 | 311 | 311 | 311 | 311 | 311 | 330 | 330 | 330 | 330 | 330
ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | 0 | 0 | 0 | 0 | 0
ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | 0 | 0 | 0 | 0 | 0
ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | 0 | 0 | 0 | 0 | 0
ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | 0 | 0 | 0 | 0 | 0
ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | 0 | 0 | 0 | 0 | 0
ELK STATION CTG 3 |  | AEEC_ELK_3_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | 0 | 0 | 0 | 0 | 0
TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -179 | -135 | -135 | -135 | -135 | -135 | -179 | -179 | -179 | -179 | 0
TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -179 | 0 | 0 | -153 | -153 | -153 | 0 | 0 | -178 | -178 | 0
TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | -150 | -150 | -150 | 0 | 0 | -185 | -185 | -185 | 0 | 0
TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | -152 | -152 | -152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -330 | -311 | -311 | -311 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | 0 | -151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGUAYO WIND U1 |  | AGUAYO_UNIT1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2023-10-17 | 193.5 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9
AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8
AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7
ANACACHO WIND |  | ANACACHO_ANA | WT | WIND-O | OPER | CONV | KINNEY | SOUTH | 2012-12-27 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
ANCHOR WIND U2 |  | ANCHOR_WIND2 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
ANCHOR WIND U3 |  | ANCHOR_WIND3 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
ANCHOR WIND U4 |  | ANCHOR_WIND4 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
ANCHOR WIND U5 |  | ANCHOR_WIND5 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3
APOGEE WIND U1 |  | APOGEE_UNIT1 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
APOGEE WIND U2 |  | APOGEE_UNIT2 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
APOGEE WIND U3 |  | APOGEE_UNIT3 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
APOGEE WIND U4 |  | APOGEE_UNIT4 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
APOGEE WIND U5 |  | APOGEE_UNIT5 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
APOGEE WIND U6 |  | APOGEE_UNIT6 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
APOGEE WIND U7 |  | APOGEE_UNIT7 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
APPALOOSA RUN WIND U1 |  | APPALOSA_UNIT1 | WT | WIND-O | OPER | CONV | UPTON | WEST | 2024-03-06 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9
APPALOOSA RUN WIND U2 |  | APPALOSA_UNIT2 | WT | WIND-O | OPER | CONV | UPTON | WEST | 2024-03-06 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8
AVIATOR WIND U1 |  | AVIATOR_UNIT1 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 180.12 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1
AVIATOR WIND U2 |  | AVIATOR_UNIT2 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 145.64 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6
AVIATOR WIND U3 |  | DEWOLF_UNIT1 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 199.26 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3
BLACKJACK CREEK WIND U1 |  | BLACKJAK_UNIT1 | WT | WIND-O | OPER | CONV | BEE | SOUTH | 2023-05-12 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLACKJACK CREEK WIND U2 |  | BLACKJAK_UNIT2 | WT | WIND-O | OPER | CONV | BEE | SOUTH | 2023-05-12 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2016-06-24 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2016-06-24 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | WT | WIND-O | OPER | CONV | ANDREWS | WEST | 2021-09-07 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | WT | WIND-O | OPER | CONV | ANDREWS | WEST | 2021-09-07 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
BARTON CHAPEL WIND |  | BRTSW_BCW1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2007-12-01 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLUE SUMMIT WIND 1 A |  | BLSUMMIT_BLSMT1_5 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2013-12-16 | 132.84 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8
BLUE SUMMIT WIND 1 B |  | BLSUMMIT_BLSMT1_6 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2013-12-16 | 6.96 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-04-06 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5
BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-04-06 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-05-19 | 13.7 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-05-19 | 186.5 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2020-04-17 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
BRISCOE WIND |  | BRISCOE_WIND | WT | WIND-P | OPER | CONV | BRISCOE | PANHANDLE | 2015-11-13 | 149.85 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2017-12-31 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2017-12-31 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2017-12-12 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2017-12-12 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2006-04-21 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2007-07-01 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2007-07-01 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2008-07-30 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND U1 |  | BULLCRK_WND1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2009-05-14 | 89 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND U2 |  | BULLCRK_WND2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2009-05-14 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2019-12-17 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2019-12-17 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4
CACTUS FLATS WIND U1 |  | CFLATS_U1 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-06-13 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
CALLAHAN WIND |  | CALLAHAN_WND1 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2004-12-15 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1
CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2016-01-27 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2007-05-26 | 134.42 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2007-11-15 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2019-12-17 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1
CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2007-08-01 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7
CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2007-08-01 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-02-15 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-05-22 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2010-11-23 | 79.42 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7
CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2010-11-23 | 78.04 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4
CHALUPA WIND |  | CHALUPA_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2021-06-10 | 173.25 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3
CHAMPION WIND |  | CHAMPION_UNIT1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-01-28 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2017-07-11 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2017-07-11 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
COTTON PLAINS WIND |  | COTPLNS_COTTONPL | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2017-01-12 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
CRANELL WIND |  | CRANELL_UNIT1 | WT | WIND-C | OPER | CONV | REFUGIO | COASTAL | 2022-01-27 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-08-01 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-08-01 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DESERT SKY WIND 1 A |  | DSKYWND1_UNIT_1A | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 65.79 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1
DESERT SKY WIND 1 B |  | DSKYWND2_UNIT_2A | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 65.79 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
DESERT SKY WIND 2 A |  | DSKYWND1_UNIT_1B | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 23.93 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7
DESERT SKY WIND 2 B |  | DSKYWND2_UNIT_2B | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 14.74 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2016-03-15 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2016-03-15 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-06-11 | 101.2 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-06-11 | 99 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
ELBOW CREEK WIND |  | ELB_ELBCREEK | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-11-21 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
ELECTRA WIND 1 |  | DIGBY_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2016-10-17 | 101.31 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
ELECTRA WIND 2 |  | DIGBY_UNIT2 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2016-10-17 | 134.29 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2022-05-11 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6
EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2022-05-11 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
ESPIRITU WIND |  | CHALUPA_UNIT2 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2021-06-10 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | WT | WIND-P | OPER | CONV | RANDALL | PANHANDLE | 2017-05-24 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
FLAT TOP WIND I |  | FTWIND_UNIT_1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2018-09-07 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-11-20 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-11-20 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2019-12-05 | 186.48 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2019-12-05 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8
FOREST CREEK WIND |  | MCDLD_FCW1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2007-03-01 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
GOAT WIND |  | GOAT_GOATWIND | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-02-21 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 |  | GOAT_GOATWIN2 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2010-04-14 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2014-05-29 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
GOODNIGHT WIND U1 |  | GOODNIT1_UNIT1 | WT | WIND-P | OPER | CONV | ARMSTRONG | PANHANDLE | 2024-04-08 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121
GOODNIGHT WIND U2 |  | GOODNIT1_UNIT2 | WT | WIND-P | OPER | CONV | ARMSTRONG | PANHANDLE | 2024-04-08 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1
GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2020-03-09 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2020-03-09 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-01 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-01 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_BRAZ_WND1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2023-07-01 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_BRAZ_WND2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2023-07-01 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4
GREEN PASTURES WIND I |  | GPASTURE_WIND_I | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2015-11-17 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-10-28 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-10-28 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
GULF WIND I |  | TGW_T1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2021-05-06 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II |  | TGW_T2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2021-05-06 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2016-09-28 | 119.93 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
HACKBERRY WIND |  | HWF_HWFG1 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2008-12-21 | 165.6 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HEREFORD WIND G |  | HRFDWIND_WIND_G | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2014-10-23 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
HEREFORD WIND V |  | HRFDWIND_WIND_V | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2014-10-23 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | WT | WIND-O | OPER | CONV | REAGAN | WEST | 2018-05-09 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | WT | WIND-O | OPER | CONV | REAGAN | WEST | 2018-05-09 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HIDALGO II WIND |  | MIRASOLE_MIR13 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2021-07-30 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
HIGH LONESOME W 1A |  | HI_LONE_WGR1A | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
HIGH LONESOME W 1B |  | HI_LONE_WGR1B | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 51.9 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
HIGH LONESOME W 1C |  | HI_LONE_WGR1C | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
HIGH LONESOME W 2 |  | HI_LONE_WGR2 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 122.4 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5
HIGH LONESOME W 2A |  | HI_LONE_WGR2A | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
HIGH LONESOME W 3 |  | HI_LONE_WGR3 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 127.5 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6
HIGH LONESOME W 4 |  | HI_LONE_WGR4 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 101.5 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-01-23 | 134.81 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-01-23 | 101.69 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2005-06-01 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2006-06-01 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2006-06-01 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4
HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2006-06-01 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND 1 |  | INDL_INADALE1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-18 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
INADALE WIND 2 |  | INDL_INADALE2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-18 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-06-01 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8
INERTIA WIND U1 |  | INRT_W_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 67.68 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7
INERTIA WIND U2 |  | INRT_W_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
INERTIA WIND U3 |  | INRT_W_UNIT3 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 205.86 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9
JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2015-12-23 | 19.69 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2015-12-23 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2015-04-09 | 146.15 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2015-04-09 | 153.55 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 100.42 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
KEECHI WIND |  | KEECHI_U1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2014-11-15 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-11-08 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-09-21 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-12-01 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-08-12 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
LANGFORD WIND POWER |  | LGD_LANGFORD | WT | WIND-O | OPER | CONV | TOM GREEN | WEST | 2009-10-31 | 159.96 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
LACY CREEK WIND U1 |  | LACY_CRK_UNIT1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
LACY CREEK WIND U2 |  | LACY_CRK_UNIT2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 15.12 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
LACY CREEK WIND U3 |  | LACY_CRK_UNIT3 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2
LACY CREEK WIND U4 |  | LACY_CRK_UNIT4 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 12.6 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1
LAS MAJADAS WIND U1 |  | LMAJADAS_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
LAS MAJADAS WIND U2 |  | LMAJADAS_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LAS MAJADAS WIND U3 |  | LMAJADAS_UNIT3 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6
LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2019-09-19 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7
LOGANS GAP WIND I U1 |  | LGW_UNIT1 | WT | WIND-O | OPER | CONV | COMANCHE | NORTH | 2015-09-30 | 106.26 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
LOGANS GAP WIND I U2 |  | LGW_UNIT2 | WT | WIND-O | OPER | CONV | COMANCHE | NORTH | 2015-09-30 | 103.85 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2006-11-21 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2007-09-15 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2007-09-15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-09-21 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-09-21 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LORAINE WINDPARK I |  | LONEWOLF_G1 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2010-02-16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LORAINE WINDPARK II |  | LONEWOLF_G2 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2010-02-16 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III |  | LONEWOLF_G3 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2011-03-01 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV |  | LONEWOLF_G4 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2011-03-01 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LOS VIENTOS III WIND |  | LV3_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2015-01-29 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS IV WIND |  | LV4_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2016-06-06 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS V WIND |  | LV5_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2016-09-01 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
LOS VIENTOS WIND I |  | LV1_LV1A | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2013-08-30 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II |  | LV2_LV2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2013-08-30 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2012-09-27 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2012-09-27 | 103.46 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | WT | WIND-P | OPER | CONV | PARMER | PANHANDLE | 2017-03-08 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | WT | WIND-P | OPER | CONV | PARMER | PANHANDLE | 2017-03-08 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8
MCADOO WIND |  | MWEC_G1 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2008-07-31 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | WT | WIND-O | OPER | CONV | DAWSON | WEST | 2015-04-15 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | WT | WIND-O | OPER | CONV | DAWSON | WEST | 2015-04-15 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
MIAMI WIND G1 |  | MIAM1_G1 | WT | WIND-P | OPER | CONV | ROBERTS | PANHANDLE | 2014-12-04 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
MIAMI WIND G2 |  | MIAM1_G2 | WT | WIND-P | OPER | CONV | ROBERTS | PANHANDLE | 2014-12-04 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
MIDWAY WIND |  | MIDWIND_UNIT1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-08-15 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2017-12-29 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
NOTREES WIND 1 |  | NWF_NWF1 | WT | WIND-O | OPER | CONV | WINKLER | WEST | 2009-04-01 | 92.61 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND 2 |  | NWF_NWF2 | WT | WIND-O | OPER | CONV | WINKLER | WEST | 2009-04-01 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND |  | OWF_OWF | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-11-01 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
OLD SETTLER WIND |  | COTPLNS_OLDSETLR | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2017-01-12 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
OVEJA WIND U1 |  | OVEJA_G1 | WT | WIND-O | OPER | CONV | IRION | WEST | 2021-10-20 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
OVEJA WIND U2 |  | OVEJA_G2 | WT | WIND-O | OPER | CONV | IRION | WEST | 2021-10-20 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2020-11-12 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-07-30 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-07-30 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-11 | 94.19 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-11 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-07-18 | 149.16 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2019-12-20 | 123.25 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2022-01-05 | 106.92 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9
PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2022-01-05 | 108.54 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
PAPALOTE CREEK WIND |  | PAP1_PAP1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2009-09-04 | 179.85 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
PAPALOTE CREEK WIND II |  | COTTON_PAP2 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2010-06-01 | 200.12 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-07-31 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7
PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-07-31 | 86 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8
PENASCAL WIND 1 |  | PENA_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2009-04-22 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND 2 |  | PENA_UNIT2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2009-04-22 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND 3 |  | PENA3_UNIT3 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2011-08-02 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
PEYTON CREEK WIND |  | PEY_UNIT1 | WT | WIND-C | OPER | CONV | MATAGORDA | COASTAL | 2020-06-04 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
PYRON WIND 1 |  | PYR_PYRON1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-23 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2
PYRON WIND 2 |  | PYR_PYRON2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-23 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7 | 137.7
RANCHERO WIND U1 |  | RANCHERO_UNIT1 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2020-05-04 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RANCHERO WIND U2 |  | RANCHERO_UNIT2 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2020-05-04 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2015-09-21 | 109.15 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2015-09-21 | 109.15 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
RED CANYON WIND |  | RDCANYON_RDCNY1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2006-04-15 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6
RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1
RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | WT | WIND-O | OPER | CONV | VAL VERDE | WEST | 2017-10-26 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | WT | WIND-O | OPER | CONV | VAL VERDE | WEST | 2017-10-26 | 27.44 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
ROSCOE WIND |  | TKWSW1_ROSCOE | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-02-20 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-02-20 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ROUTE 66 WIND |  | ROUTE_66_WIND1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2015-08-11 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2021-05-14 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2021-05-14 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
RTS WIND |  | RTS_U1 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2018-09-07 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2022-05-04 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2022-05-04 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | WT | WIND-P | OPER | CONV | DONLEY | PANHANDLE | 2017-06-13 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | WT | WIND-P | OPER | CONV | DONLEY | PANHANDLE | 2017-06-13 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
SAN ROMAN WIND |  | SANROMAN_WIND_1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2016-08-25 | 95.25 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2022-12-15 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2022-12-15 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1
SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2022-12-15 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SENATE WIND |  | SENATEWD_UNIT1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2012-12-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | WT | WIND-O | OPER | CONV | JIM HOGG | SOUTH | 2015-12-22 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2019-08-07 | 30.24 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2021-06-08 | 226.05 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1
SHANNON WIND |  | SHANNONW_UNIT_1 | WT | WIND-O | OPER | CONV | CLAY | WEST | 2015-12-23 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
SHEEP CREEK WIND |  | SHEEPCRK_UNIT1 | WT | WIND-O | OPER | CONV | EASTLAND | NORTH | 2024-10-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 WIND |  | KEO_SHRBINO2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2011-12-21 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
SILVER STAR WIND |  | FLTCK_SSI | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2008-09-26 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-11-13 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-11-13 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2016-06-08 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2016-06-08 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
SOUTH TRENT WIND |  | STWF_T1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-10-29 | 101.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2014-06-19 | 160.95 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2015-10-13 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2015-10-13 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
STANTON WIND ENERGY |  | SWEC_G1 | WT | WIND-O | OPER | CONV | MARTIN | WEST | 2008-01-28 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
STELLA WIND |  | STELLA_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2018-12-19 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2014-12-29 | 213.82 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2015-05-21 | 166.52 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
SWEETWATER WIND 1 |  | SWEETWND_WND1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2003-11-20 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
SWEETWATER WIND 2A |  | SWEETWN2_WND24 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2006-03-21 | 16 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
SWEETWATER WIND 2B |  | SWEETWN2_WND2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2004-11-22 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8
SWEETWATER WIND 3A |  | SWEETWN3_WND3A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2011-08-02 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
SWEETWATER WIND 3B |  | SWEETWN3_WND3B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2011-08-02 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-03-21 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-03-21 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-11-01 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2019-03-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2019-03-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | WT | WIND-O | OPER | CONV | HOWARD | WEST | 1999-05-27 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
TG EAST WIND U1 |  | TRUSGILL_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
TG EAST WIND U2 |  | TRUSGILL_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8
TG EAST WIND U3 |  | TRUSGILL_UNIT3 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
TG EAST WIND U4 |  | TRUSGILL_UNIT4 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
TRENT WIND 1 A |  | TRENT_TRENT | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2001-07-09 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
TRENT WIND 1 B |  | TRENT_UNIT_1B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 15.59 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
TRENT WIND 2 |  | TRENT_UNIT_2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 50.49 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
TRENT WIND 3 A |  | TRENT_UNIT_3A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
TRENT WIND 3 B |  | TRENT_UNIT_3B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 13.79 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8
TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2012-02-03 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2012-02-03 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | WT | WIND-O | OPER | CONV-SODG | NOLAN | WEST | 2008-01-01 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
TURKEY TRACK WIND |  | TTWEC_G1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-11-06 | 174.6 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | WT | WIND-O | OPER | CONV | COOKE | NORTH | 2016-10-18 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
VENADO WIND U1 |  | VENADO_UNIT1 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2021-12-06 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
VENADO WIND U2 |  | VENADO_UNIT2 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2021-12-06 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
VERA WIND 1 |  | VERAWIND_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
VERA WIND 2 |  | VERAWIND_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
VERA WIND 3 |  | VERAWIND_UNIT3 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
VERA WIND 4 |  | VERAWIND_UNIT4 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
VERA WIND 5 |  | VERAWIND_UNIT5 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2015-01-26 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
VORTEX WIND U1 |  | VORTEX_WIND1 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
VORTEX WIND U2 |  | VORTEX_WIND2 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
VORTEX WIND U3 |  | VORTEX_WIND3 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4
VORTEX WIND U4 |  | VORTEX_WIND4 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2022-04-13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
WAKE WIND 1 |  | WAKEWE_G1 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2016-10-28 | 114.91 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
WAKE WIND 2 |  | WAKEWE_G2 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2016-10-28 | 142.35 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-10-26 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6
WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-10-26 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2
WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2022-01-26 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6
WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2022-01-26 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
WHIRLWIND ENERGY |  | WEC_WECG1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2007-11-09 | 59.8 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
WHITETAIL WIND |  | EXGNWTL_WIND_1 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2012-12-20 | 92.34 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
WHITE MESA WIND U1 |  | WHMESA_UNIT1 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-01 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 13.92 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3
WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 18.56 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 132.54 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-12-29 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-12-29 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | WT | WIND-O | OPER | CONV | SCHLEICHER | WEST | 2020-04-17 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2014-12-11 | 67.62 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
WKN MOZART WIND |  | MOZART_WIND_1 | WT | WIND-O | OPER | CONV | KENT | WEST | 2012-12-20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLF RIDGE WIND |  | WHTTAIL_WR1 | WT | WIND-O | OPER | CONV | COOKE | NORTH | 2008-10-02 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2024-11-15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2025-12-31 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2025-12-31 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | WT | WIND-O | OPER-SYN | CONV | NAVARRO | NORTH | 2024-12-30 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8
BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | WT | WIND-O | OPER-SYN | CONV | NAVARRO | NORTH | 2024-12-30 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4
CANYON WIND U1 | 18INR0030 | CANYONWD_UNIT1 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 146.64 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
CANYON WIND U2 | 18INR0030 | CANYONWD_UNIT2 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 2.52 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
CANYON WIND U3 | 18INR0030 | CANYONWD_UNIT3 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 59.22 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2
CANYON WIND U4 | 18INR0030 | CANYONWD_UNIT4 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 20.16 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8
CANYON WIND U5 | 18INR0030 | CANYONWD_UNIT5 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 67.68 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
CANYON WIND U6 | 18INR0030 | CANYONWD_UNIT6 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-12-15 | 12.6 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4
COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-07-01 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-07-01 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6
COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2024-07-01 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
CRAWFISH U1 | 19INR0177 | CRAWFISH_UNIT1 | WT | WIND-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-03 | 163.2 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WT | WIND-C | OPER-SYN | CONV | WILLACY | COASTAL | 2025-01-14 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WT | WIND-C | OPER-SYN | CONV | WILLACY | COASTAL | 2025-01-14 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2024-11-04 | 130.2 | 111.9 | 111.9 | 111.9 | 111.9 | 111.9 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2
FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2024-11-04 | 84 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 84 | 84 | 84 | 84 | 84
FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2024-11-04 | 54 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54
HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | WT | WIND-O | OPER-SYN | CONV | GLASSCOCK | WEST | 2024-11-30 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | WT | WIND-O | OPER-SYN | CONV | NOLAN | WEST | 2024-12-31 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | WT | WIND-O | OPER-SYN | CONV | STARR | SOUTH | 2024-12-31 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MONTGOMERY RANCH WIND U1 | 20INR0040 | MONT_WND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | FOARD | WEST | 2024-12-31 | 106.13 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9
MONTGOMERY RANCH WIND U2 | 20INR0040 | MONT_WND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | FOARD | WEST | 2024-12-31 | 92.87 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7
PIONEER DJ WIND U1 | 23INR0387 | PIONR_DJ_UNIT1 | WT | WIND-O | OPER-SYN | CONV | MIDLAND | WEST | 2024-09-15 | 124.08 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1
PIONEER DJ WIND U2 | 23INR0387 | PIONR_DJ_UNIT2 | WT | WIND-O | OPER-SYN | CONV | MIDLAND | WEST | 2024-09-15 | 16.24 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2
PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2024-12-31 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2024-12-31 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | WT | WIND-O | OPER-SYN | CONV | MILLS | NORTH | 2024-06-28 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2
PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | WT | WIND-O | OPER-SYN | CONV | MILLS | NORTH | 2024-06-28 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
ROADRUNNER CROSSING WIND II | 21INR0515 | RRC_WIND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | EASTLAND | NORTH | 2024-11-21 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
ROADRUNNER CROSSING WIND U2 | 21INR0515 | RRC_WIND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | EASTLAND | NORTH | 2024-11-21 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
ROADRUNNER CROSSING WIND 1 | 19INR0117 | RRC_WIND_UNIT3 | WT | WIND-O | OPER-SYN | CONV | EASTLAND | NORTH | 2024-11-21 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
SHAMROCK WIND U1 | 22INR0502 | SHAMROCK_UNIT1 | WT | WIND-O | OPER-SYN | CONV | CROCKETT | WEST | 2024-12-20 | 203.1 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
SHAMROCK WIND U2 | 22INR0502 | SHAMROCK_UNIT2 | WT | WIND-O | OPER-SYN | CONV | CROCKETT | WEST | 2024-12-20 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9
WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | FISHER | WEST | 2024-10-31 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4
WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | FISHER | WEST | 2024-10-31 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5
WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2024-11-30 | 18.38 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4
WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2024-11-30 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2024-11-30 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2024-11-30 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2024-11-30 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
YOUNG WIND U1 | 21INR0401 | YNG_WND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | YOUNG | WEST | 2024-11-30 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4
YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | YOUNG | WEST | 2024-11-30 | 152.28 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | WT | WIND-O | OPER-SYN | CONV | YOUNG | WEST | 2024-11-30 | 149.46 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
ACACIA SOLAR |  | ACACIA_UNIT_1 | PV | SOLAR-FW | OPER | CONV | PRESIDIO | WEST | 2012-12-30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
AIRPORT ROAD LONEWOLFE PHASE ONE |  | AIRPRTRD_LONEWOLFE | PV | SOLAR-W | OPER | CONV | MITCHELL | WEST | 2023-06-26 | 1 | bar: Summer Capabilities, MW (As of the Season Start Date, June 1) 2025 to Winter Capabilities, MW (As of the Season Start Date, December 1) 2029/30
ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | PV | SOLAR-O | OPER | CONV-SODG | BROOKS | SOUTH | 2019-11-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ANDROMEDA SOLAR U1 |  | ANDMDSLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-03 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
ANDROMEDA SOLAR U2 |  | ANDMDSLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-03 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
ANSON SOLAR U1 |  | ANSON1_UNIT1 | PV | SOLAR-W | OPER | CONV | JONES | WEST | 2022-01-20 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ANSON SOLAR U2 |  | ANSON1_UNIT2 | PV | SOLAR-W | OPER | CONV | JONES | WEST | 2022-01-20 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ARAGORN SOLAR |  | ARAGORN_UNIT1 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-12-22 | 188.2 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
AUREOLA SOLAR U1 |  | AURO_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2024-08-12 | 201.66 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4
AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2021-11-15 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9
AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2021-11-15 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5
BECK 1 |  | DG_CECSOLAR_DG_BECK1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2016-08-09 | 1 | bar: Summer Capabilities, MW (As of the Season Start Date, June 1) 2025 to Winter Capabilities, MW (As of the Season Start Date, December 1) 2029/30
BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2017-09-28 | 50 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
BKVSOLAR_BKVSOLAR1 |  | BKVSOLAR_BKVSOLAR1 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2024-10-02 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2010-08-17 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2010-09-15 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | PV | SOLAR-W | OPER | CONV-SODG | STERLING | WEST | 2019-11-07 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | PV | SOLAR-W | OPER | CONV-SODG | STERLING | WEST | 2021-04-28 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | PV | SOLAR-W | OPER | CONV-SODG | STERLING | WEST | 2021-04-28 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | PV | SOLAR-W | OPER | CONV | DAWSON | WEST | 2018-02-18 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | PV | SOLAR-W | OPER | CONV | DAWSON | WEST | 2018-12-19 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2018-12-26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2018-12-26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BPL FILES SOLAR |  | FILESSLR_PV1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2023-08-29 | 146.09 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2023-08-19 | 53.4 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRONSON SOLAR I |  | DG_BRNSN_BRNSN | PV | SOLAR-O | OPER | CONV-SODG | FORT BEND | HOUSTON | 2018-12-27 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | PV | SOLAR-O | OPER | CONV-SODG | FORT BEND | HOUSTON | 2018-12-27 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASCADE SOLAR I |  | DG_CASCADE_CASCADE | PV | SOLAR-O | OPER | CONV-SODG | WHARTON | SOUTH | 2018-12-14 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | PV | SOLAR-O | OPER | CONV-SODG | WHARTON | SOUTH | 2018-12-14 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2018-05-31 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
CATAN SOLAR |  | DG_CS10_CATAN | PV | SOLAR-O | OPER | CONV-SODG | KARNES | SOUTH | 2020-10-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
CHISUM SOLAR |  | DG_CHISUM_CHISUM | PV | SOLAR-O | OPER | CONV-SODG | LAMAR | NORTH | 2018-11-12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2019-05-01 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | PV | SOLAR-O | OPER | CONV | FANNIN | NORTH | 2021-08-09 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7
CORAL SOLAR U1 |  | CORALSLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-09-24 | 97.7 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2
CORAL SOLAR U2 |  | CORALSLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-09-24 | 56.3 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | PV | SOLAR-O | OPER | CONV | WEBB | SOUTH | 2021-10-11 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
CROWN SOLAR |  | CRWN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-01-05 | 101.3 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1
DANCIGER SOLAR U1 |  | DAG_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2023-01-18 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DANCIGER SOLAR U2 |  | DAG_UNIT2 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2023-01-18 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DILEO SOLAR |  | DILEOSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BOSQUE | NORTH | 2023-11-14 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | PV | SOLAR-O | OPER | CONV | TRAVIS | SOUTH | 2021-08-12 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
EDDY SOLAR II |  | DG_EDDYII_EDDYII | PV | SOLAR-O | OPER | CONV-SODG | MCLENNAN | NORTH | 2018-12-13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
EIFFEL SOLAR |  | EIFSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | LAMAR | NORTH | 2023-11-30 | 241 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
ELARA SOLAR |  | ELARA_SL_UNIT1 | PV | SOLAR-O | OPER | CONV | FRIO | SOUTH | 2022-03-17 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4
ELLIS SOLAR |  | ELLISSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | ELLIS | NORTH | 2023-10-24 | 81.3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | PV | SOLAR-FW | OPER | CONV | CRANE | WEST | 2023-03-10 | 109.5 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
EUNICE SOLAR U1 |  | EUNICE_PV1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-24 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6
EUNICE SOLAR U2 |  | EUNICE_PV2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-24 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1
FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | PV | SOLAR-O | OPER | CONV-SODG | TRAVIS | SOUTH | 2016-05-31 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
FOWLER RANCH |  | FWLR_SLR_UNIT1 | PV | SOLAR-FW | OPER | CONV | CRANE | WEST | 2020-08-28 | 152.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
FRFWS_FAIRFIELD |  | FRFWS_FAIRFIELD | PV | SOLAR-O | OPER | CONV | FREESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
FRYE SOLAR U1 |  | FRYE_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2024-07-03 | 250.9 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
FRYE SOLAR U2 |  | FRYE_SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2024-07-03 | 251.1 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2015-01-05 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2017-01-25 | 126 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | PV | SOLAR-W | OPER | CONV | CONCHO | WEST | 2021-10-27 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
GALLOWAY 2 SOLAR |  | GALLOWAY_SOLAR2 | PV | SOLAR-W | OPER | CONV | CONCHO | WEST | 2024-01-04 | 111.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
GOLINDA SOLAR |  | GOLINDA_UNIT1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-02-27 | 101.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1
GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-02-09 | 126.3 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6
GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-02-09 | 132.2 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4
GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | PV | SOLAR-O | OPER | CONV-SODG | MCLENNAN | NORTH | 2019-07-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
GRIZZLY RIDGE SOLAR |  | GRIZZLY_SOLAR1 | PV | SOLAR-O | OPER | CONV | HAMILTON | NORTH | 2023-10-20 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HALO SOLAR |  | HALO_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BELL | NORTH | 2024-08-12 | 251.15 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4
HIGHWAY 56 |  | DG_HWY56_HWY56 | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-11-20 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2015-12-31 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HOLLYWOOD SOLAR U1 |  | HOL_UNIT1 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2024-09-06 | 176.14 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3
HOLLYWOOD SOLAR U2 |  | HOL_UNIT2 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2024-09-06 | 178.95 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1
HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | PV | SOLAR-W | OPER | CONV | NOLAN | WEST | 2020-05-28 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | PV | SOLAR-W | OPER | CONV | NOLAN | WEST | 2020-05-28 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3
HOPKINS SOLAR U1 |  | HOPKNSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2024-05-02 | 175.35 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8
HOPKINS SOLAR U2 |  | HOPKNSLR_UNIT2 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2024-05-02 | 76.17 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8
HORIZON SOLAR |  | HRZN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FRIO | SOUTH | 2024-03-05 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HPWHSOL_WILDHORSESOLAR |  | HPWHSOL_WILDHORSESOLAR | PV | SOLAR-W | OPER | CONV | HOWARD | WEST | 2024-06-01 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
IMPACT SOLAR |  | IMPACT_UNIT1 | PV | SOLAR-O | OPER | CONV | LAMAR | NORTH | 2021-08-20 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5
JADE SOLAR U1 |  | JADE_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-02 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
JADE SOLAR U2 |  | JADE_SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-02 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
JUNO SOLAR PHASE I |  | JUNO_UNIT1 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-05-26 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
JUNO SOLAR PHASE II |  | JUNO_UNIT2 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-08-09 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5
KELLAM SOLAR |  | KELAM_SL_UNIT1 | PV | SOLAR-O | OPER | CONV | VAN ZANDT | NORTH | 2020-12-24 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | PV | SOLAR-W | OPER | CONV-SODG | MENARD | WEST | 2019-09-12 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
LAPETUS SOLAR |  | LAPETUS_UNIT_1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-24 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
LEON |  | DG_LEON_LEON | PV | SOLAR-O | OPER | CONV-SODG | HUNT | NORTH | 2017-12-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LILY SOLAR |  | LILY_SOLAR1 | PV | SOLAR-O | OPER | CONV | KAUFMAN | NORTH | 2021-10-08 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6
LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-12-14 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-12-14 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
LONGBOW SOLAR |  | LON_SOLAR1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2024-04-17 | 78.2 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
LSSEALY_LOCALSUNSEALY |  | LSSEALY_LOCALSUNSEALY | PV | SOLAR-O | OPER | CONV | AUSTIN | SOUTH | 2023-12-01 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
MALAKOFF |  | MALAKOFF | PV | SOLAR-O | OPER | CONV | HENDERSON | NORTH | 2024-10-16 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MANDORLA SOLAR |  | MAND_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2024-09-19 | 251.45 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5
MARLIN |  | DG_MARLIN_MARLIN | PV | SOLAR-O | OPER | CONV-SODG | FALLS | NORTH | 2017-11-27 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
MARS SOLAR (DG) |  | DG_MARS_MARS | PV | SOLAR-O | OPER | CONV-SODG | WEBB | SOUTH | 2019-03-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MCLEAN (SHAKES) SOLAR |  | MCLNSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | DIMMIT | SOUTH | 2023-09-01 | 207.4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MEXIA_MEXIA |  | MEXIA_MEXIA | PV | SOLAR-O | OPER | CONV | LIMESTONE | NORTH | 2024-08-01 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MEXIA1_MEXIA1 |  | MEXIA1_MEXIA1 | PV | SOLAR-O | OPER | CONV | LIMESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MEXIA2_MEXIA2 |  | MEXIA2_MEXIA2 | PV | SOLAR-O | OPER | CONV | LIMESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MISAE SOLAR U1 |  | MISAE_UNIT1 | PV | SOLAR-W | OPER | CONV | CHILDRESS | PANHANDLE | 2021-12-20 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4
MISAE SOLAR U2 |  | MISAE_UNIT2 | PV | SOLAR-W | OPER | CONV | CHILDRESS | PANHANDLE | 2021-12-20 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
MLKF1_MALAKOFF1 |  | MLKF1_MALAKOFF1 | PV | SOLAR-O | OPER | CONV | HENDERSON | NORTH | 2024-10-23 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MLKF2_MALAKOFF2 |  | MLKF2_MALAKOFF2 | PV | SOLAR-O | OPER | CONV | HENDERSON | NORTH | 2024-10-23 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MUSTANG CREEK SOLAR U1 |  | MUSTNGCK_SOLAR1 | PV | SOLAR-O | OPER | CONV | JACKSON | SOUTH | 2023-10-09 | 61 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
MUSTANG CREEK SOLAR U2 |  | MUSTNGCK_SOLAR2 | PV | SOLAR-O | OPER | CONV | JACKSON | SOUTH | 2023-10-09 | 91.25 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | PV | SOLAR-O | OPER | CONV | CAMERON | COASTAL | 2022-10-25 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5
NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2022-09-19 | 148.8 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7
NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2022-09-19 | 130.2 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | PV | SOLAR-O | OPER | CONV-SODG | COOKE | NORTH | 2017-12-15 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
OBERON SOLAR |  | OBERON_UNIT_1 | PV | SOLAR-FW | OPER | CONV | ECTOR | WEST | 2020-07-13 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | PV | SOLAR-O | OPER | CONV | BEXAR | SOUTH | 2013-12-13 | 39.18 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2014-01-20 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2014-10-01 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | PV | SOLAR-O | OPER | CONV | KINNEY | SOUTH | 2014-08-28 | 37.62 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | PV | SOLAR-O | OPER | CONV | UVALDE | SOUTH | 2015-12-22 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-06 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2016-07-29 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
PEGASUS_PEGASUS |  | PEGASUS_PEGASUS | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2024-07-17 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | PV | SOLAR-FW | OPER | CONV | WINKLER | WEST | 2019-11-26 | 125.04 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1
PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | PV | SOLAR-FW | OPER | CONV | WINKLER | WEST | 2019-11-26 | 127.95 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1
PHOENIX SOLAR |  | PHOENIX_UNIT1 | PV | SOLAR-O | OPER | CONV | FANNIN | NORTH | 2021-09-01 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9
PISGAH RIDGE SOLAR U1 |  | PISGAH_SOLAR1 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2024-04-17 | 189.4 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
PISGAH RIDGE SOLAR U2 |  | PISGAH_SOLAR2 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2024-04-17 | 64.4 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
PITTS DUDIK SOLAR U1 |  | PITTSDDK_UNIT1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2023-11-03 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6
POWERFIN KINGSBERY |  | DG_PFK_PFKPV | PV | SOLAR-O | OPER | CONV-SODG | TRAVIS | SOUTH | 2017-12-01 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-30 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-30 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-23 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-23 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
QUEEN SOLAR U1 |  | QUEEN_SL_SOLAR1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-05-04 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
QUEEN SOLAR U2 |  | QUEEN_SL_SOLAR2 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-05-04 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
QUEEN SOLAR U3 |  | QUEEN_SL_SOLAR3 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-08-28 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
QUEEN SOLAR U4 |  | QUEEN_SL_SOLAR4 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-08-28 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
RADIAN SOLAR U1 |  | RADN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BROWN | NORTH | 2023-05-16 | 161.41 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9
RADIAN SOLAR U2 |  | RADN_SLR_UNIT2 | PV | SOLAR-O | OPER | CONV | BROWN | NORTH | 2023-05-16 | 166.02 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
RAMBLER SOLAR |  | RAMBLER_UNIT1 | PV | SOLAR-W | OPER | CONV | TOM GREEN | WEST | 2020-10-01 | 211.19 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
RATLIFF SOLAR (CONCHO VALLEY SOLAR) |  | RATLIFF_SOLAR1 | PV | SOLAR-W | OPER | CONV | TOM GREEN | WEST | 2023-05-25 | 162.43 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8
RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-13 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-13 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-10-11 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222
REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-10-11 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | PV | SOLAR-O | OPER | CONV-SODG | DENTON | NORTH | 2015-05-20 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2018-06-15 | 155.44 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RIPPEY SOLAR |  | RIPPEY_UNIT1 | PV | SOLAR-O | OPER | CONV | COOKE | NORTH | 2020-12-30 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
ROWLAND SOLAR I |  | ROW_UNIT1 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-07-10 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ROWLAND SOLAR II |  | ROW_UNIT2 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2024-06-28 | 200.7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | PV | SOLAR-FW | OPER | CONV | BREWSTER | WEST | 2018-03-30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SPARTA SOLAR U1 |  | SPARTA_UNIT1 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2023-10-16 | 147.5 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
SPARTA SOLAR U2 |  | SPARTA_UNIT2 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2023-10-16 | 104.9 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2017-08-25 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
STERLING |  | DG_STRLING_STRLING | PV | SOLAR-O | OPER | CONV-SODG | HUNT | NORTH | 2018-12-13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | PV | SOLAR-O | OPER | CONV | ELLIS | NORTH | 2022-12-29 | 135 | 135 | 135 | 135 | 135 | 135 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3
SUN VALLEY U1 |  | SUNVASLR_UNIT1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2024-04-19 | 165.75 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
SUN VALLEY U2 |  | SUNVASLR_UNIT2 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2024-04-19 | 86.19 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2
SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-04-01 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-02-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-04-01 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-02-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNRAY |  | SUN_SLR_UNIT_1 | PV | SOLAR-O | OPER | CONV | UVALDE | SOUTH | 2024-08-20 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
TALCOWST_TALCO |  | TALCOWST_TALCO | PV | SOLAR-O | OPER | CONV | TITUS | NORTH | 2024-08-01 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
TAVENER U1 (FORT BEND SOLAR) |  | TAV_UNIT1 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-10-06 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
TAVENER U2 (FORT BEND SOLAR) |  | TAV_UNIT2 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-10-06 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-06-14 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-06-14 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
TAYGETE SOLAR 2 U1 |  | TAYGETE2_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2023-07-17 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
TAYGETE SOLAR 2 U2 |  | TAYGETE2_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2023-07-17 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
TEXAS SOLAR NOVA U1 |  | NOVA1SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | KENT | WEST | 2024-04-30 | 126.81 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
TEXAS SOLAR NOVA U2 |  | NOVA1SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | KENT | WEST | 2024-04-30 | 126.7 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-11-22 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8
TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-11-22 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | PV | SOLAR-O | OPER | CONV-SODG | ERATH | NORTH | 2021-12-24 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
TRN_TRINITYBAY |  | TRN_TRINITYBAY | PV | SOLAR-O | OPER | CONV | CHAMBERS | HOUSTON | 2024-01-10 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
VANCOURT SOLAR |  | VANCOURT_UNIT1 | PV | SOLAR-O | OPER | CONV | CAMERON | COASTAL | 2023-01-25 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7
VISION SOLAR 1 |  | VISION_UNIT1 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2022-12-29 | 129.2 | 127 | 127 | 127 | 127 | 127 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7
WAGYU SOLAR |  | WGU_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2021-10-04 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BOSQUE | NORTH | 2016-07-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WAYMARK SOLAR |  | WAYMARK_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2018-12-20 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | PV | SOLAR-O | OPER | CONV | TRAVIS | SOUTH | 2011-11-23 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
WEST MOORE II |  | DG_WMOOREII_WMOOREII | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2018-10-22 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | PV | SOLAR-FW | OPER | CONV | REEVES | WEST | 2019-12-20 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WESTORIA SOLAR U1 |  | WES_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2022-11-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
WESTORIA SOLAR U2 |  | WES_UNIT2 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2022-11-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
WHITESBORO |  | DG_WBORO_WHTSBORO | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-12-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WHITESBORO II |  | DG_WBOROII_WHBOROII | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-12-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | PV | SOLAR-O | OPER | CONV-SODG | FANNIN | NORTH | 2017-12-30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | PV | SOLAR-O | OPER | CONV-SODG | BOSQUE | NORTH | 2017-11-30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WHSOLAR_WILDHORSE_SOLAR |  | WHSOLAR_WILDHORSE_SOLAR | PV | SOLAR-W | OPER | CONV | HOWARD | WEST | 2024-05-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | PV | SOLAR-O | OPER | CONV-SODG | BOSQUE | NORTH | 2018-10-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
ZIER SOLAR |  | ZIER_SLR_PV1 | PV | SOLAR-O | OPER | CONV | KINNEY | SOUTH | 2024-04-26 | 161.28 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
7V SOLAR | 21INR0351 | 7RNCHSLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FAYETTE | SOUTH | 2024-11-30 | 139.66 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2
7V SOLAR U2 | 21INR0351 | 7RNCHSLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FAYETTE | SOUTH | 2024-11-30 | 95.54 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
7V SOLAR U3 | 21INR0351 | 7RNCHSLR_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | FAYETTE | SOUTH | 2024-11-30 | 5.57 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
ANGELO SOLAR | 19INR0203 | ANG_SLR_UNIT1 | PV | SOLAR-W | OPER-SYN | CONV | TOM GREEN | WEST | 2024-10-11 | 195.41 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
BAKER BRANCH SOLAR U1 | 23INR0026 | BAKE_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2024-11-30 | 234.84 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9
BAKER BRANCH SOLAR U2 | 23INR0026 | BAKE_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2024-11-30 | 234.57 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9
BIG ELM SOLAR | 21INR0353 | BELM_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2024-12-21 | 200.99 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2
BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BASTROP | SOUTH | 2024-12-01 | 132.27 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BASTROP | SOUTH | 2024-12-01 | 70.83 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2024-11-15 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2024-11-15 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
BRIGHT ARROW SOLAR U1 | 22INR0242 | BR_ARROW_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2024-12-31 | 127.3 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
BRIGHT ARROW SOLAR U2 | 22INR0242 | BR_ARROW_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2024-12-31 | 173.9 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2024-12-15 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5
BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2024-12-15 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3
CHEVRON ALLEN SOLAR (HAYHURST TEXAS SOLAR) | 22INR0363 | CHAL_SLR_SOLAR1 | PV | SOLAR-FW | OPER-SYN | CONV | CULBERSON | WEST | 2024-07-31 | 25.22 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8
CHILLINGHAM SOLAR U1 | 23INR0070 | CHIL_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2024-11-01 | 174.3 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CHILLINGHAM SOLAR U2 | 23INR0070 | CHIL_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2024-11-01 | 178.1 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
COTTONWOOD BAYOU SOLAR I U1 | 19INR0134 | CTW_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 175.69 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
COTTONWOOD BAYOU SOLAR I U2 | 19INR0134 | CTW_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 175.71 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
DAMAZO (SECOND DIVISION) SOLAR | 20INR0248 | DMA_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-20 | 100.2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DANISH FIELDS SOLAR U1 | 20INR0069 | DAN_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-31 | 301.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
DANISH FIELDS SOLAR U2 | 20INR0069 | DAN_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-31 | 151 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2
DANISH FIELDS SOLAR U3 | 20INR0069 | DAN_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-31 | 150.5 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
DELILAH SOLAR 1 U1 | 22INR0202 | DELILA_1_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 153.54 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DELILAH SOLAR 1 U2 | 22INR0202 | DELILA_1_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 153.54 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
EASTBELL MILAM SOLAR | 21INR0203 | EBELLSLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | MILAM | SOUTH | 2024-11-30 | 244.86 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
ELIZA SOLAR | 21INR0368 | ELZA_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | KAUFMAN | NORTH | 2025-01-22 | 151.7 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
ESTONIAN SOLAR FARM U1 | 22INR0335 | ESTONIAN_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | DELTA | NORTH | 2024-10-31 | 88.4 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3
ESTONIAN SOLAR FARM U2 | 22INR0335 | ESTONIAN_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | DELTA | NORTH | 2024-10-31 | 114.4 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1
FENCE POST SOLAR U1 | 22INR0404 | FENCESLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | NAVARRO | NORTH | 2024-10-31 | 138.88 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
FENCE POST SOLAR U2 | 22INR0404 | FENCESLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | NAVARRO | NORTH | 2024-10-31 | 97.98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-03-29 | 179.5 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-03-29 | 171.8 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9
FIVE WELLS SOLAR U1 | 24INR0015 | FIVEWSLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2024-10-15 | 194.42 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4
FIVE WELLS SOLAR U2 | 24INR0015 | FIVEWSLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2024-10-15 | 126.97 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PV | SOLAR-FW | OPER-SYN | CONV | PECOS | WEST | 2024-12-31 | 7.41 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
MARKUM SOLAR | 20INR0230 | MRKM_SLR_PV1 | PV | SOLAR-O | OPER-SYN | CONV | MCLENNAN | NORTH | 2024-11-22 | 161.5 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
MERCURY SOLAR U1 | 21INR0257 | MERCURY_PV1 | PV | SOLAR-O | OPER-SYN | CONV | HILL | NORTH | 2024-12-20 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
MERCURY SOLAR U2 | 23INR0153 | MERCURY_PV2 | PV | SOLAR-O | OPER-SYN | CONV | HILL | NORTH | 2024-12-20 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
MORROW LAKE SOLAR | 19INR0155 | MROW_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | FRIO | SOUTH | 2024-10-31 | 202.2 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 171.6 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2
MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 149.6 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8
PHOTON SOLAR U1 | 25INR0493 | PHO_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-12-31 | 129.59 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1
PHOTON SOLAR U2 | 25INR0493 | PHO_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-12-31 | 106.07 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7
PHOTON SOLAR U3 | 23INR0111 | PHO_SOLAR3 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-10 | 109.99 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6
PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-03-26 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-03-26 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
PORTER SOLAR U1 | 21INR0458 | PORT_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | DENTON | NORTH | 2024-07-31 | 245.83 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2024-11-29 | 254 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2024-11-29 | 137.8 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6
ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2024-11-29 | 116.2 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4
SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 2 U1 | 21INR0490 | SAMSON_1_G3 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-01-13 | 101.52 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SAMSON SOLAR 2 U2 | 21INR0490 | SAMSON_1_G4 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-01-13 | 101.52 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SBRANCH SOLAR PROJECT | 22INR0205 | SBE_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2024-10-15 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5
STAMPEDE SOLAR U1 | 22INR0409 | STAM_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2024-10-31 | 77.75 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
STAMPEDE SOLAR U2 | 22INR0409 | STAM_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2024-10-31 | 178.55 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
STARR SOLAR RANCH U1 | 20INR0216 | STAR_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | STARR | SOUTH | 2024-12-01 | 70.45 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
STARR SOLAR RANCH U2 | 20INR0216 | STAR_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | STARR | SOUTH | 2024-12-01 | 66.28 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
TEXAS SOLAR NOVA 2 U1 | 20INR0269 | NOVA2SLR_UNIT1 | PV | SOLAR-W | OPER-SYN | CONV | KENT | WEST | 2024-09-15 | 202.37 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
TIERRA BONITA SOLAR U1 | 21INR0424 | TRBT_SLR_PV1 | PV | SOLAR-FW | OPER-SYN | CONV | PECOS | WEST | 2024-11-16 | 150 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6
TIERRA BONITA SOLAR U2 | 21INR0424 | TRBT_SLR_PV2 | PV | SOLAR-FW | OPER-SYN | CONV | PECOS | WEST | 2024-11-16 | 156.9 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3
TRES BAHIAS SOLAR | 20INR0266 | TREB_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | CALHOUN | COASTAL | 2024-12-28 | 196.29 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
TRUE NORTH SOLAR U1 | 23INR0114 | TNS_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2024-11-15 | 119.35 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8
TRUE NORTH SOLAR U2 | 23INR0114 | TNS_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2024-11-15 | 119.45 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9
TULSITA SOLAR U1 | 21INR0223 | TUL_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | GOLIAD | SOUTH | 2024-12-31 | 128.08 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
TULSITA SOLAR U2 | 21INR0223 | TUL_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | GOLIAD | SOUTH | 2024-12-31 | 128.12 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
BAT CAVE |  | BATCAVE_BES1 | BA | STORAGE | OPER | CONV | MASON | SOUTH | 2021-06-01 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
BAY CITY BESS (DGR) |  | BAY_CITY_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2023-07-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | BA | STORAGE | OPER | CONV | WILBARGER | WEST | 2017-04-30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-10-19 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-10-26 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP BRAZORIA |  | BRAZORIA_UNIT1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2020-10-08 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2022-10-19 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP DICKENS BESS U1 |  | DKNS_ESS_BES1 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-02-01 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U2 |  | DKNS_ESS_BES2 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-02-01 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U3 |  | DKNS_ESS_BES3 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-02-01 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U4 |  | DKNS_ESS_BES4 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-02-01 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2020-11-24 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP HYDRA BESS |  | HYDR_ESS_BES1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2023-12-01 | 200.8 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP LIBRA BESS |  | LBRA_ESS_BES1 | BA | STORAGE | OPER | CONV | GUADALUPE | SOUTH | 2023-11-27 | 201.02 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | BA | STORAGE | OPER | CONV-DGR | VICTORIA | SOUTH | 2021-08-11 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP LOPENO (DGR) |  | LOPENO_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-12-17 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2022-10-26 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2020-07-17 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP PALEO BESS |  | PALE_ESS_BES1 | BA | STORAGE | OPER | CONV | HALE | PANHANDLE | 2023-12-31 | 200.8 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP PAVO BESS U1 |  | PAVO_ESS_BESS1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-03-27 | 87.9 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5
BRP PAVO BESS U2 |  | PAVO_ESS_BESS2 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-03-27 | 87.9 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5
BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | BA | STORAGE | OPER | CONV-DGR | MAVERICK | SOUTH | 2021-06-25 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | BA | STORAGE | OPER | CONV-DGR | MAVERICK | SOUTH | 2021-06-25 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP RANCHTOWN (DGR) |  | K0_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BEXAR | SOUTH | 2021-07-19 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-09-14 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-06-30 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-06-30 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2022-08-01 | 50.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
CAMERON STORAGE (SABAL STORAGE) |  | CAMWIND_BESS1 | BA | STORAGE | OPER | CONV | CAMERON | COASTAL | 2023-06-30 | 16.67 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
CATARINA BESS (DGR) |  | CATARINA_BESS | BA | STORAGE | OPER | CONV-DGR | DIMMIT | SOUTH | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CHISHOLM GRID |  | CHISMGRD_BES1 | BA | STORAGE | EXT-OUT | CONV | TARRANT | NORTH | 2021-07-09 | 101.7 | 0 | 101.7 | 101.7 | 101.7 | 101.7 | 0 | 101.7 | 101.7 | 101.7 | 101.7
CISCO BESS (DGR) |  | CISC_BESS | BA | STORAGE | OPER | CONV-DGR | EASTLAND | NORTH | 2024-02-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CONTINENTAL BESS (DGR) |  | CONTINEN_BESS1 | BA | STORAGE | OPER | CONV-DGR | STARR | SOUTH | 2023-12-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
COMMERCE ST ESS (DGR) |  | X4_SWRI | BA | STORAGE | OPER | CONV-DGR | BEXAR | SOUTH | 2020-10-14 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
CORAL STORAGE U1 |  | CORALSLR_BESS1 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2023-12-15 | 48.4 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6
CORAL STORAGE U2 |  | CORALSLR_BESS2 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2023-12-15 | 52.2 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4
COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2016-06-24 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROSSETT POWER U1 |  | CROSSETT_BES1 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CROSSETT POWER U2 |  | CROSSETT_BES2 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DECORDOVA BESS U1 |  | DCSES_BES1 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
DECORDOVA BESS U2 |  | DCSES_BES2 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
DECORDOVA BESS U3 |  | DCSES_BES3 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
DECORDOVA BESS U4 |  | DCSES_BES4 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
DIBOLL BESS (DGR) |  | DIBOL_BESS | BA | STORAGE | OPER | CONV-DGR | ANGELINA | NORTH | 2023-02-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
EUNICE STORAGE |  | EUNICE_BES1 | BA | STORAGE | OPER | CONV | ANDREWS | WEST | 2020-12-31 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
FALFURRIAS BESS (DGR) |  | FALFUR_BESS | BA | STORAGE | OPER | CONV-DGR | BROOKS | SOUTH | 2024-06-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FARMERSVILLE BESS (DGR) |  | FRMRSVLW_BESS | BA | STORAGE | OPER | CONV-DGR | COLLIN | NORTH | 2024-02-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FAULKNER BESS (DGR) |  | FAULKNER_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-08-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FIVE WELLS STORAGE |  | FIVEWSLR_BESS1 | BA | STORAGE | OPER | CONV | BELL | NORTH | 2024-03-15 | 228.54 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
GARDEN CITY EAST BESS (DGR) |  | GRDNE_BESS | BA | STORAGE | OPER | CONV-DGR | GLASSCOCK | WEST | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GEORGETOWN SOUTH (RABBIT HILL ESS) (DGR) |  | GEORSO_ESS_1 | BA | STORAGE | OPER | CONV-DGR | WILLIAMSON | SOUTH | 2019-11-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GOMEZ BESS (DGR) |  | GOMZ_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2023-06-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HAMILTON BESS (DGR) U1 |  | HAMILTON_BESS | BA | STORAGE | OPER | CONV-DGR | VAL VERDE | WEST | 2023-08-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | BA | STORAGE | OPER | CONV-DGR | LA SALLE | SOUTH | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
INADALE ESS |  | INDL_ESS | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2017-12-04 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
JUDKINS BESS (DGR) |  | JDKNS_BESS | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2024-03-21 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
JUNCTION BESS (DGR) |  | JUNCTION_BESS | BA | STORAGE | OPER | CONV-DGR | KIMBLE | SOUTH | 2023-06-14 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LONESTAR BESS (DGR) |  | LONESTAR_BESS | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LUFKIN SOUTH BESS (DGR) |  | LFSTH_BESS | BA | STORAGE | OPER | CONV-DGR | ANGELINA | NORTH | 2024-03-21 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
MAINLAND BESS (DGR) |  | MAINLAND_BESS | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2024-05-24 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MINERAL WELLS EAST BESS (DGR) |  | MNWLE_BESS | BA | STORAGE | OPER | CONV-DGR | PALO PINTO | NORTH | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2018-07-23 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2022-08-01 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2022-08-01 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
NORTH ALAMO BESS (DGR) |  | N_ALAMO_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-07-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2021-07-01 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
NORTH FORK |  | NF_BRP_BES1 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2021-05-15 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
NORTH MERCEDES BESS (DGR) |  | N_MERCED_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NOTREES BATTERY FACILITY |  | NWF_NBS | BA | STORAGE | OPER | CONV | WINKLER | WEST | 2012-10-01 | 36 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
OLNEY BESS (DGR) |  | OLNEYTN_BESS | BA | STORAGE | OPER | CONV-DGR | YOUNG | WEST | 2023-06-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PAULINE BESS (DGR) |  | PAULN_BESS | BA | STORAGE | OPER | CONV-DGR | HENDERSON | NORTH | 2024-02-22 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
PAVLOV BESS (DGR) |  | PAVLOV_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2024-05-24 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PORT LAVACA BATTERY (DGR) |  | PRTLAVS_BESS1 | BA | STORAGE | OPER | CONV-DGR | CALHOUN | COASTAL | 2019-12-03 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PYRON BESS 2A |  | PYR_ESS2A | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2022-12-01 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
PYRON BESS 2B |  | PYR_ESS2B | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2022-12-01 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
PYRON ESS |  | PYR_ESS | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2017-12-08 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
REGIS MOORE FIELD BESS |  | MOORE_FL_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2024-05-24 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | BA | STORAGE | OPER | CONV | ROBERTSON | NORTH | 2021-10-29 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIVER BEND (BRAZOS BEND BESS) |  | RBN_BESS1 | BA | STORAGE | OPER | CONV | FORT BEND | HOUSTON | 2024-05-31 | 101.64 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-08-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SCREWBEAN BESS (DGR) |  | SBEAN_BESS | BA | STORAGE | OPER | CONV-DGR | CULBERSON | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SHEEP CREEK STORAGE |  | SHEEPCRK_BESS1 | BA | STORAGE | OPER | CONV | EASTLAND | NORTH | 2024-07-01 | 142.1 | 135.13 | 135.13 | 135.13 | 135.13 | 135.13 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1
SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2021-06-15 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2021-06-15 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SMT ELSA (DGR) |  | ELSA_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT GARCENO BESS (DGR) |  | GARCENO_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT LOS FRESNOS (DGR) |  | L_FRESNO_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT MAYBERRY BESS (DGR) |  | MAYBERRY_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT RIO GRANDE CITY BESS (DGR) |  | RIO_GRAN_BESS | BA | STORAGE | OPER | CONV-DGR | STARR | SOUTH | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT SANTA ROSA (DGR) |  | S_SNROSA_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SP TX-12B BESS |  | SPTX12B_BES1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2021-11-22 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1
SUN VALLEY BESS U1 |  | SUNVASLR_BESS1 | BA | STORAGE | OPER | CONV | HILL | NORTH | 2023-09-10 | 54.08 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3
SUN VALLEY BESS U2 |  | SUNVASLR_BESS2 | BA | STORAGE | OPER | CONV | HILL | NORTH | 2023-09-10 | 47.32 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7
TOYAH POWER STATION (DGR) |  | TOYAH_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2021-07-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
VAL VERDE BESS (DGR) |  | MV_VALV4_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-07-13 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WEST COLUMBIA (PROSPECT STORAGE) (DGR) |  | WCOLLOCL_BSS_U1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2019-12-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WEST HARLINGEN BESS (DGR) |  | W_HARLIN_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WEIL TRACT BESS |  | WEIL_TRC_BESS | BA | STORAGE | OPER | CONV-DGR | NUECES | COASTAL | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WOLF TANK STORAGE |  | WFTANK_ESS1 | BA | STORAGE | OPER | CONV | WEBB | SOUTH | 2023-03-15 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
AL PASTOR BESS | 24INR0273 | ALP_BESS_BESS1 | BA | STORAGE | OPER-SYN | CONV | DAWSON | WEST | 2024-11-06 | 103.1 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3
ANGELO STORAGE | 23INR0418 | ANG_SLR_BESS1 | BA | STORAGE | OPER-SYN | CONV | TOM GREEN | WEST | 2024-11-15 | 102.97 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BRP TORTOLAS BESS | 23INR0072 | TORT_ESS_BESS1 | BA | STORAGE | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-10-29 | 50.3 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
FARMERSVILLE WEST BESS 2 | 23INR0618 | FRMRSVL1_BES2 | BA | STORAGE | OPER-SYN | CONV-DGR | COLLIN | NORTH | 2024-11-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GREAT KISKADEE STORAGE | 23INR0166 | GKS_BESS_BESS1 | BA | STORAGE | OPER-SYN | CONV | HIDALGO | SOUTH | 2024-11-15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
GREGORY BESS | 23INR0539 | GREGORY_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | SAN PATRICIO | COASTAL | 2024-11-11 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HOLY ESS U1 | 24INR0147 | HLY_BESS1 | BA | STORAGE | OPER-SYN | CONV | HARRIS | HOUSTON | 2024-10-26 | 104.66 | 102.23 | 102.23 | 102.23 | 102.23 | 102.23 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
HOLY ESS U2 | 24INR0147 | HLY_BESS2 | BA | STORAGE | OPER-SYN | CONV | HARRIS | HOUSTON | 2024-10-26 | 104.66 | 102.23 | 102.23 | 102.23 | 102.23 | 102.23 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
JUNCTION NORTH BESS | 23INR0619 | JUNORTH1_BES1 | BA | STORAGE | OPER-SYN | CONV-DGR | KIMBLE | SOUTH | 2024-11-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LIGGETT SWITCH BESS | 24INR0660 | LIGSW_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | DALLAS | NORTH | 2024-12-16 | 9.9 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MIDWAY BESS U1 | 23INR0688 | MIDWY_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | ECTOR | WEST | 2025-03-07 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
REGIS PALACIOS BESS | 22INR0602 | PALACIOS_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | MATAGORDA | COASTAL | 2024-11-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
RUSSEK STREET BESS (DGR) | 24INR0614 | RUSSEKST_BESS | BA | STORAGE | OPER-SYN | CONV-DGR | REAGAN | WEST | 2024-11-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ANTLIA BESS | 22INR0349 |  | BA | STORAGE | PLAN | CONV | VAL VERDE | WEST | 2025-03-31 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4
ARROYO STORAGE | 24INR0306 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2025-08-09 | 183.8 | 0 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8
AVILA BESS | 23INR0287 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2025-05-01 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3 | 164.3
BERKMAN STORAGE | 24INR0395 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2027-04-30 | 150.9 | 0 | 0 | 150.9 | 150.9 | 150.9 | 0 | 0 | 150.9 | 150.9 | 150.9
BEXAR ESS | 23INR0381 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2025-06-23 | 102.6 | 0 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
BURKSOL BESS (DONEGAL BESS) | 23INR0103 |  | BA | STORAGE | PLAN | CONV | DICKENS | PANHANDLE | 2025-03-12 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
CACHI BESS | 22INR0388 |  | BA | STORAGE | PLAN | CONV | GUADALUPE | SOUTH | 2025-03-31 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5
CANTALOUPE STORAGE | 23INR0117 |  | BA | STORAGE | PLAN | CONV | REEVES | WEST | 2028-07-01 | 251.1 | 0 | 0 | 0 | 0 | 251.1 | 0 | 0 | 0 | 251.1 | 251.1
CANVASBACK BESS | 25INR0160 |  | BA | STORAGE | PLAN | CONV | CALHOUN | COASTAL | 2027-06-15 | 150.5 | 0 | 0 | 0 | 150.5 | 150.5 | 0 | 0 | 150.5 | 150.5 | 150.5
CARAMBOLA BESS (SMT MCALLEN II) | 24INR0436 |  | BA | STORAGE | PLAN | CONV | HIDALGO | SOUTH | 2026-05-31 | 97.4 | 0 | 97.4 | 97.4 | 97.4 | 97.4 | 0 | 97.4 | 97.4 | 97.4 | 97.4
CARINA BESS | 22INR0353 |  | BA | STORAGE | PLAN | CONV | NUECES | COASTAL | 2025-03-19 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1 | 154.1
CONEFLOWER STORAGE PROJECT | 23INR0425 |  | BA | STORAGE | PLAN | CONV | CHAMBERS | HOUSTON | 2027-02-03 | 178.9 | 0 | 0 | 178.9 | 178.9 | 178.9 | 0 | 0 | 178.9 | 178.9 | 178.9
COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-06-12 | 153 | 0 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
DAMON STORAGE | 23INR0523 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2024-12-16 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
DESNA BESS | 24INR0128 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-06-01 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5
DOGFISH BESS | 23INR0219 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2025-04-16 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2 | 78.2
EVAL STORAGE | 22INR0401 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2028-12-31 | 255 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 255
FALFUR BESS (DGR) | 24INR0593 |  | BA | STORAGE | PLAN | CONV-DGR | BROOKS | SOUTH | 2025-02-15 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
FORT MASON BESS | 23INR0500 |  | BA | STORAGE | PLAN | CONV-DGR | MASON | SOUTH | 2025-03-04 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
JARVIS BESS | 24INR0265 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2024-12-23 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4 | 308.4
LAURELES BESS (DGR) | 23INR0499 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2025-03-28 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
MAYBERRY II BESS | 23INR0807 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2024-12-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MEDINA LAKE BESS (DGR) | 24INR0499 |  | BA | STORAGE | PLAN | CONV-DGR | BANDERA | SOUTH | 2024-12-31 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
MILTON BESS (DGR) | 23INR0552 |  | BA | STORAGE | PLAN | CONV-DGR | KARNES | SOUTH | 2025-04-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MUENSTER BESS | 22INR0590 |  | BA | STORAGE | PLAN | CONV-DGR | COOKE | NORTH | 2025-03-04 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PHOTON BESS2 | 25INR0691 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2025-11-28 | 152.7 | 0 | 152.7 | 152.7 | 152.7 | 152.7 | 152.7 | 152.7 | 152.7 | 152.7 | 152.7
PINE FOREST BESS | 22INR0526 |  | BA | STORAGE | PLAN | CONV | HOPKINS | NORTH | 2025-10-29 | 200.7 | 0 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7
PINTAIL PASS BESS | 24INR0302 |  | BA | STORAGE | PLAN | CONV | SAN PATRICIO | COASTAL | 2025-08-27 | 207.3 | 0 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3
RAMSEY STORAGE | 21INR0505 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2027-12-31 | 510.4 | 0 | 0 | 0 | 510.4 | 510.4 | 0 | 0 | 0 | 510.4 | 510.4
RYAN ENERGY STORAGE | 20INR0246 |  | BA | STORAGE | PLAN | CONV | CORYELL | NORTH | 2027-03-31 | 50 | 0 | 0 | 50 | 50 | 50 | 0 | 0 | 50 | 50 | 50
SHAMROCK ENERGY STORAGE (SLF) | 24INR0568 |  | BA | STORAGE | PLAN | CONV | CROCKETT | WEST | 2025-03-31 | 99.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOHO BESS | 23INR0419 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-06-28 | 206.3 | 0 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3
SOHO II BESS | 25INR0162 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-03-02 | 206.3 | 0 | 206.3 | 206.3 | 206.3 | 206.3 | 0 | 206.3 | 206.3 | 206.3 | 206.3
SOWERS STORAGE | 22INR0552 |  | BA | STORAGE | PLAN | CONV | KAUFMAN | NORTH | 2025-12-01 | 205 | 0 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
TANZANITE STORAGE | 22INR0549 |  | BA | STORAGE | PLAN | CONV | HENDERSON | NORTH | 2025-03-20 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8 | 265.8
TORRECILLAS BESS | 23INR0529 |  | BA | STORAGE | PLAN | CONV-TGR | WEBB | SOUTH | 2025-02-07 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
TYNAN BESS | 24INR0759 |  | BA | STORAGE | PLAN | CONV-DGR | BEE | SOUTH | 2024-11-27 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
XE MURAT STORAGE | 24INR0329 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2025-03-01 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 60.1
YAUPON STORAGE SLF | 24INR0169 |  | BA | STORAGE | PLAN | CONV | MILAM | SOUTH | 2028-07-01 | 102.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ZEYA BESS | 23INR0290 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2025-06-01 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3
ANCHOR BESS U1 |  | ANCHOR_BESS1 | BA | STORAGE | OPER | CONV | CALLAHAN | WEST | 2022-02-25 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2
ANCHOR BESS U2 |  | ANCHOR_BESS2 | BA | STORAGE | OPER | CONV | CALLAHAN | WEST | 2022-02-25 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
ANEMOI ENERGY STORAGE |  | ANEM_ESS_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2024-05-14 | 200.9 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
AZURE SKY BESS |  | AZURE_BESS1 | BA | STORAGE | OPER | CONV | HASKELL | WEST | 2021-08-09 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6
BELDING TNP (TRIPLE BUTTE BATTERY) (DGR) |  | BELD_BELU1 | BA | STORAGE | OPER | CONV-DGR | PECOS | WEST | 2021-04-08 | 9.18 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
BLUE JAY BESS |  | BLUEJAY_BESS1 | BA | STORAGE | OPER | CONV | GRIMES | NORTH | 2022-11-17 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BOCO BESS |  | BOCO_ESS_ESS1 | BA | STORAGE | OPER | CONV | BORDEN | WEST | 2024-06-22 | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CALLISTO I ENERGY CENTER U1 |  | CLO_BESS1 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-09-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CALLISTO I ENERGY CENTER U2 |  | CLO_BESS2 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-09-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
EBONY ENERGY STORAGE |  | EBNY_ESS_BESS1 | BA | STORAGE | OPER | CONV | COMAL | SOUTH | 2024-04-01 | 201.2 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | BA | STORAGE | OPER | CONV | SCURRY | WEST | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
FENCE POST BESS U1 |  | FENCESLR_BESS1 | BA | STORAGE | OPER | CONV | NAVARRO | NORTH | 2023-03-03 | 72.01 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
FLAT TOP BATTERY (DGR) |  | FLAT_TOP_FLATU1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2020-05-05 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
GAMBIT BATTERY |  | GAMBIT_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2021-06-01 | 102.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
GIGA TEXAS ENERGY STORAGE |  | GIGA_ESS_BESS_1 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2023-12-15 | 125.31 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
HIGH LONESOME BESS |  | HI_LONEB_BESS1 | BA | STORAGE | OPER | CONV | CROCKETT | WEST | 2022-07-27 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
HOEFSROAD BESS (DGR) |  | HRBESS_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2020-10-07 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
HOUSE MOUNTAIN BESS |  | HOUSEMTN_BESS1 | BA | STORAGE | OPER | CONV | BREWSTER | WEST | 2023-07-29 | 61.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HUMMINGBIRD STORAGE |  | HMNG_ESS_BESS1 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2024-02-24 | 100.38 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
JOHNSON CITY BESS (DGR) |  | JOHNCI_UNIT_1 | BA | STORAGE | OPER | CONV-DGR | BLANCO | SOUTH | 2020-08-05 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2017-12-01 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
LILY STORAGE |  | LILY_BESS1 | BA | STORAGE | OPER | CONV | KAUFMAN | NORTH | 2021-06-01 | 51.7 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
LIMOUSIN OAK STORAGE |  | LMO_BESS1 | BA | STORAGE | OPER | CONV | GRIMES | NORTH | 2024-02-23 | 100.42 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MUSTANG CREEK STORAGE |  | MUSTNGCK_BES1 | BA | STORAGE | OPER | CONV | JACKSON | SOUTH | 2023-03-29 | 71.49 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
PYOTE TNP (SWOOSE BATTERY) (DGR) |  | PYOTE_SWOOSEU1 | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2021-02-05 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
QUEEN BESS |  | QUEEN_BA_BESS1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2022-05-31 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIVER VALLEY STORAGE U1 |  | RVRVLYS_ESS1 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
EAST TIE |  | DC_E | MWH | MWH | OPER | DC-TIE | FANNIN | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
NORTH TIE |  | DC_N | MWH | MWH | OPER | DC-TIE | WILBARGER | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
LAREDO VFT TIE |  | DC_L | MWH | MWH | OPER | DC-TIE | WEBB | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SHARYLAND RAILROAD TIE |  | DC_R | MWH | MWH | OPER | DC-TIE | HIDALGO | SOUTH |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
CALPINE FREESTONE PEAKER 1 (TEF) | 26INR0049 |  | GT | GAS | PLAN | CONV | FREESTONE | NORTH | 2026-05-01 | 229.5 | 0 | 214.8 | 214.8 | 214.8 | 214.8 | 0 | 228 | 228 | 228 | 228
CALPINE FREESTONE PEAKER 2 (TEF) | 26INR0109 |  | GT | GAS | PLAN | CONV | FREESTONE | NORTH | 2026-05-01 | 229.5 | 0 | 214.8 | 214.8 | 214.8 | 214.8 | 0 | 228 | 228 | 228 | 228
CEDAR BAYOU5 (TEF) | 23INR0029 |  | CC | GAS | PLAN | CONV | CHAMBERS | HOUSTON | 2027-12-15 | 721 | 0 | 0 | 0 | 674 | 674 | 0 | 0 | 0 | 697 | 697
NRG THW GT 345 (TEF) | 24INR0482 |  | GT | GAS | PLAN | CONV | HARRIS | HOUSTON | 2026-05-01 | 456 | 0 | 422 | 422 | 422 | 422 | 0 | 456 | 456 | 456 | 456
COYOTE SPRINGS AGR1 (DGR) | 24INR0645 |  | IC | DIESEL | PLAN | CONV-DGR | REEVES | WEST | 2025-01-08 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ENCHANTED ROCK NEWPP | 22INR0546 |  | IC | GAS | PLAN | CONV | HARRIS | HOUSTON | 2025-06-06 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
FRIENDSWOOD G CTG 2 | 24INR0456 |  | GT | GAS | PLAN | CONV | HARRIS | HOUSTON | 2025-07-01 | 143.7 | 0 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7
OLNEY AGR1 (DGR) | 24INR0647 |  | IC | DIESEL | PLAN | CONV-DGR | YOUNG | WEST | 2025-01-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SADDLEBACK AGR1 (DGR) | 24INR0646 |  | IC | DIESEL | PLAN | CONV-DGR | REEVES | WEST | 2025-01-08 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
UHLAND MAXWELL (TIMMERMAN POWER PLANT) | 25INR0223 |  | CC | GAS | PLAN | CONV | CALDWELL | SOUTH | 2025-06-27 | 188.4 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
AQUILLA LAKE 3 WIND | 22INR0499 |  | WT | WIND-O | PLAN | CONV | HILL | NORTH | 2027-04-09 | 308 | 0 | 0 | 308 | 308 | 308 | 0 | 0 | 308 | 308 | 308
BIG SAMPSON WIND | 16INR0104 |  | WT | WIND-O | PLAN | CONV | CROCKETT | WEST | 2025-10-04 | 265.4 | 0 | 265.4 | 265.4 | 265.4 | 265.4 | 265.4 | 265.4 | 265.4 | 265.4 | 265.4
CAROL WIND | 20INR0217 |  | WT | WIND-P | PLAN | CONV | POTTER | PANHANDLE | 2026-04-15 | 165.4 | 0 | 165.4 | 165.4 | 165.4 | 165.4 | 0 | 165.4 | 165.4 | 165.4 | 165.4
GOODNIGHT WIND II | 23INR0637 |  | WT | WIND-P | PLAN | CONV | ARMSTRONG | PANHANDLE | 2026-02-27 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2
HART WIND 2 | 24INR0116 |  | WT | WIND-P | PLAN | CONV | CASTRO | PANHANDLE | 2025-09-01 | 166.4 | 0 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4
HONEY MESQUITE WIND FARM | 26INR0447 |  | WT | WIND-O | PLAN | CONV | GLASSCOCK | WEST | 2026-12-31 | 155.1 | 0 | 0 | 155.1 | 155.1 | 155.1 | 0 | 0 | 155.1 | 155.1 | 155.1
LA CASA WIND | 21INR0240 |  | WT | WIND-O | PLAN | CONV | STEPHENS | NORTH | 2025-06-30 | 148.4 | 0 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
MONTE ALTO I WIND | 19INR0022 |  | WT | WIND-C | PLAN | CONV | WILLACY | COASTAL | 2026-10-01 | 141.5 | 0 | 0 | 141.5 | 141.5 | 141.5 | 0 | 141.5 | 141.5 | 141.5 | 141.5
MONTE ALTO 2 WIND | 19INR0023 |  | WT | WIND-C | PLAN | CONV | WILLACY | COASTAL | 2026-10-01 | 307.9 | 0 | 0 | 307.9 | 307.9 | 307.9 | 0 | 307.9 | 307.9 | 307.9 | 307.9
MONTE CRISTO 1 WIND | 19INR0054 |  | WT | WIND-O | PLAN | CONV | HIDALGO | SOUTH | 2025-08-20 | 234.5 | 0 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5
PEYTON CREEK WIND II | 20INR0155 |  | WT | WIND-C | PLAN | CONV | MATAGORDA | COASTAL | 2025-02-14 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2 | 241.2
RAY GULF WIND | 22INR0517 |  | WT | WIND-O | PLAN | CONV | WHARTON | SOUTH | 2025-06-30 | 199.5 | 0 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
RUBICON ALPHA WIND | 24INR0291 |  | WT | WIND-O | PLAN | CONV | HASKELL | WEST | 2027-07-01 | 225.6 | 0 | 0 | 0 | 225.6 | 225.6 | 0 | 0 | 225.6 | 225.6 | 225.6
SIETE | 20INR0047 |  | WT | WIND-O | PLAN | CONV | WEBB | SOUTH | 2026-10-31 | 375.1 | 0 | 0 | 375.1 | 375.1 | 375.1 | 0 | 375.1 | 375.1 | 375.1 | 375.1
YELLOW CAT WIND | 25INR0018 |  | WT | WIND-O | PLAN | CONV | NAVARRO | NORTH | 2026-03-31 | 300 | 0 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300
ALILA SOLAR | 23INR0093 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2026-05-15 | 256.5 | 0 | 256.5 | 256.5 | 256.5 | 256.5 | 0 | 256.5 | 256.5 | 256.5 | 256.5
ANGUS SOLAR | 20INR0035 |  | PV | SOLAR-O | PLAN | CONV | BOSQUE | NORTH | 2026-04-01 | 112 | 0 | 112 | 112 | 112 | 112 | 0 | 112 | 112 | 112 | 112
ANSON SOLAR CENTER, PHASE II | 20INR0242 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2025-12-01 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
ARGENTA SOLAR | 25INR0060 |  | PV | SOLAR-O | PLAN | CONV | BEE | SOUTH | 2026-07-01 | 325 | 0 | 0 | 325 | 325 | 325 | 0 | 325 | 325 | 325 | 325
ARMADILLO SOLAR | 21INR0421 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2026-12-31 | 200.1 | 0 | 0 | 200.1 | 200.1 | 200.1 | 0 | 0 | 200.1 | 200.1 | 200.1
ARROYO SOLAR | 20INR0086 |  | PV | SOLAR-O | PLAN | CONV | CAMERON | COASTAL | 2028-02-22 | 100 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 100
ASH CREEK SOLAR | 21INR0379 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2025-04-28 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7 | 417.7
AUSTIN BAYOU SOLAR | 25INR0102 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2027-06-01 | 753.4 | 0 | 0 | 753.4 | 753.4 | 753.4 | 0 | 0 | 753.4 | 753.4 | 753.4
AZALEA SPRINGS SOLAR | 19INR0110 |  | PV | SOLAR-O | PLAN | CONV | ANGELINA | NORTH | 2025-05-31 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
BLEVINS SOLAR | 23INR0118 |  | PV | SOLAR-O | PLAN | CONV | FALLS | NORTH | 2025-07-01 | 271.6 | 0 | 271.6 | 271.6 | 271.6 | 271.6 | 271.6 | 271.6 | 271.6 | 271.6 | 271.6
BLUE SKY SOL | 22INR0455 |  | PV | SOLAR-W | PLAN | CONV | CROCKETT | WEST | 2025-02-15 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
MILLER'S BRANCH I | 22INR0270 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2025-12-01 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BUZIOS SOLAR | 24INR0399 |  | PV | SOLAR-W | PLAN | CONV | MOTLEY | PANHANDLE | 2026-06-30 | 252 | 0 | 0 | 252 | 252 | 252 | 0 | 252 | 252 | 252 | 252
CACHENA SOLAR SLF | 23INR0027 |  | PV | SOLAR-O | PLAN | CONV | WILSON | SOUTH | 2027-04-29 | 600 | 0 | 0 | 600 | 600 | 600 | 0 | 0 | 600 | 600 | 600
CALICHE MOUND SOLAR | 23INR0056 |  | PV | SOLAR-W | PLAN | CONV | DEAF SMITH | PANHANDLE | 2025-08-28 | 408.2 | 0 | 408.2 | 408.2 | 408.2 | 408.2 | 408.2 | 408.2 | 408.2 | 408.2 | 408.2
CANTALOUPE SOLAR | 23INR0116 |  | PV | SOLAR-FW | PLAN | CONV | REEVES | WEST | 2028-07-01 | 303.1 | 0 | 0 | 0 | 0 | 303.1 | 0 | 0 | 0 | 303.1 | 303.1
CASCADE SOLAR | 23INR0091 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2026-01-16 | 254.2 | 0 | 254.2 | 254.2 | 254.2 | 254.2 | 0 | 254.2 | 254.2 | 254.2 | 254.2
CHARGER SOLAR | 23INR0047 |  | PV | SOLAR-O | PLAN | CONV | REFUGIO | COASTAL | 2025-05-31 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8
COMPADRE SOLAR | 24INR0023 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2024-12-25 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1 | 406.1
CRADLE SOLAR | 23INR0150 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2025-12-31 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9
CROWDED STAR SOLAR | 20INR0241 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2025-12-31 | 218.8 | 0 | 218.8 | 218.8 | 218.8 | 218.8 | 0 | 218.8 | 218.8 | 218.8 | 218.8
CROWDED STAR SOLAR II | 22INR0274 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2026-01-26 | 190.2 | 0 | 190.2 | 190.2 | 190.2 | 190.2 | 0 | 190.2 | 190.2 | 190.2 | 190.2
CUCHILLAS SOLAR | 24INR0059 |  | PV | SOLAR-O | PLAN | CONV | WEBB | SOUTH | 2026-05-01 | 305.6 | 0 | 305.6 | 305.6 | 305.6 | 305.6 | 0 | 305.6 | 305.6 | 305.6 | 305.6
DELILAH SOLAR 2 | 22INR0203 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2025-07-26 | 317.6 | 0 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6
DESERT VINE SOLAR | 22INR0307 |  | PV | SOLAR-O | PLAN | CONV | ZAPATA | SOUTH | 2026-12-30 | 121.3 | 0 | 0 | 121.3 | 121.3 | 121.3 | 0 | 0 | 121.3 | 121.3 | 121.3
DIAMONDBACK SOLAR | 20INR0162 |  | PV | SOLAR-O | PLAN | CONV | STARR | SOUTH | 2027-12-31 | 201.6 | 0 | 0 | 0 | 201.6 | 201.6 | 0 | 0 | 0 | 201.6 | 201.6
DIVER SOLAR | 25INR0105 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2026-06-30 | 225.6 | 0 | 0 | 225.6 | 225.6 | 225.6 | 0 | 225.6 | 225.6 | 225.6 | 225.6
DONEGAL SOLAR | 23INR0089 |  | PV | SOLAR-W | PLAN | CONV | DICKENS | PANHANDLE | 2027-03-01 | 201.7 | 0 | 0 | 201.7 | 201.7 | 201.7 | 0 | 0 | 201.7 | 201.7 | 201.7
DORADO SOLAR | 22INR0261 |  | PV | SOLAR-W | PLAN | CONV | CALLAHAN | WEST | 2025-12-31 | 401.4 | 0 | 401.4 | 401.4 | 401.4 | 401.4 | 0 | 401.4 | 401.4 | 401.4 | 401.4
DOVE RUN SOLAR | 21INR0326 |  | PV | SOLAR-O | PLAN | CONV | DUVAL | SOUTH | 2026-07-31 | 120.9 | 0 | 0 | 120.9 | 120.9 | 120.9 | 0 | 120.9 | 120.9 | 120.9 | 120.9
DR SOLAR | 22INR0454 |  | PV | SOLAR-FW | PLAN | CONV | CULBERSON | WEST | 2025-12-15 | 36 | 0 | 36 | 36 | 36 | 36 | 0 | 36 | 36 | 36 | 36
DRY CREEK SOLAR I | 23INR0286 |  | PV | SOLAR-O | PLAN | CONV | RUSK | NORTH | 2026-01-01 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1
DUFFY SOLAR | 23INR0057 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2027-12-31 | 545.2 | 0 | 0 | 0 | 545.2 | 545.2 | 0 | 0 | 0 | 545.2 | 545.2
EASTBELL MILAM SOLAR II | 24INR0208 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2024-11-25 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
ELDORA SOLAR | 24INR0337 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2026-06-30 | 200.9 | 0 | 0 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9
ERATH COUNTY SOLAR | 23INR0202 |  | PV | SOLAR-O | PLAN | CONV | ERATH | NORTH | 2026-08-27 | 207.4 | 0 | 0 | 207.4 | 207.4 | 207.4 | 0 | 207.4 | 207.4 | 207.4 | 207.4
FAGUS SOLAR PARK 1 SLF | 20INR0091 |  | PV | SOLAR-W | PLAN | CONV | CHILDRESS | PANHANDLE | 2025-05-15 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4 | 166.4
FEWELL SOLAR | 23INR0367 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2027-03-15 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5
GAIA SOLAR | 24INR0141 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2025-07-31 | 152.6 | 0 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6 | 152.6
GARCITAS CREEK SOLAR | 23INR0223 |  | PV | SOLAR-O | PLAN | CONV | JACKSON | SOUTH | 2026-12-30 | 201.9 | 0 | 0 | 201.9 | 201.9 | 201.9 | 0 | 0 | 201.9 | 201.9 | 201.9
GLASGOW SOLAR | 24INR0206 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2027-03-16 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5
GP SOLAR | 23INR0045 |  | PV | SOLAR-O | PLAN | CONV | VAN ZANDT | NORTH | 2025-05-15 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
GRANSOLAR TEXAS ONE | 22INR0511 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2025-03-17 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
GREYHOUND SOLAR | 21INR0268 |  | PV | SOLAR-FW | PLAN | CONV | ECTOR | WEST | 2026-03-31 | 587.8 | 0 | 587.8 | 587.8 | 587.8 | 587.8 | 0 | 587.8 | 587.8 | 587.8 | 587.8
GRIMES COUNTY SOLAR | 23INR0160 |  | PV | SOLAR-O | PLAN | CONV | GRIMES | NORTH | 2025-06-15 | 211.3 | 0 | 211.3 | 211.3 | 211.3 | 211.3 | 211.3 | 211.3 | 211.3 | 211.3 | 211.3
HANSON SOLAR | 23INR0086 |  | PV | SOLAR-W | PLAN | CONV | COLEMAN | WEST | 2027-04-17 | 400.6 | 0 | 0 | 400.6 | 400.6 | 400.6 | 0 | 0 | 400.6 | 400.6 | 400.6
HICKERSON SOLAR | 21INR0359 |  | PV | SOLAR-O | PLAN | CONV | BOSQUE | NORTH | 2026-03-01 | 316.3 | 0 | 316.3 | 316.3 | 316.3 | 316.3 | 0 | 316.3 | 316.3 | 316.3 | 316.3
HIGH CHAP SOLAR | 25INR0068 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2027-08-04 | 152.3 | 0 | 0 | 0 | 152.3 | 152.3 | 0 | 0 | 152.3 | 152.3 | 152.3
HIGH NOON SOLAR | 24INR0124 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2027-12-01 | 182 | 0 | 0 | 0 | 182 | 182 | 0 | 0 | 182 | 182 | 182
HOLLOW BRANCH CREEK SOLAR | 24INR0422 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2027-12-31 | 460 | 0 | 0 | 0 | 460 | 460 | 0 | 0 | 0 | 460 | 460
HONEYCOMB SOLAR | 22INR0559 |  | PV | SOLAR-O | PLAN | CONV | BEE | SOUTH | 2025-12-01 | 61.1 | 0 | 61.1 | 61.1 | 61.1 | 61.1 | 61.1 | 61.1 | 61.1 | 61.1 | 61.1
HORNET SOLAR | 23INR0021 |  | PV | SOLAR-W | PLAN | CONV | SWISHER | PANHANDLE | 2025-04-30 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4 | 602.4
HORNET SOLAR II SLF | 25INR0282 |  | PV | SOLAR-W | PLAN | CONV | CASTRO | PANHANDLE | 2026-06-01 | 208.9 | 0 | 208.9 | 208.9 | 208.9 | 208.9 | 0 | 208.9 | 208.9 | 208.9 | 208.9
HOYTE SOLAR | 23INR0235 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2026-03-31 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8
INDIGO SOLAR | 21INR0031 |  | PV | SOLAR-W | PLAN | CONV | FISHER | WEST | 2026-08-17 | 150 | 0 | 0 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150
INERTIA SOLAR | 22INR0374 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2027-07-01 | 202.4 | 0 | 0 | 0 | 202.4 | 202.4 | 0 | 0 | 202.4 | 202.4 | 202.4
ISAAC SOLAR | 25INR0232 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2026-03-31 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6
JUNGMANN SOLAR | 22INR0356 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2025-03-17 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2
LANGER SOLAR | 23INR0030 |  | PV | SOLAR-O | PLAN | CONV | BOSQUE | NORTH | 2027-03-01 | 249.8 | 0 | 0 | 249.8 | 249.8 | 249.8 | 0 | 0 | 249.8 | 249.8 | 249.8
LAVACA BAY SOLAR | 23INR0084 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2024-12-04 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5
LEIGHTON SOLAR SLF | 24INR0298 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2026-10-17 | 183 | 0 | 0 | 183 | 183 | 183 | 0 | 183 | 183 | 183 | 183
LEON SOLAR PARK | 26INR0023 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2026-07-01 | 212.6 | 0 | 0 | 212.6 | 212.6 | 212.6 | 0 | 212.6 | 212.6 | 212.6 | 212.6
LIMEWOOD SOLAR | 23INR0249 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2025-12-31 | 204.6 | 0 | 204.6 | 204.6 | 204.6 | 204.6 | 0 | 204.6 | 204.6 | 204.6 | 204.6
LONG POINT SOLAR | 19INR0042 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2025-12-31 | 120 | 0 | 120 | 120 | 120 | 120 | 0 | 120 | 120 | 120 | 120
LUNIS CREEK SOLAR SLF | 21INR0344 |  | PV | SOLAR-O | PLAN | CONV | JACKSON | SOUTH | 2026-12-31 | 617.1 | 0 | 0 | 617.1 | 617.1 | 617.1 | 0 | 0 | 617.1 | 617.1 | 617.1
MALDIVES SOLAR (ALTERNATE POI) | 25INR0400 |  | PV | SOLAR-W | PLAN | CONV | SCURRY | WEST | 2027-07-01 | 210 | 0 | 0 | 0 | 210 | 210 | 0 | 0 | 210 | 210 | 210
MALEZA SOLAR | 21INR0220 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2025-11-01 | 254.9 | 0 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9
MATAGORDA SOLAR | 22INR0342 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2025-12-27 | 101 | 0 | 101 | 101 | 101 | 101 | 0 | 101 | 101 | 101 | 101
MIDPOINT SOLAR | 24INR0139 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2025-08-30 | 98.3 | 0 | 98.3 | 98.3 | 98.3 | 98.3 | 98.3 | 98.3 | 98.3 | 98.3 | 98.3
MOCCASIN SOLAR | 26INR0269 |  | PV | SOLAR-W | PLAN | CONV | STONEWALL | WEST | 2027-07-06 | 806.8 | 0 | 0 | 0 | 806.8 | 806.8 | 0 | 0 | 806.8 | 806.8 | 806.8
MRG GOODY SOLAR | 23INR0225 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2025-07-07 | 171.7 | 0 | 171.7 | 171.7 | 171.7 | 171.7 | 171.7 | 171.7 | 171.7 | 171.7 | 171.7
NABATOTO SOLAR NORTH | 21INR0428 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2027-05-10 | 451.4 | 0 | 0 | 451.4 | 451.4 | 451.4 | 0 | 0 | 451.4 | 451.4 | 451.4
NAZARETH SOLAR | 16INR0049 |  | PV | SOLAR-W | PLAN | CONV | CASTRO | PANHANDLE | 2025-12-31 | 204 | 0 | 204 | 204 | 204 | 204 | 0 | 204 | 204 | 204 | 204
NIGHTFALL SOLAR SLF | 21INR0334 |  | PV | SOLAR-O | PLAN | CONV | UVALDE | SOUTH | 2026-06-30 | 181.2 | 0 | 0 | 181.2 | 181.2 | 181.2 | 0 | 181.2 | 181.2 | 181.2 | 181.2
NORIA SOLAR DCC | 23INR0061 |  | PV | SOLAR-O | PLAN | CONV | NUECES | COASTAL | 2025-09-01 | 145 | 0 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
NORTON SOLAR | 19INR0035 |  | PV | SOLAR-W | PLAN | CONV | RUNNELS | WEST | 2025-10-01 | 125 | 0 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
NORTHINGTON SOLAR | 25INR0319 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2026-12-01 | 129.8 | 0 | 0 | 129.8 | 129.8 | 129.8 | 0 | 129.8 | 129.8 | 129.8 | 129.8
NEW HICKORY SOLAR | 20INR0236 |  | PV | SOLAR-O | PLAN | CONV | JACKSON | SOUTH | 2026-07-15 | 209.1 | 0 | 0 | 209.1 | 209.1 | 209.1 | 0 | 209.1 | 209.1 | 209.1 | 209.1
ORIANA SOLAR | 24INR0093 |  | PV | SOLAR-O | PLAN | CONV | VICTORIA | SOUTH | 2025-04-06 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
OUTPOST SOLAR | 23INR0007 |  | PV | SOLAR-O | PLAN | CONV | WEBB | SOUTH | 2025-04-01 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3 | 517.3
PARLIAMENT SOLAR | 23INR0044 |  | PV | SOLAR-O | PLAN | CONV | WALLER | HOUSTON | 2025-05-12 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6 | 484.6
PEREGRINE SOLAR | 22INR0283 |  | PV | SOLAR-O | PLAN | CONV | GOLIAD | SOUTH | 2024-12-30 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3 | 301.3
PINE FOREST SOLAR | 20INR0203 |  | PV | SOLAR-O | PLAN | CONV | HOPKINS | NORTH | 2025-12-01 | 301.5 | 0 | 301.5 | 301.5 | 301.5 | 301.5 | 301.5 | 301.5 | 301.5 | 301.5 | 301.5
PINNINGTON SOLAR | 24INR0010 |  | PV | SOLAR-O | PLAN | CONV | JACK | NORTH | 2026-03-30 | 653.7 | 0 | 653.7 | 653.7 | 653.7 | 653.7 | 0 | 653.7 | 653.7 | 653.7 | 653.7
PITTS DUDIK II | 24INR0364 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-01-29 | 30.2 | 0 | 30.2 | 30.2 | 30.2 | 30.2 | 0 | 30.2 | 30.2 | 30.2 | 30.2
QUANTUM SOLAR | 21INR0207 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 374.4 | 0 | 374.4 | 374.4 | 374.4 | 374.4 | 0 | 374.4 | 374.4 | 374.4 | 374.4
REDONDA SOLAR | 23INR0162 |  | PV | SOLAR-O | PLAN | CONV | ZAPATA | SOUTH | 2026-12-30 | 253.2 | 0 | 0 | 253.2 | 253.2 | 253.2 | 0 | 0 | 253.2 | 253.2 | 253.2
RENEGADE PROJECT (DAWN SOLAR) | 20INR0255 |  | PV | SOLAR-W | PLAN | CONV | DEAF SMITH | PANHANDLE | 2026-03-12 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7
ROCINANTE SOLAR | 23INR0231 |  | PV | SOLAR-O | PLAN | CONV | GONZALES | SOUTH | 2026-05-18 | 95.3 | 0 | 95.3 | 95.3 | 95.3 | 95.3 | 0 | 95.3 | 95.3 | 95.3 | 95.3
RODEO SOLAR | 19INR0103 |  | PV | SOLAR-FW | PLAN | CONV | ANDREWS | WEST | 2026-05-01 | 200 | 0 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200
SANPAT SOLAR | 25INR0052 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2027-07-31 | 256.2 | 0 | 0 | 0 | 256.2 | 256.2 | 0 | 0 | 256.2 | 256.2 | 256.2
SANPAT SOLAR II | 25INR0081 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2026-12-31 | 308.9 | 0 | 0 | 308.9 | 308.9 | 308.9 | 0 | 0 | 308.9 | 308.9 | 308.9
SHAULA I SOLAR | 22INR0251 |  | PV | SOLAR-O | PLAN | CONV | DEWITT | SOUTH | 2026-03-31 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2
SHAULA II SOLAR | 22INR0267 |  | PV | SOLAR-O | PLAN | CONV | DEWITT | SOUTH | 2026-05-30 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2
SHORT CREEK SOLAR | 24INR0201 |  | PV | SOLAR-W | PLAN | CONV | WICHITA | WEST | 2029-03-02 | 625 | 0 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 625
SIGNAL SOLAR | 20INR0208 |  | PV | SOLAR-O | PLAN | CONV | HUNT | NORTH | 2025-02-24 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
SOLACE SOLAR | 23INR0031 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 374.4 | 0 | 374.4 | 374.4 | 374.4 | 374.4 | 0 | 374.4 | 374.4 | 374.4 | 374.4
SP JAGUAR SOLAR | 24INR0038 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2026-06-01 | 300 | 0 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300
SPACE CITY SOLAR | 21INR0341 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2026-06-01 | 609.7 | 0 | 609.7 | 609.7 | 609.7 | 609.7 | 0 | 609.7 | 609.7 | 609.7 | 609.7
STARLING SOLAR | 23INR0035 |  | PV | SOLAR-O | PLAN | CONV | GONZALES | SOUTH | 2027-05-15 | 123 | 0 | 0 | 123 | 123 | 123 | 0 | 0 | 123 | 123 | 123
STILLHOUSE SOLAR | 24INR0166 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2025-06-01 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6 | 212.6
STONERIDGE SOLAR | 24INR0031 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2025-04-30 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
SUN CACTUS SOLAR | 25INR0109 |  | PV | SOLAR-O | PLAN | CONV | DUVAL | SOUTH | 2026-08-31 | 120.6 | 0 | 0 | 120.6 | 120.6 | 120.6 | 0 | 120.6 | 120.6 | 120.6 | 120.6
SWIFT AIR SOLAR | 24INR0421 |  | PV | SOLAR-FW | PLAN | CONV | ECTOR | WEST | 2025-03-31 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
SYPERT BRANCH SOLAR PROJECT | 24INR0070 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2025-07-01 | 261.1 | 0 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1
ORANGE GROVE SOLAR | 21INR0393 |  | PV | SOLAR-O | PLAN | CONV | JIM WELLS | SOUTH | 2025-04-30 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6 | 130.6
TANGLEWOOD SOLAR | 23INR0054 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2025-09-08 | 251 | 0 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251
THREE W SOLAR | 25INR0055 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-06-01 | 110.9 | 0 | 110.9 | 110.9 | 110.9 | 110.9 | 0 | 110.9 | 110.9 | 110.9 | 110.9
TOKIO SOLAR | 23INR0349 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-08-25 | 170.4 | 0 | 0 | 0 | 170.4 | 170.4 | 0 | 0 | 170.4 | 170.4 | 170.4
TROJAN SOLAR | 23INR0296 |  | PV | SOLAR-O | PLAN | CONV | COOKE | NORTH | 2026-02-28 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6
TYSON NICK SOLAR | 20INR0222 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2025-08-01 | 90.5 | 0 | 90.5 | 90.5 | 90.5 | 90.5 | 90.5 | 90.5 | 90.5 | 90.5 | 90.5
ULYSSES SOLAR | 21INR0253 |  | PV | SOLAR-W | PLAN | CONV | COKE | WEST | 2026-02-23 | 150 | 0 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150
VALHALLA SOLAR | 26INR0042 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2026-05-31 | 306.8 | 0 | 306.8 | 306.8 | 306.8 | 306.8 | 0 | 306.8 | 306.8 | 306.8 | 306.8
XE HERMES SOLAR | 23INR0344 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2025-08-25 | 100.4 | 0 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
XE MURAT [ADLONG] SOLAR | 22INR0354 |  | PV | SOLAR-O | PLAN | CONV | HARRIS | HOUSTON | 2025-01-03 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4
YAUPON SOLAR SLF | 24INR0042 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2026-06-15 | 204.1 | 0 | 0 | 204.1 | 204.1 | 204.1 | 0 | 204.1 | 204.1 | 204.1 | 204.1
ZEISSEL SOLAR | 24INR0258 |  | PV | SOLAR-W | PLAN | CONV | KNOX | WEST | 2028-07-01 | 457.5 | 0 | 0 | 0 | 0 | 457.5 | 0 | 0 | 0 | 457.5 | 457.5
RIVER VALLEY STORAGE U2 |  | RVRVLYS_ESS2 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RODEO RANCH ENERGY STORAGE U1 |  | RRANCHES_UNIT1 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2023-11-07 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RODEO RANCH ENERGY STORAGE U2 |  | RRANCHES_UNIT2 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2023-11-07 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
ROSELAND STORAGE |  | ROSELAND_BESS1 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2022-12-05 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SANDLAKE BESS (DGR) |  | SANDLAK1_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2024-12-06 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 10 | 10 | 10 | 10 | 10
SARAGOSA BESS (DGR) |  | SGSA_BESS1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-04-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SNYDER (DGR) |  | DPCRK_UNIT1 | BA | STORAGE | OPER | CONV-DGR | SCURRY | WEST | 2021-07-13 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
STAMPEDE BESS U1 |  | STAM_SLR_BESS1 | BA | STORAGE | OPER | CONV | HOPKINS | NORTH | 2023-03-03 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
ST. GALL I ENERGY STORAGE |  | SGAL_BES_BESS1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2023-12-28 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SWEETWATER BESS (DGR) |  | SWTWR_UNIT1 | BA | STORAGE | OPER | CONV-DGR | NOLAN | WEST | 2021-04-01 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SWOOSE II |  | SWOOSEII_BESS1 | BA | STORAGE | OPER | CONV | WARD | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TIMBERWOLF BESS |  | TBWF_ESS_BES1 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2023-09-01 | 150.34 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TURQUOISE STORAGE |  | TURQBESS_BESS1 | BA | STORAGE | OPER | CONV | HUNT | NORTH | 2023-02-10 | 196.2 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
VORTEX BESS |  | VORTEX_BESS1 | BA | STORAGE | OPER | CONV | THROCKMORTON | WEST | 2022-04-13 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8
WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2021-08-01 | 10 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 10 | 10 | 10 | 10 | 10
WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2019-12-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ZIER STORAGE U1 |  | ZIER_SLR_BES1 | BA | STORAGE | OPER | CONV | KINNEY | SOUTH | 2024-03-05 | 40.08 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
AE-TELVIEW ESS (DGR) | 23INR0541 | TV_BESS | BA | STORAGE | OPER-SYN | CONV-DGR | FORT BEND | HOUSTON | 2024-11-05 | 10 | 9.96 | 9.96 | 9.96 | 9.96 | 9.96 | 10 | 10 | 10 | 10 | 10
BIG STAR STORAGE | 21INR0469 | BIG_STAR_BESS | BA | STORAGE | OPER-SYN | CONV | BASTROP | SOUTH | 2024-12-01 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
BRIGHT ARROW STORAGE U1 | 22INR0302 | BR_ARROW_BESS1 | BA | STORAGE | OPER-SYN | CONV | HOPKINS | NORTH | 2024-12-31 | 49.34 | 48.28 | 48.28 | 48.28 | 48.28 | 48.28 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
BRIGHT ARROW STORAGE U2 | 22INR0302 | BR_ARROW_BESS2 | BA | STORAGE | OPER-SYN | CONV | HOPKINS | NORTH | 2024-12-31 | 52.77 | 51.72 | 51.72 | 51.72 | 51.72 | 51.72 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7
CENTURY BESS | 24INR0610 | CNTRY_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | TARRANT | NORTH | 2024-12-17 | 9.9 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CONNOLLY STORAGE | 23INR0403 | CNLY_ESS_BESS_1 | BA | STORAGE | OPER-SYN | CONV | WISE | NORTH | 2024-10-08 | 125.41 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
CROCKETT BESS | 25INR0642 | CR_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | HARRIS | HOUSTON | 2024-12-13 | 9.9 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
DANISH FIELDS STORAGE U1 | 21INR0450 | DAN_BESS1 | BA | STORAGE | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-31 | 77.8 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3
DANISH FIELDS STORAGE U2 | 21INR0450 | DAN_BESS2 | BA | STORAGE | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-31 | 75.1 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7
ELIZA STORAGE | 22INR0260 | ELZA_SLR_BES1 | BA | STORAGE | OPER-SYN | CONV | KAUFMAN | NORTH | 2025-03-11 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ESTONIAN ENERGY STORAGE | 22INR0336 | ESTONIAN_BES1 | BA | STORAGE | OPER-SYN | CONV | DELTA | NORTH | 2024-10-20 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
JADE STORAGE U1 | 24INR0629 | JADE_SLR_BESS1 | BA | STORAGE | OPER-SYN | CONV | SCURRY | WEST | 2024-11-16 | 78.53 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1
JADE STORAGE U2 | 24INR0629 | JADE_SLR_BESS2 | BA | STORAGE | OPER-SYN | CONV | SCURRY | WEST | 2024-11-16 | 82.27 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9
LONGBOW BESS | 25INR0328 | LON_BES1 | BA | STORAGE | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-11-09 | 180.8 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
MYRTLE STORAGE U1 | 21INR0442 | MYR_BES1 | BA | STORAGE | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 76.93 | 76.32 | 76.32 | 76.32 | 76.32 | 76.32 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3
MYRTLE STORAGE U2 | 21INR0442 | MYR_BES2 | BA | STORAGE | OPER-SYN | CONV | BRAZORIA | COASTAL | 2024-12-31 | 74.27 | 73.68 | 73.68 | 73.68 | 73.68 | 73.68 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7
PHOTON STORAGE | 23INR0460 | PHO_1_BES1 | BA | STORAGE | OPER-SYN | CONV | WHARTON | SOUTH | 2024-12-20 | 152.74 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
ABILENE ELMCREEK BESS | 25INR0701 |  | BA | STORAGE | PLAN | CONV-DGR | TAYLOR | WEST | 2025-04-21 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ABILENE INDUSTRIAL PARK BESS | 25INR0702 |  | BA | STORAGE | PLAN | CONV-DGR | TAYLOR | WEST | 2025-04-21 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ALDRIN 138 BESS | 25INR0421 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-03-01 | 207 | 0 | 207 | 207 | 207 | 207 | 0 | 207 | 207 | 207 | 207
ALDRIN 345 BESS | 25INR0425 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2027-12-01 | 362 | 0 | 0 | 0 | 362 | 362 | 0 | 0 | 362 | 362 | 362
ANDROMEDA STORAGE SLF | 24INR0630 |  | BA | STORAGE | PLAN | CONV | SCURRY | WEST | 2024-12-31 | 160.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANGLETON BESS | 24INR0547 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZORIA | COASTAL | 2025-01-27 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ANOLE BESS | 23INR0299 |  | BA | STORAGE | PLAN | CONV | DALLAS | NORTH | 2025-05-30 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1 | 247.1
ANSON BAT | 22INR0457 |  | BA | STORAGE | PLAN | CONV | JONES | WEST | 2025-12-31 | 151 | 0 | 151 | 151 | 151 | 151 | 0 | 151 | 151 | 151 | 151
APACHE HILL BESS | 25INR0231 |  | BA | STORAGE | PLAN | CONV | HOOD | NORTH | 2026-11-15 | 201.2 | 0 | 0 | 201.2 | 201.2 | 201.2 | 0 | 201.2 | 201.2 | 201.2 | 201.2
ARGENTA STORAGE | 25INR0061 |  | BA | STORAGE | PLAN | CONV | BEE | SOUTH | 2026-07-01 | 192 | 0 | 0 | 192 | 192 | 192 | 0 | 192 | 192 | 192 | 192
ATASCOCITA BESS | 25INR0713 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-09-12 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BIG ELM STORAGE | 23INR0469 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2025-11-10 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
BIRD DOG BESS | 22INR0467 |  | BA | STORAGE | PLAN | CONV | LIVE OAK | SOUTH | 2025-12-11 | 60.4 | 0 | 60.4 | 60.4 | 60.4 | 60.4 | 0 | 60.4 | 60.4 | 60.4 | 60.4
BLACK & GOLD ENERGY STORAGE | 24INR0386 |  | BA | STORAGE | PLAN | CONV | MENARD | WEST | 2027-06-30 | 254.6 | 0 | 0 | 0 | 254.6 | 254.6 | 0 | 0 | 254.6 | 254.6 | 254.6
BLACK SPRINGS BESS SLF | 24INR0315 |  | BA | STORAGE | PLAN | CONV | PALO PINTO | NORTH | 2025-10-15 | 120.7 | 0 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7
BLEVINS STORAGE | 23INR0119 |  | BA | STORAGE | PLAN | CONV | FALLS | NORTH | 2025-07-01 | 181.3 | 0 | 181.3 | 181.3 | 181.3 | 181.3 | 181.3 | 181.3 | 181.3 | 181.3 | 181.3
BOCANOVA BESS | 25INR0467 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-07-19 | 150.5 | 0 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5
BRACERO PECAN STORAGE | 26INR0034 |  | BA | STORAGE | PLAN | CONV | REEVES | WEST | 2026-06-01 | 232 | 0 | 232 | 232 | 232 | 232 | 0 | 232 | 232 | 232 | 232
BYPASS BATTERY STORAGE | 23INR0336 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2025-12-15 | 207.9 | 0 | 207.9 | 207.9 | 207.9 | 207.9 | 0 | 207.9 | 207.9 | 207.9 | 207.9
CALLISTO II ENERGY CENTER | 22INR0558 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2025-12-10 | 406.1 | 0 | 406.1 | 406.1 | 406.1 | 406.1 | 0 | 406.1 | 406.1 | 406.1 | 406.1
CARTWHEEL BESS 1 | 23INR0494 |  | BA | STORAGE | PLAN | CONV | HOPKINS | NORTH | 2025-07-31 | 154.2 | 0 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2
CASTOR BESS | 23INR0358 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-06-01 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4
CITRUS CITY BESS | 24INR0591 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2025-06-17 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CITRUS FLATTS BESS | 24INR0294 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2026-02-25 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8
CITY BREEZE BESS | 25INR0271 |  | BA | STORAGE | PLAN | CONV | MATAGORDA | COASTAL | 2026-07-15 | 140.6 | 0 | 0 | 140.6 | 140.6 | 140.6 | 0 | 140.6 | 140.6 | 140.6 | 140.6
COTULLA BESS 2 | 24INR0638 |  | BA | STORAGE | PLAN | CONV-DGR | LA SALLE | SOUTH | 2025-03-01 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROSBY BESS | 24INR0546 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-01-17 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROSS TRAILS STORAGE | 23INR0372 |  | BA | STORAGE | PLAN | CONV | SCURRY | WEST | 2025-04-25 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3
CROWNED HERON BESS | 24INR0405 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2025-07-31 | 154.2 | 0 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2
CROWNED HERON BESS 2 | 24INR0493 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2025-07-31 | 154.2 | 0 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2
DESERT WILLOW BESS | 23INR0195 |  | BA | STORAGE | PLAN | CONV | ELLIS | NORTH | 2025-03-19 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4 | 154.4
DESTINY STORAGE | 24INR0397 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-01-31 | 205.6 | 0 | 205.6 | 205.6 | 205.6 | 205.6 | 0 | 205.6 | 205.6 | 205.6 | 205.6
ELDORA BESS | 24INR0338 |  | BA | STORAGE | PLAN | CONV | MATAGORDA | COASTAL | 2026-06-30 | 201.3 | 0 | 0 | 201.3 | 201.3 | 201.3 | 0 | 201.3 | 201.3 | 201.3 | 201.3
ELIO BESS | 25INR0103 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-12-02 | 317.2 | 0 | 0 | 317.2 | 317.2 | 317.2 | 0 | 0 | 317.2 | 317.2 | 317.2
EVELYN BATTERY ENERGY STORAGE SYSTEM | 24INR0460 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2025-05-06 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3
FIRST CAPITOL BESS | 26INR0226 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2025-12-31 | 256.2 | 0 | 256.2 | 256.2 | 256.2 | 256.2 | 0 | 256.2 | 256.2 | 256.2 | 256.2
FORT WATT STORAGE | 24INR0498 |  | BA | STORAGE | PLAN | CONV | TARRANT | NORTH | 2026-09-15 | 201.4 | 0 | 0 | 201.4 | 201.4 | 201.4 | 0 | 201.4 | 201.4 | 201.4 | 201.4
GAIA STORAGE | 24INR0140 |  | BA | STORAGE | PLAN | CONV | NAVARRO | NORTH | 2025-07-31 | 76.8 | 0 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8
GLASGOW STORAGE | 24INR0207 |  | BA | STORAGE | PLAN | CONV | NAVARRO | NORTH | 2027-03-16 | 101 | 0 | 0 | 101 | 101 | 101 | 0 | 0 | 101 | 101 | 101
GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | BA | STORAGE | PLAN | CONV-DGR | HAMILTON | NORTH | 2023-05-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GUAJILLO ENERGY STORAGE | 23INR0343 |  | BA | STORAGE | PLAN | CONV | WEBB | SOUTH | 2025-07-30 | 204.8 | 0 | 204.8 | 204.8 | 204.8 | 204.8 | 204.8 | 204.8 | 204.8 | 204.8 | 204.8
GUNNAR BESS | 24INR0491 |  | BA | STORAGE | PLAN | CONV | HIDALGO | SOUTH | 2025-12-01 | 203 | 0 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
HEADCAMP BESS | 23INR0401 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2025-06-16 | 152.9 | 0 | 152.9 | 152.9 | 152.9 | 152.9 | 152.9 | 152.9 | 152.9 | 152.9 | 152.9
HIDDEN LAKES BESS | 23INR0617 |  | BA | STORAGE | PLAN | CONV-DGR | GALVESTON | HOUSTON | 2025-06-06 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HIGH NOON STORAGE | 24INR0126 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2027-12-01 | 94 | 0 | 0 | 0 | 94 | 94 | 0 | 0 | 94 | 94 | 94
HONEYCOMB STORAGE SLF | 23INR0392 |  | BA | STORAGE | PLAN | CONV | BEE | SOUTH | 2025-12-01 | 61.47 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
HORNET STORAGE II SLF | 25INR0283 |  | BA | STORAGE | PLAN | CONV | CASTRO | PANHANDLE | 2026-06-01 | 207.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IRON BELT ENERGY STORAGE | 25INR0208 |  | BA | STORAGE | PLAN | CONV | BORDEN | WEST | 2026-07-31 | 401.9 | 0 | 0 | 401.9 | 401.9 | 401.9 | 0 | 401.9 | 401.9 | 401.9 | 401.9
LIMEWOOD STORAGE | 23INR0248 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2028-12-29 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 50
LOWER RIO BESS | 22INR0468 |  | BA | STORAGE | PLAN | CONV | HIDALGO | SOUTH | 2025-03-31 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4
LUCKY BLUFF BESS SLF | 24INR0295 |  | BA | STORAGE | PLAN | CONV | ERATH | NORTH | 2025-10-15 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
MIDPOINT STORAGE | 24INR0138 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2025-08-30 | 50.9 | 0 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9
MRG GOODY STORAGE | 24INR0305 |  | BA | STORAGE | PLAN | CONV | LAMAR | NORTH | 2025-07-07 | 50.4 | 0 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
NORIA STORAGE | 23INR0062 |  | BA | STORAGE | PLAN | CONV | NUECES | COASTAL | 2025-09-01 | 75 | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
ORANGE GROVE BESS | 23INR0331 |  | BA | STORAGE | PLAN | CONV | JIM WELLS | SOUTH | 2027-04-30 | 61.4 | 0 | 0 | 61.4 | 61.4 | 61.4 | 0 | 0 | 61.4 | 61.4 | 61.4
ORIANA BESS | 24INR0109 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2026-06-15 | 60.3 | 0 | 0 | 60.3 | 60.3 | 60.3 | 0 | 60.3 | 60.3 | 60.3 | 60.3
PADUA GRID BESS | 22INR0368 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2025-04-23 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1 | 51.1
PALMVIEW BESS | 24INR0628 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2025-03-01 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PEARSALL BESS | 24INR0560 |  | BA | STORAGE | PLAN | CONV-DGR | FRIO | SOUTH | 2024-12-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PLATINUM STORAGE | 22INR0554 |  | BA | STORAGE | PLAN | CONV | FANNIN | NORTH | 2025-03-03 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5 | 309.5
PROJECT LYNX BESS | 25INR0329 |  | BA | STORAGE | PLAN | CONV | NUECES | COASTAL | 2026-03-14 | 125.4 | 0 | 125.4 | 125.4 | 125.4 | 125.4 | 0 | 125.4 | 125.4 | 125.4 | 125.4
RADIAN STORAGE SLF | 24INR0631 |  | BA | STORAGE | PLAN | CONV | BROWN | NORTH | 2024-12-31 | 160.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RED EGRET BESS | 24INR0281 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2025-08-01 | 310.6 | 0 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6
RIO GRANDE CITY BESS 2 | 24INR0592 |  | BA | STORAGE | PLAN | CONV-DGR | STARR | SOUTH | 2025-06-17 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ROCINANTE BESS | 23INR0232 |  | BA | STORAGE | PLAN | CONV | GONZALES | SOUTH | 2026-05-18 | 33.2 | 0 | 33.2 | 33.2 | 33.2 | 33.2 | 0 | 33.2 | 33.2 | 33.2 | 33.2
ROCKEFELLER STORAGE | 22INR0239 |  | BA | STORAGE | PLAN | CONV | SCHLEICHER | WEST | 2027-06-01 | 206.8 | 0 | 0 | 206.8 | 206.8 | 206.8 | 0 | 0 | 206.8 | 206.8 | 206.8
SCENIC WOODS BESS | 25INR0712 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-05-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SE EDINBURG BESS | 24INR0642 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2025-03-01 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SEVEN FLAGS BESS | 23INR0351 |  | BA | STORAGE | PLAN | CONV | WEBB | SOUTH | 2025-12-01 | 102.7 | 0 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
SHEPARD ENERGY STORAGE | 25INR0262 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2026-12-31 | 260.2 | 0 | 0 | 260.2 | 260.2 | 260.2 | 0 | 0 | 260.2 | 260.2 | 260.2
SHERBINO II BESS SLF | 26INR0296 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2025-08-06 | 77.4 | 0 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4
SOSA STORAGE | 25INR0131 |  | BA | STORAGE | PLAN | CONV | MADISON | NORTH | 2026-03-31 | 157.4 | 0 | 157.4 | 157.4 | 157.4 | 157.4 | 0 | 157.4 | 157.4 | 157.4 | 157.4
SP JAGUAR BESS | 24INR0039 |  | BA | STORAGE | PLAN | CONV | MCLENNAN | NORTH | 2025-06-30 | 314.3 | 0 | 314.3 | 314.3 | 314.3 | 314.3 | 314.3 | 314.3 | 314.3 | 314.3 | 314.3
SPENCER BESS | 24INR0545 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-03-14 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ST. GALL II ENERGY STORAGE | 22INR0525 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2025-06-01 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
STOCKYARD GRID BATT | 21INR0492 |  | BA | STORAGE | PLAN | CONV | TARRANT | NORTH | 2026-12-31 | 150.6 | 0 | 0 | 150.6 | 150.6 | 150.6 | 0 | 0 | 150.6 | 150.6 | 150.6
STONERIDGE BESS | 25INR0389 |  | BA | STORAGE | PLAN | CONV | MILAM | SOUTH | 2025-09-01 | 101.9 | 0 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
TE SMITH STORAGE | 22INR0555 |  | BA | STORAGE | PLAN | CONV | ROCKWALL | NORTH | 2025-07-15 | 125.4 | 0 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4
THIRD COAST BESS | 23INR0361 |  | BA | STORAGE | PLAN | CONV | JACKSON | SOUTH | 2025-12-15 | 102.8 | 0 | 102.8 | 102.8 | 102.8 | 102.8 | 0 | 102.8 | 102.8 | 102.8 | 102.8
TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | BA | STORAGE | PLAN | CONV | ROBERTSON | NORTH | 2025-06-01 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6 | 200.6
TIERRA SECA BESS | 23INR0364 |  | BA | STORAGE | PLAN | CONV | VAL VERDE | WEST | 2025-10-01 | 102.7 | 0 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
TWO BROTHERS BATTERY ENERGY STORAGE SYSTEM | 24INR0425 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2026-12-01 | 152 | 0 | 0 | 152 | 152 | 152 | 0 | 152 | 152 | 152 | 152
TWO FORKS BESS | 24INR0198 |  | BA | STORAGE | PLAN | CONV | COOKE | NORTH | 2027-07-01 | 309.7 | 0 | 0 | 0 | 309.7 | 309.7 | 0 | 0 | 309.7 | 309.7 | 309.7
WALSTROM BESS | 22INR0540 |  | BA | STORAGE | PLAN | CONV | AUSTIN | SOUTH | 2025-04-15 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
WHARTON BESS (DGR) | 22INR0608 |  | BA | STORAGE | PLAN | CONV-DGR | WHARTON | SOUTH | 2025-05-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WIZARD BESS | 25INR0300 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2025-05-01 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8
XE HERMES STORAGE | 24INR0365 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2025-08-25 | 100.4 | 0 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
MADERO GRID U1 |  | MADERO_UNIT1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2022-01-13 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2022-03-03 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2018-12-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
INERTIA BESS | 22INR0328 | INRT_W_BESS_1 | BA | STORAGE | OPER-SYN | CONV | HASKELL | WEST | 2024-10-31 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
WIGEON WHISTLE BESS | 24INR0312 | WIG_ESS_BES1 | BA | STORAGE | OPER-SYN | CONV | COLLIN | NORTH | 2024-10-18 | 122.9 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLUE SKIES BESS | 25INR0046 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2027-12-31 | 309 | 0 | 0 | 0 | 309 | 309 | 0 | 0 | 0 | 309 | 309
BORDERTOWN BESS | 23INR0354 |  | BA | STORAGE | PLAN | CONV | STARR | SOUTH | 2026-06-01 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2
CHILLINGHAM STORAGE | 23INR0079 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2025-08-02 | 153.9 | 0 | 153.9 | 153.9 | 153.9 | 153.9 | 153.9 | 153.9 | 153.9 | 153.9 | 153.9
FORT DUNCAN BESS | 23INR0350 |  | BA | STORAGE | PLAN | CONV | MAVERICK | SOUTH | 2025-06-01 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5
INERTIA BESS 2 | 22INR0375 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2027-07-01 | 100.8 | 0 | 0 | 0 | 100.8 | 100.8 | 0 | 0 | 100.8 | 100.8 | 100.8
ROCK ROSE ENERGY BESS | 26INR0201 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2026-07-02 | 211.5 | 0 | 0 | 211.5 | 211.5 | 211.5 | 0 | 211.5 | 211.5 | 211.5 | 211.5
DAMON BESS 2 (DGR) | 23INR0603 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZORIA | COASTAL | 2025-03-12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
IEP ORCHARD BESS | 23INR0556 |  | BA | STORAGE | PLAN | CONV-DGR | FORT BEND | HOUSTON | 2025-02-14 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * |  | PLANNED_SMALL_GEN_NO_MRD | BA | STORAGE | PLAN | CONV-DGR |  |  |  | 79.36 | 69.41 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36
POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | ST | GAS | MOTH-SEA | CONV | HUNT | NORTH | 1966-08-01 | 18.75 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 0 | 0 | 0 | 0 | 0
SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | ST | GAS | MOTH-SEA | CONV | DENTON | NORTH | 1966-08-18 | 61 | 57 | 57 | 57 | 57 | 57 | 0 | 0 | 0 | 0 | 0
SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | ST | GAS | MOTH-SEA | CONV | DENTON | NORTH | 1973-05-30 | 65 | 61 | 61 | 61 | 61 | 61 | 0 | 0 | 0 | 0 | 0
BRANDON (LP&L) (DGR) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | BRANDON_UNIT1 | GT | GAS | MOTH-IND | CONV-DGR | LUBBOCK | PANHANDLE | 2021-06-03 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
R MASSENGALE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G6 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 1988-02-18 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
R MASSENGALE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G7 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
R MASSENGALE STG (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G8 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 58.9 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
RAY OLINGER STG 1 (INDEFINITE MOTHBALL AS OF 4/5/22) |  | OLINGR_OLING_1 | ST | GAS | MOTH-IND | CONV | COLLIN | NORTH | 2021-06-03 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
TEXAS BIG SPRING WIND B (INDEFINITE MOTHBALL STATUS AS ON 1/1/24) |  | SGMTN_SIGNALM2 | WT | WIND-O | MOTH-IND | CONV | HOWARD | WEST | 1967-07-01 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
TY COOKE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT2 | GT | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 1999-05-27 | 18.7 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
TY COOKE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT3 | GT | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 26.6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
WICHITA FALLS STG 4 (INDEFINITE MOTHBALL STATUS AS ON 11/1/23) |  | WFCOGEN_UNIT4 | CC | GAS | MOTH-IND | CONV | WICHITA | WEST | 2021-06-03 | 20 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16
CHAMPION WIND REPOWER | 24INR0627 |  | WT | WIND-O | PLAN-RPR | CONV | NOLAN | WEST | 2025-05-09 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
TEMPLE GENERATION I REPOWER | 22INR0533 |  | CC | GAS | PLAN-RPR | CONV | BELL | NORTH | 2024-09-01 | 67 | 65 | 65 | 65 | 65 | 65 | 67 | 67 | 67 | 67 | 67
TEMPLE II REPOWER | 23INR0524 |  | CC | GAS | PLAN-RPR | CONV | BELL | NORTH | 2024-09-01 | 0 | 43 | 43 | 43 | 43 | 43 | 0 | 0 | 0 | 0 | 0
TEXAS GULF SULPHUR REPOWER | 24INR0605 |  | GT | GAS | PLAN-RPR | CONV | WHARTON | SOUTH | 2024-06-25 | 16.1 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
WISE COUNTY POWER REPOWER (CT1, CT2) | 20INR0286 |  | CC | GAS | PLAN-RPR | CONV | WISE | NORTH | 2024-09-01 | 21 | 109 | 109 | 109 | 109 | 109 | 21 | 21 | 21 | 21 | 21
Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT | CC | GAS | OPER | PUN |  |  |  |  | 3265 | 3265 | 3265 | 3204 | 3204 | 4049 | 4049 | 4049 | 4049 | 4049
Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST | CC | GAS | OPER | PUN |  |  |  |  | 0 | -110 | 97 | 97 | 347 | 0 | -110 | 97 | 97 | 347
AMOCO OIL COGEN |  | AMOCOOIL | CC | GAS | OPER | PUN | GALVESTON |  | 1986-04-01 | 1112.04
BAYTOWN ENERGY CENTER |  | BTE | CC | GAS | OPER | PUN | CHAMBERS |  | 2002-01-16 | 851
BAYOU COGEN |  | BYU | CC | GAS | OPER | PUN | HARRIS |  | 1984-12-01 | 323
CALPINE COGEN |  | CAL | CC | GAS | OPER | PUN | HARRIS |  | 1998-07-11 | 252.5
CORPUS CHRISTI ENERGY CENTER |  | CCEC | CC | GAS | OPER | PUN | NUECES |  | 2002-10-16 | 517.6
CHANNEL ENERGY CENTER |  | CHE | CC | GAS | OPER | PUN | HARRIS |  | 2002-04-01 | 757.8
DIAMOND SHAMROCK BATTLEGROUND |  | DIB | CC | GAS | OPER | PUN | HARRIS |  | 1982-05-01 | 313.6
FORMOSA |  | FORMOSA | CC | GAS | OPER | PUN | CALHOUN |  | 1993-04-22 | 895
INGLESIDE COGEN SWITCH |  | INGLCOSW | CC | GAS | OPER | PUN | SAN PATRICIO |  | 1999-10-03 | 507
POWER SYSTEMS-ARCO COGEN |  | PSA | CC | GAS | OPER | PUN | HARRIS |  | 1985-12-18 | 597.739
BIG SPRING ELECTRICITY GENERATING FACILITY |  | CARBN_BSP_1 | ST | GAS | OPER | PUN | HOWARD |  | 2006-07-01 | 25.1
DOW G61 |  | DOWGEN_DOW_G61 | CC | GAS | OPER | PUN | BRAZORIA |  | 1982-01-01 | 75
DOW G63 |  | DOWGEN_DOW_G63 | CC | GAS | OPER | PUN | BRAZORIA |  | 1982-01-01 | 75
DOW G66 |  | DOWGEN_DOW_G66 | CC | GAS | EXT-OUT | PUN | BRAZORIA |  | 1983-01-01 | 105
DOW G67 |  | DOWGEN_DOW_G67 | CC | GAS | OPER | PUN | BRAZORIA |  | 1983-01-01 | 105
DOW G81 |  | DOWGEN_DOW_G81 | CC | GAS | OPER | PUN | BRAZORIA |  | 1994-01-01 | 80
DOW G82 |  | DOWGEN_DOW_G82 | CC | GAS | OPER | PUN | BRAZORIA |  | 1994-01-01 | 80
DOW G83 |  | DOWGEN_DOW_G83 | CC | GAS | OPER | PUN | BRAZORIA |  | 1994-01-01 | 80
DOW GT96 |  | DOWGEN_DOW_GT96 | CC | GAS | OPER | PUN | BRAZORIA |  | 2007-01-01 | 186
DOW ST64 |  | DOWGEN_DOW_ST64 | CC | GAS | MOTH-IND | PUN | BRAZORIA |  | 1982-01-01 | 50
DOW ST65 |  | DOWGEN_DOW_ST65 | CC | GAS | OPER | PUN | BRAZORIA |  | 1983-01-01 | 110
DOW ST84 |  | DOWGEN_DOW_ST84 | CC | GAS | OPER | PUN | BRAZORIA |  | 1994-01-01 | 200
DOW ST95 |  | DOWGEN_DOW_ST95 | CC | GAS | OPER | PUN | BRAZORIA |  | 2007-01-01 | 80
EXXON G1 |  | EXN_EXN_G1 | GT | GAS | OPER | PUN | HARRIS |  | 1989-02-01 | 35.7
EXXON G10 |  | EXN_EXN_G10 | GT | GAS | OPER | PUN | HARRIS |  | 1978-01-01 | 29.4
EXXON G11 |  | EXN_EXN_G11 | GT | GAS | OPER | PUN | HARRIS |  | 1978-01-01 | 29.4
EXXON G12 |  | EXN_EXN_G12 | GT | GAS | OPER | PUN | HARRIS |  | 1978-01-01 | 29.4
EXXON G13 |  | EXN_EXN_G13 | GT | GAS | OPER | PUN | HARRIS |  | 1988-06-01 | 37.4
EXXON G14 |  | EXN_EXN_G14 | GT | GAS | OPER | PUN | HARRIS |  | 2004-12-31 | 163.8
EXXON G15 |  | EXN_EXN_G15 | ST | GAS | OPER | PUN | HARRIS |  | 2011-07-01 | 7.5
EXXON G2 |  | EXN_EXN_G2 | GT | GAS | OPER | PUN | HARRIS |  | 1989-04-01 | 35.7
EXXON G3 |  | EXN_EXN_G3 | GT | GAS | OPER | PUN | HARRIS |  | 1989-03-01 | 35.7
EXXON G4 |  | EXN_EXN_G4 | GT | GAS | OPER | PUN | HARRIS |  | 1997-02-28 | 92
EXXON G8 |  | EXN_EXN_G8 | GT | GAS | OPER | PUN | HARRIS |  | 1989-08-01 | 37.4
EXXON G9 |  | EXN_EXN_G9 | GT | GAS | OPER | PUN | HARRIS |  | 1978-01-01 | 29.4
FORMOSA G11 |  | FORMOSA_FORMOSG11 | ST | GAS | OPER | PUN | CALHOUN |  | 2012-03-01 | 143.1
FORMOSA G12 |  | FORMOSA_FORMOSG12 | ST | GAS | OPER | PUN | CALHOUN |  | 2012-05-01 | 143.1
FORMOSA G8 |  | FORMOSA_FORMOSG8 | GT | GAS | OPER | PUN | CALHOUN |  | 1987-03-17 | 36.17
LYCHEM |  | LHM_CVC_G4 | CT | GAS | OPER | PUN | HARRIS |  | 2001-08-01 | 192.1
NORTH CARBIDE G1 |  | NCARBIDE_NCARBIG1 | GT | GAS | OPER | PUN | CALHOUN |  | 1987-11-01 | 35.066
NORTH CARBIDE G2 |  | NCARBIDE_NCARBIG2 | GT | GAS | OPER | PUN | CALHOUN |  | 1987-11-01 | 35.066
NORTH CARBIDE G3 |  | NCARBIDE_NCARBIG3 | GT | GAS | OPER | PUN | CALHOUN |  | 2000-11-01 | 37.61
NORTH CARBIDE G5 |  | NCARBIDE_NCARBIG5 | ST | GAS | OPER | PUN | CALHOUN |  | 1987-11-01 | 14.4
NORTH CARBIDE G6 |  | NCARBIDE_NCARBIG6 | ST | GAS | OPER | PUN | CALHOUN |  | 1987-11-01 | 6.725
NORTH CARBIDE G7 |  | NCARBIDE_NCARBIG7 | ST | GAS | OPER | PUN | CALHOUN |  | 1987-11-01 | 14.4
NORTH CARBIDE G8 |  | NCARBIDE_NCARBIG8 | ST | GAS | OPER | PUN | CALHOUN |  | 2009-07-01 | 16.43
OXYCHEM CC |  | OXY_CC_OXY_CCG1 | GT | GAS | OPER | PUN | NUECES |  | 2001-06-22 | 37.88
PETRA NOVA |  | PNPI_GT2 | CT | GAS | OPER | PUN | FORT BEND |  | 2013-06-15 | 82.16
TEXAS PETROCHEMICALS |  | PR_PR_G2 | ST | GAS | OPER | PUN | HARRIS |  | 2009-10-29 | 35
SWEENY COGEN 1 |  | SCLPCOGN_SCLPC_1 | GT | GAS | OPER | PUN | BRAZORIA |  | 1998-01-01 | 120
SWEENY COGEN 2 |  | SCLPCOGN_SCLPC_2 | GT | GAS | OPER | PUN | BRAZORIA |  | 1998-01-01 | 120
SWEENY COGEN 3 |  | SCLPCOGN_SCLPC_3 | GT | GAS | OPER | PUN | BRAZORIA |  | 1998-01-01 | 120
SWEENY COGEN 4 |  | SCLPCOGN_SCLPC_4 | GT | GAS | OPER | PUN | BRAZORIA |  | 2000-12-01 | 120
TECO |  | TC_TCHP1 | GT | GAS | OPER | PUN | HARRIS |  | 2010-06-01 | 48
UNION CARBIDE COGEN |  | UCC_COGN_UCC_C_2 | ST | GAS | OPER | PUN | GALVESTON |  | 2001-08-22 | 38
TECO |  | TC_GTG2 | GT | GAS | OPER | PUN | HARRIS |  | 2024-01-30 | 48
TEXAS BLUEBONNET SOLAR |  | BONETSLR_UNIT1 | PV | SOLAR-O | OPER | PUN | MCLENNAN |  | 2024-06-17 | 9.75
JACKALOPE SOLAR PV1 |  | JKLP_SLR_PV1 | PV | SOLAR-O | OPER | PUN | SAN PATRICIO |  | 2024-10-31 | 81.38
JACKALOPE SOLAR PV2 |  | JKLP_SLR_PV2 | PV | SOLAR-O | OPER | PUN | SAN PATRICIO |  | 2024-10-31 | 71.74
Note on F9: EXT-OUT = Extended outage MOTH-IND = Indefinitely mothballed MOTH-SEA = Seasonal mothballed (operating under a seasonal availability schedule) OPER = Operational OPER-SYN = Operational, Synchronized but not Approved for Commercial Operations OPER-UNR = Unconfirmed Planned Retirement PLAN = Planned PLAN-RPR = An existing unit being repowered RMR = Reliability Must-Run
Note on G9: CONV = Conventional generation unit CONV-DGR = Conventional, Distributed Generation Resource unit CONV-SODG = Conventional, Settlement Only Distribution Generator unit CONV-TGR = Conventional, Transmission Generation Resource unit DC-TIE = Direct Current Asynchronous Tie DGR = Distributed Generation Resource PUN = Private Use Network generator PUN-AGR = Aggregate PUN resource, used for reporting the aggregate PUN capacity contribution SWGR-AVA = Switchable Generation Resource, Available SWGR-UNA = Switchable Generation Resource, Unavailable
Note on L1132: Extended Outage starting: 1/30/25 for 12-15 month duration, Jan. 2026 - April 2026
Note on Q1132: Extended Outage starting: 1/30/25 for 12-16 month duration, Jan. 2026 - May 2026
Note on Q1564: not available during winter seasons
Note on R1564: not available during winter seasons
Note on S1564: not available during winter seasons
Note on T1564: not available during winter seasons
Note on U1564: not available during winter seasons
Note on Q1565: not available during winter seasons
Note on R1565: not available during winter seasons
Note on S1565: not available during winter seasons
Note on T1565: not available during winter seasons
Note on U1565: not available during winter seasons
Note on Q1566: not available during winter seasons
Note on R1566: not available during winter seasons
Note on S1566: not available during winter seasons
Note on T1566: not available during winter seasons
Note on U1566: not available during winter seasons

## Capacity by Resource Type
Operational Resources, MW [1] | Installed Capacity Rating [2]
| Summer 2025 | Summer 2029 | Winter 2025/26 | Winter 2029/30
Thermal | 85290.974 | 82374.974 | 85829.344 | 82756.344
Natural Gas | 65309.584 | 64530.584 | 65847.954 | 64911.954
Combined-cycle | 43449.729 | 43970.729 | 43964.729 | 44328.729
Combustion Turbine | 9595.52 | 9595.52 | 9595.52 | 9595.52
Internal Combustion Engine | 732.2 | 732.2 | 900.32 | 900.32
Steam Turbine | 11532.135 | 10232.135 | 11387.385 | 10087.385
Compressed Air Energy Storage | 0 | 0 | 0 | 0
Coal | 14713.39 | 12576.39 | 14713.39 | 12576.39
Nuclear | 5268 | 5268 | 5268 | 5268
Renewable, Intermittent [6] | 67363.98 | 67363.98 | 67363.98 | 67363.98
Solar | 27817.58 | 27817.58 | 27817.58 | 27817.58
Far West | 5262.26 | 5262.26 | 5262.26 | 5262.26
West | 4374.41 | 4374.41 | 4374.41 | 4374.41
Other | 18180.91 | 18180.91 | 18180.91 | 18180.91
Wind | 39546.4 | 39546.4 | 39546.4 | 39546.4
Coastal | 5436.37 | 5436.37 | 5436.37 | 5436.37
Panhandle | 4668.53 | 4668.53 | 4668.53 | 4668.53
Other | 29441.5 | 29441.5 | 29441.5 | 29441.5
Renewable, Other | 724.85 | 724.85 | 724.85 | 724.85
Biomass | 142.25 | 142.25 | 142.25 | 142.25
Hydroelectric [4] | 582.6 | 582.6 | 582.6 | 582.6
Energy Storage, Available State of Charge | 9187.4 | 9289.1 | 9187.4 | 9289.1
Batteries | 9187.4 | 9289.1 | 9187.4 | 9289.1
Duration 1-hour or less | 4268.11 | 4369.81 | 4268.11 | 4369.81
Duration greater than 1-hour and less than 4-hour | 4773.49 | 4773.49 | 4773.49 | 4773.49
Duration 4 hour or more | 145.8 | 145.8 | 145.8 | 145.8
Other | 0 | 0 | 0 | 0
DC Tie Net Imports | 1220 | 1220 | 1220 | 1220
Planned Resources [5] | Summer 2025 | Summer 2029 | Winter 2025/26 | Winter 2029/30
Thermal | 133.8 | 2131.9 | 495.9 | 2131.9
Natural Gas | 104.1 | 2102.2 | 466.2 | 2102.2
Combined-cycle | 88 | 997.4 | 276.4 | 997.4
Combustion Turbine | 16.1 | 1074.8 | 159.8 | 1074.8
Internal Combustion Engine | 0 | 30 | 30 | 30
Steam Turbine | 0 | 0 | 0 | 0
Compressed Air Energy Storage | 0 | 0 | 0 | 0
Diesel | 29.7 | 29.7 | 29.7 | 29.7
Renewable, Intermittent [6] | 5417.91 | 33036.51 | 10054.81 | 33036.51
Solar | 5176.4 | 29543 | 8799.1 | 29543
Far West | 146.5 | 1273.4 | 146.5 | 1273.4
West | 870 | 7747.9 | 1804.1 | 7747.9
Other | 4159.9 | 20521.7 | 6848.5 | 20521.7
Wind | 241.51 | 3493.51 | 1255.71 | 3493.51
Coastal | 241.2 | 690.6 | 241.2 | 690.6
Panhandle | 0 | 591 | 166.4 | 591
Other | 0.31 | 2211.91 | 848.11 | 2211.91
Energy Storage, Available State of Charge | 4245.46 | 17619.73 | 9077.73 | 17619.73
Batteries | 4245.46 | 17619.73 | 9077.73 | 17619.73
Duration 1-hour or less | 1966.6 | 5228.5 | 3378 | 5228.5
Duration greater than 1-hour and less than 4-hour | 2157.36 | 11388.33 | 5424.33 | 11388.33
Duration 4 hour or more | 121.5 | 1002.9 | 275.4 | 1002.9
Other | 0 | 0 | 0 | 0
Total Resources, MW | 173584.374 | 213761.044 | 183954.014 | 214142.414
NOTES:
[1] Operational resources are those for which ERCOT has approved grid synchronization or full commercial operations. Unit level details for each resource category can be found in the Resource Details tab.
[2] Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. All gas-fired Private-Use Network (PUNs) units are reflected in the combined cycle fuel type row above.
[3] Expected Available Capacity for operational units accounts for thermal seasonal sustained capability ratings, hourly capacity contribution estimates for intermittent renewables, planned retirements, reductions due to co-located loads, unavailable Switchable Generation Resources (SWGRs), mothballed capacity, and expected Private Use Network (PUN) generator net exports to the grid. For planned projects, Expected Available Capacity is based on the maximum capacity reported by the developers and accounts for net changes due to repower or upgrade projects greater than one MW, and the established limits on the total MW Injection for designated Self-Limiting Facilities. Unit level details for each resource group above can be found in the Resource Details tab.
[4] Includes a small amount of hydro units that are considered intermittent resources (run-of-river DG hydro units).
[5] Planned resources are those for which ERCOT expects to be approved for grid synchronization or has been assigned a “Model Ready Date" (for Small Generators) by the first of the month.
[6] Wind and solar values represent the 50th percentile values from hourly synthetic output profiles used in the PRRM. See the Background tab for more information.

## ELCCs
What is an Effective Load Carrying Capability?
ELCC measures the effectiveness of a resource type—wind, solar and battery energy storage—in maintaining a resource portfolio’s reliability level over a given period. Reliability is measured as the expected frequency of loss-of-load (LOL) events, where an event represents an hourly period when rotating load shed is necessary to maintain overall grid reliability. The availability of the resource type when LOL events are more likely to occur determines the ELCC. ELCC is not a direct measure of generation output available for a given period, but rather an indicator of the expected reliability benefit of the capacity for the given period.
ELCCs estimated for the CDR reflect the resource reliability benefit for a given multi-hour "risk period" rather than an individual hour. The reason is that loss-of-load events can span multiple hours, which makes it impractical to calculate ELCCs for just a given hour.
Why has ERCOT changed its method for calculating the capacity contribution of wind and solar resources?
ELCCs estimated for wind, solar and battery energy storage—Inverter Based Resources, or IBRs—are now being used for ERCOT’s CDR. ELCCs replace a methodology whereby average historical wind and solar capacity availability is estimated for a sample of the highest peak load hours during past seasons. This prior approach fails to account for the expected reliability impacts of increasing wind and solar penetration, resulting in reserve margins that belie the increased reliability risk for these intermittent resources. Importantly, the ELCC method aligns the CDR with how IBRs are represented in the probabilistic simulation model to be used to support analysis for the Texas Public Utility Commission’s new Reliability Standard.
How are ELCCs Estimated?
A resource type’s ELCC is gauged against so-called “perfect capacity,” which is hypothetical generation capacity that is available 100% of the time when the capacity is needed. For example, a wind ELCC of 25% means that the resource portfolio’s wind capacity is only 25% as effective as perfect capacity in maintaining the portfolio’s reliability level for the given period. The associated ELCC capacity is the ELCC percentage multiplied by the resource type’s aggregate installed capacity in megawatts (MW). ELCCs are determined by running a probabilistic reliability model for a future year. The model produces many reliability outcomes for the forecast year based on simulating grid conditions with variations in load and resource availabilities. ELCCs account for a resource type’s average reliability contribution across all the simulation outcomes. The basic process for estimating ELCCs is as follows: 1. The future-year resource portfolio is first modified to meet a reliability level based on the reliability criteria established for a prevailing reliability standard. 2. All the capacity for the resource type is then removed and replaced with perfect capacity until the reliability level is again reached based on simulation results. (The perfect capacity is a gas turbine plant with a zero-percent outage rate). 3. The final step is to divide the perfect capacity added by the capacity of the resource type removed. The result is the ELCC percentage. ELCCs will aways be less than 100%.
ELCC study reports are available in the "Wind, Solar and Energy Storage Resources" section of the | [7 empty] | ERCOT Resource Adequacy webpage.
Key Attributes of ELCCs
Annual ELCCs can be decomposed into values for shorter periods. ERCOT’s ELCCs are estimated by year, season, and daily risk period (afternoon and evening for non-winter months; morning, afternoon, and evening for winter months.)
ELCCs decline as more of the resource type is added to the resource portfolio. When there is not much of the resource type installed on the grid, its capacity yields a high ELCC. However, adding more capacity dilutes the reliability benefit of the existing and new capacity, thereby lowering the ELCC. This effect is most dramatic for solar capacity. At low penetration levels, solar has a large reliability benefit in the afternoon when solar output is at its highest. As more solar is added, the risk of reliability issues is then pushed into the evening hours when solar generation drops and becomes much less effective at maintaining reliability. Solar ELCCs decrease sharply for the evening risk period, but also decrease for the afternoon.
ELCCs for a resource type account for the joint reliability impacts of other portfolio resources and the grid conditions modeled. Resource diversity can have benefits for maintaining a given portfolio reliability level. For example, the combination of solar and battery energy storage can provide a combined ELCC greater than adding the ELCCs estimated separately for these resource types. This synergistic reliability effect is captured by running simulations designed to isolate the incremental ELCC increase of the combined solar/battery resource portfolio. ELCCs also reflect all modeled grid conditions that impact the timing, length and magnitude of LOL events.
ELCCs are unique for a given set of portfolio resources, load forecasts, and other modeling assumptions. ELCCs typically need to be re-estimated as resource portfolios and other grid attributes affecting reliability change. To minimize the frequency of needed updates, a library of ELCCs has been developed based on a range of future resource-type combinations and load levels. This library development approach supports ELCCs calculated for the range of planning reserve margin periods reported in the CDRs.
ELCCs for battery energy storage systems (BESSs) are estimated for a range of design durations. BESS ELCCs are impacted by system duration; the longer the duration, the higher the ELCC, not accounting for the “diminishing returns” effect of adding more BESS capacity to the resource portfolio. Estimating BESS-duration ELCCs is more complicated than estimating them for wind and solar capacity, requiring both probabilistic modeling and a separate model to estimate all the reliability impacts of these systems.
ELCCs Values used in this CDR
The following table lists the wind, solar and battery energy storage Effective Load Carrying Capability (ELCC) values used for Planning Reserve Margin calculations. ELCC values are disaggregated by time periods: forecast year, season and applicable reserve risk period.
Effective Load Carrying Capabilities (ELCCs)*
| 2025 & 2025/26 |  |  |  | 2026 & 2026/27 |  |  |  | 2027 & 2027/28 |  |  |  | 2028 & 2028/29 |  |  |  | 2029 & 2029/30
| Winter | Winter | Summer | Summer | Winter | Winter | Summer | Summer | Winter | Winter | Summer | Summer | Winter | Winter | Summer | Summer | Winter | Winter | Summer | Summer
Risk Period | Morning | Evening | Afternoon | Evening | Morning | Evening | Afternoon | Evening | Morning | Evening | Afternoon | Evening | Morning | Evening | Afternoon | Evening | Morning | Evening | Afternoon | Evening
Resource Type
Wind - Coastal | 29.9% | 29.9% | 30.83% | 16.37% | 29.75% | 29.75% | 31.56% | 17% | 29.14% | 29.14% | 31.81% | 16.46% | 29.14% | 29.14% | 31.95% | 16.46% | 29.14% | 29.14% | 31.98% | 16.46%
Wind - Panhandle | 32.56% | 32.56% | 33.58% | 17.83% | 32.4% | 32.4% | 34.36% | 18.51% | 31.73% | 31.73% | 34.64% | 17.93% | 31.73% | 31.73% | 34.79% | 17.93% | 31.73% | 31.73% | 34.83% | 17.93%
Wind - Other | 15.2% | 15.2% | 15.68% | 8.325% | 15.13% | 15.13% | 16.05% | 8.643% | 14.82% | 14.82% | 16.17% | 8.372% | 14.82% | 14.82% | 16.25% | 8.372% | 14.82% | 14.82% | 16.26% | 8.372%
Solar - FarWest | 2.594% | 2.594% | 36.14% | 7.32% | 1.968% | 1.968% | 28.46% | 3.4% | 1.823% | 1.823% | 26.87% | 1.9% | 1.75% | 1.75% | 26.24% | 0.88% | 1.759% | 1.759% | 26.38% | 0.63%
Solar - West | 2.594% | 2.594% | 36.14% | 7.32% | 1.968% | 1.968% | 28.46% | 3.4% | 1.823% | 1.823% | 26.87% | 1.9% | 1.75% | 1.75% | 26.24% | 0.88% | 1.759% | 1.759% | 26.38% | 0.63%
Solar - Other | 1.953% | 1.953% | 27.21% | 5.511% | 1.481% | 1.481% | 21.43% | 2.56% | 1.373% | 1.373% | 20.23% | 1.431% | 1.318% | 1.318% | 19.76% | 0.6625% | 1.324% | 1.324% | 19.86% | 0.4743%
BESS - 1.0 hr | 26.8% | 24.35% | 74.44% | 74.44% | 25.02% | 22.39% | 43.32% | 43.32% | 22.05% | 19.92% | 37.99% | 37.99% | 20.06% | 18.21% | 34.01% | 34.01% | 19.51% | 17.71% | 33.1% | 33.1%
BESS - 2.0 hr | 63.65% | 59.11% | 98.2% | 98.2% | 46.15% | 41.99% | 81.71% | 81.71% | 38.11% | 35.05% | 65.12% | 65.12% | 38.74% | 35.55% | 64.06% | 64.06% | 38.57% | 35.39% | 63.82% | 63.82%
BESS - 3.0 hr | 90.61% | 95.17% | 98.2% | 98.2% | 65.79% | 72.09% | 98.42% | 98.42% | 60.02% | 60.37% | 97.7% | 97.7% | 61.89% | 54.95% | 96.78% | 96.78% | 61.79% | 54.87% | 96.72% | 96.72%
BESS - 4.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 91.57% | 94.04% | 98.42% | 98.42% | 84.38% | 88.95% | 97.7% | 97.7% | 71.1% | 70.51% | 97.21% | 97.21% | 71% | 70.4% | 97.15% | 97.15%
BESS - 5.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 85.28% | 91.03% | 98.42% | 98.42% | 80.65% | 86.1% | 97.7% | 97.7% | 81.1% | 86.04% | 97.23% | 97.23% | 80.98% | 85.91% | 97.17% | 97.17%
BESS - 6.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 91.65% | 94.22% | 98.42% | 98.42% | 90.08% | 92.49% | 97.7% | 97.7% | 89.62% | 91.81% | 97.23% | 97.23% | 89.48% | 91.67% | 97.17% | 97.17%
BESS - 7.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 94.06% | 95.05% | 98.42% | 98.42% | 92.46% | 93.31% | 97.7% | 97.7% | 91.78% | 92.55% | 97.23% | 97.23% | 91.64% | 92.41% | 97.17% | 97.17%
BESS - 8.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 95.55% | 95.55% | 98.42% | 98.42% | 93.74% | 93.74% | 97.7% | 97.7% | 92.94% | 92.94% | 97.23% | 97.23% | 92.8% | 92.8% | 97.17% | 97.17%
BESS - 9.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 95.55% | 95.55% | 98.42% | 98.42% | 93.74% | 93.74% | 97.7% | 97.7% | 92.94% | 92.94% | 97.23% | 97.23% | 92.8% | 92.8% | 97.17% | 97.17%
BESS - 10.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 95.55% | 95.55% | 98.42% | 98.42% | 93.74% | 93.74% | 97.7% | 97.7% | 92.94% | 92.94% | 97.23% | 97.23% | 92.8% | 92.8% | 97.17% | 97.17%
BESS - 11.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 95.55% | 95.55% | 98.42% | 98.42% | 93.74% | 93.74% | 97.7% | 97.7% | 92.94% | 92.94% | 97.23% | 97.23% | 92.8% | 92.8% | 97.17% | 97.17%
BESS - 12.0 hr | 98.29% | 98.29% | 98.2% | 98.2% | 95.55% | 95.55% | 98.42% | 98.42% | 93.74% | 93.74% | 97.7% | 97.7% | 92.94% | 92.94% | 97.23% | 97.23% | 92.8% | 92.8% | 97.17% | 97.17%
*ELCCs for non-winter morning reserve risk periods are not reported because the occurrence of loss-of-load events is expected to be negligible or non-existent for those periods.

## New CDR-Eligible Resources
New Planned Resources Eligible for CDR Report since the Last CDR Report, Published May 2024
5.6
The table below lists the planned resources that have met certain ERCOT Planning Guide criteria necessary for the resources to be included in this CDR report. These criteria are as follows:
Large Generators 1. For all resource types a signed Standard Generation Interconnection Agreement (SGIA) or other binding agreement (for municipally-owned utilities or electric cooperatives). 2. Air permits required by the Texas Commission on Environmental Quality (TCEQ) or notice that air permits are not required. 3. Submission of a "Declaration of Adequate Water Supplies" and proof that the resource has sufficient water supplies for electricity generation. Solar, wind, and Energy Storage Resources are exempt from this requirement.
Small Generators 1. ERCOT has determined that all data submission requirements for Resource Registration have been met and the generator is added to the ERCOT Network Operations Model. These requirement are met when the Small Generator has been issued a Model Ready Date.
Notes
Year of Projected Commercial Operations: The year is based on the projected Commercial Operations Date (COD) reported by the project developer. Planned projects with a "(DGR)" suffix indicate that the resource is a Distributed Generation Resource as defined in the ERCOT Nodal Protocols (Section 2.1). Projects ending with 'SLF' represent Battery Energy Storage Systems that are Self-Limiting Facilities (SLFs), where the MW capacities are reported as zero to reflect projects for which the battery system is sized to be less than the total nameplate capacity of all registered generators at the facility. Other generators at the facility typically include one or more inverter-based resources, such as solar.
| Project Name | GENERATION INTERCONNECTION PROJECT CODE | County | Fuel | Zone | Year of Projected Commercial Operations | Installed Capacity, MW
| CEDAR BAYOU5 | 23INR0029 | CHAMBERS | GAS-CC | HOUSTON | 2027 | 721
| COYOTE SPRINGS AGR1 (DGR) | 24INR0645 | REEVES | DIESEL | WEST | 2025 | 9.9
| ENCHANTED ROCK NEWPP | 22INR0546 | HARRIS | GAS-IC | HOUSTON | 2025 | 30
| FRIENDSWOOD G CTG 2 | 24INR0456 | HARRIS | GAS-GT | HOUSTON | 2025 | 143.7
| OLNEY AGR1 (DGR) | 24INR0647 | YOUNG | DIESEL | WEST | 2025 | 9.9
| SADDLEBACK AGR1 (DGR) | 24INR0646 | REEVES | DIESEL | WEST | 2025 | 9.9
| HONEY MESQUITE WIND FARM | 26INR0447 | GLASSCOCK | WIND-O | WEST | 2026 | 155.1
| PEYTON CREEK WIND II | 20INR0155 | MATAGORDA | WIND-C | COASTAL | 2025 | 241.2
| RUBICON ALPHA WIND | 24INR0291 | HASKELL | WIND-O | WEST | 2027 | 225.6
| YELLOW CAT WIND | 25INR0018 | NAVARRO | WIND-O | NORTH | 2026 | 300
| ANSON SOLAR CENTER, PHASE II | 20INR0242 | JONES | SOLAR | WEST | 2025 | 200.9
| AUSTIN BAYOU SOLAR | 25INR0102 | BRAZORIA | SOLAR | COASTAL | 2027 | 753.4
| CANTALOUPE SOLAR | 23INR0116 | REEVES | SOLAR | WEST | 2028 | 303.1
| DIAMONDBACK SOLAR | 20INR0162 | STARR | SOLAR | SOUTH | 2027 | 201.6
| HICKERSON SOLAR | 21INR0359 | BOSQUE | SOLAR | NORTH | 2026 | 316.3
| HIGH NOON SOLAR | 24INR0124 | HILL | SOLAR | NORTH | 2027 | 182
| HOLLOW BRANCH CREEK SOLAR | 24INR0422 | LEON | SOLAR | NORTH | 2027 | 460
| HORNET SOLAR II SLF | 25INR0282 | CASTRO | SOLAR | PANHANDLE | 2026 | 208.9
| LEIGHTON SOLAR SLF | 24INR0298 | LIMESTONE | SOLAR | NORTH | 2026 | 183
| LEON SOLAR PARK | 26INR0023 | LEON | SOLAR | NORTH | 2026 | 212.6
| MOCCASIN SOLAR | 26INR0269 | STONEWALL | SOLAR | WEST | 2027 | 806.8
| NORTHINGTON SOLAR | 25INR0319 | WHARTON | SOLAR | SOUTH | 2026 | 129.8
| PITTS DUDIK II | 24INR0364 | HILL | SOLAR | NORTH | 2026 | 30.2
| SHORT CREEK SOLAR | 24INR0201 | WICHITA | SOLAR | WEST | 2029 | 625
| SWIFT AIR SOLAR | 24INR0421 | ECTOR | SOLAR | WEST | 2025 | 146.5
| ABILENE ELMCREEK BESS | 25INR0701 | TAYLOR | STORAGE | WEST | 2025 | 9.9
| ABILENE INDUSTRIAL PARK BESS | 25INR0702 | TAYLOR | STORAGE | WEST | 2025 | 9.9
| ALDRIN 138 BESS | 25INR0421 | BRAZORIA | STORAGE | COASTAL | 2026 | 207
| ALDRIN 345 BESS | 25INR0425 | BRAZORIA | STORAGE | COASTAL | 2027 | 362
| ANDROMEDA STORAGE SLF | 24INR0630 | SCURRY | STORAGE | WEST | 2024 | 160.35
| ANGLETON BESS | 24INR0547 | BRAZORIA | STORAGE | COASTAL | 2025 | 9.9
| ANSON BAT | 22INR0457 | JONES | STORAGE | WEST | 2026 | 151
| APACHE HILL BESS | 25INR0231 | HOOD | STORAGE | NORTH | 2026 | 201.2
| ATASCOCITA BESS | 25INR0713 | HARRIS | STORAGE | HOUSTON | 2025 | 9.9
| BIG ELM STORAGE | 23INR0469 | BELL | STORAGE | NORTH | 2025 | 100.8
| BLACK & GOLD ENERGY STORAGE | 24INR0386 | MENARD | STORAGE | WEST | 2027 | 254.6
| BLUE SKIES BESS | 25INR0046 | HILL | STORAGE | NORTH | 2027 | 309
| BRACERO PECAN STORAGE | 26INR0034 | REEVES | STORAGE | WEST | 2026 | 232
| CANTALOUPE STORAGE | 23INR0117 | REEVES | STORAGE | WEST | 2028 | 251.1
| CANVASBACK BESS | 25INR0160 | CALHOUN | STORAGE | COASTAL | 2027 | 150.5
| CITRUS CITY BESS | 24INR0591 | HIDALGO | STORAGE | SOUTH | 2025 | 9.9
| CITY BREEZE BESS | 25INR0271 | MATAGORDA | STORAGE | COASTAL | 2026 | 140.6
| COTULLA BESS 2 | 24INR0638 | LA SALLE | STORAGE | SOUTH | 2025 | 9.9
| CROSS TRAILS STORAGE | 23INR0372 | SCURRY | STORAGE | WEST | 2025 | 58.3
| CROWNED HERON BESS 2 | 24INR0493 | FORT BEND | STORAGE | HOUSTON | 2025 | 154.2
| ELIO BESS | 25INR0103 | BRAZORIA | STORAGE | COASTAL | 2026 | 317.2
| FALFUR BESS (DGR) | 24INR0593 | BROOKS | STORAGE | SOUTH | 2025 | 9.8
| FIRST CAPITOL BESS | 26INR0226 | BRAZORIA | STORAGE | COASTAL | 2025 | 256.2
| FORT WATT STORAGE | 24INR0498 | TARRANT | STORAGE | NORTH | 2026 | 201.4
| HIGH NOON STORAGE | 24INR0126 | HILL | STORAGE | NORTH | 2027 | 94
| HORNET STORAGE II SLF | 25INR0283 | CASTRO | STORAGE | PANHANDLE | 2026 | 207.96
| MAYBERRY II BESS | 23INR0807 | HIDALGO | STORAGE | SOUTH | 2024 | 9.9
| MRG GOODY STORAGE | 24INR0305 | LAMAR | STORAGE | NORTH | 2025 | 50.4
| PALMVIEW BESS | 24INR0628 | HIDALGO | STORAGE | SOUTH | 2025 | 9.9
| PEARSALL BESS | 24INR0560 | FRIO | STORAGE | SOUTH | 2024 | 9.9
| PHOTON BESS2 | 25INR0691 | WHARTON | STORAGE | SOUTH | 2025 | 152.7
| PINE FOREST BESS | 22INR0526 | HOPKINS | STORAGE | NORTH | 2025 | 200.7
| PROJECT LYNX BESS | 25INR0329 | NUECES | STORAGE | COASTAL | 2026 | 125.4
| RADIAN STORAGE SLF | 24INR0631 | BROWN | STORAGE | NORTH | 2024 | 160.25
| RIO GRANDE CITY BESS 2 | 24INR0592 | STARR | STORAGE | SOUTH | 2025 | 9.9
| ROCK ROSE ENERGY BESS | 26INR0201 | FORT BEND | STORAGE | HOUSTON | 2026 | 211.5
| ROCKEFELLER STORAGE | 22INR0239 | SCHLEICHER | STORAGE | WEST | 2027 | 206.8
| SCENIC WOODS BESS | 25INR0712 | HARRIS | STORAGE | HOUSTON | 2025 | 9.9
| SE EDINBURG BESS | 24INR0642 | HIDALGO | STORAGE | SOUTH | 2025 | 9.9
| SHAMROCK ENERGY STORAGE (SLF) | 24INR0568 | CROCKETT | STORAGE | WEST | 2025 | 99.33
| SHERBINO II BESS SLF | 26INR0296 | PECOS | STORAGE | WEST | 2025 | 77.4
| SPENCER BESS | 24INR0545 | HARRIS | STORAGE | HOUSTON | 2025 | 9.9
| ST. GALL II ENERGY STORAGE | 22INR0525 | PECOS | STORAGE | WEST | 2025 | 100.2
| STONERIDGE BESS | 25INR0389 | MILAM | STORAGE | SOUTH | 2025 | 101.9
| TWO BROTHERS BATTERY ENERGY STORAGE SYSTEM | 24INR0425 | VICTORIA | STORAGE | SOUTH | 2026 | 152
| TWO FORKS BESS | 24INR0198 | COOKE | STORAGE | NORTH | 2027 | 309.7
| TYNAN BESS | 24INR0759 | BEE | STORAGE | SOUTH | 2024 | 9.9
| WHARTON BESS (DGR) | 22INR0608 | WHARTON | STORAGE | SOUTH | 2025 | 10
| TOTAL | [5 empty] | 12522.49

## Acronyms
Acronyms
General
GIM = Generator Interconnection or Modification request
CDR = Capacity, Demand and Reserves Report
COD = Commercial Operations Date
ELCC = Effective Load Carrying Capability
HE = Hour Ending
INR = Interconnection Request Number
RIOO-IS = "Resource Integration and Ongoing Operations - Integration Services" system
RIOO-RS = "Resource Integration and Ongoing Operations - Registration Services" system
RTP = Regional Transmission Plan
TSP = Transmission Service Provider
CDR Status (For Unit Details table)
EXT-OUT = Extended outage
OPER = Operational
OPER-SLF = Operational Self-Limiting Facility (See the Definitions tab for the SLF definition)
OPER-SYN = Operational, synchronized only
OPER-UNR = Unconfirmed Planned Retirement
MOTH-SEA = Seasonal mothballed (Unit operating under a seasonal availability schedule)
MOTH-IND = Indefinitely mothballed
PLAN = Planned
PLAN-RPR = An existing unit being repowered and required to submit an interconnection request (See the Definitions tab for the CDR repower definition)
RMR = Reliability Must-Run, A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
CDR Resource Attributes (For Unit Details table)
CONV = Conventional generation resource (Unit that does not fall under the other CDR Attribute categories)
DC-TIE = Direct Current Asynchronous Tie
DGR = Distributed Generation Resource
PUN = Private Use Network generator
PUN-AGR = Aggregate PUN resource, used for reporting the aggregate PUN capacity contribution
SLF = Self-Limiting Facility (See the Definitions tab for the SLF definition)
SODG = Settlement Only Distribution Generator
SWGR-AVA = Switchable Generation Resource, available
SWGR-UNA = Switchable Generation Resource, Unavailable
Fuel Types (For Unit Details Table)
BIO = Biomass
COAL = Coal (bituminous, subbituminous, lignite)
GAS = National Gas
GEO = Geothermal
HYD = Hydrogen
NUC = Nuclear
OIL = Fuel Oil
OTH = Other
PET = Petcoke
SOL = Solar
WAT = Water
WIND-C = Wind from the Coastal wind region
WIND-P = Wind from the Panhandle wind region
WIND-O = Wind from the Other wind region
SOLAR-FW = Solar from the Far West CDR solar region
SOLAR-W = Solar from the West CDR solar region
SOLAR-O = Solar from the Other CDR solar region
Technology Types (For Unit Details table)
BA = Battery Energy Storage
CC = Combined-Cycle
CE = Compressed Air Energy Storage
CP = Concentrated Solar Power
EN = Energy Storage
FC = Fuel Cell
GT = Combustion (gas) Turbine, but not part of a Combined-Cycle
HY = Hydroelectric Turbine
IC = Internal Combustion Engine, eg. Reciprocating
OT = Other
PV = Photovoltaic Solar
ST = Steam Turbine other than Combined-Cycle
WT = Wind Turbine

## Definitions
Definitions
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Capacity Pending Retirement
Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2.
Contracted / Non-Contracted TSP Loads
Contracted Large Load: A Large Load, as defined in ERCOT's Planning Guide, reported to ERCOT for which an interconnection agreements and/or Facility Extension Agreements (FEA) has been signed by the customer and Transmission Service Provider, and the customer share of costs for the extension of TSP facilities has been paid to the TSP. A contracted Load typically falls into the following general categories: crypto-mining, data centers, hydrogen/ammonia production, oil and gas production, and industrial/manufacturing. Officer letter Large Load: A Load (or Loads) for which an officer of a TSP has documented in a letter sent to ERCOT attesting that there is a high likelihood that the Load(s) will materialize. These prospective Loads are not associated with a signed interconnection agreement or FEA, and are therefore considered more speculative than Loads with a signed interconnection agreement or FEA.
Decommissioned Generation Resource
A Generation Resource for which a Resource Entity has submitted a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD), for which ERCOT has declined to execute a Reliability Must-Run (RMR) Agreement, and which has been decommissioned and permanently retired.
Distribution Resource Types:
Settlement Only Distribution Generator (SODG)
A generator that is connected to the Distribution System with a rating of: (1) One MW or less that chooses to register as an SODG; or (2) Greater than one and up to ten MW that is capable of providing a net export to the ERCOT System and does not register as a Distribution Generation Resource (DGR). SODGs are settled for exported energy only, but may not participate in the Ancillary Services market, Reliability Unit Commitment (RUC), Security-Constrained Economic Dispatch (SCED), or make energy offers. SODGs are listed in the SummerCapacities and WinterCapacities with a DG_ prefix in the UNIT CODE column
Distribution Generation Resource (DGR)
A Generation Resource connected to the Distribution System that is either: (1) Greater than ten MW and not registered with the Public Utility Commission of Texas (PUCT) as a self-generator; or (2) Ten MW or less that chooses to register as a Generation Resource to participate in the ERCOT markets. DGRs must be registered with ERCOT in accordance with Planning Guide Section 6.8.2, Resource Registration Process, and will be modeled in ERCOT systems in accordance with Section 3.10.7.2, Modeling of Resources and Transmission Loads. DGRs are listed in the SummerCapacities and WinterCapacities tabs with a (DGR) suffix in the UNIT NAME column
Effective Load Carrying Capability (ELCC)
Represents the aggregate average Megawatt (MW) contribution of a resource class in maintaining a target level of resource reliability for a given resource portfolio and forecast period. ELCCs are developed using Monte Carlo system simulation techniques to capture a wide range of system reliability outcomes. ELCC derivation starts with a base portfolio constructed to achieve the target reliability level. The resource class (e.g., wind) is removed and substituted with capacity that has perfect availability until the target reliability level is again reached. The ELCC is the amount of perfect capacity added divided by the amount of the resource class capacity removed, expressed as a percentage.
Emergency Response Service
ERCOT uses the methodology specified in Protocol Section 3.2.6.2.1, Peak Load Estimate, to derive the ERS capacity forecast for future years. The Current Year for the calculations is defined as the latest year for which ERS has been procured. The ERS capacity amounts are grossed up by 2% to reflect avoided transmission line losses.
Energy Efficiency Program Savings Forecast
ERCOT's energy efficiency forecast uses the PUCT's annual verified energy efficiency program savings estimates as the starting point. (See the definition for verified energy efficiency program savings below.) Savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast. ERCOT computes the historical average annual verified savings, but excludes 2017 from the calculation due to Hurricane Harvey load impacts. (For prior forecasts, ERCOT used a formula based on the State energy efficiency goals in Utilities Code Section 39.905. Since the impacts of the goals were assumed to accumulate for just seven years from the time that the goals must be first met (2013), ERCOT no longer uses the goal-based forecasting approach.) Finally, ERCOT incorporates annual energy efficiency estimates from municipal utilities and electric cooperatives provided to the State Energy Conservation Office (SECO). Annual SECO report submission by these entities is required under S.B. No. 924. If annual reports for the previous calendar year are not available at the time the CDR is prepared, ERCOT incorporates report data for the most recently available reporting year. The energy efficiency capacity amounts are grossed up by a factor representing avoided transmission and distribution line losses. The factor is currently 1.076, reflecting 2% for avoided transmission losses and 5.6% for avoided distribution losses. The loss percentages are based on transmission and distribution loss factors posted to ERCOT's MIS website.
Energy Emergency Alert (EEA)
An ERCOT EEA declaration is made when operating reserves and system frequency drop below established severity levels (Levels 1, 2 and 3) and reserves are not projected to recover within 30 minutes unless certain actions are taken. An EEA declaration initiates an orderly, predetermined procedure for maximizing the use of available Resources, including the use of voluntary load reduction programs that are only available under EEA operations. Only under the most severe EEA level, would ERCOT direct Transmission and Distribution Service Providers to start shedding Load on a rotating basis in order to maintain system reliability and integrity. See Nodal Protocol Section 6.5.9.4, Energy Emergency Alert, for more details.
ERCOT Contingency Reserve Service (ECRS)
An Ancillary Service that provides operating reserves that is intended to: (a) Restore Responsive Reserve (RRS) within ten minutes of a frequency deviation that results in significant depletion of RRS by restoring frequency to its scheduled value to return the system to normal; (b) Provide energy or continued Load interruption to avoid or during the implementation of an Energy Emergency Alert (EEA); (c) Provide backup regulation; and (d) Be sustained at a specified level for two consecutive hours. ECRS was developed to address net load ramps and take advantage of Energy Storage Resources with maximum durations of at leat two hours.
Forecast Zone
The CDR report uses Forecast Zones to identify the geographical location of generation resources. Forecast Zones generally have the same boundaries as the 2003 Congestion Management Zones with the following exceptions: A) Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones, and B) Coastal Zone for resources in 11 counties along the Texas Gulf Coast and formerly in the South Zone of the 2003 Congestion Management Zones. There are six Forecast Zones: Coastal, Houston, North, Panhandle, South, and West. Note that the CDR Forecast Zones are only used for resource adequacy reporting and are distinct from other ERCOT geographical reporting schemes used for planning, operational, or data reporting purposes.
Full Interconnection Study (FIS)
The set of studies conducted by a Transmission Service Provider (TSP) for the purpose of identifying any electric system improvements or enhancements required to reliably interconnect a new All-Inclusive Generation Resource consistent with the provisions of Planning Guide Section 5, Generation Resource Interconnection or Change Request. These studies may include steady-state studies, system protection (short-circuit) studies, dynamic and transient stability studies, facility studies, and sub-synchronous oscillation studies.
Inactive Projects
Per Planning Guide Section 5.7.6, a proposed Resource shall be given the status of “Inactive” if the Resource has not met the conditions for inclusion in the ERCOT planning models, as specified in Section 6.9, Addition of Proposed Generation to the Planning Models, within two years of the date on which ERCOT posts the final FIS studies for the Resource to the MIS Secure Area. A developer may also elect Inactive status and stop any interconnection studies in process at its own discretion. When an Inactive Resource subsequently meets the requirements of Section 6.9, it shall be added to the planning models and the status changed back to Planned. If a Resource has been Inactive for five years, ERCOT may cancel the project pursuant to Planning Guide Section 5.7.7, Cancellation of a Project Due to Failure to Comply with Requirements. Inactive planned projects are excluded from the CDR's reserve margin calculations.
Installed Capacity Rating
The installed capacity rating is the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. ERCOT uses Real Power Ratings that reflect the continous flow of power to loads (as opposed to reactive power, which is the power that flows back and forth between the power source and loads, and doesn't perform useful work.)
Large Flexible Load (LFL)
A Large Load (as defined below) that can come online quickly and is very responsive to real time prices. An LFL is typically a crypto-currency mining site.
Large Load
One or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE). LR capacity has been grossed up by 2% to reflect avoided transmission line losses.
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Seasons
Summer months are June, July, August, and September; winter months are December, January, and February.
Net Load / Peak Net Load
The Load for a given period minus generation from PhotoVoltaic Generation Resources (PVGRs) and Wind Generation Resources (WGRs) for the same period. The peak Net Load is the highest value for the given period.
Private Use Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Repower
For CDR reporting purposes, a repower is a an operational resource that needs to project for which one of the two following conditions apply: ● The Resource Entity is changing the inverter, turbine, generator, or power converter associated with a facility with an aggregate real power rating of ten MW or greater, unless the replacement is in-kind;Repowered Facility. See Planning Guide Section 5.2.1(1)(c)(ii). ● Increasing the aggregate nameplate capacity of a generator less than ten MW to ten MW or greater. See Planning Guide Section 5.2.1(1)(c)(v).
Self-Limiting Facility (SLF)
A modeled generation station that includes one or more Generation Resources, Energy Storage Resources (ESRs), and/or Settlement Only Generators (SOGs) with an established limit on the total MW Injection that is less than the total nameplate capacity of all registered generators or Energy Storage Systems (ESSs) within the Facility. A Facility with one or more ESRs may also have an established limit on the MW Withdrawal that is less than the total nameplate MW Withdrawal rating of all ESRs within the facility. (MW Withdrawal is defined as the instantaneous Megawatt (MW) energy withdrawn from the ERCOT System as measured at the Point of Interconnection (POI) or Point of Common Coupling (POCC).
Signed SGIA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Generation Resource (SWGR)
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Synchronized but not Approved for Commerical Operations Capacity
These units have met requirements to Energize Equipment (Part 1 of Generator Commissioning Checklist): provided latest model data, verified Voltage Ride-Through capability and communication capabilities specified by ERCOT Operating Guides are in place. Output for these resources is not limited once they have passed a curtailment test and the project developer has submitted an attestation for the following plant controls: Automatic Voltage Regulator (AVR), Primary Frequency Response (PFR), Voltage Support Service (VSS), and Power System Stabilizer (PSS). A Synchronized unit get approved for Commerical Operations after the plant controls have been verified by ERCOT. More information on Synchronized units can be found in the Resource Interconnection Handbook pages 24 – 33.http://www.ercot.com/content/wcm/lists/168284/Resource_Interconnection_Handbook_v1.91_01082021.docx
TDSP Standard Offer Load Management Programs
For the May releases of the CDR report, ERCOT uses the megawatt amount of verified peak load capacity reductions, adjusted for avoided transmission losses, due to TDSP Standard Offcer load management programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. The reported amounts are for the most current reporting year, which is the calendar year prior to the year during which the May CDR is prepared. (For example, the May 2019 CDR report used verified program savings for the 2018 reporting year.) For the December CDR releases, ERCOT uses TDSP data received for the current load management program year, which is more timely than the verified savings estimates provided to the PUCT. The data obtained from the TDSPs reflect verified program performance for the summer based on testing, and is adjusted for avoided transmission losses.
Unconfirmed Retirement
The capacity of Generation Resources for which a public announcement of the intent to permanently shut the unit down has been released, but a Notice of Suspension of Operations for the unit has not been received by ERCOT. To be considered an Unconfirmed Planned Retirement, the Generation Resource must meet the following criteria: (1) a specific retirement date is cited in the announcement, or other timing information is provided that indicates the unit will be unavailable for a given season and year, and (2) the announcement, with follow-up inquiry by ERCOT, does not indicate that retirement timing is highly speculative.
Verified Energy Efficiency Program Savings
The total megawatt (MW) amount of verified peak load capacity reductions due to residential and commercial sector energy efficiency incentive programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. See Utilities Code Section 39.905. Note that savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast, but rather handled as a separate reporting line item.
Wind and Solar Regions
See the "Wind-Solar Region Mapping" tab to see which counties are assigned to each region. The assigned Wind Region for each wind generation resource is indicated as "WIND-C," "WIND-P," or "WIND-O" in the Fuel columns of the summer/winter Capacities tabs. The assigned Solar Region assigned to each solar generation resources is indicated as "SOLAR-W," SOLAR-FW," and SOLAR-O."

## Wind-Solar Region Mapping
The tables below show what counties in the ERCOT region are mapped to the CDR Wind and Solar Regions.
Note: The CDR Wind and Solar Regions are intended to facilitate calculation of geographic-based Effective Load Carrying Capabilities (ELCCs) that represent wind and solar availabilities for Planning Reserve Margin calculation purposes. These are distinct from ERCOT zone definitions defined for other uses, such as the zones used for wind and solar production forecasting and reporting.
CDR Wind Region | County | CDR Solar Region | County
Coastal | Aransas | West | Archer
Coastal | Brazoria | West | Baylor
Coastal | Calhoun | West | Borden
Coastal | Cameron | West | Callahan
Coastal | Chambers | West | Clay
Coastal | Galveston | West | Coke
Coastal | Jefferson | West | Coleman
Coastal | Kenedy | West | Concho
Coastal | Kleberg | West | Crockett
Coastal | Matagorda | West | Fisher
Coastal | Nueces | West | Glasscock
Coastal | Orange | West | Haskell
Coastal | Refugio | West | Howard
Coastal | San Patricio | West | Irion
Coastal | Willacy | West | Jones
North | Anderson | West | Knox
North | Angelina | West | Martin
North | Bell | West | Menard
North | Bosque | West | Mitchell
North | Bowie | West | Nolan
North | Brazos | West | Reagan
North | Brown | West | Runnels
North | Camp | West | Schleicher
North | Cass | West | Scurry
North | Cherokee | West | Shackelford
North | Collin | West | Sterling
North | Comanche | West | Stonewall
North | Cooke | West | Sutton
North | Coryell | West | Taylor
North | Dallas | West | Throckmorton
North | Delta | West | Tom Green
North | Denton | West | Val Verde
North | Eastland | West | Wichita
North | Ellis | West | Wilbarger
North | Erath | West | Armstrong
North | Falls | West | Bailey
North | Fannin | West | Briscoe
North | Franklin | West | Carson
North | Freestone | West | Castro
North | Grayson | West | Childress
North | Gregg | West | Cochran
North | Grimes | West | Collingsworth
North | Hamilton | West | Cottle
North | Harrison | West | Crosby
North | Henderson | West | Dallam
North | Hill | West | Dawson
North | Hood | West | Deaf Smith
North | Hopkins | West | Dickens
North | Houston | West | Donley
North | Hunt | West | Floyd
North | Jack | West | Foard
North | Jasper | West | Garza
North | Johnson | West | Gray
North | Kaufman | West | Hale
North | Lamar | West | Hall
North | Lampasas | West | Hansford
North | Leon | West | Hardeman
North | Limestone | West | Hartley
North | Madison | West | Hemphill
North | Marion | West | Hockley
North | McLennan | West | Hutchinson
North | Mills | West | Kent
North | Montague | West | King
North | Morris | West | Lamb
North | Nacogdoches | West | Lipscomb
North | Navarro | West | Lubbock
North | Newton | West | Lynn
North | Palo Pinto | West | Moore
North | Panola | West | Motley
North | Parker | West | Ochiltree
North | Polk | West | Oldham
North | Rains | West | Parmer
North | Red River | West | Potter
North | Robertson | West | Randall
North | Rockwall | West | Roberts
North | Rusk | West | Sherman
North | Sabine | West | Swisher
North | San Augustine | West | Terry
North | San Jacinto | West | Wheeler
North | San Saba | FarWest | Andrews
North | Shelby | FarWest | Brewster
North | Smith | FarWest | Crane
North | Somervell | FarWest | Culberson
North | Stephens | FarWest | Ector
North | Tarrant | FarWest | El Paso
North | Titus | FarWest | Gaines
North | Trinity | FarWest | Hudspeth
North | Tyler | FarWest | Jeff Davis
North | Upshur | FarWest | Loving
North | Van Zandt | FarWest | Midland
North | Walker | FarWest | Pecos
North | Wise | FarWest | Presidio
North | Wood | FarWest | Reeves
Panhandle | Armstrong | FarWest | Terrell
Panhandle | Bailey | FarWest | Upton
Panhandle | Briscoe | FarWest | Ward
Panhandle | Carson | FarWest | Winkler
Panhandle | Castro | FarWest | Yoakum
Panhandle | Childress | Other | Bandera
Panhandle | Cochran | Other | Bell
Panhandle | Collingsworth | Other | Blanco
Panhandle | Crosby | Other | Bosque
Panhandle | Dallam | Other | Brown
Panhandle | Deaf Smith | Other | Burnet
Panhandle | Dickens | Other | Collin
Panhandle | Donley | Other | Comal
Panhandle | Floyd | Other | Comanche
Panhandle | Gray | Other | Cooke
Panhandle | Hale | Other | Coryell
Panhandle | Hall | Other | Dallas
Panhandle | Hansford | Other | Denton
Panhandle | Hartley | Other | Eastland
Panhandle | Hemphill | Other | Edwards
Panhandle | Hockley | Other | Ellis
Panhandle | Hutchinson | Other | Erath
Panhandle | Lamb | Other | Gillespie
Panhandle | Lipscomb | Other | Grayson
Panhandle | Lubbock | Other | Hamilton
Panhandle | Moore | Other | Hays
Panhandle | Motley | Other | Hill
Panhandle | Ochiltree | Other | Hood
Panhandle | Oldham | Other | Jack
Panhandle | Parmer | Other | Johnson
Panhandle | Potter | Other | Kendall
Panhandle | Randall | Other | Kerr
Panhandle | Roberts | Other | Kimble
Panhandle | Sherman | Other | Lampasas
Panhandle | Swisher | Other | Llano
Panhandle | Wheeler | Other | Mason
South | Atascosa | Other | McCulloch
South | Austin | Other | McLennan
South | Bandera | Other | Mills
South | Bastrop | Other | Montague
South | Bee | Other | Palo Pinto
South | Bexar | Other | Parker
South | Blanco | Other | Real
South | Brooks | Other | San Saba
South | Burleson | Other | Somervell
South | Burnet | Other | Stephens
South | Caldwell | Other | Tarrant
South | Colorado | Other | Travis
South | Comal | Other | Williamson
South | DeWitt | Other | Wise
South | Dimmit | Other | Young
South | Duval | Other | Anderson
South | Edwards | Other | Angelina
South | Fayette | Other | Austin
South | Fort Bend | Other | Bastrop
South | Frio | Other | Bowie
South | Gillespie | Other | Brazoria
South | Goliad | Other | Brazos
South | Gonzales | Other | Burleson
South | Guadalupe | Other | Caldwell
South | Hardin | Other | Camp
South | Harris | Other | Cass
South | Hays | Other | Chambers
South | Hidalgo | Other | Cherokee
South | Jackson | Other | Colorado
South | Jim Hogg | Other | Delta
South | Jim Wells | Other | Falls
South | Karnes | Other | Fannin
South | Kendall | Other | Fayette
South | Kerr | Other | Fort Bend
South | Kimble | Other | Franklin
South | Kinney | Other | Freestone
South | La Salle | Other | Galveston
South | Lavaca | Other | Gregg
South | Lee | Other | Grimes
South | Liberty | Other | Hardin
South | Live Oak | Other | Harris
South | Llano | Other | Harrison
South | Mason | Other | Henderson
South | Maverick | Other | Hopkins
South | McCulloch | Other | Houston
South | McMullen | Other | Hunt
South | Medina | Other | Jackson
South | Milam | Other | Jasper
South | Montgomery | Other | Jefferson
South | Real | Other | Kaufman
South | Starr | Other | Lamar
South | Travis | Other | Lavaca
South | Uvalde | Other | Lee
South | Victoria | Other | Leon
South | Waller | Other | Liberty
South | Washington | Other | Limestone
South | Webb | Other | Madison
South | Wharton | Other | Marion
South | Williamson | Other | Matagorda
South | Wilson | Other | Milam
South | Zapata | Other | Montgomery
South | Zavala | Other | Morris
West | Andrews | Other | Nacogdoches
West | Archer | Other | Navarro
West | Baylor | Other | Newton
West | Borden | Other | Orange
West | Brewster | Other | Panola
West | Callahan | Other | Polk
West | Clay | Other | Rains
West | Coke | Other | Red River
West | Coleman | Other | Robertson
West | Concho | Other | Rockwall
West | Cottle | Other | Rusk
West | Crane | Other | Sabine
West | Crockett | Other | San Augustine
West | Culberson | Other | San Jacinto
West | Dawson | Other | Shelby
West | Ector | Other | Smith
West | El Paso | Other | Titus
West | Fisher | Other | Trinity
West | Foard | Other | Tyler
West | Gaines | Other | Upshur
West | Garza | Other | Van Zandt
West | Glasscock | Other | Walker
West | Hardeman | Other | Waller
West | Haskell | Other | Washington
West | Howard | Other | Wharton
West | Hudspeth | Other | Wood
West | Irion | Other | Aransas
West | Jeff Davis | Other | Atascosa
West | Jones | Other | Bee
West | Kent | Other | Bexar
West | King | Other | Brooks
West | Knox | Other | Calhoun
West | Loving | Other | Cameron
West | Lynn | Other | DeWitt
West | Martin | Other | Dimmit
West | Menard | Other | Duval
West | Midland | Other | Frio
West | Mitchell | Other | Goliad
West | Nolan | Other | Gonzales
West | Pecos | Other | Guadalupe
West | Presidio | Other | Hidalgo
West | Reagan | Other | Jim Hogg
West | Reeves | Other | Jim Wells
West | Runnels | Other | Karnes
West | Schleicher | Other | Kenedy
West | Scurry | Other | Kinney
West | Shackelford | Other | Kleberg
West | Sterling | Other | La Salle
West | Stonewall | Other | Live Oak
West | Sutton | Other | Maverick
West | Taylor | Other | McMullen
West | Terrell | Other | Medina
West | Terry | Other | Nueces
West | Throckmorton | Other | Refugio
West | Tom Green | Other | San Patricio
West | Upton | Other | Starr
West | Val Verde | Other | Uvalde
West | Ward | Other | Victoria
West | Wichita | Other | Webb
West | Wilbarger | Other | Willacy
West | Winkler | Other | Wilson
West | Yoakum | Other | Zapata
West | Young | Other | Zavala

## Background
CDR Report Background
The main purpose of the CDR is to provide forecasted Planning Reserve Margins by season and year. The Planning Reserve Margin represents the percentage of resource capacity, in excess of firm electricity demand, available to cover uncertainty in future demand, generator availability and new resource supply. Firm demand accounts for load reductions available through interruptible load programs controlled by ERCOT as well as incremental load reductions from rooftop solar systems. The methodologies used to develop Planning Reserve Margins and other elements of the CDR are outlined in the ERCOT Nodal Protocols, Section 3.2.6 (See https://www.ercot.com/mktrules/nprotocols/current). ERCOT's load forecasts are based on normal weather conditions and determined by the methodologies described in the methodology documents posted to the Load Forecast webpage, https://www.ercot.com/gridinfo/load/forecast. The CDR also conforms to requirements for resource adequacy reporting specified by the Public Utility Commission of Texas in their Substantive Rules, §25.505(b).
Resource data comes from generation capacity developers (Interconnecting Entities, IEs) and owners as reported in ERCOT's Resource Integration and Ongoing Operations (RIOO) system, as well as other data collection mechanisms described in the ERCOT Nodal Protocols.
Note that the CDR is not intended for characterizing the risk of capacity scarcity conditions from a real-time operations perspective.
Report Changes Introduced by Nodal Protocol Revision Requests 1219 and 945
Peak Net Load Information: Planning Reserve Margin (PRMs) and associated loads and resource information are added for the forecasted peak Net Load hour by year and season.
Shift to Effective Load Carrying Capabilities (ELCCs): Instead of using peak average capacity contributions for wind and solar resources, the CDR is now utilizing ELCCs to represent their availabilities. ELCCs are also estimated for battery energy storage systems.
Expanded Reporting Timeframe: The report will now include PRMs, associated loads, and resources for all four seasons (summer, winter, spring, and fall). Previously, only summer and winter seasons were included. The December 2024 CDR covers the Summer and Winter seasons, whereas full seasonal reporting will be implemented for the May 2025 CDR.
Introduction of New Solar Regions: Three new solar regions (West, Far West, and Other) are introduced to enable more accurate solar capacity availability forecasts. Previously, a single system capacity availability forecast was used.
Updated Criteria for Planned Resources: The criteria for including planned resources in the CDR has been expanded to include ERCOT notification that a project developer has provided the required financial security for interconnection facility construction and that the TDSP has received a notice to proceed with interconnection construction. See ERCOT Planning Guide Section 6.9(1)(d)(ii)(B).
Inclusion of Publicly Announced Planned Retirements: A new category for planned retirements has been added to account for Generation Resources associated with publicly announced retirement plans, but their Resource owners haven't yet submitted a formal Notification of Suspension of Operations (NSO) to ERCOT.
Inclusion of Distribution Voltage Reduction (DVR): Distribution voltage reduction is now included as a load-reducing adjustment for Firm Peak Load calculation.
Inclusion of Energy Storage Resources (ESRs): Existing and planned ESRs are factored into the PRM calculations as available capacity. Battery ESRs are also categorized based on their maximum (or design) duration capabilities.
Revised Emergency Response Service (ERS) Methodology: The methodology for estimating forecasted ERS capacity has been modified to match the most recent ERS procurement amounts and allow ERCOT to make adjustments based on anticipated ERS program changes. This approach avoids unrealistic forecasted year-to-year volatility caused by averaging three-year historical ERS amounts.
Elevated Probability-of-Return Threshold for Mothballed Generation Resources: The threshold for including mothballed Generation Resources in the PRM calculations has been raised from 50% to 75%.
Identification of Individual Private Use Network (PUN) generators: Implementation of NPRR945 is expected by the end of 2024. This Protocol change requires ERCOT to post a monthly report identifying all generators that are part of a PUN, their nameplate capacities, and the date upon which they can be included in the report. This reporting requirement allows PUN generators that contribute to CDR Reserve Margins to be listed in the Unit Details tab along with their capacities. However, ERCOT will continue reporting the PUN capacity contribution as an aggregate value in a separate line item.