## Slide 1: DWG Report to ROS
Fahad Qureshi – DWG Chair
March 6th, 2025

## Slide 2: DWG Update
DWG WebEx meeting held on 2/13/2025
PGRR122 (Reliability Performance Criteria for Loss of Load)
  TSPs have concerns with the 1000MW limit and absence of ride-through requirements.
  ERCOT acknowledged that ride-through requirements are necessary and is currently in discussion with developers to create a proposal, with the requirements to be presented in a separate PGRR.
  ERCOT is in the process of running a study which may revise the 1000MW limit. Plan is to have study complete by April and move forward with PGRR122 targeting May TAC Meeting.
  TSP feedback: the ride-through requirements should come prior to moving forward with PGRR122. ERCOT should consider moving forward partially with PGRR122 (limiting the 1000MW load loss to consequential and non-consequential) until the ride-through requirements are in place.

## Slide 3: DWG Update, continued
PGRR120 (SSO Prevention for Generator Interconnection)
  AEP would like to provide generator option to mitigate the condition resulting in SSO through generator funded transmission upgrades
  Lonestar proposed modifying the PGRR 120 language to offer solutions: include valid exceptions for generators which mitigate risk and allowing TSP to propose short-term/long-term transmission-based solutions to eliminate series compensation
  TSPs and ERCOT to continue discussion and provide comments
Methodology for Adding DER to Flat Start Cases
  Discussion on the possibility of updating DER_A modeling parameters based on an updated IEEE standard. However, it was determined during the meeting that the updated IEEE standard is currently under discussion and not ready for enforcement
  Suggestion to revaluate modeling of SODGs in the cases as currently many are offline and dispatched at 0MW

## Slide 4: DWG Update, continued
Extraordinary Dispatch (EXDS) Generation in Flat Start Cases
  Proposal to add language to the DWG Procedure Manual regarding dispatch of EXDS generation: continue removal of EXDS units from the flatstart cases when possible and replace with units meeting Planning Guide 6.9 requirements.
  DWG agreed with the proposal and will discuss further at next DWG meeting.
  Proposal to add Main Power Transformer modeling for all generators (including EXDS) to the SSWG cases.
Post-Flat Start update
  Flat Start finalized Jan 31st
  ERCOT is requesting UVLS/UFLS/Load Models be submitted by March 14 and plans to have the updated Contingency Tool and Stability Book posted by end of March
  ERCOT presented their modeling process for distributed generation
  Discussion on ERCOT to plans to begin PSSE 36 transition as PSSE 35 has reached End Of Life (no bug fixes or patches)

## Slide 5: DWG Update, continued
IBR model accuracy improvement opportunity
  AEP proposed potential future adoption of a smaller timestep 1ms (1/16th of a cycle) for running dynamic simulations
  Benefits: Improved accuracy, capture faster response
  Concerns: Longer simulation run time, necessity and usefulness for FIS studies
  Continue discussions with OEMs and re-evaluate at future DWG meetings
PGRR121 and NOGRR272 (AGS Requirements for Inverter-Based ESRs)
  ERCOT presented proposed Procedure Manual language updates related to PGRR121 and NOGRR272
  Updated list of applicable tests for AGS-ESR
  Added model test setup and description outlining the test, plot, and performance requirements for AGS-ESR

## Slide 6: DWG Update, continued
Continued Large Load Modeling and Stability Study Discussion
  ERCOT proposed to adopt joint TSP proposal with modifications:
    Consider the cumulative large load MWs in the study area
    DWG to make a list of acceptable screening techniques and criteria
    Suggestion to outline the study requirement in a whitepaper
  ERCOT proposed creation of a large load data survey template which would be incorporated into the DWG Procedure Manual or new whitepaper
  Survey will be in the form of an Excel file which ERCOT is asking for a small SME group to develop
  Following approval TSP will require load customers complete the template and include it in study reports

## Slide 7: Questions or Feedback?