## Reference Index
To complete the UFLS Survey Spreadsheet please reference the index and legend: |  | Instructions Legend
- Entity Requested Data Input.
- Formula Calculation for Internal Assessment (Do Not Input Data.)
"Entity Data Submission Summary" tab index:
Column A | Load Area Identifier (Ex. Transmission Operator Name)
Column B | Total Area Load (MW): Total amount of load at time of test.
Column C | Load Dropped (MW): Amount of load dropped while utilizing Supplemental Anti-Stall UFLS Stage (59.5 Hz grater than or equal to 90 seconds.
Column D | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column C.
Column E | Load Dropped (MW): Amount of load dropped while utilizing Supplemental Anti-Stall UFLS Stage (59.5 Hz grater than or equal to 120 seconds.
Column F | % Load Dropped: Automatically calculated by total load area in Column B and sum of MW shed in Column E.
Column G | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column C and E.
Column H | Load Dropped (MW): Amount of load dropped while utilizing Supplemental Anti-Stall UFLS Stage (59.5 Hz grater than or equal to 150 seconds.
Column I | % Load Dropped: Automatically calculated by total load area in Column B and sum of MW shed in Column H.
Column J | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column C, E, and H.
Column K | Yes/No: Is the load presented in Columns C, E, and H for Supplemental Anti-Stall utlized to meet standard UFLS Stages?
Column L | Load Dropped (MW) considered part of standard UFLS stages: If "Yes" is chosen in Column K, then the UFLS data will be added in the calculation for standard UFLS Stages.
Column M | Load Dropped (MW): Amount of Load dropped utilizing traditional UFLS stage 59.3 Hz
Column N | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column M.
Column O | Load Dropped (MW): Amount of Load dropped utilizing traditional UFLS stage 59.1 Hz
Column P | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column O.
Column Q | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column M and O.
Column R | Load Dropped (MW): Amount of Load dropped utilizing traditional UFLS stage 58.9 Hz
Column S | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column R.
Column T | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column M, O, and R.
Column U | Load Dropped (MW): Amount of Load dropped utilizing traditional UFLS stage 58.7 Hz
Column V | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column U.
Column W | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column M, O, R, and U.
Column X | Load Dropped (MW): Amount of Load dropped utilizing traditional UFLS stage 58.5 Hz
Column Y | % Load Dropped: Automatically calculated by total load area in Column B and MW shed in Column X.
Column Z | Cumulative Total: Automatically calculated by total load area in Column B and sum of MW shed in Column M, O, R, U, and X.
Column AA | Cumulative Total w/ Anti-Stalls: Calculation of Supplemental Anti-Stall UFLS stages if Column K is marked "Yes"
Column AB | Comments: Addittional comments for ERCOT review from the TO.
"Entity Data Relay Information" tab index:
Column A | Location/Load Area: The entity's naming convention for separate load areas within their respective control area. If all are the same, utilize TO Name.
Column B | Power System Simulatior for Engineering Bus Name (If Available)
Column C | Circuit Designation of the UFLS scheme.
Column D | Load: Automatically calculated by total load shed in Columns E - L.
Column E-G | Load in MW the amount dropped at each circuit capable of Supplemental Anti-Stall.
Column H-L | Load in MW the amount dropped at each circuit capable of standard UFLS stages.

## Entity Data Submission Summary
Registered Entity: |  |  | *Relay data (i.e. bus information, location, and relay ID numbers) is necessary for this Survey. Please enter information on the "RELAY Information" tab.
Date/Time of Survey: | 5/8/2025, 11:00 AM
Size and location of customer load, or percentage of connected load to be interrupted.* |  | Supplemental/Anti-Stall Stages | [7 empty] | Load for Supplemental anti-stall is considered to be otherwise utlized to meet standard UFLS Stages |  | Standard UFLS Stages | [14 empty] | • Any other schemes that are part of or impact the UFLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, and Special Protection Systems. • Please indicate any other ERCOT-registered Transmission/Distribution Service Providers (TDSPs) whose load is represented by your company in this survey.
|  | 59.5 Hz ≥ 90 Seconds |  | 59.5 Hz ≥ 120 Seconds |  |  | 59.5 Hz ≥ 150 Seconds |  |  |  |  | 59.3 Hz |  | 59.1 Hz |  |  | 58.9 Hz |  |  | 58.7 Hz |  |  | 58.5 Hz
|  | At least 1.5% of TO Load |  | Total of at least 3% of TO Load |  |  | Total of at least 4.5% of TO Load |  |  |  |  | At least 5% of TO Load |  | Total of at least 5% of TO Load |  |  | Total of at least 15% of TO Load |  |  | Total of at least 15% of TO Load |  |  | Total of at least 25% of TO Load
Total Load Area Entity Name (Relays on next tab) | Total Area Load (MW) | Load Dropped (MW) | % Load Dropped | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Yes/No | Load Dropped (MW) considered part of standard UFLS stages | Load Dropped (MW) | % Load Dropped | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Cumulative Total w/ Anti-Stalls | Comments
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
[10 empty] | No | 0
Total TO Load Submitted | 0 | 0 | 0% | 0 | 0% | 0% | 0 | 0% | 0% |  | 0 | 0 | 0% | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0% | 0% | 0 | 0% | 0% | 0%

## Entity Data Relay Information
Registered Entity: |  |  |  | Supplemental/Anti-Stall |  |  | UFLS
Date/Time of Survey: | 5/8/2025, 11:00 AM |  |  | Time Threshold | Time Threshold | Time Threshold | Block 1 | Block 2 | Block 3 | Block 4 | Block 5
|  |  |  | 59.5 Hz ≥ 90 Seconds | 59.5 Hz ≥ 120 Seconds | 59.5 Hz ≥ 150 Seconds | 59.3 Hz | 59.1 Hz | 58.9 Hz | 58.7 Hz | 58.5 Hz
Location/Load Area | PSSE Bus No | Circuit Designation | Load (MW) | Load Dropped for Time Threshold 1 (MW) | Load Dropped for Time Threshold 2 (MW) | Load Dropped for Time Threshold 3 (MW) | Load Dropped for Block 1 (MW) | Load Dropped for Block 2 (MW) | Load Dropped for Block 3 (MW) | Load Dropped for Block 4 (MW) | Load Dropped for Block 5 (MW)

## Example Summary REFERENCE ONLY
Registered Entity: | ABC Energy Transfer Corp |  | *Relay data (i.e. bus information, location, and relay ID numbers) is necessary for this Survey. Please enter information on the "RELAY Information" tab.
Date/Time of Survey: | 5/8/2025, 11:00 AM
Size and location of customer load, or percentage of connected load to be interrupted.* |  | Supplemental Anti-Stall Stages | [7 empty] | Load for Supplemental anti-stall is considered to be otherwise utlized to meet standard UFLS Stages |  | Standard UFLS Stages | [14 empty] | • Any other schemes that are part of or impact the UFLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, and Special Protection Systems. • Please indicate any other ERCOT-registered Transmission/Distribution Service Providers (TDSPs) whose load is represented by your company in this survey.
|  | 59.5 Hz ≥ 90 Seconds |  | 59.5 Hz ≥ 120 Seconds |  |  | 59.5 Hz ≥ 150 Seconds |  |  |  |  | 59.3 Hz |  | 59.1 Hz |  |  | 58.9 Hz |  |  | 58.7 Hz |  |  | 58.5 Hz
|  | At least 1.5% of TO Load |  | Total of at least 3% of TO Load |  |  | Total of at least 4.5% of TO Load |  |  |  |  | At least 5% of TO Load |  | Total of at least 5% of TO Load |  |  | Total of at least 15% of TO Load |  |  | Total of at least 15% of TO Load |  |  | Total of at least 25% of TO Load
Total Load Area Entity Name (Relays on next tab) | Total Area Load (MW) | Load Dropped (MW) | % Load Dropped | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Yes/No | Load Dropped (MW) considered part of standard UFLS stages | Load Dropped (MW) | % Load Dropped | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Load Dropped (MW) | % Load Dropped | Cumulative Total | Cumulative Total w/ Anti-Stalls | Comments
ABC Energy Transfer Corp. | 1000 | 20 | 2% | 10 | 1% | 3% | 20 | 2% | 5% | Yes | 50 | 50 | 5% | 0 | 0% | 5% | 100 | 10% | 15% | 0 | 0% | 15% | 50 | 5% | 20% | 25%
0
0
Total TO Load Submitted | 1000 | 20 | 2% | 10 | 1% | 3% | 20 | 2% | 5% |  | 50 | 50 | 5% | 0 | 0% | 5% | 100 | 10% | 15% | 0 | 0% | 15% | 50 | 5% | 20% | 25%

## Relay Information Ex. REFERENCE
Registered Entity: | ABC Energy Transfer Corp. |  |  | Supplemental/Anti-Stall |  |  | UFLS
Date/Time of Survey: | 5/8/2025, 11:00 AM |  |  | Time Threshold | Time Threshold | Time Threshold | Block 1 | Block 2 | Block 3 | Block 4 | Block 5
|  |  |  | 59.5 Hz ≥ 90 Seconds | 59.5 Hz ≥ 120 Seconds | 59.5 Hz ≥ 150 Seconds | 59.3 Hz | 59.1 Hz | 58.9 Hz | 58.7 Hz | 58.5 Hz
Location/Load Area | PSSE Bus No | Circuit Designation | Load (MW) | Load Dropped for Time Threshold 1 (MW) | Load Dropped for Time Threshold 2 (MW) | Load Dropped for Time Threshold 3 (MW) | Load Dropped for Block 1 (MW) | Load Dropped for Block 2 (MW) | Load Dropped for Block 3 (MW) | Load Dropped for Block 4 (MW) | Load Dropped for Block 5 (MW)
ABRRD-EDP | 1001 | BKRF1 | 3.2731 |  |  |  | 3.2731
ABRRD-EDP | 1002 | BKRF0 | 2.98 |  |  |  | 2.98
ADISN-EDP | 1003 | BKR1655 | 3.39 | [5 empty] | 3.39
ADISN-EDP | 1004 | BKR1598 | 2.0501 | [5 empty] | 2.0501
ADISN-EDP | 1005 | BKR1700 | 3.848 | [7 empty] | 3.848
ADISN-EDP | 1006 | BKR1800 | 3.2601 | [5 empty] | 3.2601
ADISN-EDP | 1007 | BKR0048 | 0.48 | [5 empty] | 0.48
ADISN-EDP | 1008 | BKR0238 | 3.3901 | [5 empty] | 3.3901
BLTLN-EDP | 1009 | CB0908 | 2.1 | 2.1
BLTON-EDP | 1010 | CB0263 | 2.3 | 2.3
BLTON-EDP | 1011 | CB5858 | 2.1 |  | 2.1
BLTON-EDP | 1012 | CB0982 | 2.6 |  | 2.6
BLTON-EDP | 1013 | CB1111 | 3.5 |  |  | 3.5
BLTON-EDP | 1014 | CB1023 | 3.9 |  |  | 3.9