## Slide 1
Potential Price Corrections for Operating Days August 12 – September 11, 2024 – Usage of Incorrect MW Values in the Calculation of Constraint Math Limits
Matthew Young
Supervisor, Market Validation
Technical Advisory Committee (TAC)
March 26, 2025

## Slide 2: Background
When a Resource telemeters its data quality as suspect, the Energy Management System (EMS) will use the Resource’s last good telemetered MW value.
In the Market Management System (MMS), a Resource’s telemetered MW value is used in the calculation of a constraint’s Mathematical Limit.
In November of 2023, a new version of EMS was released which contained a software defect. The defect removed EMS’s ability to update a Resource’s last good telemetered MW value. This resulted in a Resource’s last good telemetered MW value never getting updated and being kept to whatever its value was right before the software release.
This could have a large impact if the following situation occurs.
    One or more Resources are telemetering suspect data quality
    Their current MW output is vastly different than the stale MW value captured before the software defect was introduced.
    They have a large shift factor associated with a binding or violated constraint.

## Slide 3: Price Correction Event
On September 5, 2024 at approximately 8:35 AM, multiple Resources represented by a single Qualified Scheduling Entity (QSE) telemetered suspect quality measurement on their MW telemetry, resulting in the EMS sending stale MW values to the MMS.
When Security-Constrained Economic Dispatch (SCED) ran at 08:35:10, the stale MW values impacted the optimization and resulted in System Lambda spiking from $20.99/MWh to $199.17/MWh. System Lambda returned to $27.88/MWh following the 08:40:09 SCED run after the telemetered values were no longer flagged as suspect.
The unusual spike in System Lambda – occurring at a time of day when a price spike would otherwise be unexpected - prompted an investigation to determine the cause. This then led to the discovery of the software defect noted on the previous slide. A fix for the defect was implemented on September 11, 2024, at 11:40 AM to address the issue.
Market Notice M-A091124-01 was issued on September 11, 2024, notifying the market of the issue and ERCOT’s intent, upon completion of impact analysis, to seek ERCOT Board of Directors (Board) approval for price correction as specified by ERCOT Protocol Section 6.3(7)(b) for the Real-Time Market (RTM) and to preserve the eligibility of the ERCOT Board to review prices for the affected Operating Days that were within 30 days of the notice.
  While the software defect first appeared in November 2023, only Operating Days between August 12, 2024 and September 11, 2024 are considered eligible for Board review, assuming the necessary criteria for significance are met.

## Slide 4: Real-Time Market Impact Analysis
ERCOT Protocols Section 6.3(7)(b) requires that the absolute value impact to any single Counter-Party meet at least one of the following two criteria before seeking approval from the Board:
  2% and also greater than $20,000; or
  20% and also greater than $2,000.
ERCOT determined that 27 Operating Days met criteria for significance.
Operating Day | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(i) | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(ii)
8/12/2024 | 3 | 14
8/13/2024 | 3 | 7
8/14/2024 | 0 | 7
8/15/2024 | 0 | 1
8/16/2024 | 1 | 8
8/17/2024 | 2 | 2
8/19/2024 | 32 | 43
8/20/2024 | 5 | 5
8/21/2024 | 13 | 24
8/22/2024 | 1 | 4
8/23/2024 | 22 | 37
8/24/2024 | 4 | 3
8/25/2024 | 0 | 5
8/27/2024 | 1 | 4
Operating Day | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(i) | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(ii)
8/29/2024 | 1 | 3
8/30/2024 | 11 | 24
8/31/2024 | 3 | 2
9/1/2024 | 11 | 14
9/3/2024 | 0 | 1
9/4/2024 | 0 | 1
9/5/2024 | 21 | 33
9/6/2024 | 16 | 34
9/7/2024 | 16 | 19
9/8/2024 | 16 | 27
9/9/2024 | 6 | 11
9/10/2024 | 6 | 17
9/11/2024 | 3 | 6

## Slide 5: Real-Time Market Impact Analysis
The tables below show the maximum estimated absolute value impact to Counter-Parties.
Operating Day | Maximum Amount ($Thousands) | Maximum Percentage for Criteria (i)* | Maximum Percentage for Criteria (ii)**
8/12/2024 | 22.87 | 6431.64% | 6431.64%
8/13/2024 | 51.69 | 118.12% | 226.67%
8/14/2024 | 17.29 | N/A | 2438.99%
8/15/2024 | 4.39 | N/A | 26.96%
8/16/2024 | 31.39 | 448.45% | 448.45%
8/17/2024 | 24.74 | 5.33% | 33.16%
8/19/2024 | 240.46 | 3581.92% | 3581.92%
8/20/2024 | 94.26 | 21.67% | 51.25%
8/21/2024 | 119.36 | 28.24% | 4620.96%
8/22/2024 | 29.40 | 5.74% | 60.18%
8/23/2024 | 188.21 | 99.21% | 896.34%
8/24/2024 | 56.02 | 58.64% | 88.58%
8/25/2024 | 8.36 | N/A | 48.26%
8/27/2024 | 53.62 | 26.44% | 295.85%
* The maximum of percentage change to any single Counter-Party with impact more than $20,000.
** The maximum of percentage change to any single Counter-Party with impact more than $2,000.
Operating Day | Maximum Amount ($Thousands) | Maximum Percentage for Criteria (i)* | Maximum Percentage for Criteria (ii)**
8/29/2024 | 22.16 | 11.69% | 38.95%
8/30/2024 | 115.58 | 33.59% | 245.99%
8/31/2024 | 25.64 | 249.37% | 249.37%
9/1/2024 | 69.00 | 117.30% | 203.19%
9/3/2024 | 2.87 | N/A | 31.02%
9/4/2024 | 9.95 | N/A | 23.43%
9/5/2024 | 128.10 | 423.86% | 444.51%
9/6/2024 | 125.14 | 44.18% | 391.75%
9/7/2024 | 95.50 | 904.99% | 904.99%
9/8/2024 | 125.37 | 844.21% | 952.62%
9/9/2024 | 103.92 | 552.31% | 552.31%
9/10/2024 | 107.26 | 58.43% | 7044.49%
9/11/2024 | 92.91 | 172.93% | 172.93%

## Slide 6: Real-Time Market Impact Analysis
The table below has the maximum estimated change in charges due to ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges. The percent amount is the absolute value of the percent impact to the previously settlement net amount due to/from ERCOT.
Operating Day | Change in Statement Charges Due to ERCOT ($ thousands) | 
8/12/2024 | (156,677) | 1.054%
8/13/2024 | (231,226) | 1.385%
8/14/2024 | (92,998) | 0.517%
8/15/2024 | (225,231) | 1.078%
8/16/2024 | (245,310) | 1.318%
8/17/2024 | 62,912 | 0.384%
8/19/2024 | 163,412 | 0.324%
8/20/2024 | (654,610) | 0.455%
8/21/2024 | (458,868) | 1.268%
8/22/2024 | (134,290) | 0.553%
8/23/2024 | (642,600) | 2.888%
8/24/2024 | 111,500 | 0.823%
8/25/2024 | 67,152 | 0.486%
8/27/2024 | 72,661 | 0.432%
Operating Day | Change in Statement Charges Due to ERCOT ($ thousands) | 
8/29/2024 | (47,015) | 0.317%
8/30/2024 | (386,927) | 2.503%
8/31/2024 | (10,772) | 0.057%
9/1/2024 | 84,768 | 0.618%
9/3/2024 | (25,285) | 0.225%
9/4/2024 | (4,887) | 0.036%
9/5/2024 | (841,422) | 5.788%
9/6/2024 | (507,244) | 4.207%
9/7/2024 | 53,607 | 0.484%
9/8/2024 | 378,514 | 3.826%
9/9/2024 | (42,770) | 0.335%
9/10/2024 | 141,376 | 1.179%
9/11/2024 | 91,183 | 0.719%

## Slide 7: Price Correction Process and Methodology Enhancement
Due to the significant number of days involved in the price correction, we were only recently able to conclude our analysis with definitive findings.
Throughout the course of the analysis, it was discovered that the existing methodology for calculating the impact to Counter-Parties would have resulted unwarranted payments to certain Resources.
  These Resources were those whose basepoints did not change between the actual SCED optimization and the re-calculated optimization using the appropriate telemetry MW.
  Since their basepoints did not change, it is understood that their dispatched quantities were indifferent to the price and they were effectively price-takers.
Upon discovery of these unwarranted payments, we undertook the analysis again, considering settlement changes only for those for whom it was appropriate to be held whole under the price correction principles.
  This resulted in a reduction in the number of impacted Operating Days, Counter-Parties, and changes in statement charges due to ERCOT.
Going forward, ERCOT will continue to use this enhanced methodology to ensure that load will not make unwarranted payments in future price correction events.