- Power Operations Bulletin # 1163

ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	System Overview

Procedure Purpose: Review, monitor and analyze data to maintain system security.

| Protocol Reference | 6.3.2(3)(a)(i) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-7 R5 | NUC-001-4 R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.2.2, R9.4, R9.4.1, R9.4.2 | TOP-001-6 R10, R10.1, R10.2, R10.4, R10.5, R10.6 | VAR-001-5 R2 |

| Version: 1 | Revision: 13 | Effective Date: December 1, 2024 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Review | REVIEW each of the following as necessary to confirm system reliability status: - Alarms - State Estimator (SE) - Real Time Contingency Analysis (RTCA) - Transmission Constraint Manager (TCM) - Approved and Forced Outages - Load Forecast - Voltage and Stability Limits - Real Time Monitoring (RTMONI) - Security Constrained Economic Dispatch (SCED) - Real Time Reserve Monitoring |
| Gap Study | Run a gap study for the next day’s peak hour to ensure all contingencies can be solved. If necessary: - Request the Operations Support Engineer to review results and create CMPs as needed - Coordinate with TOs - If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units - Refer to Desktop Guide Transmission Desk Section 2.5 Conducting Future Security Analysis - Save study - Log the following: - Study name - Any issues that could not be resolved and actions taken. |
| STP Lines | A minimum of two transmission lines should be always in service. The in-service lines should be from at least two of the groups in the table below: Independent Groups of STP Transmission Lines Group 1; Group 2; Group 3. ANGSTR_STP1; STPELM18; JCKSTP18. STPELM27; REFSTP27. STPWAP39. Note: Transmission lines, STP – Blessing (BLESSING), STP – HILLJE (HLJSTP64), and STP – HILLJE (CKT_3124) (EMS naming convention) are not included in this table because these circuits are not part of STP’s credited offsite sources. IF: - A minimum of two lines are not in service; THEN: - Notify the Nuclear Plant’s QSE. - Explain the event, and an estimate of when expected to return to normal |
| Dynamic Transmission Limits | IF: - Any changes in the system that could affect the security and dynamic transmission limits; THEN: - Post message on the ERCOT Website. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch, Hartmann & Weldon | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Solis and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch, Hartmann, Lopez, and Solis | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy, Frosch and Solis | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 30, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 28, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | August 28, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | January 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 1, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | May 25, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | September 27, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 1, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | April 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 26, 2023 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | March 27, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | August 29, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | September 28, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | October 26, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | November 2, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | November 28, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | December 20, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | January 30, 2024 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | February 27, 2024 |
| Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | March 26, 2024 |
| Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | April 29, 2024 |
| Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | May 28, 2024 |
| Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | June 25, 2024 |
| Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | July 29, 2024 |
| Frosch, Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | August 28, 2024 |
| Hartmann, Luker, and Smith | Procedure writers and editors | September 26, 2024 |
| Frosch, Hartmann, Cyphers, Luker, and Smith | Procedure writers and editors | October 28, 2024 |
| Hartmann, Luker, and Smith | Procedure writers and editors | November 22, 2024 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 - / 1 - / 1 - / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and “Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 - / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | - / 8 - / 4 - / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 - / 6 - / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 - / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 - / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 - / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 - / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 - / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | - / 6 - / 16 - / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9, QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |
| 2.3 2.4 3.1 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 9 1.0 / 3 1.0 / 5 1.0 / 11 1.0 / 1 1.0 / 21 1.0 / 7 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 7 1.0 / 15 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts and steps in Caution, Phase Shifters, Constraint Shift Factor Cut Off, Post Contingency Overloads, deleted Input Displays, added step In Series & Same Element in Managing Constraints in SCED & deleted Managing Congestion during SCED Failure Updated step 2 Deleted 2nd Note, added GTL and updated scripts Deleted 2nd Note, added GTL and updated scripts Deleted Directives, 1st Note in Mitigation Plan, 1st Note in Temporary Outage Action Plan and updated scripts Updated scripts Updated all steps and deleted Cancelation Updated script Updated script Added Generic script and Specific scripts Updated scripts Updated scripts Updated scripts Updated script Updated scripts Updated script Updated script Correct spelling and updated script | June 1, 2013 |
| 2.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 7.1 7.2 7.4 7.5 | 1.0 / 10 1.0 / 22 1.0 / 9 1.0 / 8 1.0 / 13 1.0 / 15 1.0 / 13 1.0 / 9 1.0 / 5 1.0 / 13 1.0 / 14 1.0 / 8 1.0 / 5 | Updated step EMS Changes and added MMS Changes Updated step Caution Updated and moved section 7.4 and renamed to 4.2 Changed section # Updated and changed section # Changed section #, IROL & updated step 0MW Changed section # & updated step 4 in RAPs Changed section # Changed section # Updated step 1 in Watch, Emergency Notice & DRUC Timeline not Met Updated 2nd Note Changed section # & step 2 Changed section # | July 15, 2013 |
| 2.3 4.1 4.2 4.5 6.1 7.1 | 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 16 1.0 / 16 - / 14 | Spelling correction to step MMS Changes Updated Caution, Constraint Shift Factor Cut Off, step 8 of Post-Contingency Overloads & PUN procedure Removed the word “load” Updated step VSAT Updated 2nd note & step 1 on Voltage Security Assessment Tool (VSAT) Updated Specific Scripts EMMS (LFC and RLC/SCED) Failure | August 9, 2013 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.8 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 | - / 12 - / 4 - / 12 - / 2 - / 24 1.0 / 11 1.0 / 14 1.0 / 17 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 15 1.0 / 13 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 7 1.0 / 7 | Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference | August 30, 2013 |
| 4.1 5.1 6.1 | 1.0 / 25 1.0 / 8 1.0 / 17 | Updated step 5 in Post-Contingency Overloads Updated to reflect SCR770 changes Updated script and added new script for Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | September 27, 2013 |
| 3.3 3.4 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 5.2 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 9.2 10.1 | 1.0 / 13 1.0 / 3 1.0/ 3 1.0 / 26 1.0 / 12 1.0 / 15 1.0 / 18 1.0 / 15 1.0 / 10 1.0 / 7 1.0 / 0 1.0 / 9 1.0 / 1 1.0 / 18 1.0 / 16 1.0 / 16 1.0 / 14 1.0 / 7 1.0 / 8 1.0 / 8 - / 8 1.0 / 8 1.0 / 4 1.0 / 4 | Updated Log steps Updated Log steps Updated Log step Updated step 1 on Review Planned Outage Notes, step 1 for PUNs, Managing Constraints in SCED and Logs Updated Title, added step 2 and Log steps Deleted step GTL, updated step 1, and Log Updated step VSAT, Log and deleted GTL Updated Log steps Updated Log steps Updated Log steps Added new procedure Updated steps Definition, Approve Maintenance Outage, Coordinate Maintenance, Coordinate Maintenance Level 2 and 3, Log and step 1 in Simple Transmission Outage Updated Log steps Updated VSAT section Updated Log steps Updated Log steps Added step Reserves and Log steps Updated Log steps Updated note, OCN, Advisory and Log step Added note, updated OCN, Advisory, Watch and Log step Added note, updated OCN, Advisory, Watch and Log step Updated note and Log step Updated Log steps Updated Log steps All procedures in this manual have been reviewed | December 13, 2013 |
| 4.2 4.4 4.5 4.6 4.7 4.8 4.9 4.10 7.1 | 1.0 / 13 1.0 / 16 1.0 / 19 1.0 / 0 1.0 / 16 1.0 / 11 1.0 / 8 1.0 / 1 1.0 / 17 | Updated 1st Note, step 3, added step 4 & deleted step 5 in Transmission Issues within ERCOT. Added Note to Transmission/Capacity Issues within the CFE Area Removed posting requirement Removed posting requirement New procedure for new GTL Updated section number Updated section number Updated section number Updated section number & changed Watch to OCN Updated to incorporate NPRR542 and update scripts | January 1, 2014 |
| 4.1 4.2 4.6 7.3 8.4 | 1.0 / 27 1.0 / 14 1.0 / 1 1.0 / 15 1.0 / 9 | Updated step 3 in Post-Contingency Overloads Updated step 3, 4 in Transmission Issues within ERCOT and step 1, 2 & 3 in Transmission/Capacity Issues within the CFE Area Updated step 1 & 2 Updated steps Reserves and 1 in Restore Firm Load Updated 1st Note | February 25, 2014 |
| 4.1 4.2 4.4 4.5 4.8 6.1 7.2 7.4 9.1 | 1.0 / 28 1.0 / 15 1.0 / 17 1.0 / 20 1.0 / 12 1.0 / 19 1.0 / 17 1.0 / 9 1.0 / 5 | Updated VDI information Updated steps in Transmission Issues within ERCOT Updated VDI information Updated VDI information Updated Manual commitment process Updated VDI information Updated media appeal language & LM Program Updated VDI information Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 4.1 4.2 4.4 4.6 4.7 4.9 6.1 7.1 8.1 | 1.0 / 2 1.0 / 29 1.0 / 16 1.0 / 18 1.0 / 2 1.0 / 17 1.0 / 9 1.0 / 20 1.0 / 18 1.0 / 9 | Added VDI to Master QSEs Updated step 1 in Review Planned Outage Notes, QSGR & Log in Post-Contingency Overloads & PUN steps Updated section title & step 5, deleted step 3 Updated step 2 Updated step 1 & 2 Updated step 1 in RAP Deleted Note Updated Note & Step 1 in Voltage Issues Added Note, updated Market Notices Advisory & Watch Updated scripts | June 1, 2014 |
| 4.1 4.2 4.7 7.2 | 1.0 / 30 1.0 / 17 1.0 / 18 1.0 / 18 | Changed WGR to IRR & updated desktop reference Updated step 4 & 6 Updated 1st Note Added Media Appeal & updated step 1 script | August 1, 2014 |
| 4.1 5.1 6.1 7.1 | 1.0 / 31 1.0 / 10 1.0 / 21 1.0 / 19 | Updated desktop reference number & step 3 in Post-Contingency Overloads, added step 4 to PUN section Updated desktop reference number Updated step 1, 2 & 3 in Real-Time Voltage Issues, added Future Voltage Issues Updated Generic Script | October 1, 2014 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 6.1 7.1 7.2 10.1 | 1.0 / 13 1.0 / 5 1.0 / 14 1.0 / 4 1.0 / 32 1.0 / 18 1.0 / 21 1.0 / 3 1.0 / 19 1.0 / 13 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 22 1.0 / 20 1.0 / 19 1.0 / 5 | Removed references to W-N Updated scripts Removed references to W-N/TSAT, combined SE/RTCA Updated for Operating Guide 4.7 Updated Phase Shifters & removed references to TSAT Removed references to TSAT & added Future Studies Deleted West to North procedure and re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Updated step 1 Updated step 2 & 3 in Real-Time Voltage Issues, Future Voltage Issues & Requesting Resource to operate beyond URL Updated Specific Scripts Updated EEA2 script Deleted Requests to decommit in Operating Period All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 4.1 4.2 4.3 4.4 4.7 4.8 6.1 7.4 8.2 | 1.0 / 3 1.0 / 33 1.0 / 19 1.0 / 9 1.0 / 22 1.0 / 14 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 9 | Added definitions for Dispatch and VDIs Updated “Review Planned Outage Notes” and provided a better flow, deleted redundant steps & added Basecase Overloads, Added step Topology Change Updated to reflect SOL Methodology and provide a better flow Updated step <200MW Updated step 1 Updated script Updated step Exceeding URL or Reducing Output Updated all steps for better flow Updated scripts | March 1, 2015 |
| 3.5 4.2 4.5 4.9 9.1 | 1.0 / 5 1.0 / 20 1.0 / 4 1.0 / 3 1.0 / 6 | Updated GMD process Updated step 2 of Rio Grande Valley Renamed to GTC Stability and added Ajo – Zorrillo Updated to new name Generic Transmission Constraint Updated scripts | March 30, 2015 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.2 7.3 7.4 7.5 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 6 1.0 / 34 1.0 / 21 1.0 / 10 1.0 / 23 1.0 / 5 1.0 / 20 1.0 / 12 - / 4 - / 21 - / 0 - / 20 - / 16 1.0 / 11 1.0 / 8 - / 10 - / 10 - / 9 - / 10 1.0 / 7 | Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Moved scripts to script procedure Updated step 1 QSE Requests to Decommit a Resource, updated GTL to GTC, and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Renamed and updated Zorrillo – Ajo table Moved scripts to script procedure Updated for implementation of NOGRR135/NPRR642 and moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Updated 50% Probability Of Down Ramp to 30%, removed 70% Probability Of Up Ramp, added note and moved scripts to script procedure New process for implementation of NOGRR135/NPRR642 Updated section number and moved scripts to script procedure Updated section number and moved scripts to script procedure Updated section number Updated section number and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure | May 1, 2015 |
| All Sections 2.3 3.1 3.5 4.4 | 1.0 / 1 1.0 / 15 1.0 / 6 1.0 / 7 1.0 / 24 | Added a “T” for TO scripts Renamed section to Site Failovers and Database Loads Updated Gap Study Updated Procedure Purpose. Updated GMD MIS Posting Scripts to include “until time” Updated procedure purpose and step ≤500MW | July 15, 2015 |
| 4.1 4.5 | 1.0 / 35 1.0 / 6 | Updated step 1 Post-Contingency Overloads Replaced East Texas Stability with Panhandle Stability Added Laredo Import Stability Removed Zorillo – Ajo Table | September 9, 2015 |
| 4.5 7.2 | 1.0 / 7 1.0 / 1 | Removed Panhandle Stability Step 1, updated Step 2, and Laredo Area Stability Updated Double-Circuit Contingency actions | October 1, 2015 |
| 2.3 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.3 7.4 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 16 - / 16 - / 8 - / 36 - / 22 - / 11 - / 25 - / 8 - / 21 - / 13 1.0 / 5 1.0 / 22 - / 21 - / 17 1.0 / 9 1.0 / 11 - / 11 - / 10 1.0 / 11 1.0 / 8 | Updated step Site Failover T#17 Updated step Site Failover Complete T#18 Updated State Estimator/RTCA step 3 T#21 & step 7 T#22 Updated Voltage Security Assessment Tool (VSAT) step 2 T#23 & step 6 T#24 Updated step 1 T#25 Updated step K Level Increases/Decreases T#26 Updated step Cancel T#27 Updated Review Planned Outage notes step Cascading Condition Updated Basecase Overloads step Qualifying Facilities T#28 Updated Rio Grande Valley step 2 Added Rio Grande Valley step Reliability Margin <100 MW Updated Rio Grande Valley step 3 T#29 Updated step Cascading Condition Updated Pre-Contingency Load Shedding to avoid Post-Contingency cascading step 3 T#30 Updated step ≤300 T#31 Updated step ≤100 T#32 Updated step 0MW T#33 Updated Laredo Area Stability step 4 T#29 Updated Zorrillo – Ajo 345kV Stability step 1 & step 2 Added Liston Stability Added Molina Stability Updated Special Protective Systems (SPS) step SPS Posting Updated Mitigation Plan (MP) step Issue Watch T#34 Updated Mitigation Plan (MP) step Cancel Watch T#35 Updated Advisory step Cancel Advisory T#2 Updated Watch step Issue Watch T#3 Updated Watch step Cancel Watch T#4 Updated step GTC T#36 Updated Title Operating Condition Scripts Updated Operating Condition Scripts step Hotline T#37 Updated Operating Condition Scripts step Hotline Cancellation T#38 Updated Title Specific Scripts for QSE’s Updated Specific Scripts for QSE’s step 30% Probability Of Down Ramp T#39 & T#40 Updated Specific Scripts for QSE’s step Failure T#41 & T#42 Updated Specific Scripts for QSE’s step EMMS (LFC and RLC/SCED) Failure T#43 & T#44 Updated Specific Scripts for QSE’s step Increasing Amount of Ancillary Services T#45 & T#46 Updated Specific Scripts for QSE’s step A/S Insufficiency Offers in DAM T#47 & T#48 Updated Specific Scripts for QSE’s step REG/RRS – RUC Committed Shortages T#51 & T#52 Updated Specific Scripts for QSE’s step DAM Timeline Deviation T#53 & T#54 Updated Specific Scripts for QSE’s step DAM Failure T#55 & T#56 Updated Specific Scripts for QSE’s step DRUC Delay or Timeline Deviation T#57 & T#58 Updated Specific Scripts for QSE’s step DRUC Timeline not Met T#59 & T#60 Updated Specific Scripts for QSE’s step HRUC Failure or Timeline Deviation T#61 & T#62 Updated Specific Scripts for QSE’s step DRUC Committed for Capacity Shortage T#63 & T#64 Updated Specific Scripts for QSE’s step Excess Generation T#65 & T#66 Updated Specific Scripts for QSE’s step Projected Reserve Capacity Shortage with no market solution T#67 & T#68 Updated Specific Scripts for QSE’s step RMR Projected Reserve Capacity Shortage T#69 & T#70 Update first note, Updated Implement EEA Level 1 step Load Management title T#6 Updated Implement EEA Level 2 step 1 T#7 Updated Implement EEA Level 3 step 1 T#8, and Implement NPRR708 for EEA Updated Restore Firm Load step 1 T#9 & T#10 Updated Move from EEA Level 1 to EEA 0 step 1 T#13 Updated step Return to Normal TO Notification T#71 Updated step OCN #72 Updated step Advisory T#73 Updated step Watch T#74 Updated step Emergency T#75 Updated step OCN T#76 Updated step Advisory T#77 Updated step Watch T#78 Updated step Emergency Notice T#79 Updated step OCN T#80 Updated step Advisory T#81 Updated step Watch T#82 Updated step Emergency Notice T#83 Updated step OCN/Advisory/Watch T#84 Updated step 2 T#85 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 4.1 4.3 4.5 4.6 5.1 6.1 7.1 9.1 | 1.0 / 3 1.0 / 37 1.0 / 12 1.0 / 9 1.0 / 22 1.0 / 12 1.0 / 24 - / 23 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated NERC Standard Reference Updated Molina Stability Updated NERC Standard Reference Updated NERC Standard Reference Updated NERC standard Reference Updated Voltage Security Assessment Tool step 1 table Updated PSS & AVR step Note Added Specific Scripts for QSE’s T#86 Updated Specific Scripts for QSE’s T#51 Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 6.1 7.1 | 1.0 / 2 1.0 / 25 1.0 / 24 | Removed Interchange Coordinator Updated STP Voltage Table Updated Execute a SASM script title T#86 |  |
| 3.1 4.1 4.2 4.4 4.5 6.1 | 1.0 / 11 1.0 / 38 1.0 / 23 1.0 / 26 1.0 / 10 1.0 / 26 | Updated step STP Lines Updated Review Planned Outages Cascading Condition Updated Reliability Margin Updated ≤300MW Updated Zorrillo – Ajo 345kV Stability step 1 Updated step STP Voltage Table, 1 and 2 | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.1 7.4 7.5 | 1.0 / 4 1.0 / 4 1.0 / 39 1.0 / 24 1.0 / 13 1.0 / 27 1.0 / 11 1.0 / 23 1.0 / 27 1.0 / 25 1.0 / 18 1.0 / 12 | Updated for COM-002-4 Updated steps for COM-002-4 Updated steps for NPRR748, NOSCED and COM-002-4 Updated Reliability Margin Updated steps for COM-002-4 Updated steps for COM-002-4 Updated step for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 & added Typical Script T#87 BAAL Firm Load Shed Updated Restore Firm Load step 1 Updated steps for COM-002-4 | June 30, 2016 |
| 4.2 4.5 6.1 7.1 | 1.0 / 25 1.0 / 12 - / 28 - / 26 | Updated RUC/Future Studies & Deleted Note Added Zorillo-Ajo 345 kV Stability note Replaced step 1 with note Updated Liston Stability Step 1 & Step 2 Removed Molina Stability Added Red Tap Stability Updated Real-Time Voltage Issues note Updated ERCOT requesting Resource to operate beyond URL Exceeding URL or Reducing Output Updated Voltage Security Assessment Tool step 1 Updated Specific Scripts for QSE’s T#43 T#44, T#61 & T#62 | September 30, 2016 |
| 4.1 4.5 | - / 40 - / 13 | Updated Review Planned Outage Notes step Cascading Condition Added Basecase / Post-Contingency Exceedance of Phase Angle Added Panhandle Stability step Weighted Short Circuit Ratio and updated step 1 Added Pomelo Stability | November 2, 2016 |
| 3.3 3.6 4.1 4.5 4.6 6.1 10.1 | 1.0 / 17 1.0 / 0 1.0 / 41 1.0 / 14 1.0 / 24 1.0 / 29 1.0 / 6 | Updated Notes and State Estimator/RTCA section Created a new procedure for resolving Real-time Data Issues per NOGRR162 Updated 2nd Note, step 3 Post-Contingency Overloads Updated Laredo Area Stability step 1 Updated Special Protection Systems (SPS) to Remedial Action Schemes (RAS) Updated per STP agreement Deleted Telemetry Issue that could affect SCED and/or LMPs All procedures in this manual have been reviewed | December 30, 2016 |
| 1.1 1.3 2.1 2.3 2.4 3.1 3.2 3.3 3.5 3.6 4.1 4.2 4.3 4.5 4.6 4.7 5.2 6.1 7.1 7.3 7.5 7.6 8.2 8.3 10.1 | 1.0 / 3 1.0 / 5 1.0 / 17 1.0 / 7 1.0 / 8 1.0 / 4 1.0 / 18 - / 9 1.0 / 1 1.0 / 42 - / 26 1.0 / 14 1.0 / 15 - / 25 1.0 / 15 1.0 / 2 1.0 / 30 - / 27 - / 22 1.0 / 13 1.0 / 10 1.0 / 12 1.0 / 11 1.0 / 7 | Updated Introduction Purpose Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated procedure purpose Updated GAP Study Updated categories to show RAS Updated Notes Updated Voltage Security Assessment Tool step 2 Updated procedure purpose Changed step Situational Awareness to Mitigating Activities Added step IROL Deleted step Unknown State Updated step ONTEST Updated Reliability Margin Updated CFE to CENACE Updated step Note Updated Zorillo - AJO Stability step 1 Removed Liston Stability Updated Red Tap Stability step 1 Updated Pomelo Stability step 1 Added Bakersfield Stability Updated title with AMP Updated Remedial Action Schemes (RAS) steps Added Automatic Mitigation Plan (AMP) Updated Remedial Action Plan (RAP) step 1 & 5 Updated Pre-Contingency Action Plan (PCAP) step 1 & 2 Updated Mitigation Plan (MP) steps fully resolve constraint, <2% Absolute Shift Factors and Contingency Occurs Updated Note & Manual Dispatch to take a Unit Off-Line Updated Planned Outage Updated title to Voltage Issues at Nuclear Power Plants Added Real-Time Voltage Issues step 3 Updated ERCOT requesting Resource to operate beyond URL steps Updated heading title, OCN step 1, Advisory step 1, Watch step 1, and Emergency Notice step 1 Implement EEA Level 3 Moved step 1 to step 2 & added step 1 Updated CFE to CENACE Updated note Updated Procedure Purpose Updated Procedure Purpose Updated Heading title to QSE Issues | March 31, 2017 |
| 3.3 3.6 4.1 4.2 4.4 | 1.0 / 19 1.0 / 2 1.0 / 43 1.0 / 27 1.0 / 28 | Added Section on ICCP Outages Updated IROL Added Section Post-Contingency Overloads on the South DC Ties Updated Model Inconsistencies/Updates step 2 Updated step Reliability Margin, step 1 and added Cancel Updated step Reliability Margin | April 6, 2017 |
| 3.6 4.1 4.4 4.5 5.2 | 1.0 / 3 1.0 / 44 1.0 / 29 1.0 / 16 1.0 / 3 | Updated step IROL Updated Post-Contingency Overloads on the South DC Ties step 1 Updated step ≤400MW Removed Bakersfield Stability Updated steps | June 1, 2017 |
| 7.1 7.3 | 1.0 / 28 1.0 / 23 | Updated step BAAL Firm Load Shed Updated Implement EEA Level 3 step 2 | June 30, 2017 |
| 3.3 3.7 4.1 7.3 | 1.0 / 20 - / 0 - / 45 1.0 / 24 | Updated Procedure Purpose Deleted notes and updated State Estimator/RTCA step 1 Added new section Real-time Assessment (RTA) Added new procedure Manual Real-time Assessment (RTA) Added new section Monitoring Sub Synchronous Resonance (SSR) Added Note to EEA Level 2 and EEA Level 3 | July 28, 2017 |
| 4.5 5.1 7.3 | 1.0 / 17 1.0 / 13 1.0 / 25 | Deleted Laredo Area Stability Renamed Pomelo to North Edinburg – Lobo & updated Added Rescheduled High Impact Outage (RO) Updated 1st note | August 31, 2017 |
| 6.1 | 1.0 / 31 | Added East HVDC Tie Voltage Limits | September 29, 2017 |
| 4.5 6.1 | - / 18 - / 32 | Renamed Zorillo - Ajo 345kV Stability to Nelson Sharpe – Rio Hondo 345kV Stability Added new GTC East Texas Stability Updated Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) note | October 31, 2017 |
| 4.1 9.2 | - / 46 1.0 / 5 | All procedures in this manual have been reviewed Added Operating Instruction and EDI scenario Unsolved Contingencies Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 6.1 | - / 21 - / 33 | Updated Procedure Purpose, added ICCP Outages to include MIS and outage scheduler Updated Future Voltage Issues and updated Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) step 1 | February 28, 2018 |
| 3.6 4.5 | 1.0 / 4 1.0 / 19 | Updated Real-Time Data Issues known by the TO and Real-Time Data Issues that affect Network Security Analysis steps Added new GTC McCamey Stability | March 30, 2018 |
| 2.2 4.2 4.5 7.1 | 1.0 / 5 1.0 / 28 1.0 / 20 1.0 / 29 | Updated procedure purpose Updated Rio Grande Valley step Reliability Margin Added new GTC Treadwell Stability Added Unannounced Constant Frequency Control Test | May 1, 2018 |
| 4.1 4.2 4.4 4.5 6.1 7.5 | 1.0 / 47 1.0 / 29 1.0 / 30 1.0 / 21 1.0 / 34 1.0 / 14 | Added Phase Shifter Updated Rio Grande Valley step 2 Updated North – Houston step ≤400MW Updated Treadwell Stability Added Generator Voltage Set Points Updated steps and added Emergency Dispatch Instruction Confirmation Emergency | May 31, 2018 |
| 3.1 4.1 4.2 4.3 4.4 7.4 | 1.0 / 9 1.0 / 48 1.0 / 30 1.0 / 15 1.0 / 31 1.0 / 19 | Updated step STP Lines Updated note Updates step 1 for Rio Grande Valley Updated 1st note and Studies step Updated step ≤300MW Clarified step in Move from EEA Level 1 to EEA 0 | August 31, 2018 |
| 4.1 4.2 | 1.0 / 49 1.0 / 31 | Updated Post-Contingency Overloads on the South DC Ties step 1 for NPRR 825 Updated Unsolved Contingencies step 1 Updated SSR Alerts to SSR Alarms Updated Rio Grande Valley step 1 for NPRR 825 | October 1, 2018 |
| 7.5 | 1.0 / 15 | BLT RC Notification | November 1, 2018 |
| 4.6 6.1 | 1.0 / 26 1.0 / 35 | ## Added step 6 to Remedial Action Plan (RAP) Added step and renumbered steps to Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 4.9 | 1.0 / 32 1.0 / 6 | ## Updated step 1 ## Updated GTC | January 31, 2019 |
| 3.5 4.1 4.5 4.9 | 1.0 / 10 1.0 / 50 1.0 / 22 1.0 / 7 | ## Updated step Mitigating Activities ## Updated step Qualifying Resources Added Raymondville – Rio Hondo Stability Updated step GTC and added note | March 29, 2019 |
| 4.1 | 1.0 / 51 | ## Added Note | May 01, 2019 |
| 7.3 | 1.0 / 26 | ## Moved Load Management Program from EEA1 to EEA2 | May 31, 2019 |
| 4.3 7.3 | 1.0 / 16 1.0 / 27 | ## Updated step Cascading Condition Updated Implement EEA Level 3 step 2 | August 1, 2019 |
| 3.3 4.1 4.5 4.6 7.1 7.3 9.1 | 1.0 / 22 1.0 / 52 - / 23 1.0 / 27 1.0 / 30 1.0 / 28 1.0 / 10 | ## Updated State Estimator/RTCA step 1 Updated Title to Monitoring Sub Synchronous Resonance (SSR) and process, Added Monitoring Sub Synchronous Resonance (SSR) without Capacitor Switching action and Added Unresolvable Congestion with EMR Generation available ## Updated Panhandle Stability steps and updated Raymondville – Rio Hondo Stability step 1 Updated step RAS Status Change Updated Specific Scripts for QSE’s steps Added Typical Hotline Script for Media Appeal Added step 3 and renumbered steps | November 1, 2019 |
| 3.1 4.1 4.5 7.3 7.4 | 1.0 / 10 1.0 / 53 1.0 / 24 1.0 / 29 1.0 / 20 | Updated STP lines Updated step 3 in Managing Constraints in SCED Deleted GTC Notes and added Bearkat Stability Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 4.1 4.2 4.4 4.7 5.1 6.1 7.4 9.2 | 1.0 / 54 1.0 / 33 1.0 / 32 1.0 / 16 1.0 / 14 1.0 / 36 1.0 / 21 1.0 / 6 | Clarified RUC commits/decommits and updated step Caution Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 4.1 9.2 | 1.0 / 55 1.0 / 7 | Updated Model Inconsistencies/Updates step 2 Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 4.5 5.1 7.1 | 1.0 / 6 1.0 / 25 1.0 / 15 1.0 / 31 | Added Advance Action Notice per NPRR930 Added W_TO_C Stability & PIGSOL Stability Added Advance Action Notice section per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 4.1 4.3 | 1.0 / 56 1.0 / 17 | Added Post Contingency Overload of Relay Loadability Rating Added step 4 to Basecase overloads Added Basecase Overload of Relay Loadability Rating Added Relay Loadability Rating | September 1, 2020 |
| 2.1 4.1 4.2 4.3 4.4 4.5 7.5 | 1.0 / 7 1.0 / 57 - / 34 1.0 / 18 1.0 / 33 1.0 / 26 1.0 / 16 | Updated second paragraph Updated Basecase overloads and Basecase overloads of Relay Loadability Rating Updated Title and moved Rio Grande Valley to 4.4 Updated steps Added and updated steps for new SOL Methodology Updated Title, Purpose and added new IROL’s Deleted GTC’s that became IROL’s in 4.4 Updated steps Electronic Dispatch Instruction Confirmation Non-Emergency | October 1, 2020 |
| 4.1 4.3 4.5 | 1.0 / 58 - / 19 1.0 / 27 | Updated Post-Contingency Overloads of Relay Loadability Rating step 4, Basecase Overloads step 4 & Managing Constraints in SCED step 3 Updated step Monitoring, West Texas Export IROL step 6, Panhandle Export IROL step 6 & McCamey Export IROL step 6 Added Valley Export Stability & Zapata_Starr Stability | October 31, 2020 |
| 2.4 3.1 3.3 3.5 4.1 4.3 4.4 4.6 4.9 5.1 7.1 8.1 8.2 8.3 8.4 10.1 | 1.0 / 8 1.0 / 11 1.0 / 23 1.0 / 11 1.0 / 59 1.0 / 20 1.0 / 34 1.0 / 28 1.0 / 8 1.0 / 16 1.0 / 32 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 12 1.0 / 8 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.1 4.4 4.5 6.1 | 1.0 / 12 1.0 / 35 1.0 / 28 1.0 / 37 | Updated STP lines Removed McCamey Export IROL Added McCamey Stability Updated for NOGRR195 | February 4, 2021 |
| 4.5 | - / 29 | Updated Bearkat Stability step 1 Deleted PIGSOL Stability and added CULBSN Stability | March 1, 2021 |
| 4.1 4.5 | 1.0 / 60 1.0 / 30 | Organization change Updated Culberson Stability and added Williamson Burnet Stability | April 1, 2021 |
| 5.1 7.1 | 1.0 / 17 1.0 / 33 | Added information on AAN information Changed Notice Builder to Grid Conditions Communications (GCC) Notices | May 6, 2021 |
| 4.4 | 1.0 / 36 | Updated Panhandle Export IROL 3rd Note | May 28, 2021 |
| 4.5 | - / 31 | Deleted Valley Export Stability Note Added Culberson & McCamey Stability Note | July 31, 2021 |
| 7.3 | 1.0 / 30 | Updated 1st Note | September 1, 2021 |
| 4.1 4.4 4.5 | 1.0 / 61 1.0 / 37 1.0 / 32 | Updated CAUTION Added McCamey Export IROL Removed McCamey Stability | October 7, 2021 |
| 4.4 4.8 7.3 | 1.0 / 38 1.0 / 14 1.0 / 31 | Added Note to Westex & Panhandle IROL to reference Wiki page Updated Steps for distribution voltage reduction during an Advisory Updated for NPRR1105 | December 1, 2021 |
| 4.5 4.8 7.3 7.4 | 1.0 / 33 1.0 / 15 1.0 / 32 1.0 / 22 | Updated Eastex GTC updated Updated Load Management Programs Updated Load Management Program Updated Move from EEA Level 2 to EEA Level 1 | December 17, 2021 |
| 2.2 3.7 4.1 4.4 4.6 4.8 5.1 6.1 7.1 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 6 1.0 / 1 1.0 / 62 1.0 / 39 1.0 / 29 1.0 / 16 1.0 / 18 1.0 / 38 1.0 / 34 1.0 / 33 1.0 / 23 1.0 / 13 1.0 / 14 1.0 / 13 1.0 / 13 1.0 / 11 | Updated step 1 Updated Notes Updated instruct to coordinate Updated instruct to coordinate Updated instruct to coordinate Updated step issue advisory Updated step 1 Updated instruct to coordinate Updated all steps Updated all steps implement EEA2 Updated Move from EEA Level 2 to EEA Level 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated step 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 4.3 4.8 7.3 8.4 | 1.0 / 21 1.0 / 17 1.0 / 34 1.0 / 14 | Updated Cascading Condition Updated Issue Advisory Updated Implement EEA Level 2 step 1 Updated Implement EEA Level 3 step 2 Updated Note | February 1, 2022 |
| 2.5 4.5 | 1.0 / 0 1.0 / 34 | New procedure section Updated Eastex GTC to reflect VSAT steps | March 1, 2022 |
| 4.5 | 1.0 / 35 | Added Wharton Stability GTC | May 5, 2022 |
| 7.1 | 1.0 / 35 | Updated for NOGRR191 | May 26, 2022 |
| 4.5 4.8 | 1.0 / 36 1.0 / 18 | Added Hamilton Stability GTC Update steps for Advisory | July 29, 2022 |
| 3.6 7.3 | 1.0 / 5 1.0 / 35 | Updated Notes and step 1 & 2 Added ESR note | October 7, 2022 |
| 4.8 7.3 | - / 19 1.0 / 36 | Added Media Appeal, TCEQ and Large Load Curtailment Program steps Added TCEQ step and clarify Implement EEA Level 3 Step 2 All procedures in this manual have been reviewed | December 30, 2022 |
| 7.3 | 1.0 / 37 | Notify TO’s during EEA2/3 on which load shed table (winter/summer) to view/use during a load shed event | February 1, 2023 |
| 4.1 8.4 | 1.0 / 63 1.0 / 15 | Updated Cascading Condition Updated procedure title | March 31, 2023 |
| 4.4 | 1.0 / 40 | Updated for NPRR863 | June 9, 2023 |
| 3.4 4.1 | 1.0 / 4 1.0 / 64 | Updated 3rd Note and Immediate Action Added 2nd Note for ECRS release Added ECRS to 3rd Note | September 1, 2023 |
| 4.6 | 1.0 / 30 | Updated GCC posting | October 4, 2023 |
| 4.1 4.3 4.5 4.8 7.3 7.4 | 1.0 / 65 1.0 / 22 1.0 / 37 1.0 / 20 1.0 / 39 1.0 / 24 | Updated Scripts due to ECEII Updated Scripts due to ECEII Updated Scripts due to ECEII Updated for NPRR1176 Updated for NPRR1176 Updated for NPRR1176 | November 1, 2023 |
| 4.5 | 1.0 / 38 | Added Kinney GTC | November 7, 2023 |
| 4.5 5.1 | 1.0 / 39 1.0 / 19 | Retired Bearkat GTC Added OSA Script T#88 | December 1, 2023 |
| 7.2 8.4 | 1.0 / 2 1.0 / 16 | Updated System Conditions Updated First Note All procedures in this manual have been reviewed | December 29, 2023 |
| 4.5 | 1.0 / 40 | Updated the Eastex GTC step #1 | February 2, 2024 |
| 4.4 | 1.0 / 41 | Added South Texas Export IROL; Added South Texas Import IROL | March 1, 2024 |
| 3.6 3.8 4.1 4.3 4.4 4.5 4.6 6.1 | 1.0 / 6 1.0 / 0 1.0 / 66 1.0 / 23 1.0 / 42 1.0 / 41 1.0 / 31 1.0 / 39 | Updated step IROLs New SOL Exceedance Communication procedure Added step SOL Comms Added step SOL Comms, updated step Cascading Conditions, and step 4 Added step IROL Comms Added step SOL Comms Added step SOL Comms Added ESR to Voltage Control, Added SOL Comms | March 29, 2024 |
| 4.4 7.4 | 1.0 / 43 1.0 / 25 | Added DTCN reminder, adjusted Transmission Emergency bullets for South Tx IROL Updated PRC Level | May 1, 2024 |
| 4.1 4.5 7.5 | 1.0 / 67 1.0 / 42 1.0 / 17 | Updated Caution note and rearranged order; Updated Red Tap GTC note; Added UVALDE GTC Updated ALMC to PRES BLT Note | May 31,2024 |
| 4.4 4.5 | 1.0 / 44 1.0 / 43 | Updated note in IROL; added NTE steps Updated note in GTC; added NTE steps | June 28, 2024 |
| 4.5 6.1 7.1 8.4 11 11.1 11.2 | 1.0 / 44 1.0 / 40 1.0 / 36 1.0 / 17 1.0 / 0 1.0 / 0 1.0 / 0 | Updated note in GTC; added NTE steps Added Voltage Studies Updated Emergency Notice reasons Updated step OCN/Advisory/Watch Added Primary Control Center Functionality Added Loss of Primary Control Center Functionality Added Restoration of PCC | August 1, 2024 |
| 4.4 | 1.0 / 45 | Minor updates | August 30, 2024 |
| 4.5 | 1.0 / 45 | Retired Red Tap GTC | October 1, 2024 |
| 3.3 4.1 4.3 4.5 7.3 7.6 11.2 | 1.0 / 24 1.0 / 68 1.0 / 24 1.0 / 46 1.0 / 40 1.0 / 11 1.0 / 1 | Added TSAT to the Analysis Tool Outage; Added TSAT to Transmission Congestion; Added TSAT to Closely Monitored SOL control; Added TSAT to EASTEX and RV_RH under GTC Stability Limits; Updated Step 1 of EEA 3 to include frequency timing Removed 7.6 Added Information from 7.6 to 11.2 | November 1, 2024 |
| 3.1 | 1.0 / 13 | Updated STP lines | December 1, 2024 |